## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-08-11 | Saturday
|  | Date (day): | 2018-08-11 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11300 | MW |  |  | (b) At Evening Peak Hour : |  | 12300 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-08-10 | 2018-08-11 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 72 | 74 | 74 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 84 | 84 | 84 | 85 | 23 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 372 | 350 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 40 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 241 | 292 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 400 | 400 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 90 | 90 | 90 |  | 10 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 200 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 64 | 64 | 64 |  | 36 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 63 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 35 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 212 | 213 | 217 | 217
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 20 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 33 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 50 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 132 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 8 | 8 | 8 |  | 100 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 57 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 23 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 51 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint. |  | 14/08/2018
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 82 | 210 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 311 |  |  | On test
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 75 | 146 | 150 | 150
| Dhaka area Total |  |  |  |  | 5784 | 5548 | 2538 | 3626 | 4386 | 4752 | 628 | 465
38 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 16 | 16 | 16 |  | 9 | Engine problem
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 37 | 32 | 40 |  | 10
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 159 | 163 | 190 | 200
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 228 | 225 | 225
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 135 | 135 | 135
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 8 | 50 | 50 | 50
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 76 | 40 | 80
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 47 | 50 | 50
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 100 | 100 | 100
49 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 31 | 38 | 10 | 15
50 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 19 | 99 | 100 | 100
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 658 | 1008 | 967 | 1030 | 360 | 59
51 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 120 | 120 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Under maint.
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100 | 34 |  | Gas shortage
52 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 219 | 225 | 225 |  |  | FGMO
53 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 0 | 0 |  | 360 | Under maint.
54 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 368 | 338 | 360 | 360
55 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 43 | 43 | 43
56 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
57 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 5 | 48 |  | Gas shortage
58 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 73 | 73 | 73 | 122 |  | Gas shortage
59 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 45 | 38 | 45 | 45 |  | 6 | Engine problem
60 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
61 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
62 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 57 | ST under maint.
63 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
64 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 116 | 170 | 121 | 172
65 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 34 | 33 | 33 | 33
66 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
67 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 22 | 22
68 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1520 | 1624 | 1517 | 1718 | 368 | 478
69 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 48 | 48 | 50 | 50 | 152 |  | Gas shortage
70 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
71 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 90 | 90 | 90
72 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.7 | 0 | 2 | 0
73 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 100 | 133 | 156 | 160
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 180.7 | 293 | 320 | 322 | 152 | 0
74 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 64 | 64 | 64 | 64
75 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 62 | 62 | 62 | 62
76 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
77 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 298 | 321 | 330 | 330
78 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
79 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
80 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
81 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 30 | 30 |  |  | GT-9 under maint.
82 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
83 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 47 | 47 | 47
84 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 130 | 128 | 130 | 130
85 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 19 | 19
86 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 46 | 48 | 48
87 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 23 | 23 | 23
88 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 310 | 341 | 341 |  |  | FGMO
89 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 7 | 7
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1227 | 1257 | 1299 | 1299 | 0 | 163
90 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 48 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 494 | 494 | 497 | 497
91 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 98 | 60 | 98 |  | 12 | Engine problem
92 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
93 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 48 | 45 | 48
94 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 100 | 225
95 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 68 | 80 | 80
96 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 410 | 410 | 410
97 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
98 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Date Experied
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 95 | 100 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 938 | 1416 | 1447 | 1661 | 0 | 12
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 80 | 80 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 32 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 190 | 189 | 190 | 194
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 292 | 398 | 428 | 462 | 0 | 0
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 0 | 32
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 35 | 43 | 43 | 43 |  | 7 | Engine problem
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 44 | 44
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 199 | 214 | 210 | 215
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 131 | 191 | 210 | 210
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 151 | 149 | 154 | 154 |  |  | On test
113 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 39 | 40 | 40
114 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18
115 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
116 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 11 | 11 | 11
117 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
118 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 25 | 90 | 60 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 677 | 985 | 902 | 1022 | 71 | 107
119 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
120 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 274 |  | Coal shortage
121 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 16 | 16
122 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 0 | 10 | 34 | 34 | 359 | 85
| Total |  |  |  |  | 16102 | 15559 | 8030.7 | 10617 | 11300 | 12300 | 1938 | 1369
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7648.7179 | 10112 | 10762.513 | 11714.9477
A. |  | 2018-08-10 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10662 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7749.6 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10617 | MW
3 | Day peak Generation : |  |  | 8030.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10112 | MW
4 | Evening peak Generation : |  |  | 10617 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 217.8137 | MKWHr | By Solar | 0.01475 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 135.9127 | MKWHr |  | By Oil: | 62.8888 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 0 | MKWHr |  | By Hydro: | 3.7962 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1938 | MW | Dhaka | 3658 | 3658 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1369 | MW | Chittagong | 1043 | 1043 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3307 | MW | Khulna | 1273 | 1273 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1123.15 | MMCFD |  |  | Rajshahi | 1017 | 1017 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 94445770.158 | ii) Oil : | Taka | 626507383.5 | Comilla | 1012 | 1012 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 0 | Total | Taka | 720953153.658 | Mymensingh | 773 | 773 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 6.605 | MKWHr. | Sylhet | 473 | 473 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -550 | MW at | 21:00 | hrs | Barisal | 272 | 272 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -580 | MW at | 4:00 | hrs | Rangpur | 591 | 591 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.6° C |  |  | Total | 10112 | 10112 |  | 0
B. |  | 2018-08-11 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 34° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12300 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 900 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 232.8903 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8310.7 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.872 | MKWHr. | ii) HVDC Flow at Peak Time |  | 494 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3293 | MKWHr. | iii) Maximum HVDC Flow : |  | 495 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.79 |  | (b) Today: | 104.85 |  | (c) Rule Curve: |  | 92.2
.

## YesterdayGen
2018-08-10
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 120 | 0 | 0 | 365 | 84 | 60 | 402 | 242 | 110 | 0 | 380 | 200 | 94 | 65 | 55 | 220 | 0 | 0 | 100 | 100 | 102 | 149 | 88 | 8 | 10 | 40 | 18 | 55 | 55 | 17 | 25 | 32 | 33 | 33 | 51 | 0 | 75 | 80 | 0 | 0 | 26 | 0 | 201 | 0 | 100 | 0 | 50 | 24 | 47 | 90 | 99 | 44 | 19 | 30 | 80 | 0 | 80 | 265 | 279 | 222 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 49 | 0 | 19 | 11 | 33 | 22 | 158 | 49 | 90 | 22 | 0 | 70 | 62 | 50 | 50 | 0 | 192 | 30 | 86 | 48 | 78 | 19 | 45 | 7 | 290 | 23 | 11 | 0 | 203 | 0 | 0 | 139 | 0 | 113 |  | 491 | 0 | 415 | 95 | 101 | 0 | 0 | 0 | 42 | 25 | 32 | 188 | 34 | 109 | 0 | 0 | 0 | 18 | 31 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 13 | 0 | 220 | 0 | 0 | 184 | 96 | 96 | 154 | 0 |  | 7501 | 2712 | 10213 | 4021 | 491 | 1738 | 2583 | 0 | 155 | 1067 | 158 | 0 | 0 | 104.79
2:00 | 70 | 120 | 0 | 0 | 365 | 84 | 60 | 423 | 273 | 55 | 0 | 390 | 200 | 80 | 65 | 55 | 220 | 0 | 0 | 17 | 100 | 70 | 149 | 70 | 8 | 11 | 40 | 18 | 55 | 55 | 17 | 25 | 32 | 33 | 33 | 51 | 0 | 75 | 80 | 0 | 0 | 25 | 0 | 200 | 0 | 100 | 0 | 50 | 24 | 47 | 90 | 99 | 44 | 19 | 32 | 80 | 0 | 80 | 265 | 279 | 225 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 158 | 49 | 90 | 22 | 0 | 70 | 62 | 50 | 50 | 0 | 280 | 30 | 86 | 48 | 78 | 19 | 46 | 7 | 285 | 23 | 11 | 0 | 198 | 0 | 0 | 139 | 0 | 113 |  | 494 | 0 | 413 | 95 | 105 | 0 | 0 | 0 | 42 | 10 | 32 | 178 | 32 | 98 | 0 | 0 | 0 | 0 | 31 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 13 | 0 | 220 | 0 | 0 | 173 | 95 | 70 | 155 | 0 |  | 7395 | 2624 | 10019 | 4122 | 494 | 1774 | 2343 | 0 | 155 | 973 | 158 | 0 | 0 | 104.79
3:00 | 70 | 120 | 0 | 0 | 365 | 84 | 60 | 425 | 272 | 0 | 0 | 390 | 200 | 50 | 65 | 55 | 220 | 0 | 0 | 0 | 100 | 7 | 98 | 30 | 8 | 10 | 40 | 18 | 55 | 55 | 17 | 25 | 32 | 33 | 33 | 51 | 0 | 75 | 80 | 0 | 0 | 26 | 0 | 200 | 0 | 80 | 0 | 50 | 24 | 47 | 90 | 99 | 44 | 19 | 32 | 80 | 0 | 80 | 260 | 283 | 223 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 146 | 49 | 90 | 22 | 0 | 70 | 62 | 50 | 50 | 0 | 306 | 30 | 86 | 48 | 78 | 19 | 46 | 7 | 290 | 23 | 11 | 0 | 188 | 0 | 0 | 139 | 0 | 113 |  | 494 | 0 | 413 | 51 | 100 | 0 | 0 | 0 | 36 | 6 | 32 | 189 | 31 | 98 | 0 | 0 | 0 | 0 | 31 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 14 | 0 | 220 | 0 | 0 | 178 | 95 | 10 | 155 | 0 |  | 7126 | 2521 | 9647 | 4158 | 494 | 1777 | 2019 | 0 | 155 | 898 | 146 | 0 | 0 | 104.79
4:00 | 70 | 120 | 0 | 0 | 365 | 84 | 60 | 425 | 293 | 0 | 0 | 390 | 200 | 50 | 65 | 55 | 220 | 0 | 0 | 0 | 50 | 7 | 65 | 10 | 8 | 0 | 40 | 18 | 55 | 55 | 17 | 25 | 32 | 33 | 33 | 51 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 80 | 0 | 51 | 0 | 17 | 90 | 68 | 44 | 19 | 33 | 80 | 0 | 80 | 260 | 279 | 222 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 146 | 49 | 90 | 22 | 0 | 70 | 62 | 50 | 50 | 0 | 308 | 30 | 86 | 48 | 78 | 19 | 46 | 7 | 295 | 23 | 11 | 0 | 190 | 0 | 0 | 139 | 0 | 113 |  | 494 | 0 | 413 | 51 | 106 | 0 | 0 | 0 | 36 | 6 | 32 | 190 | 31 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 14 | 0 | 220 | 0 | 0 | 178 | 96 | 0 | 155 | 0 |  | 6938 | 2486 | 9424 | 4156 | 494 | 1805 | 1887 | 0 | 155 | 781 | 146 | 0 | 0 | 104.79
5:00 | 70 | 120 | 0 | 0 | 365 | 84 | 60 | 423 | 293 | 0 | 0 | 400 | 200 | 29 | 65 | 55 | 218 | 0 | 0 | 0 | 23 | 7 | 48 | 10 | 8 | 0 | 40 | 18 | 55 | 55 | 17 | 25 | 32 | 33 | 33 | 51 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 80 | 0 | 51 | 0 | 17 | 90 | 52 | 44 | 19 | 33 | 80 | 0 | 80 | 260 | 301 | 222 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 140 | 49 | 90 | 22 | 0 | 70 | 62 | 50 | 50 | 0 | 311 | 30 | 86 | 48 | 78 | 19 | 46 | 7 | 310 | 23 | 11 | 0 | 190 | 0 | 0 | 141 | 0 | 113 |  | 495 | 0 | 411 | 27 | 90 | 0 | 0 | 0 | 36 | 6 | 32 | 190 | 28 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 14 | 0 | 219 | 0 | 0 | 179 | 96 | 0 | 154 | 0 |  | 6901 | 2441 | 9342 | 4173 | 495 | 1827 | 1785 | 0 | 155 | 767 | 140 | 0 | 0 | 104.79
6:00 | 70 | 120 | 0 | 0 | 365 | 84 | 76 | 420 | 293 | 0 | 0 | 400 | 200 | 10 | 15 | 15 | 220 | 0 | 0 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 35 | 18 | 18 | 36 | 17 | 25 | 32 | 33 | 33 | 16 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 70 | 0 | 32 | 0 | 0 | 70 | 32 | 35 | 19 | 37 | 80 | 0 | 80 | 260 | 279 | 224 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 132 | 49 | 24 | 22 | 0 | 70 | 62 | 50 | 50 | 0 | 308 | 30 | 86 | 48 | 78 | 19 | 45 | 7 | 280 | 23 | 11 | 0 | 146 | 0 | 0 | 124 | 0 | 110 |  | 494 | 0 | 414 | 10 | 49 | 0 | 0 | 0 | 36 | 6 | 32 | 191 | 26 | 96 | 0 | 0 | 0 | 0 | 0 | 25 | 42 | 43 | 44 | 25 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 170 | 50 | 0 | 156 | 0 |  | 6412 | 2204 | 8616 | 4152 | 494 | 1768 | 1273 | 0 | 155 | 642 | 132 | 0 | 0 | 104.79
7:00 | 70 | 120 | 0 | 0 | 350 | 84 | 76 | 358 | 273 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 219 | 0 | 0 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 32 | 18 | 18 | 36 | 17 | 25 | 32 | 33 | 33 | 16 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 70 | 0 | 24 | 0 | 0 | 70 | 19 | 25 | 19 | 23 | 80 | 0 | 80 | 260 | 279 | 223 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 0 | 33 | 22 | 112 | 49 | 24 | 22 | 0.2 | 70 | 62 | 50 | 50 | 0 | 301 | 30 | 84 | 48 | 77 | 19 | 45 | 7 | 275 | 23 | 0 | 0 | 98 | 0 | 0 | 113 | 0 | 95 |  | 494 | 0 | 415 | 10 | 49 | 0 | 0 | 0 | 36 | 9 | 32 | 190 | 25 | 96 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 43 | 27 | 25 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 130 | 21 | 0 | 155 | 0 |  | 6130.2 | 2101 | 8231.2 | 4016 | 494 | 1697 | 1170 | 0 | 155 | 587 | 112 | 0.2 | 0 | 104.79
8:00 | 70 | 120 | 0 | 0 | 350 | 84 | 40 | 345 | 242 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 219 | 0 | 0 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 33 | 0 | 18 | 36 | 17 | 25 | 32 | 33 | 33 | 16 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 70 | 0 | 24 | 0 | 0 | 70 | 19 | 25 | 19 | 26 | 80 | 0 | 80 | 260 | 280 | 222 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 16 | 11 | 34 | 12 | 110 | 49 | 8 | 22 | 0.8 | 70 | 62 | 50 | 50 | 0 | 303 | 30 | 50 | 46 | 77 | 20 | 45 | 7 | 270 | 23 | 0 | 0 | 95 | 0 | 0 | 105 | 0 | 78 |  | 494 | 0 | 360 | 27 | 49 | 0 | 0 | 0 | 36 | 11 | 16 | 190 | 22 | 100 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 43 | 0 | 25 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 131 | 0 | 0 | 155 | 0 |  | 5951.8 | 1994 | 7945.8 | 3941 | 494 | 1568 | 1114 | 0 | 155 | 563 | 110 | 0.8 | 0 | 104.8
9:00 | 70 | 120 | 0 | 0 | 320 | 84 | 40 | 345 | 185 | 0 | 0 | 380 | 200 | 7 | 16 | 15 | 219 | 0 | 0 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 33 | 0 | 18 | 36 | 17 | 25 | 31 | 33 | 33 | 16 | 0 | 77 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 50 | 0 | 24 | 0 | 0 | 70 | 19 | 25 | 19 | 30 | 80 | 0 | 80 | 260 | 280 | 182 | 73 | 100 | 30 | 0 | 5 | 45 | 85 | 0 | 0 | 16 | 11 | 34 | 15 | 108 | 49 | 8 | 22 | 1.6 | 70 | 62 | 50 | 50 | 0 | 299 | 30 | 84 | 46 | 80 | 20 | 45 | 7 | 270 | 23 | 0 | 0 | 87 | 0 | 0 | 100 | 0 | 78 |  | 494 | 0 | 300 | 27 | 49 | 0 | 0 | 0 | 36 | 16 | 16 | 190 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 25 | 40 | 18 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 0 | 131 | 0 | 0 | 154 | 0 |  | 5813.6 | 1936 | 7749.6 | 3808 | 494 | 1528 | 1104 | 0 | 157 | 549 | 108 | 1.6 | 0 | 0
10:00 | 70 | 120 | 0 | 0 | 365 | 84 | 40 | 357 | 240 | 0 | 0 | 380 | 200 | 7 | 15 | 15 | 215 | 0 | 0 | 0 | 7 | 7 | 36 | 10 | 8 | 0 | 33 | 0 | 18 | 36 | 17 | 25 | 31 | 0 | 33 | 16 | 0 | 79 | 80 | 0 | 0 | 8 | 0 | 204 | 0 | 50 | 0 | 24 | 0 | 0 | 70 | 19 | 10 | 19 | 32 | 80 | 0 | 80 | 260 | 295 | 187 | 73 | 100 | 39 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 34 | 15 | 106 | 47 | 8 | 22 | 1.5 | 68 | 62 | 47 | 50 | 0 | 310 | 30 | 84 | 46 | 80 | 19 | 44 | 7 | 250 | 23 | 0 | 0 | 80 | 0 | 0 | 100 | 0 | 78 |  | 494 | 0 | 360 | 27 | 49 | 0 | 0 | 0 | 32 | 11 | 16 | 189 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 8 | 39 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 131 | 0 | 0 | 151 | 0 |  | 5870.5 | 1975 | 7845.5 | 3932 | 494 | 1561 | 1064 | 0 | 159 | 528 | 106 | 1.5 | 0 | 0
11:00 | 70 | 120 | 0 | 0 | 365 | 84 | 60 | 348 | 242 | 0 | 0 | 370 | 200 | 7 | 15 | 15 | 211 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 24 | 0 | 18 | 36 | 17 | 25 | 16 | 0 | 33 | 8 | 0 | 79 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 8 | 0 | 0 | 70 | 21 | 6 | 19 | 32 | 80 | 0 | 80 | 260 | 290 | 190 | 73 | 100 | 40 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 34 | 15 | 110 | 47 | 8 | 22 | 2.1 | 65 | 62 | 50 | 50 | 0 | 313 | 30 | 84 | 46 | 80 | 19 | 43 | 7 | 290 | 22 | 8 | 0 | 80 | 0 | 0 | 100 | 0 | 75 |  | 494 | 0 | 360 | 10 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 188 | 22 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 8 | 40 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 151 | 0 | 0 | 150 | 0 |  | 5846.1 | 1904 | 7750.1 | 3907 | 494 | 1616 | 979 | 0 | 159 | 483 | 110 | 2.1 | 0 | 0
12:00 | 70 | 120 | 0 | 0 | 365 | 84 | 72 | 372 | 241 | 0 | 0 | 370 | 200 | 7 | 15 | 15 | 212 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 33 | 0 | 18 | 36 | 0 | 25 | 22 | 25 | 23 | 8 | 0 | 79 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 135 | 0 | 8 | 0 | 0 | 70 | 19 | 6 | 19 | 31 | 80 | 0 | 80 | 260 | 368 | 186 | 73 | 100 | 43 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 34 | 15 | 116 | 48 | 8 | 22 | 2.7 | 64 | 62 | 50 | 50 | 0 | 298 | 30 | 84 | 46 | 130 | 19 | 44 | 7 | 310 | 22 | 11 | 0 | 82 | 0 | 0 | 100 | 0 | 75 |  | 494 | 0 | 410 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 190 | 22 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 8 | 40 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 131 | 0 | 0 | 151 | 0 |  | 6123.7 | 1907 | 8030.7 | 4115 | 494 | 1647 | 947 | 0 | 159 | 550 | 116 | 2.7 | 0 | 0
13:00 | 70 | 120 | 0 | 0 | 365 | 84 | 72 | 386 | 230 | 0 | 0 | 370 | 305 | 10 | 15 | 20 | 213 | 0 | 0 | 0 | 7 | 14 | 16 | 30 | 8 | 20 | 33 | 0 | 36 | 36 | 0 | 25 | 22 | 25 | 29 | 8 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 205 | 0 | 135 | 0 | 11 | 0 | 0 | 90 | 21 | 6 | 19 | 31 | 100 | 0 | 80 | 260 | 301 | 184 | 73 | 100 | 43 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 34 | 20 | 128 | 48 | 16 | 22 | 1.8 | 59 | 62 | 50 | 50 | 0 | 302 | 30 | 84 | 46 | 130 | 19 | 44 | 7 | 295 | 22 | 11 | 0 | 80 | 0 | 0 | 114 | 0 | 75 |  | 494 | 0 | 410 | 33 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 167 | 22 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 16 | 39 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 139 | 0 | 0 | 151 | 0 |  | 6305.8 | 1924 | 8229.8 | 4062 | 494 | 1621 | 1209 | 0 | 155 | 559 | 128 | 1.8 | 0 | 0
14:00 | 70 | 120 | 0 | 0 | 325 | 84 | 71 | 390 | 270 | 0 | 0 | 360 | 200 | 24 | 37 | 40 | 212 | 0 | 0 | 0 | 20 | 24 | 16 | 38 | 8 | 21 | 33 | 0 | 37 | 55 | 0 | 25 | 16 | 25 | 0 | 16 | 0 | 75 | 80 | 0 | 0 | 8 | 0 | 215 | 0 | 50 | 0 | 24 | 0 | 0 | 90 | 22 | 12 | 19 | 32 | 80 | 0 | 80 | 260 | 340 | 208 | 73 | 100 | 43 | 0 | 5 | 45 | 85 | 0 | 2 | 19 | 11 | 33 | 20 | 132 | 46 | 24 | 22 | 2.1 | 70 | 61 | 50 | 55 | 0 | 300 | 30 | 84 | 46 | 120 | 13 | 43 | 7 | 275 | 22 | 11 | 0 | 80 | 0 | 0 | 130 | 0 | 32 |  | 494 | 0 | 410 | 33 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 188 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 16 | 38 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 187 | 0 | 0 | 145 | 0 |  | 6223.1 | 2072 | 8295.1 | 4027 | 494 | 1635 | 1319 | 0 | 155 | 531 | 132 | 2.1 | 0 | 0
15:00 | 70 | 120 | 0 | 0 | 365 | 84 | 71 | 405 | 271 | 13 | 0 | 370 | 305 | 57 | 64 | 55 | 207 | 0 | 0 | 0 | 30 | 58 | 20 | 60 | 8 | 50 | 37 | 0 | 55 | 55 | 0 | 25 | 15 | 25 | 33 | 32 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 209 | 0 | 134 | 0 | 26 | 0 | 0 | 90 | 90 | 23 | 19 | 32 | 80 | 0 | 80 | 260 | 260 | 202 | 73 | 100 | 23 | 0 | 5 | 45 | 85 | 0 | 8 | 19 | 11 | 33 | 16 | 144 | 46 | 64 | 22 | 0.4 | 66 | 61 | 47 | 50 | 0 | 313 | 30 | 83 | 46 | 128 | 13 | 43 | 7 | 300 | 22 | 11 | 0 | 77 | 0 | 0 | 122 | 0 | 31 |  | 494 | 0 | 410 | 90 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 187 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 40 | 38 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 188 | 0 | 0 | 148 | 0 |  | 6785.4 | 2218 | 9003.4 | 4035 | 494 | 1666 | 1890 | 0 | 160 | 614 | 144 | 0.4 | 0 | 0
16:00 | 70 | 120 | 0 | 0 | 262 | 84 | 40 | 380 | 272 | 13 | 0 | 370 | 200 | 87 | 64 | 55 | 208 | 0 | 0 | 0 | 60 | 58 | 82 | 75 | 8 | 51 | 39 | 0 | 55 | 55 | 19 | 25 | 5 | 33 | 33 | 50 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 31 | 0 | 17 | 90 | 92 | 26 | 19 | 32 | 80 | 0 | 80 | 260 | 290 | 184 | 73 | 100 | 23 | 0 | 5 | 38 | 85 | 0 | 8 | 19 | 11 | 33 | 16 | 172 | 48 | 90 | 22 | 0.3 | 66 | 61 | 50 | 50 | 0 | 301 | 30 | 82 | 45 | 110 | 13 | 43 | 7 | 280 | 0 | 11 | 0 | 80 | 0 | 0 | 117 | 0 | 64 |  | 494 | 0 | 360 | 90 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 186 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 3 | 50 | 38 | 18 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 134 | 46 | 0 | 149 | 0 |  | 6656.3 | 2169 | 8825.3 | 3818 | 494 | 1655 | 1974 | 0 | 162 | 550 | 172 | 0.3 | 0 | 0
17:00 | 70 | 120 | 0 | 0 | 250 | 45 | 40 | 300 | 272 | 13 | 0 | 370 | 200 | 84 | 64 | 42 | 208 | 0 | 0 | 0 | 50 | 58 | 82 | 50 | 8 | 10 | 37 | 0 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 51 | 0 | 17 | 90 | 99 | 35 | 19 | 35 | 80 | 0 | 80 | 260 | 309 | 184 | 73 | 100 | 23 | 0 | 5 | 38 | 85 | 0 | 8 | 19 | 11 | 33 | 16 | 124 | 47 | 48 | 22 | 0 | 66 | 61 | 50 | 50 | 0 | 307 | 30 | 83 | 44 | 70 | 13 | 43 | 7 | 300 | 16 | 5 | 0 | 165 | 0 | 0 | 127 | 0 | 102 |  | 494 | 0 | 250 | 10 | 115 | 0 | 0 | 0 | 0 | 15 | 8 | 185 | 23 | 110 | 0 | 0 | 0 | 5 | 0 | 25 | 50 | 35 | 44 | 25 | 39 | 18 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 0 | 132 | 52 | 0 | 149 | 0 |  | 6543 | 1982 | 8525 | 3620 | 494 | 1643 | 1871 | 0 | 162 | 611 | 124 | 0 | 0 | 0
18:00 | 70 | 120 | 0 | 0 | 200 | 22 | 40 | 300 | 251 | 13 | 0 | 320 | 200 | 57 | 64 | 15 | 128 | 0 | 0 | 0 | 50 | 30 | 82 | 10 | 8 | 0 | 6 | 0 | 36 | 55 | 19 | 25 | 19 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 50 | 0 | 51 | 0 | 17 | 90 | 99 | 43 | 19 | 35 | 80 | 0 | 80 | 260 | 276 | 184 | 73 | 100 | 23 | 0 | 5 | 12 | 50 | 0 | 8 | 19 | 11 | 33 | 21 | 116 | 48 | 8 | 20 | 0.1 | 68 | 61 | 22 | 20 | 0 | 301 | 20 | 50 | 20 | 68 | 13 | 22 | 7 | 280 | 22 | 11 | 0 | 180 | 0 | 0 | 128 | 0 | 133 |  | 494 | 0 | 200 | 10 | 115 | 0 | 0 | 0 | 40 | 31 | 8 | 175 | 23 | 80 | 0 | 0 | 0 | 17 | 10 | 25 | 50 | 43 | 44 | 8 | 39 | 18 | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 131 | 55 | 0 | 151 | 0 |  | 5895.1 | 1964 | 7859.1 | 3398 | 494 | 1335 | 1665 | 0 | 162 | 689 | 116 | 0.1 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 120 | 0 | 0 | 358 | 22 | 40 | 330 | 301 | 13 | 0 | 400 | 305 | 73 | 64 | 15 | 160 | 0 | 0 | 0 | 50 | 30 | 82 | 50 | 8 | 48 | 6 | 0 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 135 | 0 | 50 | 27 | 45 | 101 | 99 | 43 | 19 | 37 | 80 | 0 | 80 | 260 | 320 | 218 | 73 | 100 | 43 | 0 | 5 | 12 | 85 | 0 | 8 | 19 | 11 | 33 | 21 | 164 | 48 | 20 | 20 | 0 | 64 | 61 | 26 | 30 | 0 | 324 | 30 | 86 | 20 | 130 | 19 | 21 | 7 | 300 | 22 | 11 | 25 | 188 | 0 | 26 | 127 | 30 | 133 |  | 493 | 0 | 410 | 80 | 115 | 0 | 0 | 0 | 48 | 45 | 16 | 188 | 27 | 71 | 0 | 0 | 0 | 43 | 31 | 33 | 50 | 43 | 47 | 25 | 40 | 18 | 10 | 5 | 0 | 0 | 0 | 17 | 0 | 193 | 0 | 0 | 155 | 71 | 95 | 149 | 0 |  | 7072 | 2518 | 9590 | 4045 | 493 | 1591 | 2184 | 0 | 162 | 951 | 164 | 0 | 0 | 0
19:30 | 70 | 120 | 0 | 0 | 365 | 22 | 40 | 350 | 300 | 40 | 0 | 400 | 250 | 92 | 64 | 55 | 213 | 0 | 0 | 20 | 55 | 65 | 132 | 75 | 8 | 51 | 25 | 0 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 135 | 0 | 50 | 76 | 47 | 101 | 99 | 37 | 19 | 37 | 80 | 0 | 80 | 260 | 305 | 220 | 73 | 100 | 43 | 0 | 5 | 16 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 168 | 48 | 85 | 20 | 0 | 70 | 62 | 53 | 50 | 0 | 300 | 30 | 86 | 44 | 108 | 19 | 46 | 7 | 290 | 22 | 11 | 50 | 210 | 0 | 10 | 129 | 11 | 148 |  | 493 | 32 | 410 | 101 | 115 | 0 | 0 | 0 | 48 | 55 | 32 | 179 | 30 | 96 | 0 | 0 | 0 | 43 | 31 | 85 | 50 | 43 | 47 | 51 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 15 | 0 | 215 | 0 | 0 | 191 | 94 | 95 | 152 | 0 |  | 7561 | 2782 | 10343 | 4095 | 493 | 1706 | 2490 | 0 | 162 | 1229 | 168 | 0 | 0 | 0
20:00 | 70 | 120 | 0 | 0 | 365 | 40 | 60 | 370 | 301 | 40 | 0 | 390 | 200 | 86 | 64 | 50 | 214 | 0 | 0 | 20 | 70 | 102 | 135 | 75 | 8 | 51 | 19 | 18 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 135 | 0 | 45 | 76 | 47 | 100 | 99 | 37 | 19 | 37 | 80 | 0 | 80 | 260 | 305 | 220 | 73 | 100 | 43 | 0 | 5 | 30 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 168 | 48 | 91 | 22 | 0 | 68 | 62 | 53 | 50 | 0 | 300 | 30 | 86 | 46 | 88 | 19 | 46 | 7 | 290 | 23 | 11 | 0 | 205 | 0 | 0 | 148 | 0 | 148 |  | 494 | 48 | 410 | 101 | 115 | 0 | 0 | 0 | 48 | 80 | 32 | 176 | 31 | 80 | 0 | 0 | 0 | 43 | 31 | 91 | 50 | 43 | 47 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 15 | 0 | 215 | 0 | 0 | 191 | 96 | 95 | 153 | 0 |  | 7569 | 2815 | 10384 | 4108 | 494 | 1754 | 2421 | 0 | 162 | 1277 | 168 | 0 | 0 | 0
21:00 | 70 | 120 | 0 | 0 | 365 | 84 | 74 | 350 | 292 | 40 | 0 | 400 | 200 | 90 | 64 | 55 | 213 | 0 | 0 | 35 | 100 | 102 | 132 | 63 | 8 | 20 | 40 | 50 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 80 | 0 | 0 | 16 | 0 | 228 | 0 | 135 | 0 | 50 | 76 | 47 | 100 | 99 | 37 | 19 | 38 | 80 | 0 | 80 | 260 | 338 | 219 | 73 | 100 | 43 | 0 | 5 | 38 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 170 | 48 | 90 | 22 | 0 | 64 | 62 | 53 | 50 | 0 | 321 | 30 | 86 | 47 | 128 | 19 | 46 | 7 | 310 | 23 | 11 | 0 | 210 | 0 | 0 | 133 | 0 | 146 |  | 494 | 48 | 410 | 98 | 115 | 0 | 0 | 0 | 48 | 68 | 40 | 189 | 32 | 80 | 0 | 0 | 0 | 43 | 31 | 90 | 50 | 43 | 44 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 10 | 0 | 214 | 0 | 0 | 191 | 97 | 95 | 149 | 0 |  | 7808 | 2809 | 10617 | 4184 | 494 | 1845 | 2482 | 0 | 163 | 1279 | 170 | 0 | 0 | 0
22:00 | 70 | 120 | 0 | 0 | 365 | 87 | 74 | 370 | 293 | 40 | 0 | 400 | 200 | 92 | 65 | 55 | 214 | 0 | 0 | 35 | 100 | 102 | 132 | 75 | 8 | 10 | 41 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 80 | 0 | 0 | 16 | 0 | 228 | 0 | 135 | 0 | 50 | 76 | 47 | 100 | 99 | 38 | 19 | 38 | 80 | 0 | 80 | 260 | 331 | 220 | 73 | 100 | 43 | 0 | 5 | 38 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 170 | 48 | 90 | 22 | 0 | 68 | 62 | 53 | 50 | 0 | 311 | 30 | 86 | 47 | 128 | 19 | 46 | 7 | 320 | 23 | 11 | 0 | 210 | 0 | 0 | 141 | 0 | 145 |  | 494 | 48 | 410 | 98 | 115 | 0 | 0 | 0 | 48 | 62 | 32 | 189 | 33 | 110 | 0 | 0 | 0 | 43 | 31 | 90 | 50 | 43 | 44 | 52 | 39 | 18 | 10 | 0 | 0 | 0 | 0 | 5 | 0 | 214 | 0 | 0 | 191 | 98 | 95 | 151 | 0 |  | 7849 | 2813 | 10662 | 4184 | 494 | 1861 | 2522 | 0 | 163 | 1268 | 170 | 0 | 0 | 104.82
23:00 | 70 | 120 | 0 | 0 | 365 | 87 | 74 | 357 | 292 | 55 | 0 | 400 | 250 | 92 | 65 | 55 | 213 | 0 | 0 | 35 | 100 | 102 | 132 | 75 | 8 | 10 | 40 | 18 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 50 | 76 | 47 | 90 | 99 | 38 | 19 | 38 | 80 | 0 | 80 | 260 | 290 | 216 | 73 | 100 | 43 | 0 | 5 | 38 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 166 | 48 | 90 | 22 | 0 | 70 | 62 | 53 | 50 | 0 | 317 | 30 | 86 | 47 | 127 | 19 | 46 | 7 | 320 | 23 | 11 | 0 | 210 | 0 | 0 | 141 | 0 | 145 |  | 493 | 48 | 410 | 98 | 115 | 0 | 0 | 0 | 48 | 55 | 32 | 188 | 32 | 110 | 0 | 0 | 0 | 43 | 31 | 90 | 50 | 43 | 44 | 52 | 39 | 18 | 10 | 10 | 0 | 0 | 0 | 12 | 0 | 215 | 0 | 0 | 191 | 98 | 95 | 150 | 0 |  | 7807 | 2820 | 10627 | 4141 | 493 | 1859 | 2540 | 0 | 161 | 1267 | 166 | 0 | 0 | 104.82
24:00 | 70 | 120 | 0 | 0 | 365 | 87 | 74 | 378 | 293 | 96 | 0 | 400 | 305 | 91 | 65 | 55 | 218 | 0 | 0 | 35 | 100 | 102 | 132 | 75 | 8 | 31 | 40 | 18 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 50 | 76 | 47 | 90 | 99 | 38 | 19 | 37 | 80 | 0 | 80 | 260 | 253 | 222 | 73 | 100 | 20 | 0 | 5 | 45 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 158 | 48 | 90 | 22 | 0 | 65 | 62 | 50 | 50 | 0 | 305 | 31 | 86 | 47 | 127 | 19 | 46 | 7 | 285 | 23 | 11 | 0 | 210 | 0 | 0 | 141 | 0 | 145 |  | 494 | 48 | 414 | 100 | 115 | 0 | 0 | 0 | 48 | 56 | 32 | 181 | 34 | 110 | 0 | 0 | 0 | 43 | 31 | 90 | 50 | 43 | 44 | 52 | 38 | 18 | 10 | 10 | 0 | 0 | 0 | 12 | 0 | 214 | 0 | 0 | 184 | 98 | 96 | 154 | 0 |  | 7840 | 2819 | 10659 | 4097 | 494 | 1830 | 2659 | 0 | 161 | 1260 | 158 | 0 | 0 | 104.82
KWH | 1583000 | 2979585 | 0 | 0 | 8278436 | 1800273 | 1622880 | 8991920 | 6322000 | 494800 | 0 | 8425937 | 5524015 | 1245120 | 1161768 | 933580 | 5067111 | 0 | 0 | 319680 | 1290240 | 1047600 | 1937760 | 1011099 | 174720 | 309000 | 823680 | 286920 | 994577 | 1190626 | 332460 | 600000 | 608400 | 629396 | 760100 | 885720 | 0 | 1885589 | 1910600 | 0 | 0 | 314280 | 0 | 4942268 | 0 | 2212465 | 0 | 901920 | 481160 | 509557 | 2065560 | 1559040 | 743040 | 458208 | 752640 | 1996972 | 0 | 1923456 | 6546000 | 7204000 | 5041000 | 1773091 | 2377120 | 810792 | 0 | 120000 | 969441 | 1161768 | 266368 | 48758 | 445572 | 251820 | 826300 | 476910 | 3329280 | 1149160 | 1286400 | 505530 | 14750 | 1569000 | 1472840 | 1169400 | 1150000 | 0 | 6783204 | 694000 | 1954560 | 1045800 | 2388250 | 419000 | 1042700 | 165420 | 7358300 | 509960 | 201792 | 53760 | 3580470 | 0 | 22192 | 2985600 | 20210 | 2458080 |  | 11872000 | 227300 | 9149184 | 1212480 | 1970880 | 0 | 0 | 0 | 662880 | 469248 | 591000 | 4480654 | 633214 | 2363712 | 0 | 0 | 0 | 288504 | 286973 | 1322302 | 1158150 | 919520 | 617460 | 836640 | 949975 | 425760 | 240804 | 224874 | 0 | 0 | 0 | 146000 | 0 | 5098636 | 0 | 0 | 4054100 | 1251309 | 729600 | 3692800 | 0 |  | 161937756 | 55875959 | 217813715 | 96527442 | 11872000 | 39385297 | 43514437 | 0 | 3796189 | 19374320 | 3329280 | 14750 | 0
Fuel Cost | 1361380 | 2562443.1 | 0 | 0 | 5298199.04 | 1458221.13 | 1525507.2 | 5485071.2 | 3856420 | 4755028 | 0 | 5645377.79 | 83909787.85 | 7819353.6 | 7760610.24 | 5704173.8 | 3293622.15 | 0 | 0 | 4974220.8 | 8064000 | 6903684 | 18738139.2 | 6440700.63 | 1046572.8 | 4940910 | 5493945.6 | 2045739.6 | 6216106.25 | 7465225.02 | 249345 | 450000 | 0 | 0 | 0 | 8378911.2 | 0 | 0 | 0 | 0 | 0 | 2976231.6 | 0 | 67461958.2 | 0 | 48475108.15 | 0 | 7927876.8 | 5182093.2 | 4957989.61 | 12785816.4 | 10071398.4 | 4859481.6 | 389476.8 | 0 | 1817244.52 | 0 | 1750344.96 | 4058520 | 4970760 | 3528700 | 1223432.79 | 2282035.2 | 543230.64 | 0 | 110400 | 794941.62 | 1103679.6 | 2887429.12 | 361784.36 | 343090.44 | 188865 | 636251 | 357682.5 | 22772275.2 | 861870 | 11822016 | 389258.1 | 0 | 1631760 | 1531753.6 | 1122624 | 1035000 | 0 | 4748242.8 | 791160 | 2091379.2 | 1150380 | 2722605 | 536320 | 969711 | 153840.6 | 4709312 | 382470 | 153361.92 | 931660.8 | 25994212.2 | 0 | 378373.6 | 21347040 | 344580.5 | 0 |  | 60547200 | 6625795 | 6129953.28 | 9711964.8 | 16338595.2 | 0 | 0 | 0 | 7464028.8 | 5527741.44 | 4657080 | 3091651.26 | 626881.86 | 17491468.8 | 0 | 0 | 0 | 3303370.8 | 3076350.56 | 11847825.92 | 10017997.5 | 8183728 | 6575949 | 8299468.8 | 11181205.75 | 468336 | 226355.76 | 170229.618 | 0 | 0 | 0 | 4705580 | 0 | 3467072.48 | 0 | 0 | 59433106 | 0 | 12643968 | 0 | 0 |  | 522459724.23 | 281812904.628 | 804272628.858 | 66173969.608 | 60547200 | 28271800.55 | 359063712.75 | 0 | 0 | 267443670.75 | 22772275.2 | 0 | 0
Yesterday Day Peak | 70 | 120 | 0 | 0 | 365 | 84 | 72 | 372 | 241 | 0 | 0 | 370 | 200 | 7 | 15 | 15 | 212 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 33 | 0 | 18 | 36 | 0 | 25 | 22 | 25 | 23 | 8 | 0 | 79 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 135 | 0 | 8 | 0 | 0 | 70 | 19 | 6 | 19 | 31 | 80 | 0 | 80 | 260 | 368 | 186 | 73 | 100 | 43 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 34 | 15 | 116 | 48 | 8 | 22 | 2.7 | 64 | 62 | 50 | 50 | 0 | 298 | 30 | 84 | 46 | 130 | 19 | 44 | 7 | 310 | 22 | 11 | 0 | 82 | 0 | 0 | 100 | 0 | 75 |  | 494 | 0 | 410 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 190 | 22 | 80 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 8 | 40 | 18 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 131 | 0 | 0 | 151 | 0 |  | 8030.7 | DayPeak
Yesterday Evening Peak | 70 | 120 | 0 | 0 | 365 | 84 | 74 | 350 | 292 | 40 | 0 | 400 | 200 | 90 | 64 | 55 | 213 | 0 | 0 | 35 | 100 | 102 | 132 | 63 | 8 | 20 | 40 | 50 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 83 | 80 | 0 | 0 | 16 | 0 | 228 | 0 | 135 | 0 | 50 | 76 | 47 | 100 | 99 | 37 | 19 | 38 | 80 | 0 | 80 | 260 | 338 | 219 | 73 | 100 | 43 | 0 | 5 | 38 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 170 | 48 | 90 | 22 | 0 | 64 | 62 | 53 | 50 | 0 | 321 | 30 | 86 | 47 | 128 | 19 | 46 | 7 | 310 | 23 | 11 | 0 | 210 | 0 | 0 | 133 | 0 | 146 |  | 494 | 48 | 410 | 98 | 115 | 0 | 0 | 0 | 48 | 68 | 40 | 189 | 32 | 80 | 0 | 0 | 0 | 43 | 31 | 90 | 50 | 43 | 44 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 10 | 0 | 214 | 0 | 0 | 191 | 97 | 95 | 149 | 0 |  | 10617 | EvPeak
Forecast for Evening | 70 | 120 | 0 | 0 | 365 | 85 | 78 | 412 | 360 | 110 | 0 | 450 | 305 | 90 | 64 | 55 | 217 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 135 | 0 | 50 | 80 | 50 | 100 | 100 | 40 | 19 | 15 | 120 | 0 | 100 | 0 | 360 | 225 | 73 | 100 | 43 | 0 | 5 | 45 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 172 | 50 | 90 | 22 | 0 | 64 | 62 | 51 | 50 | 0 | 330 | 30 | 86 | 47 | 130 | 19 | 48 | 7 | 341 | 23 | 11 | 200 | 300 | 311 | 100 | 160 | 100 | 150 |  | 497 | 48 | 410 | 98 | 115 | 225 | 0 | 0 | 48 | 80 | 40 | 194 | 33 | 110 | 30 | 0 | 0 | 43 | 32 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 18 | 215 | 0 | 0 | 210 | 95 | 100 | 154
Forecast for Day | 70 | 120 | 0 | 0 | 365 | 84 | 74 | 412 | 360 | 110 | 0 | 400 | 305 | 90 | 64 | 55 | 217 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 110 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 135 | 0 | 50 | 40 | 50 | 100 | 100 | 32 | 19 | 10 | 120 | 0 | 100 | 0 | 360 | 225 | 73 | 100 | 43 | 0 | 5 | 45 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 121 | 50 | 90 | 22 | 2 | 64 | 62 | 51 | 50 | 0 | 330 | 30 | 86 | 47 | 130 | 19 | 48 | 7 | 341 | 23 | 11 | 100 | 300 | 0 | 100 | 156 | 100 | 150 |  | 497 | 0 | 410 | 60 | 115 | 100 | 0 | 0 | 45 | 80 | 40 | 190 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 60 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 18 | 210 | 0 | 0 | 210 | 95 | 100 | 154
Generation at 08:00(Today) | 70 | 120 | 0 | 0 | 365 | 87 | 60 | 345 | 281 | 0 | 0 | 410 | 200 | 7 | 15 | 55 | 216 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 20 | 39 | 18 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 230 | 0 | 80 | 0 | 32 | 0 | 0 | 90 | 33 | 24 | 19 | 5 | 120 | 0 | 100 | 0 | 375 | 182 | 68 | 100 | 40 | 0 | 5 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 124 | 65 | 24 | 22 | 0.7 | 65 | 62 | 44 | 50 | 0 | 313 | 30 | 86 | 46 | 98 | 19 | 46 | 7 | 275 | 23 | 11 | 0 | 168 | 0 | 0 | 144 | 0 | 0 | 0 | 427 | 0 | 412 | 10 | 98 | 0 | 0 | 0 | 0 | 0 | 32 | 190 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 35 | 0 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 124 | 97 | 0 | 154 | 0 | 0
199
| Minimum Generation |  | 7749.6 | 9:00
| Highest Generation |  | 10662 | 22:00
| Day Peak Generation |  | 8030.7 | 12:00
| Evening Peak Generation |  | 10617 | 21:00
| HVDC Max Flow |  | 495 | 5:00
| HVDC EvPeak Flow |  | 494 | 21:00
| Load factor L.F |  | 85.12%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-08-11
Till now the maximum generation is : - |  |  | 11387 | 22:00 | Hrs on | 2018-07-18
The Summary of Yesterday's |  | 2018-08-10 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8030.7 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8310.7 | MW
Evening Peak Generation : |  | 10617 | MW Hour : | 21:00 | Available Max Generation : |  | 12300 | MW
E.P. Demand (at gen end) : |  | 10617 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11400 | MW
Maximum Generation : |  | 10662 | MW Hour : | 22:00 | Reserve(Generation end) |  | 900 | MW
Total Gen. (MKWH) : |  | 217.8137 | System Load Factor : | 85.12% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -580 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-08-11
Actual : | 104.85 | Ft.(MSL) , | Rule curve : | 92.2 | Ft.( MSL )
Gas Consumed : | Total = | 1123.15 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 94445770.158
|  | Coal : | 0 | Oil : | 626507383.5 | Total : | 720953153.658
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4041.6586 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1375.0671 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1232.1356 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1113.3814 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1006.123 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 811.9073 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 453.1043 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 209.0212 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 626.1874 |  |  | 0 | 0%
Total | 0 |  | 10868.5858 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2,3 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Ashuganj Unit-4
|  |  |  | 3) Ghorasal Unit-4,5 |  | 12) Ashuganj(N)-360 MW
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Mymensing 132/33 kV T-2 transformer was under shut down from 08:36 to 19:54 for C/M.
b) Kustia 132/33 kV T-2 transformer was under shut down from 08:18 to 11:36 for C/M.
c) Baghabari 230/132 kV TR-1 transformer was under shut down from 08:24 to 16:34 for C/M.
d) Faridpur 132/33 kV T-1 transformer was under shut down from 09:06 to 10:49 for C/M.
e) Munsiganj 133 kV Bus was under shut down from 08:36 to 09:46 for C/M.
f) Kishorganj 133 kV Bus-2 was under shut down from 09:03 to 15:37 for C/M.
g) Kaliakoir 400 kV Bus-1 was under shut down from 10:40 to 18:23 for D/W.
h) Rajshahi 132/33 kV T-1,T-2 & T-3 transformers tripped at 19:37 showing E/F relay due to 33 kV |  |  |  | About 150 MW Power interruption occurred under Rajshahi
Salbagan feeder fault and were switched on at 19:58, 20:07 & 19:59 respectively. |  |  |  | S/S area from 19:37 to 19:58.
i) Patuakhali 132/33 kV T-2 transformer was shut down at 20:04 due to red hot maintenance at 33 |  |  |  | About 30 MW Power interruption occurred under Patuakhali
kV, B-phase isolator of incoming breaker and was switched on at 20:56. |  |  |  | S/S area from 20:04 to 20:56.
j) Kishorganj 132/33 kV T-2 transformer was shut down at 20:05 due to red hot maintenance at 132 |  |  |  | About 25 MW Power interruption occurred under Kishorganj
kV, Y-phase isolator of Bus-B and was switched on at 20:53. |  |  |  | S/S area from 20:05 to 20:53.
k) Ashuganj(N)-360 MW CCPP ST & GT were shut down at 03:48 & 04:36(11/8/18) for filter replacement
l) Saidpur-Purbasadipur 132 kV Ckt-2 tripped at 07:19(11/8/18) showing dist.BC at Saidpur end
and was switched on at 07:25(11/8/18).
m) Purbasadipur-Thakurgaon 132 kV Ckt-1 & 2 tripped at 07:18(11/8/18) showing O/C relay and |  |  |  | About 65 MW Power interruption occurred under Thakurgaon
was switched on at 07:28(11/8/18). |  |  |  | & Panchaghar S/S areas from 07:18 to 07:28(11/8/18).
n) Mymensing 132/33 kV T-1 transformer is under shut down at 07:58(11/8/18) for C/M.
o) Kodda-Joydevpur 132 kV Ckt-1 & 2 are under shut down at 07:39(11/8/18) for D/W.
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-08-10 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 70 | 1583000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2979585
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8278436
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 74 | 1622880 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 84 | 1800273 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8991920 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 40 | 494800 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 292 | 6322000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 8425937 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 90 | 1245120 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 200 | 5524015 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 64 | 1161768 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 933580
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 63 | 1011099 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 332460
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 35 | 319680 | Low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1290240
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 213 | 5067111
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 20 | 309000 | Low demand
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1047600
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 823680 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 50 | 286920 | Engine problem
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 1937760 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 994577
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1190626
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 174720 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1208400 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 629396
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 760100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 885720
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 210 | 3580470 | Engine problem
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0 | Reserve
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 22192 | Reserve
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 20210 | Reserve
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 146 | 2458080 | Engine problem
| Dhaka area Total |  |  |  | 5548 | 3626 | 73713355
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 314280
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 37 | 743040 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 163 | 3796189 | # 1 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Gas shortage
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 228 | 4942268
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2212465
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 901920
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 76 | 481160
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 47 | 509557
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2065560
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 458208
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 752640
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 1559040
| Chittagong area Total |  |  |  | 1561 | 1008 | 18736327
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1996972 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Under maint.
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 219 | 5041000
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6546000 | DP high
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 338 | 7204000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 43 | 810792
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 73 | 1773091 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 38 | 969441 | Engine problem
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1161768
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 266368
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2377120
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 445572
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251820
** | Tripura |  | Imported power | 0 | 160 | 170 | 3329280
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 826300
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 48758 | Line over load.
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 476910
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 53760 | Reserve
| Comilla Area Total |  |  |  | 2541 | 1624 | 35622408
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 48 | 1149160 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 505530
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 90 | 1286400
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14750
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 133 | 2985600 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 293 | 5941440
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 64 | 1569000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1472840
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 321 | 6783204 | FGMO
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1169400
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1150000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 201792
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 30 | 694000 | FGMO, GT-9 Under maint.
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1954560
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 1045800
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 128 | 2388250
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 419000
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 1042700
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 509960
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 310 | 7358300 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 7 | 165420 | Engine problem
| Sylhet Area Total |  |  |  | 1549 | 1257 | 27924226
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 48 | 227300
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 494 | 11872000
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 98 | 1212480 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1970880
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 48 | 662880
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Low demand
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 68 | 469248
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9149184
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 591000
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 0 | 0
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 95 | 729600
| Khulna Area Total |  |  |  | 1769 | 1416 | 26884572
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 80 | 2363712 | Line over load.
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 32 | 633214
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 189 | 4480654 | FGMO
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1251309
| Barisal Area Total |  |  |  | 462 | 398 | 8728889
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 288504 | Engine problem
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 31 | 286973
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1158150
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 919520 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 617460
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 191 | 0
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 149 | 3692800 | On test
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 39 | 949975
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 425760 | Engine problem
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 240804
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 224874
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 836640
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 90 | 1322302
| Rajshahi Area Total |  |  |  | 1123 | 771 | 10963762
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage
120 | Rangpur GT |  | PDB | 1*20 | 20 | 10 | 146000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0 | condenser.
| Rangpur Area Total |  |  |  | 484 | 10 | 146000
| Total |  |  |  | 15559 | 10403 | 208660979
| Eastern Grid Total |  |  |  | 11721 | 7808 | 161937756
| Western Grid Total |  |  |  | 3838 | 2595 | 46723223
| National Grid Total |  |  |  | 15559 | 10403 | 208660979
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-08-10 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6959 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3153 | MW
i) Dhaka area |  |  | 3658 | MW | i) Khulna area |  |  | 1273 | MW
ii) Chittagong area |  |  | 1043 | MW | ii) Rajshahi area |  |  | 1017 | MW
iii) Comilla area |  |  | 1012 | MW | iii) Barisal area |  |  | 272 | MW
iv) Mymensingh area |  |  | 773 | MW | iv) Rangpur area |  |  | 591 | MW
v) Sylhet area |  |  | 473 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10112 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 100 | Netrokona | 80 | 2300 | Central s/s | 75 | 2000
Munsiganj | 110 | 2200 | Jamalpur | 114 | 2200 | Noapara | 83 | 2000
Sonargaon | 52 | 1830 | Sherpur | 82 | 1930 | Jessore | 142 | 2100
Shyampur | 165 | 2400 | Srimongal | 38 | 1930 | Jhenida | 94 | 1930
Bhulta | 170 | 2200 | Shahjibazar | 108 | 2000 | Bottail | 114 | 1930
Madanganj | 55 | 200 | Fenchuganj | 49 | 2100 | G.K Project | 54 | 2000
Shitalakhya | 102 | 100 | Kulawara | 43 | 1930 | Faridpur | 152 | 2000
Rahim steel | 2 | 100 | Sylhet | 136 | 2100 | Madaripur | 140 | 2000
Matuail | 82 | 2400 | Chatak | 27 | 2000 | Gopalganj | 84 | 1930
Ghorasal | 99 | 100 | Sunamganj | 35 | 2100 | Bagerhat | 76 | 1930
Narsingdi | 124 | 2000 | Biani Bazar | 42 | 2200 | Mongla | 32 | 100
Haripur (SBU) | 92 | 100 | Comilla (S) | 170 | 2100 | Satkhira | 87 | 2000
Ullon | 95 | 2000 | Comilla(N) | 103 | 2100 | Gallamari | 44 | 1300
Hasnabad | 205 | 2200 | Chandpur | 122 | 2000 | Magura | 54 | 2000
Magbazar | 104 | 1930 | Feni | 136 | 2100 | Chuadanga | 80 | 2000
Maniknagar | 78 | 2100 | Chowmuhani | 180 | 2000 | Barisal | 112 | 1930
Bangabhaban | 16 | 1300 | Ashuganj | 60 | 2200 | Patuakhali | 92 | 2100
Narinda | 76 | 2100 | Daudkandi | 108 | 1900 | Bhandaria | 48 | 2200
Dhanmondi | 111 | 1900 | B.Baria | 131 | 2000 | Ishurdi | 54 | 2100
Lalbag | 61 | 2300 | Ramganj | 34 | 2200 | Ruppur Paromanobik | 1 | 100
Madartek | 53 | 1930 | Madunaghat | 60 | 2000 | Natore | 103 | 1930
Mirpur | 99 | 1900 | Hathazari | 90 | 2100 | Bogra | 223 | 2000
Kalyanpur | 120 | 1930 | Khulshi | 76 | 1200 | Noagaon | 87 | 500
Gulshan | 106 | 1930 | Halishahar | 122 | 2000 | Rajshahi | 151 | 1930
Uttara | 88 | 1930 | Baraulia | 156 | 100 | C.Nawabganj | 67 | 2000
Kamrangirchar | 63 | 1900 | Sikalbaha | 33 | 2000 | Amnura | 37 | 2100
Savar | 100 | 2000 | Dohazari | 94 | 1930 | Pabna | 108 | 2100
Bhasantec | 151 | 2000 | Cox'sbazar | 71 | 2100 | Shahjadpur | 80 | 2100
Agargaon | 43 | 2000 | Chandraghona | 35 | 1930 | Serajganj | 82 | 2000
Satmosjid | 99 | 1500 | Kaptai | 4.2 | 1900 | Niyamatpur | 34 | 100
Tongi | 137 | 1000 | A. Khaer Stl. | 11 | 100 | Joypurhat | 32 | 2000
Kabirpur | 176 | 2100 | Bakulia | 94 | 1930 | Rangpur | 119 | 2100
Basundhara | 122 | 2000 | Julda | 22 | 100 | Lalmonirhat | 87 | 1900
Manikganj | 97 | 2100 | TK chemical | 0.6 | 100 | Saidpur | 100 | 2100
Joydevpur | 218 | 2100 | Modern Steel | 12 | 300 | Purbasadipur | 79 | 800
New Tongi | 87 | 1600 | Shahmirpur | 29 | 100 | Thakurgaon | 58 | 2000
Korda | 236 | 2000 | Abul Khair 230 | 202 | 1400 | Palashbari | 98 | 1930
Dhamrai | 49 | 2200 | BSRM | 119 | 1700 | Barapukuria | 52 | 2100
Tangail | 178 | 2100 | Khagrachhari | 16 | 1930 | Panchagar | 32 | 1830
Mymensing | 244 | 2100 | Matarbari | 26.5 | 2100
Kishorganj | 98 | 1900 | Goalpara | 32 | 2300
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-08-10
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 394 | 7:00 | 385 | 12:00 | Kaliakoir | 376 | 5:00 | 364 | 12:00
Bheramara | 405 | 19:00 | 386 | 15:00 | Bhulta | 383 | 18:00 | 376 | 11:00
Ashuganj(N) | 388 | 2:00 | 383 | 18:30
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 18:00 | 213 | 14:00
Ishurdi | 233 | 18:00 | 220 | 22:00 | Megnaghat | 228 | 16:00 | 222 | 12:00
Ashuganj | 237 | 18:00 | 233 | 15:00 | Fenchuganj | 237 | 17:00 | 230 | 11:00
Serajganj | 222 | 18:00 | 211 | 21:00 | Siddhirganj | 225 | 2:00 | 221 | 11:00
Baghabari | 227 | 18:00 | 215 | 1:00 | Maniknagar | 224 | 18:00 | 218 | 15:00
Barapukuria | 229 | 10:00 | 202 | 22:00 | Old Airport | 224 | 5:00 | 218 | 11:00
Bogra | 218 | 10:00 | 194 | 22:00 | Barisal | 232 | 6:00 | 217 | 13:00
Khulna South | 241 | 18:00 | 222 | 13:00 | AKSML | 220 | 18:00 | 210 | 8:00
Rampura | 221 | 3:00 | 220 | 1:00 | BSRM | 222 | 18:00 | 214 | 10:00
Haripur | 223 | 5:00 | 220 | 10:00 | Bibiyana | 235 | 18:00 | 230 | 19:00
Hasnabad | 225 | 2:00 | 219 | 12:00 | Bhulta | 225 | 18:00 | 220 | 11:00
Aminbazar | 225 | 3:00 | 218 | 12:00 | Ashuganj (S) | 235 | 18:00 | 230 | 21:00
Tongi | 223 | 4:00 | 216 | 12:00 | Kaliakoir | 229 | 3:00 | 222 | 12:00
Comilla (N) | 232 | 7:00 | 225 | 2:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1800 | 132 | 1100 | Ramganj | 122 | 1800 | 112 | 2300
Munsiganj | 135 | 2100 | 130 | 1200 | Madanhat | 133 | 1700 | 128 | 1400
Megnaghat | 137 | 1930 | 128 | 1000 | Hathazari | 131 | 1800 | 127 | 1400
Shyampur | 133 | 1900 | 126 | 1100 | Khulshi | 128 | 1800 | 124 | 1400
Bhulta | 130 | 300 | 127 | 700 | Halishahar | 132 | 1800 | 126 | 1400
Madanganj | 133 | 700 | 130 | 400 | Baraulia | 129 | 1800 | 124 | 1400
Shitalakhya | 138 | 1700 | 129 | 1200 | Sikalbaha | 131 | 1800 | 127 | 1400
Rahim steal | 134 | 100 | 132 | 1000 | Dohazari | 130 | 1800 | 126 | 1400
Matuail | 135 | 1930 | 130 | 1200 | Cox'sbazar | 125 | 1800 | 115 | 2100
Ghorasal | 135 | 100 | 135 | 200 | Chandraghona | 132 | 1800 | 127 | 1400
Narsinghdi | 132 | 1700 | 127 | 100 | Kaptai | 128 | 1800 | 126 | 1400
Haripur (SBU) | 135 | 1800 | 131 | 1200 | A. Khaer Stl. | 128 | 1800 | 126 | 1400
Ullon | 134 | 700 | 130 | 1500 | Bakulia | 130 | 1800 | 124 | 1400
Hasnabad | 136 | 1700 | 130 | 1100 | Julda | 131 | 1800 | 126 | 1400
Magbazar | 135 | 700 | 130 | 1100 | TK Chemical | 132 | 1800 | 127 | 400
Maniknagar | 140 | 700 | 138 | 1100 | Modern Steel | 130 | 1800 | 124 | 1200
Bangabhaban | 140 | 700 | 138 | 1100 | Shahmirpur | 130 | 1800 | 126 | 1200
Narinda | 140 | 700 | 138 | 1100 | Khagrachhari | 131 | 1800 | 127 | 1200
Dhanmondi | 134 | 700 | 130 | 1500 | Matarbari | 129 | 1800 | 118 | 2100
Lalbag | 134 | 1800 | 128 | 1200 | Goalpara | 137 | 1600 | 126 | 2100
Madartek | 134 | 700 | 130 | 1200 | Central s/s | 137 | 1600 | 125 | 2100
Mirpur | 133 | 300 | 129 | 1200 | Noapara | 136 | 1600 | 123 | 2100
Kalyanpur | 135 | 200 | 130 | 1200 | Jessore | 130 | 1600 | 116 | 2100
Gulshan | 134 | 400 | 130 | 1200 | Jhenida | 131 | 900 | 114 | 2100
Uttara | 131 | 200 | 126 | 1100 | Bottail | 137 | 1800 | 125 | 2100
Kamrangirchar | 134 | 100 | 128 | 1200 | G.K.Project | 144 | 900 | 134 | 2200
Savar | 133 | 200 | 127 | 1200 | Faridpur | 135 | 700 | 124 | 100
Bhasantec | 132 | 300 | 127 | 1200 | Madaripur | 136 | 800 | 125 | 2100
Agargaon | 133 | 200 | 128 | 1200 | Gopalganj | 136 | 800 | 123 | 1930
Satmosjid | 133 | 400 | 128 | 1200 | Bagerhat | 135 | 1700 | 121 | 2200
Tongi | 136 | 800 | 132 | 2100 | Mongla | 135 | 1600 | 122 | 2200
Kabirpur | 138 | 1800 | 129 | 1000 | Satkhira | 136 | 1800 | 121 | 2200
Basundhara | 133 | 700 | 129 | 1300 | Gallamari | 137 | 1600 | 126 | 2100
Manikganj | 140 | 600 | 134 | 2100 | Magura | 130 | 900 | 112 | 2100
Joydevpur | 137 | 2000 | 131 | 1300 | Chuadanga | 127 | 900 | 106 | 2100
New Tongi | 137 | 1800 | 132 | 1500 | Barisal | 139 | 500 | 130 | 1300
Kodda | 138 | 1700 | 127 | 1400 | Patuakhali | 136 | 1600 | 125 | 2100
Dhamrai | 137 | 1800 | 130 | 2100 | Bhandaria | 137 | 1600 | 125 | 2100
Tangail | 135 | 500 | 125 | 2200 | Ishurdi | 141 | 1800 | 132 | 1900
Mymensing | 132 | 2000 | 114 | 1900 | Ruppur Paromanobik | 141 | 1800 | 135 | 100
Kishorganj | 130 | 1800 | 119 | 2100 | Natore | 137 | 1800 | 124 | 2100
Netrokona | 130 | 600 | 114 | 2200 | Bogra | 129 | 1800 | 115 | 100
Jamalpur | 137 | 2000 | 120 | 2100 | Noagaon | 127 | 1800 | 111 | 2100
Sherpur | 136 | 2000 | 119 | 2100 | Rajshahi | 134 | 1800 | 120 | 2100
Srimongal | 138 | 700 | 134 | 100 | C.Nawabganj | 132 | 1800 | 122 | 1930
Shahjibazar | 138 | 700 | 131 | 2100 | Amnura | 136 | 1800 | 123 | 1900
Fenchuganj | 136 | 800 | 132 | 2100 | Pabna | 135 | 800 | 125 | 100
Khulawara | 136 | 500 | 132 | 1900 | Shahjadpur | 140 | 1800 | 125 | 1500
Sylhet | 135 | 500 | 131 | 1930 | Serajganj | 135 | 1800 | 122 | 2100
Chatak | 135 | 600 | 130 | 2000 | Niyamatpur | 128 | 1800 | 109 | 100
Sunamganj | 135 | 700 | 129 | 2100 | Joypurhat | 128 | 1800 | 110 | 100
Biani Bazar | 135 | 600 | 129 | 2100 | Rangpur | 122 | 1200 | 98 | 2100
Comilla(s) | 127 | 1800 | 122 | 1900 | Lalmonirhat | 112 | 1800 | 89 | 2100
Comilla(n) | 135 | 1800 | 134 | 2200 | Saidpur | 122 | 1800 | 98 | 2100
Chandpur | 126 | 700 | 120 | 100 | Purbasadipur | 125 | 1000 | 105 | 1900
Feni | 120 | 700 | 113 | 2300 | Thakurgaon | 118 | 1000 | 92 | 1900
Chowmuhani | 123 | 1400 | 114 | 2100 | Palashbari | 121 | 1000 | 102 | 100
Ashuganj | 136 | 800 | 131 | 100 | Barapukuria | 129 | 1000 | 104 | 1900
Daudkandi | 132 | 1800 | 129 | 1000 | Panchagar | 117 | 1000 | 84 | 1930
B.Baria | 138 | 1200 | 130 | 2100

## L-Curve
Date | 2018-08-10
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 520 | 7840 | 2819 | 10659 |  |  |  | QF-LDC-12
0:30 | 535 | 7670.5 | 2765.5 | 10436 | Date: | 2018-08-10
1:00 | 550 | 7501 | 2712 | 10213
1:30 | 550 | 7448 | 2668 | 10116
2:00 | 550 | 7395 | 2624 | 10019
2:30 | 550 | 7260.5 | 2572.5 | 9833 | [5 empty] | Gen. at Eve. Peak | 10617 | 10617 MW (21:00 )
3:00 | 550 | 7126 | 2521 | 9647 | [6 empty] | 21:00
3:30 | 565 | 7032 | 2503.5 | 9535.5 | [5 empty] | Gen. at Day Peak | 8030.7 | 8030.7 MW (12:00 )
4:00 | 580 | 6938 | 2486 | 9424 | [6 empty] | 12:00
4:30 | 575 | 6919.5 | 2463.5 | 9383 | [5 empty] | Highest Generation | 10662
5:00 | 570 | 6901 | 2441 | 9342 | [6 empty] | 22:00
5:30 | 560 | 6656.5 | 2322.5 | 8979
6:00 | 550 | 6412 | 2204 | 8616
6:30 | 535 | 6271.1 | 2152.5 | 8423.6
7:00 | 520 | 6130.2 | 2101 | 8231.2
7:30 | 500 | 6041 | 2047.5 | 8088.5
8:00 | 480 | 5951.8 | 1994 | 7945.8
8:30 | 420 | 5882.7 | 1965 | 7847.7
9:00 | 360 | 5813.6 | 1936 | 7749.6
9:30 | 260 | 5842.05 | 1955.5 | 7797.55
10:00 | 160 | 5870.5 | 1975 | 7845.5
10:30 | 200 | 5858.3 | 1939.5 | 7797.8
11:00 | 240 | 5846.1 | 1904 | 7750.1
11:30 | 290 | 5984.9 | 1905.5 | 7890.4
12:00 | 340 | 6123.7 | 1907 | 8030.7
12:30 | 430 | 6214.75 | 1915.5 | 8130.25
13:00 | 520 | 6305.8 | 1924 | 8229.8
13:30 | 475 | 6264.45 | 1998 | 8262.45
14:00 | 430 | 6223.1 | 2072 | 8295.1
14:30 | 445 | 6504.25 | 2145 | 8649.25
15:00 | 460 | 6785.4 | 2218 | 9003.4
15:30 | 430 | 6720.85 | 2193.5 | 8914.35
16:00 | 400 | 6656.3 | 2169 | 8825.3
16:30 | 420 | 6599.65 | 2075.5 | 8675.15
17:00 | 440 | 6543 | 1982 | 8525
17:30 | 385 | 6219.05 | 1973 | 8192.05
18:00 | 330 | 5895.1 | 1964 | 7859.1
18:30 | 400 | 6483.55 | 2241 | 8724.55
19:00 | 470 | 7072 | 2518 | 9590
19:30 | 550 | 7561 | 2782 | 10343
20:00 | 480 | 7569 | 2815 | 10384 |  |  |  | Executive Engineer
20:30 | 515 | 7688.5 | 2812 | 10500.5 |  |  |  | Network Operation Division
21:00 | 550 | 7808 | 2809 | 10617
21:30 | 550 | 7828.5 | 2811 | 10639.5
22:00 | 550 | 7849 | 2813 | 10662 |  |  |  |  | Page 6 of 7
22:30 | 540 | 7828 | 2816.5 | 10644.5
23:00 | 530 | 7807 | 2820 | 10627
23:30 | 525 | 7823.5 | 2819.5 | 10643
24:00 | 520 | 7840 | 2819 | 10659
10617 MW (21:00 )
8030.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-08-10 |  | Energy | 217813715
[10 empty] | 2018-08-10 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4097 | 494 | 1830 | 2659 | 0 | 161 | 1260 | 0 | 158
0:30 | 4059 | 492.5 | 1784 | 2621 | 0 | 158 | 1163.5 | 0 | 158 | Date: | 2018-08-10
1:00 | 4021 | 491 | 1738 | 2583 | 0 | 155 | 1067 | 0 | 158
1:30 | 4071.5 | 492.5 | 1756 | 2463 | 0 | 155 | 1020 | 0 | 158 | [7 empty] | Total Energy | 217.8137 | Total Energy Gen 217.814 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 217.814 MKWHr
2:00 | 4122 | 494 | 1774 | 2343 | 0 | 155 | 973 | 0 | 158 | [7 empty] | Energy not Served | 0
2:30 | 4140 | 494 | 1775.5 | 2181 | 0 | 155 | 935.5 | 0 | 152 | [7 empty] | Energy Requirement | 217.8137
3:00 | 4158 | 494 | 1777 | 2019 | 0 | 155 | 898 | 0 | 146
3:30 | 4157 | 494 | 1791 | 1953 | 0 | 155 | 839.5 | 0 | 146 | [6 empty] | Shortage
4:00 | 4156 | 494 | 1805 | 1887 | 0 | 155 | 781 | 0 | 146
4:30 | 4164.5 | 494.5 | 1816 | 1836 | 0 | 155 | 774 | 0 | 143
5:00 | 4173 | 495 | 1827 | 1785 | 0 | 155 | 767 | 0 | 140
5:30 | 4162.5 | 494.5 | 1797.5 | 1529 | 0 | 155 | 704.5 | 0 | 136
6:00 | 4152 | 494 | 1768 | 1273 | 0 | 155 | 642 | 0 | 132
6:30 | 4084 | 494 | 1732.5 | 1221.5 | 0 | 155 | 614.5 | 0 | 122 |  |  |  |  | Coal
7:00 | 4016 | 494 | 1697 | 1170 | 0 | 155 | 587 | 0 | 112
7:30 | 3978.5 | 494 | 1632.5 | 1142 | 0 | 155 | 575 | 0 | 111 |  |  |  | Oil |  |  |  | ,
8:00 | 3941 | 494 | 1568 | 1114 | 0 | 155 | 563 | 0 | 110
8:30 | 3874.5 | 494 | 1548 | 1109 | 0 | 156 | 556 | 0 | 109
9:00 | 3808 | 494 | 1528 | 1104 | 0 | 157 | 549 | 0 | 108
9:30 | 3870 | 494 | 1544.5 | 1084 | 0 | 158 | 538.5 | 0 | 107
10:00 | 3932 | 494 | 1561 | 1064 | 0 | 159 | 528 | 0 | 106
10:30 | 3919.5 | 494 | 1588.5 | 1021.5 | 0 | 159 | 505.5 | 0 | 108
11:00 | 3907 | 494 | 1616 | 979 | 0 | 159 | 483 | 0 | 110
11:30 | 4011 | 494 | 1631.5 | 963 | 0 | 159 | 516.5 | 0 | 113
12:00 | 4115 | 494 | 1647 | 947 | 0 | 159 | 550 | 0 | 116
12:30 | 4088.5 | 494 | 1634 | 1078 | 0 | 157 | 554.5 | 0 | 122
13:00 | 4062 | 494 | 1621 | 1209 | 0 | 155 | 559 | 0 | 128
13:30 | 4062 | 494 | 1621 | 1209 | 0 | 155 | 559 | 0 | 128
14:00 | 4062 | 494 | 1621 | 1209 | 0 | 155 | 559 | 0 | 128
14:30 | 4048.5 | 494 | 1643.5 | 1549.5 | 0 | 157.5 | 586.5 | 0 | 136
15:00 | 4035 | 494 | 1666 | 1890 | 0 | 160 | 614 | 0 | 144
15:30 | 3926.5 | 494 | 1660.5 | 1932 | 0 | 161 | 582 | 0 | 158
16:00 | 3818 | 494 | 1655 | 1974 | 0 | 162 | 550 | 0 | 172
16:30 | 3719 | 494 | 1649 | 1922.5 | 0 | 162 | 580.5 | 0 | 148
17:00 | 3620 | 494 | 1643 | 1871 | 0 | 162 | 611 | 0 | 124
17:30 | 3509 | 494 | 1489 | 1768 | 0 | 162 | 650 | 0 | 120
18:00 | 3398 | 494 | 1335 | 1665 | 0 | 162 | 689 | 0 | 116
18:30 | 3721.5 | 493.5 | 1463 | 1924.5 | 0 | 162 | 820 | 0 | 140
19:00 | 4045 | 493 | 1591 | 2184 | 0 | 162 | 951 | 0 | 164
19:30 | 4095 | 493 | 1706 | 2490 | 0 | 162 | 1229 | 0 | 168
20:00 | 4108 | 494 | 1754 | 2421 | 0 | 162 | 1277 | 0 | 168
20:30 | 4146 | 494 | 1799.5 | 2451.5 | 0 | 162.5 | 1278 | 0 | 169
21:00 | 4184 | 494 | 1845 | 2482 | 0 | 163 | 1279 | 0 | 170
21:30 | 4184 | 494 | 1853 | 2502 | 0 | 163 | 1273.5 | 0 | 170
22:00 | 4184 | 494 | 1861 | 2522 | 0 | 163 | 1268 | 0 | 170
22:30 | 4162.5 | 493.5 | 1860 | 2531 | 0 | 162 | 1267.5 | 0 | 168
23:00 | 4141 | 493 | 1859 | 2540 | 0 | 161 | 1267 | 0 | 166
23:30 | 4119 | 493.5 | 1844.5 | 2599.5 | 0 | 161 | 1263.5 | 0 | 162 | Max Temp. in Dhaka |  | 35.6° C
24:00 | 4097 | 494 | 1830 | 2659 | 0 | 161 | 1260 | 0 | 158
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
HYDRO
Total Energy Gen 217.814 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 217.814 MKWHr
Note on W13: Author:

## Generation
2018-08-10
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 77 | 79 | 79 | 79 | 75 | 75 | 80 | 82 | 82 | 82 |  | 82 | 82 | 82 | 83 | 83 | 81 | 81 | 1885589
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1910600
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 26 | 25 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 314280
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 201 | 200 | 200 | 201 | 203 | 203 | 202 | 202 | 203 | 204 | 201 | 203 | 205 | 215 | 209 | 201 | 202 | 203 |  | 203 | 203 | 202 | 228 | 228 | 227 | 227 | 4942268
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 100 | 100 | 80 | 80 | 80 | 70 | 70 | 70 | 50 | 50 | 50 | 135 | 135 | 50 | 134 | 50 | 50 | 50 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2212465
| Dohazari Peaking | 47 | 47 | 47 | 17 | 17 | 0 | [9 empty] | 17 | 17 | 17 |  | 45 | 47 | 47 | 47 | 47 | 47 | 47 | 509557
12 | Hathazari peaking | 24 | 24 | 24 | 0 | 0 | 0 | [13 empty] | 27 | 76 | 76 | 76 | 76 | 76 | 76 | 481160
| Daudkandi bangla trak | [19 empty] | 25 | 50 | 0 |  |  |  |  | 53760
14 | Daudkandi Peaking 52MW | 49 | [18 empty] | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 266368
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 220 | 220 | 220 | 220 | 218 | 220 | 219 | 219 | 219 | 215 | 211 | 212 | 213 | 212 | 207 | 208 | 208 | 128 |  | 160 | 213 | 214 | 213 | 214 | 213 | 218 | 5067111
18 | Summit Gazipur | 203 | 198 | 188 | 190 | 190 | 146 | 98 | 95 | 87 | 80 | 80 | 82 | 80 | 80 | 77 | 80 | 165 | 180 |  | 188 | 210 | 205 | 210 | 210 | 210 | 210 | 3580470
19 | Ashuganj 195MW Modular | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1773091
20 | Ghorasal ST: Unit-1,2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1583000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2979585
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 365 | 350 | 350 | 320 | 365 | 365 | 365 | 365 | 325 | 365 | 262 | 250 | 200 |  | 358 | 365 | 365 | 365 | 365 | 365 | 365 | 8278436
26
28 | Ashuganj ST: Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1996972
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj Engines TSK | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 39 | 40 | 43 | 43 | 43 | 23 | 23 | 23 | 23 |  | 43 | 43 | 43 | 43 | 43 | 43 | 20 | 810792
33 | Ashuganj CCPP 225 MW | 222 | 225 | 223 | 222 | 222 | 224 | 223 | 222 | 182 | 187 | 190 | 186 | 184 | 208 | 202 | 184 | 184 | 184 |  | 218 | 220 | 220 | 219 | 220 | 216 | 222 | 5041000
34 | Ashuganj CCPP(South) | 279 | 279 | 283 | 279 | 301 | 279 | 279 | 280 | 280 | 295 | 290 | 368 | 301 | 340 | 260 | 290 | 309 | 276 |  | 320 | 305 | 305 | 338 | 331 | 290 | 253 | 7204000
| Ashuganj CCPP(North) | 265 | 265 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6546000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2377120
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 402 | 423 | 425 | 425 | 423 | 420 | 358 | 345 | 345 | 357 | 348 | 372 | 386 | 390 | 405 | 380 | 300 | 300 |  | 330 | 350 | 370 | 350 | 370 | 357 | 378 | 8991920
40 | Meghnaghat CCPP 450MW | 380 | 390 | 390 | 390 | 400 | 400 | 400 | 400 | 380 | 380 | 370 | 370 | 370 | 360 | 370 | 370 | 370 | 320 |  | 400 | 400 | 390 | 400 | 400 | 400 | 400 | 8425937
41 | Haripur Power CCPP 360MW | 242 | 273 | 272 | 293 | 293 | 293 | 273 | 242 | 185 | 240 | 242 | 241 | 230 | 270 | 271 | 272 | 272 | 251 |  | 301 | 300 | 301 | 292 | 293 | 292 | 293 | 6322000
42 | Mymensingh RPCL 210MW | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 47 | 47 | 48 | 48 | 46 | 46 | 48 | 47 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 1149160
43 | Haripur NEPC 110MW | 110 | 55 | 0 | [11 empty] | 13 | 13 | 13 | 13 |  | 13 | 40 | 40 | 40 | 40 | 55 | 96 | 494800
44 | Fenchugonj CCPP-1 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 68 | 65 | 64 | 59 | 70 | 66 | 66 | 66 | 68 |  | 64 | 70 | 68 | 64 | 68 | 70 | 65 | 1569000
45 | Fenchugonj CCPP-2 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 61 | 61 | 61 |  | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 1472840
46 | Shajibazar 330 MW | 192 | 280 | 306 | 308 | 311 | 308 | 301 | 303 | 299 | 310 | 313 | 298 | 302 | 300 | 313 | 301 | 307 | 301 |  | 324 | 300 | 300 | 321 | 311 | 317 | 305 | 6783204
47 | Shahjibazar GT: Unit- 8, 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 |  | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 694000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 50 | 84 | 84 | 84 | 84 | 84 | 84 | 83 | 82 | 83 | 50 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1954560
49 | Shahjibazar (EPL) 50MW | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 45 | 44 | 20 |  | 20 | 44 | 46 | 47 | 47 | 47 | 47 | 1045800
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 78 | 78 | 78 | 77 | 77 | 80 | 80 | 80 | 130 | 130 | 120 | 128 | 110 | 70 | 68 |  | 130 | 108 | 88 | 128 | 128 | 127 | 127 | 2388250
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 19 | 19 | 19 | 19 | 13 | 13 | 13 | 13 | 13 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 419000
52 | Sylhet (EPL) 50MW | 45 | 46 | 46 | 46 | 46 | 45 | 45 | 45 | 45 | 44 | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 22 |  | 21 | 46 | 46 | 46 | 46 | 46 | 46 | 1042700
53 | Sylhet (Desh) 10MW | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 165420
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 0 |  | 0 | 8 | 11 | 11 | 11 | 11 | 11 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 201792
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 22 |  | 26 | 53 | 53 | 53 | 53 | 53 | 50 | 1169400
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 22 | 0 | 16 | 22 |  | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 509960
57 | Summit Bibiana- 2 | 290 | 285 | 290 | 295 | 310 | 280 | 275 | 270 | 270 | 250 | 290 | 310 | 295 | 275 | 300 | 280 | 300 | 280 |  | 300 | 290 | 290 | 310 | 320 | 320 | 285 | 7358300
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1190626
59 | Sikalbaha (Energis) | 50 | 50 | 50 | 51 | 51 | 32 | 24 | 24 | 24 | 24 | 8 | 8 | 11 | 24 | 26 | 31 | 51 | 51 |  | 50 | 50 | 45 | 50 | 50 | 50 | 50 | 901920
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 458208
61 | Narshingdi (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 |  |  | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 332460
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 |  | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 505530
63 | Tripura | 158 | 158 | 146 | 146 | 140 | 132 | 112 | 110 | 108 | 106 | 110 | 116 | 128 | 132 | 144 | 172 | 124 | 116 |  | 164 | 168 | 168 | 170 | 170 | 166 | 158 | 3329280
64 | Malancha, Ctg. EPZ (United) | 30 | 32 | 32 | 33 | 33 | 37 | 23 | 26 | 30 | 32 | 32 | 31 | 31 | 32 | 32 | 32 | 35 | 35 |  | 37 | 37 | 37 | 38 | 38 | 38 | 37 | 752640
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 445572
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251820
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826300
68 | Summit Comilla 25MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 12 | 15 | 15 | 15 | 15 | 20 | 20 | 16 | 16 | 16 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 476910
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 16 | 22 | 22 | 16 | 15 | 5 | 19 | 19 |  | 19 | 19 | 32 | 32 | 32 | 32 | 32 | 608400
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 25 | 25 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 629396
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 23 | 29 | 0 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 760100
73 | Ghorashal (Regent) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 45 | 22 |  | 22 | 22 | 40 | 84 | 87 | 87 | 87 | 1800273
76 | Siddhirganj (Desh) | 100 | 17 | 0 | [17 empty] | 20 | 20 | 35 | 35 | 35 | 35 | 319680
77 | Siddhirganj (Dutch Bangla) | 100 | 100 | 100 | 50 | 23 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 30 | 60 | 50 | 50 |  | 50 | 55 | 70 | 100 | 100 | 100 | 100 | 1290240
78 | Gazipur (RPCL) | 51 | 51 | 51 | 51 | 51 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 16 | 32 | 50 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 885720
79 | Kodda 149 MW | 149 | 149 | 98 | 65 | 48 | 48 | 48 | 48 | 48 | 36 | 16 | 16 | 16 | 16 | 20 | 82 | 82 | 82 |  | 82 | 132 | 135 | 132 | 132 | 132 | 132 | 1937760
80 | Jamalpur 95MW | 90 | 90 | 90 | 90 | 90 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 16 | 24 | 64 | 90 | 48 | 8 |  | 20 | 85 | 91 | 90 | 90 | 90 | 90 | 1286400
81 | Lakdhanvi 52 MW | 0 | [12 empty] | 2 | 8 | 8 | 8 | 8 |  | 8 | 0 | [5 empty] | 48758
82 | Madanganj 102MW | 65 | 65 | 65 | 65 | 65 | 15 | 15 | 15 | 16 | 15 | 15 | 15 | 15 | 37 | 64 | 64 | 64 | 64 |  | 64 | 64 | 64 | 64 | 65 | 65 | 65 | 1161768
83 | Pagla (DPA ) | 10 | 11 | 10 | [9 empty] | 20 | 21 | 50 | 51 | 10 | 0 |  | 48 | 51 | 51 | 20 | 10 | 10 | 31 | 309000
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1161768
85 | Keraniganj (Powerpac) 100MW | 88 | 70 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 38 | 60 | 75 | 50 | 10 |  | 50 | 75 | 75 | 63 | 75 | 75 | 75 | 1011099
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 305 | 200 | 305 | 200 | 200 | 200 |  | 305 | 250 | 200 | 200 | 200 | 250 | 305 | 5524015
87 | Meghnaghat (IEL) | 94 | 80 | 50 | 50 | 29 | 10 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 24 | 57 | 87 | 84 | 57 |  | 73 | 92 | 86 | 90 | 92 | 92 | 91 | 1245120
88 | Ghorashal 78MW (MAX) | 60 | 60 | 60 | 60 | 60 | 76 | 76 | 40 | 40 | 40 | 60 | 72 | 72 | 71 | 71 | 40 | 40 | 40 |  | 40 | 40 | 60 | 74 | 74 | 74 | 74 | 1622880
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 90 | 90 | 90 | 90 | 90 | 90 |  | 101 | 101 | 100 | 100 | 100 | 90 | 90 | 2065560
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 50 | 50 | 50 | 20 |  | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 1150000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 38 | 38 | 12 |  | 12 | 16 | 30 | 38 | 38 | 38 | 45 | 969441
94 | Gagnagar (Orion) | 102 | 70 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 14 | 24 | 58 | 58 | 58 | 30 |  | 30 | 65 | 102 | 102 | 102 | 102 | 102 | 1047600
95 | Patenga 50MW | 44 | 44 | 44 | 44 | 44 | 35 | 25 | 25 | 25 | 10 | 6 | 6 | 6 | 12 | 23 | 26 | 35 | 43 |  | 43 | 37 | 37 | 37 | 38 | 38 | 38 | 743040
96 | Chittagong ECPV 108 MW | 99 | 99 | 99 | 68 | 52 | 32 | 19 | 19 | 19 | 19 | 21 | 19 | 21 | 22 | 90 | 92 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1559040
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 40 | 35 | 32 | 33 | 33 | 33 | 24 | 33 | 33 | 33 | 37 | 39 | 37 | 6 |  | 6 | 25 | 19 | 40 | 41 | 40 | 40 | 823680
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 174720
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 40 | 55 | 55 | 42 | 15 |  | 15 | 55 | 50 | 55 | 55 | 55 | 55 | 933580
100 | Northern 55 MW | 55 | 55 | 55 | 55 | 55 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 37 | 55 | 55 | 55 | 36 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 994577
101 | Kushiara 163 MW CCPP GT
102 | Sarishabari (Solar) | [6 empty] | 0.2 | 0.8 | 1.6 | 1.5 | 2.1 | 2.7 | 1.8 | 2.1 | 0.4 | 0.3 | 0 | 0.1 |  | 0 | [6 empty] | 14750
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 18 | 50 | 54 | 18 | 18 | 286920
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [19 empty] | 26 | 10 | 0 |  |  |  |  | 22192
106 | United Mymensingh PPL | 139 | 139 | 139 | 139 | 141 | 124 | 113 | 105 | 100 | 100 | 100 | 100 | 114 | 130 | 122 | 117 | 127 | 128 |  | 127 | 129 | 148 | 133 | 141 | 141 | 141 | 2985600
112 | Aggreko Aurahati 100MW | [19 empty] | 30 | 11 | 0 |  |  |  |  | 20210
114 | Summit Gazipur-1 150MW | 113 | 113 | 113 | 113 | 113 | 110 | 95 | 78 | 78 | 78 | 75 | 75 | 75 | 32 | 31 | 64 | 102 | 133 |  | 133 | 148 | 148 | 146 | 145 | 145 | 145 | 2458080
115
116
117
118
120 | Eastern Zone Total | 7501 | 7395 | 7126 | 6938 | 6901 | 6412 | 6130.2 | 5951.8 | 5813.6 | 5870.5 | 5846.1 | 6123.7 | 6305.8 | 6223.1 | 6785.4 | 6656.3 | 6543 | 5895.1 |  | 7072 | 7561 | 7569 | 7808 | 7849 | 7807 | 7840 | 161937756
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 95 | 95 | 51 | 51 | 27 | 10 | 10 | 27 | 27 | 27 | 10 | 10 | 33 | 33 | 90 | 90 | 10 | 10 |  | 80 | 101 | 101 | 98 | 98 | 98 | 100 | 1212480
125 | Khulna (KPCL-2) | 101 | 105 | 100 | 106 | 90 | 49 | 49 | 49 | 49 | 49 | 49 | 16 | 24 | 66 | 99 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1970880
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 42 | 42 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 32 | 0 | [6 empty] | 40 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 662880
129 | Khulna CCPP 225MW
130
131
132
133
| Summit Barisal 110 MW | 109 | 98 | 98 | 96 | 96 | 96 | 96 | 100 | 110 | 110 | 80 | 80 | 80 | 110 | 110 | 110 | 110 | 80 |  | 71 | 96 | 80 | 80 | 110 | 110 | 110 | 2363712
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 96 | 95 | 95 | 96 | 96 | 50 | 21 | [8 empty] | 46 | 52 | 55 |  | 71 | 94 | 96 | 97 | 98 | 98 | 98 | 1251309
| Bhola CCPP 194MW | 188 | 178 | 189 | 190 | 190 | 191 | 190 | 190 | 190 | 189 | 188 | 190 | 167 | 188 | 187 | 186 | 185 | 175 |  | 188 | 179 | 176 | 189 | 189 | 188 | 181 | 4480654
140 | Bhola (Venture) 33MW | 34 | 32 | 31 | 31 | 28 | 26 | 25 | 22 | 21 | 21 | 22 | 22 | 22 | 22 | 26 | 25 | 23 | 23 |  | 27 | 30 | 31 | 32 | 33 | 32 | 34 | 633214
141 | Bangla Trak Noapara | 96 | 70 | 10 | 0 | [15 empty] | 95 | 95 | 95 | 95 | 95 | 95 | 96 | 729600
142 | Noapara (KZA) 40MW | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 8 | 8 | 32 | 40 | 40 | 8 | 8 |  | 16 | 32 | 32 | 40 | 32 | 32 | 32 | 591000
143 | Gopalganj Peaking | 25 | 10 | 6 | 6 | 6 | 6 | 9 | 11 | 16 | 11 | 0 | [5 empty] | 15 | 31 |  | 45 | 55 | 80 | 68 | 62 | 55 | 56 | 469248
144 | Bheramara GT-1,2,3 | [20 empty] | 32 | 48 | 48 | 48 | 48 | 48 | 227300
145
146 | Bheramara HVDC | 491 | 494 | 494 | 494 | 495 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 |  | 493 | 493 | 494 | 494 | 494 | 493 | 494 | 11872000
147 | Bheramara 360 MW | 415 | 413 | 413 | 413 | 411 | 414 | 415 | 360 | 300 | 360 | 360 | 410 | 410 | 410 | 410 | 360 | 250 | 200 |  | 410 | 410 | 410 | 410 | 410 | 410 | 414 | 9149184
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 18 | [15 empty] | 5 | 17 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 288504
157 | Sirajgonj Unit-1 225MW (Gas) | 220 | 220 | 220 | 220 | 219 | 216 | 190 | 181 | 181 | 189 | 188 | 199 | 193 | 183 | 200 | 186 | 183 | 182 |  | 193 | 215 | 215 | 214 | 214 | 215 | 214 | 5098636
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 184 | 173 | 178 | 178 | 179 | 170 | 130 | 131 | 131 | 131 | 151 | 131 | 139 | 187 | 188 | 134 | 132 | 131 |  | 155 | 191 | 191 | 191 | 191 | 191 | 184 | 4054100
159 | Sirajgonj Unit-3 225 MW(Gas) | 154 | 155 | 155 | 155 | 154 | 156 | 155 | 155 | 154 | 151 | 150 | 151 | 151 | 145 | 148 | 149 | 149 | 151 |  | 149 | 152 | 153 | 149 | 151 | 150 | 154 | 3692800
160 | Sirajgonj Unit-3 225 MW(Oil)
161 | Bera Peaking | 31 | 31 | 31 | [14 empty] | 10 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 286973
162 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425760
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240804
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 0 | 10 | 10 | 224874
165 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 42 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1158150
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 919520
167 | Katakhali Peaking | 44 | 44 | 44 | 44 | 44 | 44 | 27 | 0 | 0 | 0 | 0 |  |  |  |  | 3 | 44 | 44 |  | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 617460
168 | Santahar Peaking | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 40 | 40 | 39 | 38 | 38 | 38 | 39 | 39 |  | 40 | 40 | 39 | 39 | 39 | 39 | 38 | 949975
169 | Rajlanka 52 MW | 52 | 52 | 52 | 52 | 52 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 16 | 16 | 40 | 50 | 25 | 8 |  | 25 | 51 | 52 | 52 | 52 | 52 | 52 | 836640
170 | Chapainawabganj-100 MW | 100 | 100 | 100 | 100 | 100 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 85 | 91 | 90 | 90 | 90 | 90 | 1322302
171
172
173 | Rangpur GT | 13 | 13 | 14 | 14 | 14 | [14 empty] | 17 | 15 | 15 | 10 | 5 | 12 | 12 | 146000
175 | Saidpur GT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
176
177
178
178 | Western Zone Total | 2712 | 2624 | 2521 | 2486 | 2441 | 2204 | 2101 | 1994 | 1936 | 1975 | 1904 | 1907 | 1924 | 2072 | 2218 | 2169 | 1982 | 1964 | 0 | 2518 | 2782 | 2815 | 2809 | 2813 | 2820 | 2819 | 55875959
176
177