## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-07-26 | Thursday
|  | Date (day): | 2018-07-26 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10837 | MW |  |  | (b) At Evening Peak Hour : |  | 12112 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-07-25 | 2018-07-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 67 | 67 | 70 | 70 |  | 18
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 363 | 365 | 365 | 0
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 60 | 40 | 60 | 18
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 77 | 79 | 85 | 90 | 18 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 349 | 412 | 412 | 0 |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 96 | 98 | 98 |  | 12 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 250 | 222 | 303 | 300 |  |  | Gas shortage
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 350 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 250 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 16 | 68 | 42 | 81 |  | 19 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 48 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 87 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22 | 0
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 104 | 105 | 85 | 110 | 100 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 17 | 100 | 100 | 0
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 80 | 93 | 100 |  | 0
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | Under maint.
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 20 | 10 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 34 | 41 | 12 | 50
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 135 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 8 | 8 | 8 |  | 100 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 51 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 52 | 51 | 43 | 51
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 100 | 300 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 0 | 0 | 70 | 135 | 115 | 145
| Dhaka area Total |  |  |  |  | 5635 | 5399 | 2544 | 3416 | 3892 | 4161 | 461 | 863
37 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 16 | 16 | 16 |  | 9 | Engine problem
39 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 44 | 50 | 50
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 120 | 150 | 165 | 165 |  | 65 | # 3 under maint
41 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
42 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 201 | 202 | 213 | 213
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 50 | 50 | 100 | 135
44 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 50 | 51 | 51
45 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 9 | 83 | 74 | 84
46 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 45 | 51 | 51
47 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 90 | 80 | 90 |  | 10 | Engine problem
48 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 10 | 12 | 30
49 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 44 | 100 | 100 | 100 |  | 8 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 592 | 859 | 931 | 1004 | 360 | 135
50 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 100 |  | 135 | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 80 | 0 | 29 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34
51 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 185 | 220 | 225 |  |  | FGMO
52 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 350 | 360 | 360
53 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 272 | 360 | 360 |  |  | FGMO
54 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 43 | 20 | 43 | 43 |  | 2 | Engine problem
55 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
56 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 10 |  |  | Gas shortage
57 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 105 | 68 | 80 | 80 | 115 |  | Gas shortage
58 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 42 | 45 | 51 | 51
59 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 86 | 85 | 85 | 85
60 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
61 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST under maint.
62 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
63 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 120 | 170 | 112 | 160
64 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
65 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 3 | 52 | 52
66 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 15 | 20 | 22 |  | 3
67 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1628 | 1633 | 1834 | 2064 | 178 | 258
68 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 48 | 49 | 48 | 50 | 152 |  | Gas shortage
69 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
70 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 75 | 95 | 95
71 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.7 | 0 | 2 | 0
72 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 103 | 148 | 103 | 150
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 159.7 | 294 | 270 | 317 | 152 | 0
73 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 70 | 70 | 70 | 70
74 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 66 | 66 | 66 | 66
75 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 130 | 163 | 163
76 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 313 | 278 | 330 | 330
77 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 53 | 53
78 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 47 | 50 | 50
79 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
80 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 55 | 65 | 70
81 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 89 | 86 | 86
82 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 43 | 45 | 45 | 45
83 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 118 | 0 | 135 |  | 7
84 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
85 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 47 | 47 | 47 |  | 3
86 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 23 | 23 |  | 2
87 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 300 | 341 | 341 |  |  | FGMO
88 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 7 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1337 | 1339 | 1360 | 1500 | 0 | 32
89 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 460 | 461 | 427 | 481
90 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 5 | 101 | 101 | 101 |  |  | Engine problem
91 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 99 | 99 |  | 16 | Engine problem
92 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 37 | 44 | 37 | 42
93 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 244 | 210 | 230 | 230 |  | 0
94 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 26 | 85 | 28 | 80
95 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 407 | 419 | 410 | 410 | 0
96 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 40 | 40
97 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 55
98 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 1179 | 1501 | 1372 | 1670 | 0 | 16
99 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
100 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
101 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 32 | 33 | 33
102 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 179 | 178 | 178 | 194
103 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 91 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 205 | 411 | 416 | 462 | 0 | 0
104 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
105 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
106 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 44 | 0 | 44
107 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 50 | 50
108 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
109 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 0 | 45
110 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 185 | 200 | 223 | 220
111 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 177 | 202 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
112 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 34 | 35 | 35 | 35 |  | 50 | Transformer problem.
113 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18
114 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 11 | 10 | 10
115 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
116 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 40 | 52 | 52 | 52
117 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 25 | 101 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 580 | 854 | 762 | 898 | 71 | 157
118 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
119 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
120 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 17
121 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 0 | 33 | 0 | 36 | 0 | 444
| Total |  |  |  |  | 15953 | 15410 | 8224.7 | 10340 | 10837 | 12112 | 1222 | 1905
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7846.8729 | 9865 | 10339.1688 | 11555.5977
A. |  | 2018-07-25 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10340 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 6935.2 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10340 | MW
3 | Day peak Generation : |  |  | 8224.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9865 | MW
4 | Evening peak Generation : |  |  | 10340 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 203.245 | MKWHr | By Solar | 0.0056 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 133.0028 | MKWHr |  | By Oil: | 52.6539 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 0 | MKWHr |  | By Hydro: | 3.2652 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1222 | MW | Dhaka | 3763 | 3763 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1905 | MW | Chittagong | 1076 | 1076 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3127 | MW | Khulna | 1235 | 1235 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1054.62 | MMCFD |  |  | Rajshahi | 929 | 929 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 95793401.44 | ii) Oil : | Taka | 527317751.65 | Comilla | 950 | 950 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 0 | Total | Taka | 623111153.09 | Mymensingh | 745 | 745 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 4.317 | MKWHr. | Sylhet | 418 | 418 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -360 | MW at | 20:00 | hrs | Barisal | 245 | 245 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -460 | MW at | 19:30 | hrs | Rangpur | 504 | 504 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 9865 | 9865 |  | 0
B. |  | 2018-07-26 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12112 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8200 | MW
4 | Reserve(Generation end) |  |  |  | 1512 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 208.3556 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7328 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.0909 | MKWHr. | ii) HVDC Flow at Peak Time |  | 461 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2266 | MKWHr. | iii) Maximum HVDC Flow : |  | 462 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.21 |  | (b) Today: | 103.35 |  | (c) Rule Curve: |  | 88
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-07-25
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 67 | 0 | 0 | 0 | 345 | 25 | 40 | 345 | 283 | 0 | 0 | 400 | 200 | 45 | 15 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 60 | 10 | 8 | 10 | 41 | 54 | 18 | 55 | 19 | 25 | 32 | 25 | 33 | 48 | 0 | 38 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 50 | 0 | 15 | 80 | 73 | 18 | 19 | 38 | 0 | 80 | 100 | 290 | 242 | 150 | 68 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 22 | 11 | 33 | 16 | 140 | 50 | 64 | 22 | 0 | 70 | 66 | 53 | 50 | 163 | 305 | 56 | 86 | 45 | 78 | 0 | 47 | 9 | 270 | 23 | 11 | 0 | 301 | 0 | 0 | 64 | 0 | 151 |  | 461 | 0 | 415 | 5 | 32 | 120 | 0 | 0 | 37 | 22 | 8 | 178 | 33 | 96 | 0 | 0 | 0 | 50 | 44 | 25 | 40 | 43 | 44 | 51 | 0 | 7 | 10 | 8 | 0 | 0 | 0 | 16 | 18 | 221 | 0 | 150 | 0 | 95 | 0 | 0 | 0 |  | 6434 | 2229 | 8663 | 3754 | 461 | 1863 | 1625 | 0 | 118 | 702 | 140 | 0 | 0 | 103.16
2:00 | 67 | 0 | 0 | 0 | 345 | 25 | 40 | 345 | 293 | 0 | 0 | 410 | 200 | 12 | 15 | 15 | 0 | 0 | 103 | 0 | 7 | 7 | 65 | 10 | 8 | 0 | 41 | 18 | 18 | 36 | 19 | 25 | 32 | 25 | 33 | 51 | 0 | 38 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 50 | 0 | 15 | 80 | 53 | 18 | 0 | 38 | 0 | 80 | 100 | 290 | 242 | 222 | 68 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 22 | 11 | 33 | 16 | 138 | 49 | 64 | 22 | 0 | 70 | 66 | 53 | 50 | 163 | 306 | 61 | 50 | 45 | 78 | 0 | 47 | 9 | 305 | 23 | 11 | 0 | 244 | 0 | 0 | 55 | 0 | 41 |  | 462 | 0 | 414 | 5 | 32 | 120 | 0 | 0 | 37 | 20 | 8 | 178 | 32 | 80 | 0 | 0 | 0 | 50 | 44 | 25 | 40 | 43 | 44 | 17 | 0 | 10 | 10 | 8 | 0 | 0 | 0 | 17 | 18 | 220 | 0 | 155 | 0 | 96 | 0 | 0 | 0 |  | 6222 | 2185 | 8407 | 3814 | 462 | 1885 | 1284 | 0 | 118 | 706 | 138 | 0 | 0 | 103.17
3:00 | 67 | 0 | 0 | 0 | 345 | 25 | 40 | 345 | 312 | 0 | 0 | 430 | 200 | 7 | 15 | 15 | 0 | 0 | 103 | 0 | 7 | 7 | 65 | 10 | 8 | 0 | 6 | 18 | 18 | 36 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 38 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 50 | 0 | 0 | 80 | 53 | 18 | 16 | 39 | 0 | 80 | 100 | 290 | 242 | 222 | 68 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 8 | 16 | 126 | 50 | 64 | 22 | 0 | 70 | 66 | 53 | 50 | 163 | 312 | 61 | 86 | 45 | 78 | 0 | 47 | 9 | 300 | 23 | 11 | 0 | 114 | 0 | 0 | 55 | 0 | 16 |  | 462 | 0 | 415 | 5 | 32 | 120 | 0 | 0 | 37 | 0 | 8 | 178 | 28 | 16 | 0 | 0 | 0 | 50 | 44 | 25 | 40 | 43 | 44 | 8 | 0 | 10 | 10 | 8 | 0 | 0 | 0 | 17 | 18 | 220 | 0 | 145 | 0 | 96 | 0 | 0 | 0 |  | 6057 | 2079 | 8136 | 3800 | 462 | 1952 | 1007 | 0 | 118 | 671 | 126 | 0 | 0 | 103.18
4:00 | 67 | 0 | 0 | 0 | 345 | 25 | 40 | 345 | 312 | 0 | 0 | 450 | 200 | 7 | 15 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 65 | 10 | 8 | 0 | 6 | 18 | 18 | 36 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 38 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 24 | 0 | 0 | 78 | 30 | 18 | 19 | 40 | 0 | 80 | 100 | 290 | 242 | 222 | 68 | 100 | 43 | 0 | 5 | 42 | 50 | 0 | 8 | 22 | 11 | 8 | 16 | 120 | 48 | 64 | 22 | 0 | 70 | 66 | 53 | 50 | 130 | 311 | 61 | 50 | 45 | 78 | 0 | 47 | 9 | 300 | 23 | 11 | 0 | 100 | 0 | 0 | 55 | 0 | 16 |  | 462 | 0 | 420 | 5 | 32 | 120 | 0 | 0 | 37 | 0 | 8 | 178 | 27 | 16 | 0 | 0 | 0 | 50 | 44 | 25 | 40 | 43 | 44 | 8 | 0 | 13 | 10 | 8 | 0 | 0 | 0 | 17 | 18 | 221 | 0 | 145 | 0 | 95 | 0 | 0 | 0 |  | 5898 | 2086 | 7984 | 3810 | 462 | 1861 | 942 | 0 | 118 | 671 | 120 | 0 | 0 | 103.19
5:00 | 67 | 0 | 0 | 0 | 345 | 25 | 40 | 345 | 322 | 0 | 0 | 450 | 200 | 7 | 15 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 65 | 10 | 8 | 0 | 6 | 18 | 18 | 36 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 38 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 8 | 0 | 0 | 50 | 20 | 18 | 19 | 41 | 0 | 80 | 100 | 290 | 242 | 222 | 68 | 100 | 43 | 0 | 5 | 42 | 50 | 0 | 8 | 22 | 11 | 8 | 16 | 118 | 48 | 64 | 22 | 0 | 70 | 66 | 53 | 50 | 130 | 300 | 61 | 50 | 45 | 78 | 0 | 48 | 9 | 300 | 23 | 11 | 0 | 79 | 0 | 0 | 55 | 0 | 16 |  | 461 | 0 | 419 | 5 | 32 | 120 | 0 | 0 | 37 | 0 | 8 | 178 | 20 | 16 | 0 | 0 | 0 | 0 | 15 | 25 | 40 | 43 | 0 | 8 | 0 | 10 | 10 | 8 | 0 | 0 | 0 | 17 | 18 | 221 | 0 | 145 | 0 | 95 | 0 | 0 | 0 |  | 5822 | 1951 | 7773 | 3798 | 461 | 1863 | 867 | 0 | 118 | 548 | 118 | 0 | 0 | 103.2
6:00 | 67 | 0 | 0 | 0 | 300 | 25 | 40 | 340 | 322 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 0 | 0 | 105 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 6 | 18 | 18 | 17 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 38 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 8 | 0 | 0 | 30 | 20 | 18 | 19 | 41 | 0 | 80 | 100 | 290 | 242 | 222 | 68 | 100 | 43 | 0 | 5 | 6 | 30 | 0 | 0 | 22 | 11 | 8 | 16 | 118 | 49 | 8 | 22 | 0 | 70 | 66 | 53 | 50 | 100 | 302 | 50 | 30 | 45 | 78 | 0 | 47 | 9 | 270 | 23 | 11 | 0 | 49 | 0 | 0 | 55 | 0 | 16 |  | 462 | 0 | 350 | 5 | 16 | 120 | 0 | 0 | 37 | 0 | 8 | 153 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 8 | 0 | 8 | 0 | 10 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 221 | 0 | 165 | 0 | 11 | 0 | 0 | 0 |  | 5428 | 1658 | 7086 | 3667 | 462 | 1589 | 651 | 0 | 118 | 481 | 118 | 0 | 0 | 103.21
7:00 | 67 | 0 | 0 | 0 | 300 | 25 | 40 | 340 | 315 | 0 | 0 | 380 | 200 | 7 | 15 | 15 | 0 | 0 | 105 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 6 | 18 | 18 | 17 | 19 | 25 | 32 | 25 | 33 | 42 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 8 | 0 | 0 | 30 | 20 | 18 | 19 | 26 | 0 | 80 | 100 | 290 | 242 | 222 | 68 | 100 | 43 | 0 | 5 | 6 | 11 | 0 | 0 | 22 | 11 | 8 | 16 | 104 | 50 | 8 | 22 | 0.2 | 70 | 66 | 22 | 50 | 100 | 301 | 60 | 10 | 10 | 78 | 0 | 46 | 9 | 280 | 23 | 11 | 0 | 49 | 0 | 0 | 55 | 0 | 16 |  | 462 | 0 | 300 | 5 | 0 | 150 | 0 | 0 | 37 | 22 | 0 | 154 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 8 | 0 | 8 | 0 | 10 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 185 | 0 | 11 | 0 | 0 | 0 |  | 5288.2 | 1647 | 6935.2 | 3647 | 462 | 1454 | 615 | 0 | 120 | 533 | 104 | 0.2 | 0 | 103.22
8:00 | 67 | 0 | 0 | 0 | 300 | 25 | 40 | 345 | 303 | 0 | 0 | 380 | 200 | 7 | 15 | 15 | 0 | 0 | 40 | 0 | 7 | 7 | 48 | 10 | 8 | 10 | 6 | 18 | 18 | 17 | 19 | 25 | 25 | 25 | 33 | 43 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 199 | 0 | 50 | 0 | 8 | 0 | 0 | 30 | 20 | 18 | 19 | 12 | 0 | 80 | 100 | 290 | 268 | 220 | 68 | 100 | 43 | 0 | 5 | 6 | 11 | 0 | 0 | 22 | 11 | 8 | 16 | 102 | 50 | 8 | 22 | 0.6 | 70 | 66 | 22 | 47 | 100 | 307 | 60 | 10 | 10 | 78 | 0 | 46 | 9 | 280 | 23 | 11 | 0 | 47 | 0 | 0 | 55 | 0 | 16 |  | 462 | 0 | 305 | 5 | 0 | 195 | 0 | 0 | 37 | 28 | 0 | 154 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 8 | 0 | 8 | 0 | 10 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 223 | 0 | 201 | 0 | 11 | 0 | 0 | 0 |  | 5227.6 | 1722 | 6949.6 | 3634 | 462 | 1425 | 624 | 0 | 120 | 582 | 102 | 0.6 | 0 | 102.96
9:00 | 67 | 0 | 0 | 0 | 330 | 25 | 60 | 360 | 290 | 0 | 0 | 420 | 200 | 7 | 15 | 15 | 0 | 0 | 70 | 0 | 7 | 7 | 82 | 10 | 8 | 10 | 6 | 18 | 18 | 17 | 19 | 25 | 25 | 25 | 33 | 48 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 208 | 0 | 50 | 0 | 8 | 0 | 0 | 30 | 20 | 18 | 19 | 5 | 0 | 80 | 100 | 320 | 309 | 200 | 68 | 100 | 43 | 0 | 5 | 6 | 11 | 0 | 0 | 22 | 11 | 8 | 16 | 114 | 50 | 8 | 22 | 0.2 | 70 | 66 | 40 | 47 | 130 | 320 | 60 | 10 | 10 | 80 | 0 | 45 | 9 | 320 | 23 | 11 | 0 | 47 | 0 | 0 | 55 | 0 | 16 |  | 462 | 0 | 414 | 5 | 0 | 244 | 0 | 0 | 37 | 27 | 0 | 178 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 32 | 0 | 25 | 20 | 15 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 209 | 0 | 196 | 0 | 11 | 0 | 0 | 0 |  | 5555.2 | 1976 | 7531.2 | 3889 | 462 | 1555 | 698 | 0 | 120 | 693 | 114 | 0.2 | 0 | 102.95
10:00 | 67 | 0 | 0 | 0 | 365 | 79 | 73 | 350 | 281 | 0 | 0 | 420 | 200 | 7 | 15 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 115 | 10 | 8 | 10 | 6 | 18 | 18 | 17 | 19 | 25 | 25 | 25 | 33 | 52 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 50 | 0 | 8 | 9 | 0 | 53 | 20 | 18 | 16 | 6 | 0 | 100 | 100 | 355 | 300 | 185 | 103 | 100 | 37 | 0 | 5 | 20 | 85 | 0 | 0 | 22 | 11 | 33 | 0 | 114 | 50 | 8 | 22 | 0 | 70 | 66 | 49 | 47 | 130 | 312 | 60 | 84 | 45 | 100 | 0 | 45 | 9 | 305 | 23 | 11 | 0 | 50 | 0 | 0 | 55 | 0 | 16 |  | 461 | 0 | 418 | 5 | 0 | 244 | 0 | 0 | 37 | 26 | 0 | 178 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 43 | 0 | 25 | 34 | 18 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 182 | 0 | 11 | 0 | 0 | 0 |  | 6008 | 1966 | 7974 | 3961 | 461 | 1844 | 732 | 0 | 120 | 742 | 114 | 0 | 0 | 102.95
11:00 | 67 | 0 | 0 | 0 | 365 | 78 | 73 | 345 | 270 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 122 | 10 | 8 | 21 | 34 | 18 | 19 | 30 | 19 | 25 | 25 | 25 | 33 | 52 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 50 | 0 | 20 | 9 | 0 | 80 | 20 | 18 | 16 | 6 | 0 | 100 | 100 | 360 | 300 | 183 | 105 | 100 | 37 | 0 | 5 | 45 | 85 | 0 | 0 | 22 | 11 | 33 | 16 | 122 | 50 | 8 | 22 | 0.2 | 70 | 66 | 53 | 47 | 130 | 312 | 57 | 84 | 43 | 90 | 0 | 45 | 9 | 300 | 23 | 8 | 0 | 90 | 0 | 0 | 74 | 0 | 16 |  | 461 | 0 | 411 | 5 | 0 | 245 | 0 | 0 | 37 | 26 | 0 | 179 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 43 | 0 | 25 | 33 | 15 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 176 | 0 | 11 | 0 | 0 | 0 |  | 6164.2 | 1946 | 8110.2 | 3942 | 461 | 1833 | 883 | 0 | 120 | 749 | 122 | 0.2 | 0 | 102.94
12:00 | 67 | 0 | 0 | 0 | 365 | 77 | 40 | 345 | 250 | 0 | 0 | 400 | 200 | 7 | 16 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 133 | 10 | 8 | 20 | 34 | 18 | 36 | 36 | 19 | 25 | 25 | 25 | 33 | 52 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 32 | 9 | 0 | 80 | 44 | 25 | 16 | 7 | 0 | 100 | 100 | 360 | 300 | 185 | 105 | 100 | 43 | 0 | 5 | 42 | 86 | 0 | 0 | 22 | 11 | 33 | 16 | 120 | 48 | 8 | 0 | 0.7 | 70 | 66 | 53 | 47 | 130 | 313 | 59 | 84 | 43 | 80 | 0 | 44 | 9 | 305 | 23 | 11 | 0 | 100 | 0 | 0 | 103 | 0 | 70 |  | 460 | 0 | 407 | 5 | 0 | 244 | 0 | 0 | 37 | 26 | 0 | 179 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 40 | 34 | 18 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 177 | 0 | 11 | 0 | 0 | 0 |  | 6260.7 | 1964 | 8224.7 | 3920 | 460 | 1781 | 1064 | 0 | 120 | 759 | 120 | 0.7 | 0 | 102.93
13:00 | 67 | 0 | 0 | 0 | 365 | 55 | 40 | 345 | 230 | 0 | 0 | 370 | 200 | 7 | 46 | 30 | 0 | 0 | 103 | 0 | 7 | 7 | 133 | 10 | 8 | 21 | 41 | 18 | 36 | 36 | 0 | 25 | 25 | 25 | 33 | 43 | 0 | 70 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 32 | 0 | 0 | 80 | 53 | 16 | 16 | 2 | 0 | 100 | 100 | 340 | 305 | 170 | 68 | 100 | 43 | 0 | 5 | 42 | 85 | 0 | 0 | 22 | 8 | 33 | 15 | 130 | 48 | 8 | 22 | 0.6 | 70 | 65 | 53 | 47 | 130 | 302 | 59 | 84 | 43 | 80 | 0 | 45 | 9 | 310 | 23 | 11 | 0 | 100 | 0 | 0 | 103 | 0 | 115 |  | 460 | 0 | 410 | 5 | 0 | 245 | 0 | 0 | 37 | 27 | 0 | 179 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 52 | 33 | 18 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 176 | 0 | 11 | 0 | 0 | 0 |  | 6227.6 | 1980 | 8207.6 | 3877 | 460 | 1674 | 1165 | 0 | 150 | 751 | 130 | 0.6 | 0 | 102.92
14:00 | 67 | 0 | 0 | 0 | 330 | 55 | 40 | 330 | 222 | 0 | 0 | 350 | 200 | 7 | 48 | 30 | 0 | 0 | 102 | 0 | 7 | 7 | 128 | 10 | 8 | 21 | 40 | 18 | 36 | 36 | 0 | 25 | 25 | 25 | 33 | 43 | 0 | 70 | 80 | 0 | 0 | 8 | 0 | 208 | 0 | 50 | 0 | 35 | 0 | 0 | 80 | 53 | 39 | 16 | 3 | 0 | 100 | 100 | 340 | 298 | 150 | 68 | 100 | 43 | 0 | 5 | 42 | 85 | 0 | 0 | 22 | 8 | 33 | 16 | 130 | 48 | 8 | 22 | 0.9 | 70 | 65 | 53 | 47 | 163 | 305 | 59 | 84 | 40 | 80 | 0 | 45 | 9 | 300 | 23 | 5 | 0 | 100 | 0 | 0 | 103 | 0 | 115 |  | 461 | 0 | 410 | 5 | 0 | 248 | 0 | 0 | 0 | 21 | 0 | 179 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 52 | 34 | 18 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 183 | 0 | 48 | 0 | 0 | 0 |  | 6169.9 | 1994 | 8163.9 | 3810 | 461 | 1706 | 1192 | 0 | 150 | 714 | 130 | 0.9 | 0 | 103.29
15:00 | 67 | 0 | 0 | 0 | 365 | 77 | 40 | 331 | 207 | 0 | 0 | 340 | 305 | 35 | 48 | 42 | 0 | 0 | 102 | 0 | 15 | 40 | 117 | 35 | 8 | 21 | 40 | 18 | 37 | 55 | 0 | 25 | 25 | 25 | 33 | 46 | 0 | 70 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 135 | 0 | 50 | 0 | 0 | 80 | 53 | 43 | 16 | 2 | 0 | 100 | 100 | 330 | 276 | 152 | 68 | 100 | 20 | 0 | 5 | 42 | 85 | 0 | 0 | 22 | 8 | 33 | 0 | 144 | 48 | 8 | 22 | 0.7 | 70 | 65 | 53 | 48 | 163 | 279 | 59 | 83 | 42 | 131 | 0 | 44 | 9 | 320 | 21 | 11 | 0 | 100 | 0 | 0 | 103 | 0 | 115 |  | 461 | 0 | 411 | 5 | 0 | 248 | 0 | 0 | 0 | 17 | 0 | 179 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 51 | 34 | 0 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 195 | 0 | 49 | 0 | 0 | 0 |  | 6518.7 | 1999 | 8517.7 | 3829 | 461 | 1710 | 1444 | 0 | 150 | 779 | 144 | 0.7 | 0 | 103.3
16:00 | 67 | 0 | 0 | 0 | 364 | 76 | 40 | 331 | 206 | 0 | 0 | 330 | 250 | 83 | 48 | 47 | 0 | 0 | 103 | 0 | 40 | 7 | 117 | 40 | 8 | 20 | 40 | 18 | 56 | 55 | 0 | 25 | 25 | 25 | 33 | 47 | 0 | 70 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 70 | 0 | 50 | 0 | 0 | 80 | 53 | 44 | 19 | 3 | 0 | 100 | 100 | 330 | 272 | 167 | 68 | 100 | 20 | 0 | 5 | 42 | 85 | 0 | 0 | 22 | 8 | 33 | 0 | 138 | 48 | 8 | 22 | 0.5 | 70 | 66 | 53 | 47 | 163 | 286 | 59 | 84 | 42 | 133 | 0 | 44 | 9 | 300 | 21 | 11 | 0 | 100 | 0 | 0 | 104 | 0 | 115 |  | 460 | 0 | 413 | 5 | 0 | 200 | 0 | 0 | 0 | 21 | 8 | 178 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 51 | 33 | 0 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 161 | 0 | 51 | 0 | 0 | 0 |  | 6455.5 | 1928 | 8383.5 | 3802 | 460 | 1681 | 1484 | 0 | 150 | 668 | 138 | 0.5 | 0 | 103.31
17:00 | 67 | 0 | 0 | 0 | 365 | 78 | 40 | 330 | 206 | 0 | 0 | 330 | 200 | 83 | 48 | 48 | 0 | 0 | 104 | 0 | 60 | 7 | 120 | 10 | 8 | 21 | 40 | 18 | 56 | 55 | 19 | 25 | 25 | 25 | 33 | 51 | 0 | 70 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 50 | 0 | 50 | 0 | 0 | 80 | 53 | 44 | 19 | 7 | 0 | 100 | 100 | 330 | 272 | 178 | 68 | 100 | 20 | 0 | 5 | 34 | 85 | 0 | 0 | 22 | 8 | 33 | 0 | 128 | 49 | 8 | 22 | 0.5 | 70 | 66 | 53 | 47 | 163 | 281 | 50 | 86 | 42 | 78 | 0 | 43 | 9 | 300 | 21 | 11 | 0 | 100 | 0 | 0 | 104 | 0 | 117 |  | 461 | 0 | 416 | 5 | 0 | 150 | 0 | 0 | 0 | 40 | 8 | 178 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 51 | 33 | 0 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 178 | 0 | 50 | 0 | 0 | 0 |  | 6338.5 | 1921 | 8259.5 | 3789 | 461 | 1679 | 1432 | 0 | 150 | 620 | 128 | 0.5 | 0 | 103.31
18:00 | 67 | 0 | 0 | 0 | 280 | 78 | 40 | 330 | 206 | 0 | 0 | 340 | 200 | 54 | 45 | 48 | 0 | 0 | 103 | 0 | 40 | 7 | 125 | 10 | 8 | 10 | 41 | 54 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 70 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 50 | 8 | 0 | 90 | 53 | 44 | 19 | 4 | 0 | 100 | 100 | 345 | 272 | 177 | 68 | 100 | 30 | 0 | 5 | 38 | 21 | 5 | 0 | 22 | 8 | 33 | 0 | 128 | 48 | 8 | 22 | 0.2 | 70 | 66 | 22 | 20 | 100 | 280 | 59 | 20 | 20 | 78 | 0 | 23 | 7 | 270 | 23 | 11 | 0 | 228 | 0 | 0 | 104 | 0 | 117 |  | 461 | 0 | 380 | 5 | 5 | 120 | 0 | 0 | 0 | 63 | 8 | 178 | 21 | 16 | 0 | 0 | 0 | 0 | 10 | 25 | 40 | 43 | 25 | 25 | 35 | 15 | 11 | 8 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 172 | 0 | 50 | 0 | 0 | 0 |  | 6101.2 | 1898 | 7999.2 | 3691 | 461 | 1379 | 1523 | 0 | 150 | 667 | 128 | 0.2 | 0 | 103.32
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9
19:00 | 67 | 0 | 0 | 0 | 353 | 78 | 60 | 343 | 221 | 55 | 0 | 350 | 200 | 69 | 48 | 48 | 0 | 0 | 103 | 7 | 50 | 102 | 135 | 70 | 8 | 10 | 41 | 54 | 56 | 55 | 19 | 25 | 22 | 25 | 33 | 51 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 205 | 0 | 50 | 0 | 50 | 84 | 20 | 90 | 96 | 44 | 19 | 13 | 0 | 100 | 100 | 350 | 305 | 169 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 49 | 0 | 22 | 11 | 33 | 0 | 166 | 48 | 50 | 22 | 0 | 70 | 66 | 31 | 28 | 130 | 282 | 64 | 50 | 20 | 98 | 0 | 45 | 7 | 300 | 23 | 11 | 0 | 300 | 0 | 0 | 148 | 0 | 117 |  | 461 | 0 | 413 | 79 | 66 | 135 | 0 | 0 | 42 | 93 | 33 | 178 | 27 | 80 | 0 | 0 | 0 | 50 | 44 | 75 | 40 | 43 | 45 | 51 | 35 | 18 | 11 | 11 | 0 | 0 | 0 | 17 | 0 | 188 | 0 | 180 | 0 | 73 | 14 | 0 | 0 |  | 7133 | 2502 | 9635 | 3873 | 461 | 1665 | 2241 | 0 | 150 | 1079 | 166 | 0 | 0 | 103.32
19:30 | 67 | 0 | 0 | 0 | 364 | 79 | 60 | 349 | 222 | 75 | 0 | 350 | 270 | 100 | 60 | 48 | 0 | 0 | 104 | 15 | 60 | 102 | 135 | 87 | 8 | 10 | 41 | 54 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 50 | 83 | 45 | 90 | 100 | 44 | 19 | 8 | 0 | 100 | 100 | 350 | 305 | 177 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 49 | 0 | 22 | 11 | 33 | 15 | 170 | 50 | 58 | 22 | 0 | 70 | 66 | 53 | 47 | 163 | 280 | 65 | 86 | 42 | 128 | 0 | 47 | 7 | 320 | 23 | 11 | 0 | 300 | 0 | 0 | 148 | 0 | 135 |  | 460 | 0 | 416 | 97 | 83 | 165 | 0 | 0 | 44 | 80 | 32 | 179 | 31 | 100 | 0 | 0 | 0 | 42 | 44 | 101 | 40 | 43 | 45 | 51 | 35 | 18 | 11 | 11 | 0 | 0 | 0 | 15 | 18 | 200 | 0 | 206 | 0 | 90 | 50 | 0 | 0 |  | 7583 | 2707 | 10290 | 3991 | 460 | 1837 | 2529 | 0 | 150 | 1153 | 170 | 0 | 0 | 0
20:00 | 67 | 0 | 0 | 0 | 363 | 79 | 60 | 349 | 222 | 96 | 0 | 350 | 250 | 100 | 68 | 48 | 0 | 0 | 105 | 17 | 80 | 102 | 135 | 87 | 8 | 10 | 41 | 54 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 50 | 83 | 45 | 90 | 100 | 44 | 19 | 10 | 0 | 100 | 100 | 350 | 272 | 185 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 49 | 3 | 22 | 11 | 33 | 15 | 170 | 49 | 75 | 22 | 0 | 70 | 66 | 53 | 47 | 130 | 278 | 55 | 89 | 45 | 118 | 0 | 47 | 7 | 300 | 23 | 11 | 0 | 300 | 0 | 0 | 148 | 0 | 135 |  | 461 | 0 | 419 | 101 | 99 | 210 | 0 | 0 | 44 | 85 | 32 | 178 | 32 | 110 | 0 | 0 | 0 | 50 | 44 | 101 | 40 | 43 | 47 | 52 | 35 | 18 | 11 | 11 | 0 | 0 | 0 | 15 | 18 | 200 | 0 | 202 | 0 | 91 | 50 | 0 | 0 |  | 7541 | 2799 | 10340 | 3941 | 461 | 1794 | 2611 | 0 | 150 | 1213 | 170 | 0 | 0 | 103.32
21:00 | 67 | 0 | 0 | 0 | 365 | 79 | 60 | 349 | 222 | 106 | 0 | 350 | 200 | 100 | 80 | 48 | 0 | 0 | 103 | 0 | 100 | 102 | 135 | 87 | 8 | 0 | 41 | 54 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 105 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 50 | 82 | 45 | 90 | 100 | 44 | 19 | 23 | 0 | 100 | 100 | 350 | 272 | 185 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 14 | 22 | 11 | 33 | 15 | 172 | 48 | 95 | 22 | 0 | 70 | 66 | 53 | 47 | 130 | 276 | 61 | 89 | 45 | 118 | 0 | 47 | 7 | 290 | 23 | 11 | 0 | 300 | 0 | 0 | 148 | 0 | 136 |  | 461 | 0 | 417 | 98 | 99 | 200 | 0 | 0 | 44 | 74 | 33 | 178 | 34 | 110 | 0 | 0 | 0 | 42 | 44 | 101 | 40 | 43 | 45 | 51 | 35 | 18 | 11 | 11 | 0 | 0 | 0 | 14 | 18 | 200 | 0 | 206 | 0 | 95 | 50 | 0 | 0 |  | 7531 | 2772 | 10303 | 3946 | 461 | 1803 | 2605 | 0 | 185 | 1131 | 172 | 0 | 0 | 0
22:00 | 67 | 0 | 0 | 0 | 365 | 79 | 72 | 349 | 222 | 55 | 0 | 350 | 200 | 100 | 81 | 48 | 0 | 0 | 102 | 0 | 100 | 64 | 133 | 87 | 8 | 0 | 41 | 54 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 105 | 50 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 50 | 76 | 33 | 80 | 100 | 44 | 19 | 36 | 0 | 100 | 100 | 350 | 283 | 173 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 16 | 22 | 11 | 33 | 15 | 172 | 48 | 95 | 22 | 0 | 70 | 66 | 53 | 47 | 130 | 275 | 65 | 89 | 45 | 78 | 0 | 47 | 7 | 290 | 23 | 11 | 0 | 300 | 0 | 0 | 148 | 0 | 136 |  | 460 | 0 | 416 | 98 | 99 | 150 | 0 | 0 | 44 | 73 | 40 | 169 | 33 | 110 | 0 | 0 | 0 | 43 | 44 | 101 | 40 | 43 | 45 | 52 | 35 | 18 | 5 | 11 | 0 | 0 | 0 | 14 | 18 | 200 | 0 | 201 | 0 | 97 | 50 | 0 | 0 |  | 7371 | 2709 | 10080 | 3892 | 460 | 1823 | 2517 | 0 | 155 | 1061 | 172 | 0 | 0 | 103.13
23:00 | 67 | 0 | 0 | 0 | 365 | 79 | 72 | 349 | 222 | 20 | 0 | 350 | 200 | 40 | 81 | 48 | 0 | 0 | 103 | 0 | 50 | 7 | 120 | 50 | 8 | 0 | 41 | 54 | 55 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 105 | 50 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 50 | 76 | 45 | 80 | 100 | 41 | 19 | 37 | 0 | 100 | 100 | 350 | 272 | 180 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 16 | 22 | 11 | 33 | 22 | 163 | 48 | 95 | 22 | 0 | 70 | 66 | 53 | 47 | 130 | 278 | 65 | 89 | 45 | 78 | 0 | 47 | 7 | 300 | 23 | 11 | 0 | 301 | 0 | 0 | 146 | 0 | 138 |  | 461 | 0 | 416 | 101 | 99 | 150 | 0 | 0 | 44 | 70 | 40 | 174 | 33 | 110 | 0 | 0 | 0 | 43 | 44 | 101 | 40 | 43 | 45 | 52 | 35 | 18 | 5 | 11 | 0 | 0 | 0 | 14 | 16 | 200 | 0 | 201 | 0 | 98 | 50 | 0 | 0 |  | 7136 | 2714 | 9850 | 3904 | 461 | 1835 | 2278 | 0 | 155 | 1054 | 163 | 0 | 0 | 103.14
24:00 | 67 | 0 | 0 | 0 | 365 | 79 | 60 | 349 | 222 | 0 | 0 | 350 | 200 | 9 | 30 | 48 | 0 | 0 | 105 | 0 | 7 | 7 | 98 | 50 | 8 | 0 | 38 | 36 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 105 | 50 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 51 | 76 | 48 | 80 | 100 | 43 | 19 | 37 | 0 | 100 | 100 | 350 | 272 | 187 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 16 | 22 | 11 | 33 | 22 | 158 | 49 | 95 | 22 | 0 | 70 | 66 | 53 | 47 | 130 | 280 | 66 | 89 | 45 | 77 | 0 | 47 | 7 | 280 | 23 | 11 | 0 | 300 | 0 | 0 | 149 | 0 | 154 |  | 461 | 0 | 420 | 100 | 99 | 150 | 0 | 0 | 38 | 60 | 40 | 151 | 31 | 110 | 0 | 0 | 0 | 43 | 43 | 99 | 40 | 43 | 45 | 52 | 35 | 18 | 5 | 11 | 0 | 0 | 0 | 14 | 16 | 200 | 0 | 201 | 0 | 97 | 20 | 0 | 0 |  | 6948 | 2642 | 9590 | 3897 | 461 | 1800 | 2103 | 0 | 155 | 1016 | 158 | 0 | 0 | 103.15
KWH | 1364000 | 0 | 0 | 0 | 8079345 | 1320409 | 1495872 | 8280060 | 6131000 | 303700 | 0 | 8458250 | 5303215 | 861120 | 942576 | 755515 | 0 | 0 | 2460000 | 28800 | 820800 | 549072 | 2454720 | 702922 | 182400 | 219290 | 710112 | 703080 | 856808 | 976000 | 365652 | 600000 | 635400 | 617000 | 840500 | 1160988 | 0 | 1445513 | 1819700 | 0 | 0 | 236160 | 0 | 4783882 | 0 | 1340192 | 0 | 857280 | 462890 | 252343 | 1644120 | 1328640 | 728640 | 417840 | 432480 | 0 | 2216480 | 2394302 | 8110000 | 6680000 | 4562000 | 1756363 | 2376580 | 814032 | 0 | 120000 | 821650 | 942576 | 118456 | 116102 | 514656 | 239040 | 636000 | 305610 | 3226560 | 1190760 | 937920 | 493164 | 5600 | 1611000 | 1584000 | 1145400 | 1104000 | 3365632 | 6743475 | 1410000 | 1620480 | 876240 | 2160880 | 0 | 1068180 | 198180 | 7489300 | 541702 | 247632 | 0 | 2491526 | 0 | 0 | 2229600 | 0 | 3334580 |  | 11090909 | 0 | 9648576 | 588000 | 714240 | 4282560 | 0 | 0 | 691680 | 799618 | 270000 | 4256220 | 568625 | 860160 | 0 | 0 | 0 | 457384 | 463448 | 984638 | 896320 | 882912 | 442230 | 825600 | 509150 | 299520 | 235368 | 215910 | 0 | 0 | 0 | 164000 | 177000 | 5112545 | 0 | 4490472 | 0 | 1338442 | 251520 | 0 | 0 |  | 151727944 | 51517047 | 203244991 | 92214833 | 11090909 | 40787967 | 34269718 | 0 | 3265213 | 18384191 | 3226560 | 5600 | 0
Fuel Cost | 1173040 | 0 | 0 | 0 | 5170780.8 | 1069531.29 | 1406119.68 | 5050836.6 | 3739910 | 2918557 | 0 | 5667027.5 | 80555835.85 | 5407833.6 | 6296407.68 | 4616196.65 | 0 | 0 | 2730600 | 448128 | 5130000 | 3618384.48 | 23737142.4 | 4477613.14 | 1092576 | 3506447.1 | 4736447.04 | 5012960.4 | 5355050 | 6119520 | 274239 | 450000 | 0 | 0 | 0 | 10982946.48 | 0 | 0 | 0 | 0 | 0 | 2236435.2 | 0 | 65299989.3 | 0 | 29363606.72 | 0 | 7535491.2 | 4985325.3 | 2455297.39 | 10177102.8 | 8583014.4 | 4765305.6 | 355164 | 0 | 0 | 2016996.8 | 2178814.82 | 5028200 | 4609200 | 3193400 | 1211890.47 | 2281516.8 | 545401.44 | 0 | 110400 | 673753 | 895447.2 | 1284063.04 | 861476.84 | 396285.12 | 179280 | 489720 | 229207.5 | 22069670.4 | 893070 | 8619484.8 | 379736.28 | 0 | 1675440 | 1647360 | 1099584 | 993600 | 2625192.96 | 4720432.5 | 1607400 | 1733913.6 | 963864 | 2463403.2 | 0 | 993407.4 | 184307.4 | 4793152 | 406276.5 | 188200.32 | 0 | 18088478.76 | 0 | 0 | 15941640 | 0 | 0 |  | 56563635.9 | 0 | 6464545.92 | 4709880 | 5921049.6 | 68863564.8 | 0 | 0 | 7788316.8 | 9419500.04 | 2127600 | 2936791.8 | 562938.75 | 6365184 | 0 | 0 | 0 | 5237046.8 | 4968162.56 | 8822356.48 | 7753168 | 7857916.8 | 4709749.5 | 8189952 | 5992695.5 | 329472 | 221245.92 | 163443.87 | 0 | 0 | 0 | 5285720 | 4738290 | 3476530.6 | 0 | 3143330.4 | 0 | 0 | 4358841.6 | 0 | 0 |  | 454773529.75 | 246970929.64 | 701744459.39 | 66518644.27 | 56563635.9 | 29274757.17 | 274366925.02 | 0 | 0 | 252950826.63 | 22069670.4 | 0 | 0
Yesterday Day Peak | 67 | 0 | 0 | 0 | 365 | 77 | 40 | 345 | 250 | 0 | 0 | 400 | 200 | 7 | 16 | 15 | 0 | 0 | 104 | 0 | 7 | 7 | 133 | 10 | 8 | 20 | 34 | 18 | 36 | 36 | 19 | 25 | 25 | 25 | 33 | 52 | 0 | 40 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 32 | 9 | 0 | 80 | 44 | 25 | 16 | 7 | 0 | 100 | 100 | 360 | 300 | 185 | 105 | 100 | 43 | 0 | 5 | 42 | 86 | 0 | 0 | 22 | 11 | 33 | 16 | 120 | 48 | 8 | 0 | 0.7 | 70 | 66 | 53 | 47 | 130 | 313 | 59 | 84 | 43 | 80 | 0 | 44 | 9 | 305 | 23 | 11 | 0 | 100 | 0 | 0 | 103 | 0 | 70 |  | 460 | 0 | 407 | 5 | 0 | 244 | 0 | 0 | 37 | 26 | 0 | 179 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 40 | 34 | 18 | 10 | 8 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 177 | 0 | 11 | 0 | 0 | 0 |  | 8224.7 | DayPeak
Yesterday Evening Peak | 67 | 0 | 0 | 0 | 363 | 79 | 60 | 349 | 222 | 96 | 0 | 350 | 250 | 100 | 68 | 48 | 0 | 0 | 105 | 17 | 80 | 102 | 135 | 87 | 8 | 10 | 41 | 54 | 56 | 55 | 19 | 25 | 26 | 25 | 33 | 51 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 50 | 83 | 45 | 90 | 100 | 44 | 19 | 10 | 0 | 100 | 100 | 350 | 272 | 185 | 68 | 100 | 20 | 0 | 5 | 45 | 85 | 49 | 3 | 22 | 11 | 33 | 15 | 170 | 49 | 75 | 22 | 0 | 70 | 66 | 53 | 47 | 130 | 278 | 55 | 89 | 45 | 118 | 0 | 47 | 7 | 300 | 23 | 11 | 0 | 300 | 0 | 0 | 148 | 0 | 135 |  | 461 | 0 | 419 | 101 | 99 | 210 | 0 | 0 | 44 | 85 | 32 | 178 | 32 | 110 | 0 | 0 | 0 | 50 | 44 | 101 | 40 | 43 | 47 | 52 | 35 | 18 | 11 | 11 | 0 | 0 | 0 | 15 | 18 | 200 | 0 | 202 | 0 | 91 | 50 | 0 | 0 |  | 10340 | EvPeak
Forecast for Evening | 70 | 0 | 0 | 0 | 365 | 90 | 60 | 412 | 300 | 98 | 0 | 450 | 305 | 100 | 81 | 55 | 0 | 0 | 110 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 50 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 213 | 0 | 135 | 0 | 51 | 84 | 51 | 90 | 100 | 50 | 19 | 30 | 100 | 0 | 100 | 360 | 360 | 225 | 80 | 100 | 43 | 0 | 10 | 51 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 160 | 50 | 95 | 22 | 0 | 70 | 66 | 53 | 50 | 163 | 330 | 70 | 86 | 45 | 135 | 0 | 47 | 10 | 341 | 23 | 11 | 200 | 300 | 0 | 100 | 150 | 100 | 145 |  | 481 | 32 | 410 | 101 | 99 | 230 | 0 | 55 | 42 | 80 | 40 | 194 | 33 | 110 | 30 | 0 | 0 | 50 | 44 | 100 | 50 | 43 | 45 | 52 | 35 | 18 | 10 | 11 | 0 | 0 | 0 | 17 | 19 | 220 | 0 | 220 | 0 | 95 | 100
Forecast for Day | 70 | 0 | 0 | 0 | 365 | 85 | 40 | 412 | 303 | 98 | 0 | 450 | 305 | 100 | 42 | 55 | 0 | 0 | 85 | 100 | 93 | 102 | 149 | 100 | 8 | 50 | 12 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 43 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 213 | 0 | 100 | 0 | 51 | 74 | 51 | 80 | 100 | 50 | 19 | 12 | 0 | 80 | 100 | 360 | 360 | 220 | 80 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 20 | 112 | 48 | 95 | 22 | 2 | 70 | 66 | 53 | 50 | 163 | 330 | 65 | 86 | 45 | 0 | 0 | 47 | 10 | 341 | 23 | 11 | 100 | 300 | 0 | 0 | 103 | 100 | 115 |  | 427 | 0 | 410 | 101 | 99 | 230 | 0 | 0 | 37 | 28 | 40 | 178 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 0 | 52 | 35 | 18 | 10 | 11 | 0 | 0 | 0 |  | 0 | 223 | 0 | 220 | 0 | 95 | 0
Generation at 08:00(Today) | 67 | 0 | 0 | 0 | 300 | 25 | 40 | 360 | 297 | 0 | 0 | 350 | 200 | 7 | 15 | 15 | 0 | 0 | 85 | 0 | 7 | 7 | 48 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 17 | 25 | 32 | 25 | 33 | 30 | 0 | 105 | 80 | 0 | 0 | 0 | 0 | 222 | 0 | 50 | 0 | 8 | 16 | 17 | 80 | 25 | 6 | 19 | 6 | 0 | 100 | 100 | 350 | 327 | 152 | 80 | 100 | 20 | 0 | 5 | 40 | 21 | 0 | 0 | 22 | 11 | 8 | 15 | 106 | 49 | 8 | 22 | 0.6 | 70 | 66 | 5 | 44 | 100 | 310 | 65 | 20 | 5 | 0 | 0 | 47 | 7 | 290 | 23 | 11 | 0 | 48 | 0 | 0 | 103 | 0 | 115 | 0 | 427 | 0 | 300 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 178 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 99 | 33 | 43 | 0 | 8 | 35 | 18 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 202 | 0 | 71 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6935.2 | 7:00
| Highest Generation |  | 10340 | 20:00
| Day Peak Generation |  | 8224.7 | 12:00
| Evening Peak Generation |  | 10340 | 20:00
| HVDC Max Flow |  | 462 | 2:00
| HVDC EvPeak Flow |  | 461 | 20:00
| Load factor L.F |  | 81.9%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-07-26
Till now the maximum generation is : - |  |  | 11387 | 22:00 | Hrs on | 2018-07-18
The Summary of Yesterday's |  | 2018-07-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8224.7 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7328 | MW
Evening Peak Generation : |  | 10340 | MW Hour : | 20:00 | Available Max Generation : |  | 12112 | MW
E.P. Demand (at gen end) : |  | 10340 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10600 | MW
Maximum Generation : |  | 10340 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1512 | MW
Total Gen. (MKWH) : |  | 203.245 | System Load Factor : | 81.9% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -460 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-07-26
Actual : | 103.35 | Ft.(MSL) , | Rule curve : | 88 | Ft.( MSL )
Gas Consumed : | Total = | 1054.62 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 95793401.44
|  | Coal : | 0 | Oil : | 527317751.65 | Total : | 623111153.09
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3767.9062 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1279.9914 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1146.5973 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1035.9648 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 936.2319 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 755.5027 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 424.1196 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 194.5661 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 582.6732 |  |  | 0 | 0%
Total | 0 |  | 10123.5532 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2,3 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
3) Ghorasal Unit-3,4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Madaripur-Barisal(N) 132 kV Ckt-1 was under shut down from 04:40 to 13:37 for red hot maintenance
at B-phase loop of tower no 592.
b) Khulna(S)-Gallamari 132 kV Ckt-1 was under shut down from 09:11 to 19:29 for project work of Railway.
c)After maintenance Niamotpur 132/33 kV T2 transformer was switched on at 14:07.
d) Ghorasal-Ishurdi 230 kV Ckt-1 was under shut down from 14:57 to 16:49 for DS maintenance at Ishurdi end.
e) Manikganj 132/33 kV GT2 transformer was under shut down from 14:18 to 15:16 for red hot maintenance at 33 kV side.
f) Bogra 132/33 kV T3 transformer associated with 33 kV bus was under shut down from 15:05 to 16:54 for |  |  |  | About 15 MW power interruption occurred under Bogra
red hot maintenance at bus loop. |  |  |  | S/S areas from 15:05 to 16:54.
g) After maintenance Comilla(N)-Daudkandi 132 kV Ckt-1 was switched on at 16:10.
h) After maintenance Gallamari-Khulna (S) 132 kV Ckt was switched on at 19:29.
i) Chatak 132/33 kV T1 transformer tripped at 23:40 due to 33 kV Sunamganj feeder fault and was |  |  |  | About 2 MW power interruption occurred under Sunamganj
switched on at 23:52. |  |  |  | S/S areas from 23:40 to 23:52.
j) Sylhet 150 MW GT was shut down at 05:59 (26/07/2018) due to CW pump leakage.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-07-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 67 | 1364000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 363 | 8079345
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 60 | 1495872 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 79 | 1320409 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 8280060 | Gas shortage
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 96 | 303700 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 222 | 6131000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 350 | 8458250 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 861120
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 250 | 5303215 | low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 68 | 942576 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 48 | 755515 | Engine problem
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 87 | 702922 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 365652
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 105 | 2460000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 17 | 28800 | low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 80 | 820800 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 10 | 219290 | low demand
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 549072
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 41 | 710112 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 703080
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 135 | 2454720 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 856808
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 976000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 182400 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1235400
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 617000 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 840500
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 1160988
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 300 | 2491526
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | low demand
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | low demand
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 0 | 135 | 3334580
| Dhaka area Total |  |  |  | 5399 | 3416 | 64004712
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 236160 | Engine problem
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 44 | 728640 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 150 | 3265213 | # 3 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4783882 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 50 | 1340192 | low demand
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 857280
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 83 | 462890
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 45 | 252343
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1644120 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 417840
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 432480
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 100 | 1328640 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 859 | 15749680
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Under maint.
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2216480 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2394302 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 185 | 4562000 | STG under maint.
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 350 | 8110000
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 272 | 6680000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 20 | 814032 | Gas shortage
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 68 | 1756363 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 821650
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 942576
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 118456
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2376580 | ST S/D
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 514656
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239040
** | Tripura |  | Imported power | 0 | 160 | 170 | 3226560
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 636000
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 3 | 116102 | low demand
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 305610 | Engine problem
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Comilla Area Total |  |  |  | 2541 | 1633 | 35950407
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 49 | 1190760 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 493164
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 75 | 937920 | Engine problem
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 5600
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 148 | 2229600 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 294 | 4857044
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 70 | 1611000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 66 | 1584000
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3365632 | frequency Control.
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 278 | 6743475 | FGMO
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1145400
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 1104000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 247632
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 55 | 1410000 | FGMO
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 89 | 1620480
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 876240 | Engine problem
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 118 | 2160880
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 1068180
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 541702
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 300 | 7489300 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 7 | 198180 | Engine problem
| Sylhet Area Total |  |  |  | 1549 | 1339 | 31166101
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 461 | 11090909
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 101 | 588000 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 714240 | Engine problem
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 44 | 691680
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 210 | 4282560
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 85 | 799618
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 419 | 9648576
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 32 | 270000 | Line problem.
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 0 | 0 | Reserve
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 50 | 251520 | low demand
| Khulna Area Total |  |  |  | 1769 | 1501 | 28337103
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 860160
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 32 | 568625
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 178 | 4256220
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 91 | 1338442
| Barisal Area Total |  |  |  | 462 | 411 | 7023447
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 50 | 457384
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 44 | 463448
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 896320 | Engine problem
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 882912 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 47 | 442230
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | Under maint.
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 35 | 509150
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 299520 | Engine problem
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 235368 | Engine problem
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 215910
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 825600
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 101 | 984638
| Rajshahi Area Total |  |  |  | 1123 | 452 | 6212480
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage
120 | Rangpur GT |  | PDB | 1*20 | 20 | 15 | 164000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 177000
| Rangpur Area Total |  |  |  | 484 | 33 | 341000
| Total |  |  |  | 15410 | 9938 | 193641974
| Eastern Grid Total |  |  |  | 11572 | 7541 | 151727944
| Western Grid Total |  |  |  | 3838 | 2397 | 41914030
| National Grid Total |  |  |  | 15410 | 9938 | 193641974
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-07-25 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6952 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2913 | MW
i) Dhaka area |  |  | 3763 | MW | i) Khulna area |  |  | 1235 | MW
ii) Chittagong area |  |  | 1076 | MW | ii) Rajshahi area |  |  | 929 | MW
iii) Comilla area |  |  | 950 | MW | iii) Barisal area |  |  | 245 | MW
iv) Mymensingh area |  |  | 745 | MW | iv) Rangpur area |  |  | 504 | MW
v) Sylhet area |  |  | 418 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9865 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 1200 | Kishorganj | 108 | 2100 | Goalpara | 36 | 2000
Munsiganj | 100 | 2000 | Netrokona | 80 | 2000 | Central s/s | 72 | 2100
Sonargaon | 57 | 2100 | Jamalpur | 103 | 2100 | Noapara | 83 | 1930
Shyampur | 166 | 1100 | Sherpur | 76 | 2000 | Jessore | 130 | 2100
Bhulta | 181 | 2100 | Srimongal | 32 | 1830 | Jhenida | 90 | 2000
Madanganj | 53 | 100 | Shahjibazar | 104 | 2100 | Bottail | 118 | 1930
Shitalakhya | 102 | 1700 | Fenchuganj | 38 | 2200 | G.K Project | 50 | 1930
Rahim steel | 4 | 1000 | Kulawara | 37 | 1900 | Faridpur | 138 | 2000
Matuail | 90 | 900 | Sylhet | 128 | 2000 | Madaripur | 110 | 1930
Ghorasal | 78 | 2000 | Chatak | 26 | 2000 | Gopalganj | 77 | 2000
Narsingdi | 122 | 2100 | Sunamganj | 30 | 2000 | Bagerhat | 79 | 1930
Haripur (SBU) | 95 | 2100 | Biani Bazar | 40 | 2000 | Mongla | 32 | 700
Ullon | 86 | 2000 | Comilla (S) | 172 | 2100 | Satkhira | 84 | 1930
Hasnabad | 172 | 2100 | Comilla(N) | 101 | 2000 | Gallamari | 38 | 1930
Magbazar | 117 | 1500 | Chandpur | 110 | 2200 | Magura | 48 | 1930
Maniknagar | 92 | 1700 | Feni | 109 | 1900 | Chuadanga | 78 | 2000
Bangabhaban | 36 | 1300 | Chowmuhani | 170 | 2100 | Barisal | 108 | 1930
Narinda | 92 | 1200 | Ashuganj | 57 | 2300 | Patuakhali | 82 | 2100
Dhanmondi | 123 | 1600 | Daudkandi | 100 | 2000 | Bhandaria | 44 | 2100
Lalbag | 75 | 1930 | B.Baria | 122 | 2000 | Ishurdi | 49 | 2100
Madartek | 46 | 1930 | Ramganj | 32 | 1930 | Ruppur Paromanobik | 1 | 100
Mirpur | 102 | 1900 | Madunaghat | 43.5 | 1930 | Natore | 102 | 2000
Kalyanpur | 117 | 169 | Hathazari | 90 | 2100 | Bogra | 188 | 1930
Gulshan | 122 | 1700 | Khulshi | 180 | 1300 | Noagaon | 76 | 2000
Uttara | 79 | 1830 | Halishahar | 129 | 1500 | Rajshahi | 144 | 2100
Kamrangirchar | 72 | 1600 | Baraulia | 146 | 1200 | C.Nawabganj | 65 | 2100
Savar | 127 | 1900 | Sikalbaha | 36 | 1930 | Amnura | 37 | 2100
Bhasantec | 145 | 1300 | Dohazari | 88 | 2000 | Pabna | 97 | 2100
Agargaon | 40 | 1800 | Cox'sbazar | 79 | 1900 | Shahjadpur | 88 | 2100
Satmosjid | 91 | 700 | Chandraghona | 33 | 2000 | Serajganj | 78 | 2000
Tongi | 145 | 1600 | Kaptai | 4 | 2100 | Niyamatpur | 37 | 1930
Kabirpur | 201 | 1500 | A. Khaer Stl. | 12 | 2100 | Joypurhat | 35 | 1930
Basundhara | 109 | 2000 | Bakulia | 100 | 1930 | Rangpur | 110 | 2100
Manikganj | 94 | 2100 | Julda | 18 | 100 | Lalmonirhat | 78 | 2100
Joydevpur | 227 | 1600 | TK chemical | 1.5 | 600 | Saidpur | 90 | 100
New Tongi | 94 | 1900 | Modern Steel | 12 | 600 | Purbasadipur | 71 | 100
Korda | 263 | 1930 | Shahmirpur | 25 | 100 | Thakurgaon | 58 | 2000
Dhamrai | 24 | 2200 | Abul Khair 230 | 12 | 2100 | Palashbari | 81 | 100
Tangail | 162 | 2100 | BSRM | 120 | 2000 | Barapukuria | 50 | 2000
Mymensing | 227 | 2100 | Khagrachhari | 17 | 2100 | Panchagar | 34 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-07-25
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 377 | 6:00 | 368 | 16:00 | Kaliakoir | 378 | 23:00 | 363 | 11:00
Bheramara | 393 | 24:00 | 386 | 13:00 | Bhulta | 386 | 19:30 | 375 | 11:00
Ashuganj(N) | 392 | 19:00 | 384 | 9:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 223 | 6:00 | 219 | 24:00 | Tongi | 239 | 24:00 | 234 | 13:00
Ishurdi | 227 | 14:00 | 212 | 21:00 | Comilla (N) | 225 | 3:00 | 219 | 11:00
Ashuganj | 216 | 7:00 | 199 | 22:00 | Hathazari | 223 | 7:00 | 217 | 11:00
Serajganj | 240 | 23:00 | 224 | 2:00 | Megnaghat | 224 | 6:00 | 217 | 10:00
Baghabari | 222 | 1:00 | 219 | 14:00 | Fenchuganj | 231 | 18:30 | 221 | 2:00
Barapukuria | 223 | 7:00 | 218 | 11:00 | Siddhirganj | 220 | 7:00 | 211 | 12:00
Bogra | 226 | 21:00 | 217 | 11:00 | Maniknagar | 222 | 6:00 | 215 | 12:00
Khulna South | 225 | 5:00 | 218 | 11:00 | Old Airport | 237 | 7:00 | 230 | 15:00
Rampura | 225 | 1:00 | 217 | 10:00 | Barisal | 226 | 7:00 | 219 | 12:00
Haripur | 232 | 7:00 | 225 | 6:00 | AKSML | 235 | 1:00 | 232 | 12:00
Hasnabad | 221 | 21:00 | 214 | 13:00 | BSRM | 230 | 18:00 | 222 | 10:00
Aminbazar | 228 | 6:00 | 220 | 14:00 | Bibiyana | 401 | 7:00 | 389 | 19:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1830 | 130 | 1200 | B.Baria | 137 | 1700 | 131 | 100
Munsiganj | 136 | 1830 | 130 | 1100 | Ramganj | 125 | 1000 | 118 | 2000
Megnaghat | 133 | 600 | 127 | 1300 | Madanhat | 133 | 700 | 130 | 200
Shyampur | 130 | 1800 | 125 | 1200 | Hathazari | 130 | 300 | 126 | 1300
Bhulta | 131 | 1800 | 127 | 1300 | Khulshi | 128 | 400 | 123 | 1000
Madanganj | 136 | 100 | 130 | 1200 | Halishahar | 131 | 700 | 125 | 1100
Shitalakhya | 137 | 2100 | 128 | 1200 | Baraulia | 129 | 700 | 124 | 1100
Rahim steal | 134 | 2100 | 130 | 1200 | Sikalbaha | 130 | 700 | 125 | 900
Matuail | 134 | 2000 | 129 | 1200 | Dohazari | 128 | 700 | 125 | 1200
Ghorasal | 138 | 1900 | 130 | 700 | Cox'sbazar | 125 | 1700 | 116 | 1900
Narsinghdi | 131 | 1830 | 124 | 1400 | Chandraghona | 131 | 2100 | 127 | 1100
Haripur (SBU) | 134 | 2100 | 130 | 1300 | Kaptai | 130 | 2100 | 128 | 1300
Ullon | 137 | 6900 | 132 | 1200 | A. Khaer Stl. | 128 | 1800 | 124 | 1000
Hasnabad | 136 | 700 | 128 | 1200 | Bakulia | 128 | 100 | 125 | 900
Magbazar | 137 | 500 | 132 | 1200 | Julda | 129 | 2100 | 124 | 900
Maniknagar | 133 | 2000 | 128 | 1000 | TK Chemical | 132 | 2100 | 129 | 1300
Bangabhaban | 133 | 2000 | 128 | 1000 | Modern Steel | 129 | 600 | 125 | 1000
Narinda | 133 | 2000 | 128 | 1000 | Shahmirpur | 130 | 200 | 126 | 1000
Dhanmondi | 137 | 6900 | 132 | 1200 | Khagrachhari | 130 | 100 | 127 | 1100
Lalbag | 133 | 600 | 126 | 1200 | Goalpara | 138 | 900 | 131 | 1600
Madartek | 138 | 700 | 132 | 1200 | Central s/s | 135 | 600 | 131 | 1200
Mirpur | 134 | 400 | 130 | 600 | Noapara | 133 | 600 | 128 | 100
Kalyanpur | 135 | 100 | 130 | 1100 | Jessore | 130 | 600 | 123 | 1200
Gulshan | 137 | 600 | 131 | 1500 | Jhenida | 130 | 500 | 121 | 1930
Uttara | 132 | 600 | 125 | 1000 | Bottail | 135 | 500 | 129 | 2100
Kamrangirchar | 134 | 600 | 126 | 900 | G.K.Project | 140 | 900 | 135 | 2100
Savar | 132 | 500 | 126 | 1100 | Faridpur | 133 | 1300 | 127 | 1930
Bhasantec | 132 | 400 | 127 | 1000 | Madaripur | 135 | 600 | 123 | 200
Agargaon | 134 | 600 | 128 | 1000 | Gopalganj | 141 | 1830 | 125 | 100
Satmosjid | 133 | 600 | 127 | 900 | Bagerhat | 137 | 900 | 130 | 100
Tongi | 136 | 400 | 131 | 1500 | Mongla | 131 | 1300 | 127 | 1930
Kabirpur | 136 | 700 | 131 | 1900 | Satkhira | 137 | 900 | 128 | 1900
Basundhara | 133 | 600 | 128 | 1400 | Gallamari | 138 | 900 | 130 | 1600
Manikganj | 138 | 1600 | 133 | 2100 | Magura | 130 | 600 | 118 | 2100
Joydevpur | 136 | 1300 | 129 | 1100 | Chuadanga | 127 | 600 | 113 | 2100
New Tongi | 136 | 1800 | 131 | 1400 | Barisal | 137 | 1830 | 132 | 1100
Kodda | 136 | 1800 | 126 | 1000 | Patuakhali | 135 | 900 | 129 | 600
Dhamrai | 137 | 600 | 130 | 1930 | Bhandaria | 135 | 900 | 130 | 200
Tangail | 135 | 700 | 129 | 1930 | Ishurdi | 140 | 700 | 135 | 1100
Mymensing | 131 | 800 | 121 | 1930 | Ruppur Paromanobik | 138 | 700 | 136 | 1930
Kishorganj | 130 | 700 | 120 | 1930 | Natore | 136 | 1830 | 127 | 2100
Netrokona | 131 | 900 | 118 | 1930 | Bogra | 129 | 600 | 118 | 2100
Jamalpur | 133 | 1200 | 121 | 2000 | Noagaon | 125 | 400 | 112 | 2100
Sherpur | 134 | 1900 | 124 | 1930 | Rajshahi | 134 | 1800 | 124 | 2100
Srimongal | 137 | 500 | 135 | 900 | C.Nawabganj | 134 | 1830 | 125 | 2100
Shahjibazar | 137 | 1000 | 134 | 100 | Amnura | 137 | 1830 | 126 | 2100
Fenchuganj | 137 | 1100 | 135 | 700 | Pabna | 132 | 500 | 126 | 2100
Khulawara | 136 | 100 | 134 | 1700 | Shahjadpur | 140 | 1830 | 134 | 1000
Sylhet | 135 | 500 | 134 | 100 | Serajganj | 130 | 100 | 124 | 1200
Chatak | 136 | 500 | 132 | 1900 | Niyamatpur | 123 | 1400 | 71 | 100
Sunamganj | 132 | 2400 | 129 | 1100 | Joypurhat | 124 | 1400 | 112 | 2100
Biani Bazar | 135 | 300 | 132 | 1900 | Rangpur | 119 | 600 | 104 | 2100
Comilla(s) | 126 | 700 | 120 | 1930 | Lalmonirhat | 112 | 700 | 94 | 2100
Comilla(n) | 136 | 700 | 135 | 900 | Saidpur | 118 | 700 | 98 | 2100
Chandpur | 132 | 1000 | 124 | 1700 | Purbasadipur | 126 | 700 | 106 | 2100
Feni | 125 | 700 | 118 | 2200 | Thakurgaon | 120 | 1800 | 98 | 2100
Chowmuhani | 129 | 800 | 120 | 2200 | Palashbari | 120 | 600 | 105 | 100
Ashuganj | 136 | 800 | 132 | 100 | Barapukuria | 127 | 1400 | 112 | 2100
Daudkandi | 132 | 1800 | 127 | 1400 | Panchagar | 116 | 1800 | 92 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division

## L-Curve
Date | 2018-07-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 340 | 6948 | 2642 | 9590 |  |  |  | QF-LDC-12
0:30 | 380 | 6691 | 2435.5 | 9126.5 | Date: | 2018-07-25
1:00 | 420 | 6434 | 2229 | 8663
1:30 | 420 | 6328 | 2207 | 8535
2:00 | 420 | 6222 | 2185 | 8407
2:30 | 420 | 6139.5 | 2132 | 8271.5 | [5 empty] | Gen. at Eve. Peak | 10340 | 10340 MW (20:00 )
3:00 | 420 | 6057 | 2079 | 8136 | [6 empty] | 20:00
3:30 | 420 | 5977.5 | 2082.5 | 8060 | [5 empty] | Gen. at Day Peak | 8224.7 | 8224.7 MW (12:00 )
4:00 | 420 | 5898 | 2086 | 7984 | [6 empty] | 12:00
4:30 | 430 | 5860 | 2018.5 | 7878.5 | [5 empty] | Highest Generation | 10340
5:00 | 440 | 5822 | 1951 | 7773 | [6 empty] | 20:00
5:30 | 440 | 5625 | 1804.5 | 7429.5
6:00 | 440 | 5428 | 1658 | 7086
6:30 | 445 | 5358.1 | 1652.5 | 7010.6
7:00 | 450 | 5288.2 | 1647 | 6935.2
7:30 | 445 | 5257.9 | 1684.5 | 6942.4
8:00 | 440 | 5227.6 | 1722 | 6949.6
8:30 | 325 | 5391.4 | 1849 | 7240.4
9:00 | 210 | 5555.2 | 1976 | 7531.2
9:30 | 265 | 5781.6 | 1971 | 7752.6
10:00 | 320 | 6008 | 1966 | 7974
10:30 | 320 | 6086.1 | 1956 | 8042.1
11:00 | 320 | 6164.2 | 1946 | 8110.2
11:30 | 330 | 6212.45 | 1955 | 8167.45
12:00 | 340 | 6260.7 | 1964 | 8224.7
12:30 | 320 | 6244.15 | 1972 | 8216.15
13:00 | 300 | 6227.6 | 1980 | 8207.6
13:30 | 260 | 6198.75 | 1987 | 8185.75
14:00 | 220 | 6169.9 | 1994 | 8163.9
14:30 | 215 | 6344.3 | 1996.5 | 8340.8
15:00 | 210 | 6518.7 | 1999 | 8517.7
15:30 | 195 | 6487.1 | 1963.5 | 8450.6
16:00 | 180 | 6455.5 | 1928 | 8383.5
16:30 | 220 | 6397 | 1924.5 | 8321.5
17:00 | 260 | 6338.5 | 1921 | 8259.5
17:30 | 270 | 6219.85 | 1909.5 | 8129.35
18:00 | 280 | 6101.2 | 1898 | 7999.2
18:30 | 310 | 6617.1 | 2200 | 8817.1
19:00 | 340 | 7133 | 2502 | 9635
19:30 | 460 | 7583 | 2707 | 10290
20:00 | 360 | 7541 | 2799 | 10340 |  |  |  | Executive Engineer
20:30 | 380 | 7536 | 2785.5 | 10321.5 |  |  |  | Network Operation Division
21:00 | 400 | 7531 | 2772 | 10303
21:30 | 380 | 7451 | 2740.5 | 10191.5
22:00 | 360 | 7371 | 2709 | 10080 |  |  |  |  | Page 6 of 7
22:30 | 340 | 7253.5 | 2711.5 | 9965
23:00 | 320 | 7136 | 2714 | 9850
23:30 | 330 | 7042 | 2678 | 9720
24:00 | 340 | 6948 | 2642 | 9590
10340 MW (20:00 )
8224.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-07-25 |  | Energy | 203244991
[10 empty] | 2018-07-25 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3897 | 461 | 1800 | 2103 | 0 | 155 | 1016 | 0 | 158
0:30 | 3825.5 | 461 | 1831.5 | 1864 | 0 | 136.5 | 859 | 0 | 149 | Date: | 2018-07-25
1:00 | 3754 | 461 | 1863 | 1625 | 0 | 118 | 702 | 0 | 140
1:30 | 3784 | 461.5 | 1874 | 1454.5 | 0 | 118 | 704 | 0 | 139 | [7 empty] | Total Energy | 203.245 | Total Energy Gen 203.245 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 203.245 MKWHr
2:00 | 3814 | 462 | 1885 | 1284 | 0 | 118 | 706 | 0 | 138 | [7 empty] | Energy not Served | 0
2:30 | 3807 | 462 | 1918.5 | 1145.5 | 0 | 118 | 688.5 | 0 | 132 | [7 empty] | Energy Requirement | 203.245
3:00 | 3800 | 462 | 1952 | 1007 | 0 | 118 | 671 | 0 | 126
3:30 | 3805 | 462 | 1906.5 | 974.5 | 0 | 118 | 671 | 0 | 123 | [6 empty] | Shortage
4:00 | 3810 | 462 | 1861 | 942 | 0 | 118 | 671 | 0 | 120
4:30 | 3804 | 461.5 | 1862 | 904.5 | 0 | 118 | 609.5 | 0 | 119
5:00 | 3798 | 461 | 1863 | 867 | 0 | 118 | 548 | 0 | 118
5:30 | 3732.5 | 461.5 | 1726 | 759 | 0 | 118 | 514.5 | 0 | 118
6:00 | 3667 | 462 | 1589 | 651 | 0 | 118 | 481 | 0 | 118
6:30 | 3657 | 462 | 1521.5 | 633 | 0 | 119 | 507 | 0 | 111 |  |  |  |  | Coal
7:00 | 3647 | 462 | 1454 | 615 | 0 | 120 | 533 | 0 | 104
7:30 | 3640.5 | 462 | 1439.5 | 619.5 | 0 | 120 | 557.5 | 0 | 103 |  |  |  | Oil |  |  |  | ,
8:00 | 3634 | 462 | 1425 | 624 | 0 | 120 | 582 | 0 | 102
8:30 | 3761.5 | 462 | 1490 | 661 | 0 | 120 | 637.5 | 0 | 108
9:00 | 3889 | 462 | 1555 | 698 | 0 | 120 | 693 | 0 | 114
9:30 | 3925 | 461.5 | 1699.5 | 715 | 0 | 120 | 717.5 | 0 | 114
10:00 | 3961 | 461 | 1844 | 732 | 0 | 120 | 742 | 0 | 114
10:30 | 3951.5 | 461 | 1838.5 | 807.5 | 0 | 120 | 745.5 | 0 | 118
11:00 | 3942 | 461 | 1833 | 883 | 0 | 120 | 749 | 0 | 122
11:30 | 3931 | 460.5 | 1807 | 973.5 | 0 | 120 | 754 | 0 | 121
12:00 | 3920 | 460 | 1781 | 1064 | 0 | 120 | 759 | 0 | 120
12:30 | 3898.5 | 460 | 1727.5 | 1114.5 | 0 | 135 | 755 | 0 | 125
13:00 | 3877 | 460 | 1674 | 1165 | 0 | 150 | 751 | 0 | 130
13:30 | 3877 | 460 | 1674 | 1165 | 0 | 150 | 751 | 0 | 130
14:00 | 3877 | 460 | 1674 | 1165 | 0 | 150 | 751 | 0 | 130
14:30 | 3853 | 460.5 | 1692 | 1304.5 | 0 | 150 | 765 | 0 | 137
15:00 | 3829 | 461 | 1710 | 1444 | 0 | 150 | 779 | 0 | 144
15:30 | 3815.5 | 460.5 | 1695.5 | 1464 | 0 | 150 | 723.5 | 0 | 141
16:00 | 3802 | 460 | 1681 | 1484 | 0 | 150 | 668 | 0 | 138
16:30 | 3795.5 | 460.5 | 1680 | 1458 | 0 | 150 | 644 | 0 | 133
17:00 | 3789 | 461 | 1679 | 1432 | 0 | 150 | 620 | 0 | 128
17:30 | 3740 | 461 | 1529 | 1477.5 | 0 | 150 | 643.5 | 0 | 128
18:00 | 3691 | 461 | 1379 | 1523 | 0 | 150 | 667 | 0 | 128
18:30 | 3782 | 461 | 1522 | 1882 | 0 | 150 | 873 | 0 | 147
19:00 | 3873 | 461 | 1665 | 2241 | 0 | 150 | 1079 | 0 | 166
19:30 | 3991 | 460 | 1837 | 2529 | 0 | 150 | 1153 | 0 | 170
20:00 | 3941 | 461 | 1794 | 2611 | 0 | 150 | 1213 | 0 | 170
20:30 | 3943.5 | 461 | 1798.5 | 2608 | 0 | 167.5 | 1172 | 0 | 171
21:00 | 3946 | 461 | 1803 | 2605 | 0 | 185 | 1131 | 0 | 172
21:30 | 3919 | 460.5 | 1813 | 2561 | 0 | 170 | 1096 | 0 | 172
22:00 | 3892 | 460 | 1823 | 2517 | 0 | 155 | 1061 | 0 | 172
22:30 | 3898 | 460.5 | 1829 | 2397.5 | 0 | 155 | 1057.5 | 0 | 167.5
23:00 | 3904 | 461 | 1835 | 2278 | 0 | 155 | 1054 | 0 | 163
23:30 | 3900.5 | 461 | 1817.5 | 2190.5 | 0 | 155 | 1035 | 0 | 160.5 | Max Temp. in Dhaka |  | 34.2° C
24:00 | 3897 | 461 | 1800 | 2103 | 0 | 155 | 1016 | 0 | 158
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 203.245 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 203.245 MKWHr
Note on W13: Author:

## Generation
2018-07-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 38 | 38 | 38 | 38 | 38 | 38 | 40 | 40 | 40 | 40 | 40 | 40 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 105 | 105 | 105 | 105 | 1445513
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 50 | 50 | 50 | 1819700
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 236160
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 199 | 208 | 202 | 202 | 201 | 201 | 208 | 203 | 202 | 202 | 201 |  | 205 | 202 | 202 | 202 | 202 | 201 | 201 | 4783882
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 135 | 70 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1340192
| Dohazari Peaking | 15 | 15 | 0 | [14 empty] | 0 |  | 20 | 45 | 45 | 45 | 33 | 45 | 48 | 252343
12 | Hathazari peaking | [8 empty] | 0 | 9 | 9 | 9 | 0 |  |  |  | 0 | 8 |  | 84 | 83 | 83 | 82 | 76 | 76 | 76 | 462890
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [16 empty] | 0 | 5 |  | 49 | 49 | 49 | 0 | 0 |  |  | 118456
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 104 | 103 | 103 | 104 | 104 | 105 | 105 | 40 | 70 | 104 | 104 | 104 | 103 | 102 | 102 | 103 | 104 | 103 |  | 103 | 104 | 105 | 103 | 102 | 103 | 105 | 2460000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 301 | 244 | 114 | 100 | 79 | 49 | 49 | 47 | 47 | 50 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 228 |  | 300 | 300 | 300 | 300 | 300 | 301 | 300 | 2491526
19 | Ashuganj 195MW Modular | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 103 | 105 | 105 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1756363
20 | Ghorasal ST: Unit-1,2 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 67 |  | 67 | 67 | 67 | 67 | 67 | 67 | 67 | 1364000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 345 | 345 | 345 | 345 | 345 | 300 | 300 | 300 | 330 | 365 | 365 | 365 | 365 | 330 | 365 | 364 | 365 | 280 |  | 353 | 364 | 363 | 365 | 365 | 365 | 365 | 8079345
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2216480
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2394302
32 | Ashuganj Engines TSK | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 37 | 37 | 43 | 43 | 43 | 20 | 20 | 20 | 30 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 814032
33 | Ashuganj CCPP 225 MW | 150 | 222 | 222 | 222 | 222 | 222 | 222 | 220 | 200 | 185 | 183 | 185 | 170 | 150 | 152 | 167 | 178 | 177 |  | 169 | 177 | 185 | 185 | 173 | 180 | 187 | 4562000
34 | Ashuganj CCPP(South) | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 268 | 309 | 300 | 300 | 300 | 305 | 298 | 276 | 272 | 272 | 272 |  | 305 | 305 | 272 | 272 | 283 | 272 | 272 | 6680000
| Ashuganj CCPP(North) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 320 | 355 | 360 | 360 | 340 | 340 | 330 | 330 | 330 | 345 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8110000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2376580
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 345 | 345 | 345 | 345 | 345 | 340 | 340 | 345 | 360 | 350 | 345 | 345 | 345 | 330 | 331 | 331 | 330 | 330 |  | 343 | 349 | 349 | 349 | 349 | 349 | 349 | 8280060
40 | Meghnaghat CCPP 450MW | 400 | 410 | 430 | 450 | 450 | 400 | 380 | 380 | 420 | 420 | 400 | 400 | 370 | 350 | 340 | 330 | 330 | 340 |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 8458250
41 | Haripur Power CCPP 360MW | 283 | 293 | 312 | 312 | 322 | 322 | 315 | 303 | 290 | 281 | 270 | 250 | 230 | 222 | 207 | 206 | 206 | 206 |  | 221 | 222 | 222 | 222 | 222 | 222 | 222 | 6131000
42 | Mymensingh RPCL 210MW | 50 | 49 | 50 | 48 | 48 | 49 | 50 | 50 | 50 | 50 | 50 | 48 | 48 | 48 | 48 | 48 | 49 | 48 |  | 48 | 50 | 49 | 48 | 48 | 48 | 49 | 1190760
43 | Haripur NEPC 110MW | [17 empty] | 0 |  | 55 | 75 | 96 | 106 | 55 | 20 | 0 | 303700
44 | Fenchugonj CCPP-1 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1611000
45 | Fenchugonj CCPP-2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 66 | 66 | 66 |  | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 1584000
46 | Shajibazar 330 MW | 305 | 306 | 312 | 311 | 300 | 302 | 301 | 307 | 320 | 312 | 312 | 313 | 302 | 305 | 279 | 286 | 281 | 280 |  | 282 | 280 | 278 | 276 | 275 | 278 | 280 | 6743475
47 | Shahjibazar GT: Unit- 8, 9 | 56 | 61 | 61 | 61 | 61 | 50 | 60 | 60 | 60 | 60 | 57 | 59 | 59 | 59 | 59 | 59 | 50 | 59 |  | 64 | 65 | 55 | 61 | 65 | 65 | 66 | 1410000
48 | Shahjibazar 86MW | 86 | 50 | 86 | 50 | 50 | 30 | 10 | 10 | 10 | 84 | 84 | 84 | 84 | 84 | 83 | 84 | 86 | 20 |  | 50 | 86 | 89 | 89 | 89 | 89 | 89 | 1620480
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 10 | 10 | 10 | 45 | 43 | 43 | 43 | 40 | 42 | 42 | 42 | 20 |  | 20 | 42 | 45 | 45 | 45 | 45 | 45 | 876240
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 80 | 100 | 90 | 80 | 80 | 80 | 131 | 133 | 78 | 78 |  | 98 | 128 | 118 | 118 | 78 | 78 | 77 | 2160880
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 48 | 47 | 46 | 46 | 45 | 45 | 45 | 44 | 45 | 45 | 44 | 44 | 43 | 23 |  | 45 | 47 | 47 | 47 | 47 | 47 | 47 | 1068180
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 198180
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 5 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247632
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 53 | 22 | 22 | 40 | 49 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 22 |  | 31 | 53 | 53 | 53 | 53 | 53 | 53 | 1145400
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 21 | 21 | 21 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 541702
57 | Summit Bibiana- 2 | 270 | 305 | 300 | 300 | 300 | 270 | 280 | 280 | 320 | 305 | 300 | 305 | 310 | 300 | 320 | 300 | 300 | 270 |  | 300 | 320 | 300 | 290 | 290 | 300 | 280 | 7489300
58 | Southern 55MW | 55 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 30 | 36 | 36 | 36 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 976000
59 | Sikalbaha (Energis) | 50 | 50 | 50 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 20 | 32 | 32 | 35 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 51 | 857280
60 | Barabkunda (Regent) | 19 | 0 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 417840
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  |  | 0 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 365652
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 493164
63 | Tripura | 140 | 138 | 126 | 120 | 118 | 118 | 104 | 102 | 114 | 114 | 122 | 120 | 130 | 130 | 144 | 138 | 128 | 128 |  | 166 | 170 | 170 | 172 | 172 | 163 | 158 | 3226560
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 39 | 40 | 41 | 41 | 26 | 12 | 5 | 6 | 6 | 7 | 2 | 3 | 2 | 3 | 7 | 4 |  | 13 | 8 | 10 | 23 | 36 | 37 | 37 | 432480
65 | Feni (Doreen) 22MW | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 514656
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239040
67 | Jangalia (Summit) 33MW | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 636000
68 | Summit Comilla 25MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 16 | 16 | 15 | 16 | 0 |  |  |  |  | 0 | 15 | 15 | 15 | 15 | 22 | 22 | 305610
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 |  | 22 | 26 | 26 | 26 | 26 | 26 | 26 | 635400
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 617000
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 840500
73 | Ghorashal (Regent) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 79 | 78 | 77 | 55 | 55 | 77 | 76 | 78 | 78 |  | 78 | 79 | 79 | 79 | 79 | 79 | 79 | 1320409
76 | Siddhirganj (Desh) | [17 empty] | 0 |  | 7 | 15 | 17 | 0 |  |  |  | 28800
77 | Siddhirganj (Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 15 | 40 | 60 | 40 |  | 50 | 60 | 80 | 100 | 100 | 50 | 7 | 820800
78 | Gazipur (RPCL) | 48 | 51 | 42 | 42 | 42 | 42 | 42 | 43 | 48 | 52 | 52 | 52 | 43 | 43 | 46 | 47 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1160988
79 | Kodda 149 MW | 60 | 65 | 65 | 65 | 65 | 48 | 48 | 48 | 82 | 115 | 122 | 133 | 133 | 128 | 117 | 117 | 120 | 125 |  | 135 | 135 | 135 | 135 | 133 | 120 | 98 | 2454720
80 | Jamalpur 95MW | 64 | 64 | 64 | 64 | 64 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 50 | 58 | 75 | 95 | 95 | 95 | 95 | 937920
81 | Lakdhanvi 52 MW | 8 | 8 | 8 | 8 | 8 | 0 | [13 empty] | 0 | 0 | 3 | 14 | 16 | 16 | 16 | 116102
82 | Madanganj 102MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 46 | 48 | 48 | 48 | 48 | 45 |  | 48 | 60 | 68 | 80 | 81 | 81 | 30 | 942576
83 | Pagla (DPA ) | 10 | 0 |  |  |  |  | 0 | 10 | 10 | 10 | 21 | 20 | 21 | 21 | 21 | 20 | 21 | 10 |  | 10 | 10 | 10 | 0 | 0 |  |  | 219290
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 50 | 50 | 30 | 11 | 11 | 11 | 85 | 85 | 86 | 85 | 85 | 85 | 85 | 85 | 21 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 942576
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 35 | 40 | 10 | 10 |  | 70 | 87 | 87 | 87 | 87 | 50 | 50 | 702922
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 305 | 250 | 200 | 200 |  | 200 | 270 | 250 | 200 | 200 | 200 | 200 | 5303215
87 | Meghnaghat (IEL) | 45 | 12 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 35 | 83 | 83 | 54 |  | 69 | 100 | 100 | 100 | 100 | 40 | 9 | 861120
88 | Ghorashal 78MW (MAX) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 73 | 73 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 60 | 60 | 60 | 60 | 72 | 72 | 60 | 1495872
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 80 | 80 | 80 | 78 | 50 | 30 | 30 | 30 | 30 | 53 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 1644120
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 48 | 47 | 47 | 20 |  | 28 | 47 | 47 | 47 | 47 | 47 | 47 | 1104000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 42 | 42 | 6 | 6 | 6 | 6 | 20 | 45 | 42 | 42 | 42 | 42 | 42 | 34 | 38 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 821650
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 40 | 7 | 7 | 7 |  | 102 | 102 | 102 | 102 | 64 | 7 | 7 | 549072
95 | Patenga 50MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 25 | 16 | 39 | 43 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 41 | 43 | 728640
96 | Chittagong ECPV 108 MW | 73 | 53 | 53 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 44 | 53 | 53 | 53 | 53 | 53 | 53 |  | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 1328640
97 | Katpotti 51 MW | 41 | 41 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 34 | 34 | 41 | 40 | 40 | 40 | 40 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 38 | 710112
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 182400
99 | Madanganj-55 MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 42 | 47 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 755515
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 36 | 36 | 36 | 37 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 856808
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 163 | 130 | 130 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 100 |  | 130 | 163 | 130 | 130 | 130 | 130 | 130 | 3365632
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.2 | 0.6 | 0.2 | 0 | 0.2 | 0.7 | 0.6 | 0.9 | 0.7 | 0.5 | 0.5 | 0.2 | [8 empty] | 5600
103 | Banco Energy 54MW | 54 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 703080
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 64 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 74 | 103 | 103 | 103 | 103 | 104 | 104 | 104 |  | 148 | 148 | 148 | 148 | 148 | 146 | 149 | 2229600
112 | Aggreko Aurahati 100MW
114 | Summit Gazipur-1 150MW | 151 | 41 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 70 | 115 | 115 | 115 | 115 | 117 | 117 |  | 117 | 135 | 135 | 136 | 136 | 138 | 154 | 3334580
115
116
117
118
120 | Eastern Zone Total | 6434 | 6222 | 6057 | 5898 | 5822 | 5428 | 5288.2 | 5227.6 | 5555.2 | 6008 | 6164.2 | 6260.7 | 6227.6 | 6169.9 | 6518.7 | 6455.5 | 6338.5 | 6101.2 |  | 7133 | 7583 | 7541 | 7531 | 7371 | 7136 | 6948 | 151727944
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 79 | 97 | 101 | 98 | 98 | 101 | 100 | 588000
125 | Khulna (KPCL-2) | 32 | 32 | 32 | 32 | 32 | 16 | 0 | [9 empty] | 0 | 5 |  | 66 | 83 | 99 | 99 | 99 | 99 | 99 | 714240
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 0 |  |  |  | 0 |  | 42 | 44 | 44 | 44 | 44 | 44 | 38 | 691680
129 | Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 195 | 244 | 244 | 245 | 244 | 245 | 248 | 248 | 200 | 150 | 120 |  | 135 | 165 | 210 | 200 | 150 | 150 | 150 | 4282560
130
131
132
133
| Summit Barisal 110 MW | 96 | 80 | 16 | 16 | 16 | 0 | [8 empty] | 0 | 16 | 16 | 16 |  | 80 | 100 | 110 | 110 | 110 | 110 | 110 | 860160
136 | Barisal GT: Unit-1, 2
137 | Bhola Aggreko 95MW | 95 | 96 | 96 | 95 | 95 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 48 | 49 | 51 | 50 | 50 |  | 73 | 90 | 91 | 95 | 97 | 98 | 97 | 1338442
| Bhola CCPP 194MW | 178 | 178 | 178 | 178 | 178 | 153 | 154 | 154 | 178 | 178 | 179 | 179 | 179 | 179 | 179 | 178 | 178 | 178 |  | 178 | 179 | 178 | 178 | 169 | 174 | 151 | 4256220
140 | Bhola (Venture) 33MW | 33 | 32 | 28 | 27 | 20 | 16 | 19 | 20 | 18 | 19 | 19 | 15 | 17 | 19 | 22 | 22 | 22 | 21 |  | 27 | 31 | 32 | 34 | 33 | 33 | 31 | 568625
141 | Bangla Trak Noapara | [17 empty] | 0 |  | 14 | 50 | 50 | 50 | 50 | 50 | 20 | 251520
142 | Noapara (KZA) 40MW | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [7 empty] | 0 | 8 | 8 | 8 |  | 33 | 32 | 32 | 33 | 40 | 40 | 40 | 270000
143 | Gopalganj Peaking | 22 | 20 | 0 |  |  |  | 22 | 28 | 27 | 26 | 26 | 26 | 27 | 21 | 17 | 21 | 40 | 63 |  | 93 | 80 | 85 | 74 | 73 | 70 | 60 | 799618
144 | Bheramara GT-1,2,3
145
146 | Bheramara HVDC | 461 | 462 | 462 | 462 | 461 | 462 | 462 | 462 | 462 | 461 | 461 | 460 | 460 | 461 | 461 | 460 | 461 | 461 |  | 461 | 460 | 461 | 461 | 460 | 461 | 461 | 11090909
147 | Bheramara 360 MW | 415 | 414 | 415 | 420 | 419 | 350 | 300 | 305 | 414 | 418 | 411 | 407 | 410 | 410 | 411 | 413 | 416 | 380 |  | 413 | 416 | 419 | 417 | 416 | 416 | 420 | 9648576
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 50 | 50 | 0 | [12 empty] | 0 |  | 50 | 42 | 50 | 42 | 43 | 43 | 43 | 457384
157 | Sirajgonj Unit-1 225MW (Gas) | 221 | 220 | 220 | 221 | 221 | 221 | 220 | 223 | 209 | 189 | 184 | 185 | 184 | 190 | 200 | 182 | 186 | 182 |  | 188 | 200 | 200 | 200 | 200 | 200 | 200 | 5112545
158 | Sirajgonj Unit-1 225MW (Oil) | [12 empty] | 0
| Sirajgonj Unit-2 225MW (Gas) | 150 | 155 | 145 | 145 | 145 | 165 | 185 | 201 | 196 | 182 | 176 | 177 | 176 | 183 | 195 | 161 | 178 | 172 |  | 180 | 206 | 202 | 206 | 201 | 201 | 201 | 4490472
Sirajgonj Unit-2 225MW (Oil)
159 | Sirajgonj Unit-3 225 MW(Gas)
160 | Sirajgonj Unit-3 225 MW(Oil)
161 | Bera Peaking | 44 | 44 | 44 | 44 | 15 | 0 | [10 empty] | 0 | 10 |  | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 463448
162 | Bogra (GBB) | 7 | 10 | 10 | 13 | 10 | 10 | 10 | 10 | 15 | 18 | 15 | 18 | 18 | 18 | 0 |  | 0 | 15 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 299520
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 235368
164 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 215910
165 | Amnura 50MW | 40 | 40 | 40 | 40 | 40 | 24 | 12 | 12 | 40 | 33 | 33 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 896320
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 32 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 882912
167 | Katakhali Peaking | 44 | 44 | 44 | 44 | 0 | [11 empty] | 0 | 25 |  | 45 | 45 | 47 | 45 | 45 | 45 | 45 | 442230
168 | Santahar Peaking | [8 empty] | 20 | 34 | 33 | 34 | 33 | 34 | 34 | 33 | 33 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 509150
169 | Rajlanka 52 MW | 51 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 40 | 52 | 52 | 51 | 51 | 51 | 25 |  | 51 | 51 | 52 | 51 | 52 | 52 | 52 | 825600
170 | Chapainawabganj-100 MW | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 75 | 101 | 101 | 101 | 101 | 101 | 99 | 984638
171
172
173 | Rangpur GT | 16 | 17 | 17 | 17 | 17 | 0 | [11 empty] | 0 |  | 17 | 15 | 15 | 14 | 14 | 14 | 14 | 164000
175 | Saidpur GT | 18 | 18 | 18 | 18 | 18 | 0 | [13 empty] | 0 | 18 | 18 | 18 | 18 | 16 | 16 | 177000
176
177
178
178 | Western Zone Total | 2229 | 2185 | 2079 | 2086 | 1951 | 1658 | 1647 | 1722 | 1976 | 1966 | 1946 | 1964 | 1980 | 1994 | 1999 | 1928 | 1921 | 1898 | 0 | 2502 | 2707 | 2799 | 2772 | 2709 | 2714 | 2642 | 51517047
176
177