## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-20 | Wednesday
|  | Date (day): | 2018-06-20 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10002 | MW |  |  | (b) At Evening Peak Hour : |  | 11645 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-19 | 2018-06-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 30 | 30 | 30 | 30 |  | 55 | # 1 under maint
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 |  | 50 | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 180 | 300 | 260 | 330
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 30 | 79 | 40 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 13 | 103 | 102 | 102 | 6
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 20 | 20 | 20 | 20 | 20 |  | # 1 under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 340 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 84 | 84 |  | 26 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 212 | 354 | 350 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 33 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 15 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 170 | 160 | 150 | 200 | 10 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 32 | 84 | 88 |  | 12 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 205 | 180 | 180 | 200 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 0 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 7 | 94 | 102 |  | 0
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 24 | 49 | 49
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 36 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 100 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 36 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 36 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 51 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 30 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 7 | 14 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 24 | 40 | 51
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 50 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 1761 | 2601 | 3780 | 4345 | 341 | 450
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 44 | 44 |  | 5
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 158 | 158 | 160 | 160 |  | 70 | # 2 under maint
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 226 | 196 | 215 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 60 | 50 | 52 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 11 | 3 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 51 | 85 | 85
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 74 | 62 | 80
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 68 | 90 | 90 |  |  | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | gas line problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 45 | 99 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 576 | 724 | 882 | 993 | 360 | 125
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 120 | 120 | 120 |  |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Under maint.
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  |  | Gas shortage
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 195 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint.
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 261 | 301 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 42 | 42 | 42
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 3 | 24 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 55 | 78 | 78 | 117 |  | Gas shortage
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 6 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 5 | 62 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  |  | Under maint.
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | gas line problem
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  |  | gas line problem
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 62 | 116 | 136 | 182
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 25 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 3 | 14 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200 |  |  | On test
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 650 | 1005 | 1214 | 1510 | 160 | 55
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 203 | 165 | 200 | 2 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 20 | 0 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 48 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.1 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 0 | 100 | 100 | 100
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 158.1 | 371 | 362 | 417 | 2 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 58 | 60 | 60
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 44 | 60 | 61 | 61
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 100 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 286 | 279 | 310 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 50 | 50
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 2 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 0 | 11
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 62 | 54 | 66
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 60 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 5 | 48 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 78 | 80 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 20
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 3 | 42 | 44 | 44
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 8 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 275 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 8 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 993 | 1192 | 1381 | 1464 | 0 | 0
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 31 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 477 | 476 | 472 | 472
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 106 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 99 | 99 | 99
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 44 | 0 | 46
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 5 | 64 | 50 | 74
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27/06/2018
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 55
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 628 | 972 | 996 | 1269 | 0 | 360
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 2 | 31 | 35 | 35
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 67 | 66 | 66 |  |  | # 2 under maint.
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 14 | 99 | 96 | 98
| Barisal Area Total |  |  |  |  | 472 | 462 | 31 | 307 | 307 | 339 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 43
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 38 | 0 | 47
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 30 | 40 | 50 | 50
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 24 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 45 | 45
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 193 | 180 | 215 | 215
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 150 | 172 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 0 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 11 | 11 |  |  | Engine problem
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 102 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 441 | 794 | 760 | 938 | 71 | 16
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 70 | 70 | 74
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 160 | 159 | 250 | 260
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 232 | 263 | 320 | 370 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 5470.1 | 8229 | 10002 | 11645 | 934 | 1091
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5159.669 | 7762 | 9434.3813 | 10984.1402
A. |  | 2018-06-19 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 8788 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 5197.1 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8229 | MW
3 | Day peak Generation : |  |  | 5470.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7762 | MW
4 | Evening peak Generation : |  |  | 8229 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 161.6413 | MKWHr | By Solar | 0.008842 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 101.7158 | MKWHr |  | By Oil: | 36.3856 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 5.6281 | MKWHr |  | By Hydro: | 3.6477 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 934 | MW | Dhaka | 2243 | 2243 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1091 | MW | Chittagong | 798 | 798 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2025 | MW | Khulna | 1114 | 1114 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 868.52 | MMCFD |  |  | Rajshahi | 935 | 935 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 74020062.792 | ii) Oil : | Taka | 321803852.9 | Comilla | 799 | 799 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 10539280.3 | Total | Taka | 406363195.992 | Mymensingh | 667 | 667 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 9.8465 | MKWHr. | Sylhet | 392 | 392 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -760 | MW at | 21:00 | hrs | Barisal | 233 | 233 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -820 | MW at | 1:00 | hrs | Rangpur | 581 | 581 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.5° C |  |  | Total | 7762 | 7762 |  | 0
B. |  | 2018-06-20 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 38.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 9500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11645 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6500 | MW
4 | Reserve(Generation end) |  |  |  | 2145 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 174.7375 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5756.2 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.6393 | MKWHr. | ii) HVDC Flow at Peak Time |  | 476 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.616 | MKWHr. | iii) Maximum HVDC Flow : |  | 477 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.9 |  | (b) Today: | 103.35 |  | (c) Rule Curve: |  | 20
.

## YesterdayGen
2018-06-19
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 30 | 120 | 0 | 0 | 300 | 105 | 76 | 345 | 351 | 0 | 20 | 420 | 0 | 7 | 14 | 15 | 198 | 0 | 201 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 10 | 33 | 14 | 24 | 0 | 77 | 80 | 0 | 0 | 25 | 0 | 221 | 0 | 115 | 0 | 51 | 57 | 74 | 80 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 184 | 186 | 0 | 41 | 0 | 53 | 51 | 85 | 0 | 0 | 0 | 0 | 33 | 21 | 160 | 201 | 8 | 22 | 0 | 60 | 60 | 53 | 50 | 163 | 292 | 52 | 86 | 45 | 78 | 0 | 48 | 8 | 310 | 23 | 11 | 0 | 101 | 0 | 0 | 126 |  | 476 | 33 | 0 | 107 | 100 | 120 | 0 | 0 | 45 | 40 | 40 | 90 | 34 | 110 | 0 | 0 | 0 | 43 | 36 | 101 | 33 | 43 | 44 | 43 | 42 | 22 | 10 | 5 | 0 | 73 | 160 | 17 | 18 | 180 | 0 | 0 | 167 | 98 | 78 | 0 | 0 |  | 6380 | 2408 | 8788 | 3092 | 476 | 2254 | 1228 | 233 | 157 | 1188 | 160 | 0 | 0 | 104.05
2:00 | 30 | 120 | 0 | 0 | 300 | 106 | 77 | 344 | 350 | 0 | 20 | 400 | 0 | 7 | 14 | 15 | 198 | 0 | 160 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 10 | 33 | 14 | 0 | 0 | 77 | 80 | 0 | 0 | 25 | 0 | 221 | 0 | 100 | 0 | 51 | 57 | 74 | 80 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 183 | 186 | 0 | 41 | 0 | 53 | 51 | 85 | 0 | 0 | 0 | 0 | 33 | 21 | 160 | 201 | 8 | 22 | 0 | 60 | 60 | 53 | 50 | 163 | 292 | 63 | 86 | 45 | 78 | 0 | 48 | 8 | 280 | 0 | 11 | 0 | 16 | 0 | 0 | 0 |  | 477 | 0 | 0 | 69 | 100 | 120 | 0 | 0 | 45 | 41 | 40 | 89 | 33 | 110 | 0 | 0 | 0 | 43 | 36 | 67 | 40 | 43 | 44 | 25 | 42 | 22 | 10 | 5 | 0 | 73 | 159 | 17 | 0 | 176 | 0 | 0 | 165 | 98 | 78 | 0 | 0 |  | 6026 | 2267 | 8293 | 3032 | 477 | 2204 | 944 | 232 | 157 | 1087 | 160 | 0 | 0 | 104.02
3:00 | 30 | 120 | 0 | 0 | 300 | 106 | 40 | 344 | 351 | 0 | 20 | 400 | 0 | 7 | 14 | 15 | 170 | 0 | 160 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 10 | 33 | 14 | 0 | 0 | 77 | 80 | 0 | 0 | 0 | 0 | 222 | 0 | 50 | 0 | 51 | 57 | 74 | 80 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 184 | 186 | 0 | 41 | 0 | 10 | 6 | 10 | 0 | 0 | 0 | 0 | 8 | 21 | 158 | 207 | 8 | 22 | 0 | 60 | 60 | 19 | 50 | 100 | 297 | 63 | 10 | 5 | 78 | 0 | 48 | 0 | 280 | 8 | 11 | 0 | 16 | 0 | 0 | 7 |  | 477 | 0 | 0 | 69 | 100 | 120 | 0 | 0 | 45 | 38 | 40 | 87 | 37 | 110 | 0 | 0 | 0 | 0 | 0 | 67 | 40 | 43 | 44 | 8 | 42 | 19 | 10 | 5 | 0 | 72 | 159 | 0 | 0 | 170 | 0 | 0 | 162 | 98 | 78 | 0 | 0 |  | 5504 | 2140 | 7644 | 2991 | 477 | 1785 | 909 | 231 | 157 | 936 | 158 | 0 | 0 | 103.99
4:00 | 30 | 120 | 0 | 0 | 300 | 23 | 40 | 345 | 348 | 0 | 20 | 380 | 0 | 7 | 14 | 15 | 170 | 0 | 160 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 22 | 25 | 10 | 33 | 14 | 0 | 0 | 77 | 80 | 0 | 0 | 0 | 0 | 221 | 0 | 50 | 0 | 51 | 57 | 74 | 80 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 184 | 148 | 0 | 10 | 0 | 10 | 6 | 10 | 0 | 0 | 0 | 0 | 8 | 21 | 154 | 191 | 8 | 22 | 0 | 60 | 60 | 5 | 2 | 100 | 299 | 52 | 10 | 5 | 77 | 0 | 2 | 0 | 290 | 15 | 11 | 0 | 16 | 0 | 0 | 7 |  | 477 | 0 | 0 | 51 | 84 | 120 | 0 | 0 | 45 | 27 | 40 | 90 | 36 | 110 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 43 | 45 | 8 | 0 | 17 | 10 | 5 | 0 | 73 | 159 | 0 | 0 | 178 | 0 | 0 | 168 | 97 | 78 | 0 | 0 |  | 5208 | 2027 | 7235 | 2953 | 477 | 1539 | 875 | 232 | 157 | 848 | 154 | 0 | 0 | 103.96
5:00 | 30 | 120 | 0 | 0 | 250 | 23 | 20 | 344 | 321 | 0 | 20 | 380 | 0 | 7 | 14 | 15 | 172 | 0 | 100 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 0 | 25 | 10 | 33 | 14 | 0 | 0 | 77 | 80 | 0 | 0 | 0 | 0 | 169 | 0 | 51 | 0 | 24 | 57 | 74 | 80 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 287 | 183 | 102 | 0 | 10 | 0 | 10 | 6 | 10 | 0 | 0 | 0 | 0 | 8 | 21 | 148 | 190 | 8 | 0 | 0 | 60 | 60 | 5 | 2 | 100 | 240 | 45 | 10 | 5 | 78 | 0 | 2 | 0 | 270 | 21 | 0 | 0 | 16 | 0 | 0 | 7 |  | 477 | 0 | 0 | 51 | 100 | 120 | 0 | 0 | 45 | 22 | 40 | 89 | 36 | 110 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 45 | 8 | 0 | 17 | 10 | 5 | 0 | 73 | 160 | 0 | 0 | 177 | 0 | 0 | 168 | 98 | 78 | 0 | 0 |  | 4772 | 1975 | 6747 | 2712 | 477 | 1427 | 801 | 233 | 157 | 792 | 148 | 0 | 0 | 103.93
6:00 | 30 | 120 | 0 | 0 | 165 | 25 | 20 | 300 | 231 | 0 | 20 | 270 | 0 | 7 | 14 | 15 | 172 | 0 | 80 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 10 | 16 | 14 | 0 | 0 | 76 | 80 | 0 | 0 | 0 | 0 | 169 | 0 | 51 | 0 | 8 | 40 | 60 | 80 | 72 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 250 | 183 | 72 | 0 | 10 | 0 | 10 | 6 | 10 | 0 | 0 | 0 | 0 | 8 | 21 | 138 | 147 | 0 | 0 | 0 | 30 | 44 | 5 | 2 | 100 | 239 | 53 | 10 | 5 | 78 | 0 | 2 | 0 | 280 | 0 | 0 | 0 | 16 | 0 | 0 | 7 |  | 477 | 0 | 0 | 10 | 66 | 120 | 0 | 0 | 26 | 22 | 40 | 89 | 35 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 3 | 0 | 5 | 0 | 75 | 159 | 0 | 0 | 175 | 0 | 0 | 167 | 98 | 0 | 0 | 0 |  | 4138 | 1705 | 5843 | 2404 | 477 | 1184 | 580 | 234 | 156 | 670 | 138 | 0 | 0 | 103.9
7:00 | 30 | 120 | 0 | 0 | 162 | 25 | 20 | 255 | 202 | 0 | 20 | 240 | 0 | 7 | 14 | 15 | 170 | 0 | 80 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 0 | 14 | 0 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 169 | 0 | 52 | 0 | 8 | 40 | 60 | 68 | 44 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 250 | 182 | 25 | 0 | 10 | 0 | 10 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 126 | 145 | 0 | 0 | 0.1 | 30 | 44 | 5 | 2 | 100 | 240 | 46 | 5 | 5 | 78 | 0 | 4 | 0 | 280 | 15 | 0 | 0 | 16 | 0 | 0 | 7 |  | 477 | 0 | 0 | 10 | 66 | 120 | 0 | 0 | 0 | 19 | 16 | 89 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 3 | 0 | 5 | 0 | 76 | 160 | 0 | 0 | 175 | 0 | 0 | 167 | 97 | 0 | 0 | 0 |  | 3904.1 | 1644 | 5548.1 | 2331 | 477 | 1060 | 516 | 236 | 160 | 642 | 126 | 0.1 | 0 | 103.89
8:00 | 30 | 120 | 0 | 0 | 131 | 15 | 20 | 250 | 212 | 0 | 20 | 240 | 0 | 7 | 14 | 15 | 120 | 0 | 80 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 0 | 14 | 0 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 169 | 0 | 52 | 0 | 8 | 40 | 59 | 68 | 45 | 44 | 0 | 0 | 105 | 0 | 0 | 0 | 257 | 184 | 8 | 0 | 10 | 0 | 10 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 145 | 0 | 0 | 0.1 | 30 | 44 | 5 | 2 | 100 | 242 | 54 | 5 | 5 | 78 | 0 | 4 | 0 | 260 | 21 | 0 | 0 | 15 | 0 | 0 | 7 |  | 477 | 0 | 0 | 10 | 32 | 120 | 0 | 0 | 0 | 19 | 16 | 90 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 3 | 0 | 0 | 0 | 75 | 160 | 0 | 0 | 177 | 0 | 0 | 167 | 60 | 0 | 0 | 0 |  | 3687.1 | 1510 | 5197.1 | 2233 | 477 | 988 | 420 | 235 | 160 | 641 | 43 | 0.1 | 0 | 103.88
9:00 | 30 | 120 | 0 | 0 | 184 | 14 | 20 | 280 | 212 | 0 | 20 | 240 | 0 | 7 | 14 | 15 | 120 | 0 | 80 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 0 | 14 | 0 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 196 | 0 | 50 | 0 | 8 | 40 | 59 | 68 | 45 | 43 | 0 | 0 | 100 | 0 | 0 | 0 | 228 | 183 | 8 | 0 | 10 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 145 | 0 | 0 | 0.5 | 30 | 44 | 5 | 2 | 100 | 265 | 58 | 5 | 5 | 77 | 0 | 3 | 0 | 300 | 21 | 2 | 0 | 15 | 0 | 0 | 7 |  | 477 | 0 | 0 | 10 | 32 | 120 | 0 | 0 | 0 | 19 | 0 | 85 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 7 | 0 | 5 | 0 | 74 | 160 | 0 | 0 | 170 | 0 | 0 | 156 | 53 | 0 | 0 | 0 |  | 3814.5 | 1439 | 5253.5 | 2302 | 477 | 1015 | 371 | 234 | 160 | 640 | 54 | 0.5 | 0 | 103.87
10:00 | 30 | 120 | 0 | 0 | 184 | 13 | 20 | 345 | 212 | 0 | 20 | 240 | 0 | 7 | 14 | 15 | 120 | 0 | 100 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 0 | 7 | 0 | 0 | 80 | 80 | 0 | 0 | 0 | 0 | 196 | 0 | 80 | 0 | 8 | 0 | 27 | 68 | 40 | 44 | 0 | 0 | 100 | 0 | 0 | 0 | 231 | 225 | 8 | 0 | 10 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 6 | 3 | 54 | 156 | 0 | 0 | 0.9 | 30 | 44 | 5 | 2 | 100 | 280 | 64 | 5 | 5 | 77 | 0 | 3 | 0 | 300 | 21 | 3 | 0 | 15 | 0 | 0 | 7 |  | 476 | 0 | 0 | 10 | 32 | 120 | 0 | 0 | 0 | 8 | 0 | 90 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 9 | 0 | 5 | 0 | 74 | 160 | 0 | 0 | 165 | 0 | 0 | 148 | 32 | 0 | 0 | 0 |  | 3932.9 | 1399 | 5331.9 | 2467 | 476 | 994 | 367 | 234 | 160 | 579 | 54 | 0.9 | 0 | 103.86
11:00 | 30 | 120 | 0 | 0 | 190 | 13 | 20 | 345 | 212 | 0 | 20 | 260 | 0 | 7 | 14 | 15 | 120 | 0 | 120 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 7 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 195 | 0 | 80 | 0 | 0 | 0 | 16 | 68 | 45 | 40 | 0 | 0 | 100 | 0 | 0 | 0 | 228 | 184 | 8 | 0 | 10 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 3 | 70 | 157 | 0 | 0 | 1.9 | 30 | 44 | 5 | 2 | 130 | 266 | 55 | 5 | 5 | 78 | 0 | 3 | 0 | 290 | 23 | 2 | 0 | 15 | 0 | 0 | 7 |  | 476 | 0 | 0 | 10 | 32 | 120 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 24 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 74 | 160 | 0 | 0 | 190 | 0 | 0 | 151 | 32 | 0 | 0 | 0 |  | 3973.9 | 1365 | 5338.9 | 2399 | 476 | 1028 | 402 | 234 | 158 | 570 | 70 | 1.9 | 0 | 103.85
12:00 | 30 | 120 | 0 | 0 | 180 | 13 | 30 | 350 | 212 | 0 | 20 | 260 | 0 | 7 | 0 | 15 | 205 | 0 | 170 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 7 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 226 | 0 | 60 | 0 | 11 | 0 | 0 | 68 | 45 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 261 | 204 | 8 | 0 | 10 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 3 | 62 | 156 | 0 | 0 | 2.1 | 30 | 44 | 5 | 2 | 130 | 286 | 64 | 5 | 5 | 78 | 0 | 3 | 0 | 310 | 23 | 8 | 0 | 15 | 0 | 0 | 0 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 5 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 24 | 0 | 8 | 0 | 21 | 10 | 5 | 0 | 72 | 160 | 0 | 0 | 193 | 0 | 0 | 150 | 14 | 0 | 0 | 0 |  | 4138.1 | 1332 | 5470.1 | 2614 | 477 | 1044 | 320 | 232 | 158 | 561 | 62 | 2.1 | 0 | 103.84
13:00 | 30 | 120 | 0 | 0 | 180 | 13 | 35 | 370 | 212 | 0 | 20 | 280 | 0 | 10 | 0 | 15 | 202 | 0 | 206 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 14 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 214 | 0 | 100 | 0 | 16 | 0 | 0 | 68 | 45 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 261 | 206 | 8 | 0 | 17 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 74 | 159 | 0 | 0 | 1.2 | 30 | 44 | 5 | 2 | 163 | 296 | 62 | 5 | 5 | 78 | 0 | 3 | 0 | 320 | 23 | 8 | 0 | 15 | 0 | 0 | 0 |  | 476 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 7 | 0 | 43 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 24 | 0 | 8 | 0 | 21 | 10 | 8 | 0 | 72 | 160 | 0 | 0 | 196 | 0 | 0 | 161 | 12 | 0 | 0 | 0 |  | 4342.2 | 1380 | 5722.2 | 2737 | 476 | 1114 | 328 | 232 | 158 | 602 | 74 | 1.2 | 0 | 103.83
14:00 | 30 | 120 | 0 | 0 | 250 | 14 | 35 | 365 | 314 | 0 | 20 | 360 | 0 | 7 | 0 | 15 | 207 | 0 | 207 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 14 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 195 | 0 | 80 | 0 | 16 | 0 | 0 | 68 | 45 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 264 | 185 | 8 | 0 | 34 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 78 | 202 | 0 | 0 | 0.8 | 60 | 60 | 5 | 2 | 163 | 268 | 64 | 5 | 5 | 78 | 0 | 3 | 0 | 305 | 23 | 8 | 0 | 15 | 0 | 0 | 7 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 24 | 0 | 16 | 0 | 21 | 10 | 8 | 0 | 70 | 160 | 0 | 0 | 193 | 0 | 0 | 179 | 62 | 0 | 0 | 0 |  | 4611.8 | 1428 | 6039.8 | 2824 | 477 | 1332 | 358 | 230 | 158 | 582 | 78 | 0.8 | 0 | 103.82
15:00 | 30 | 120 | 0 | 0 | 250 | 14 | 35 | 340 | 331 | 0 | 20 | 360 | 0 | 7 | 0 | 15 | 223 | 0 | 160 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 14 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 195 | 0 | 60 | 0 | 16 | 0 | 0 | 68 | 45 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 301 | 183 | 8 | 0 | 36 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 94 | 201 | 0 | 0 | 0.7 | 58 | 60 | 5 | 2 | 163 | 262 | 64 | 5 | 5 | 79 | 0 | 3 | 8 | 270 | 22 | 8 | 0 | 15 | 0 | 0 | 7 |  | 476 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 4 | 8 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 35 | 0 | 8 | 0 | 20 | 10 | 8 | 0 | 70 | 160 | 0 | 0 | 177 | 0 | 0 | 170 | 61 | 0 | 0 | 0 |  | 4569.7 | 1428 | 5997.7 | 2780 | 476 | 1323 | 361 | 230 | 158 | 575 | 94 | 0.7 | 0 | 103.81
16:00 | 30 | 120 | 0 | 0 | 250 | 14 | 35 | 340 | 331 | 0 | 20 | 360 | 0 | 7 | 0 | 15 | 180 | 0 | 130 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 7 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 196 | 0 | 60 | 0 | 16 | 17 | 0 | 68 | 45 | 12 | 0 | 0 | 80 | 0 | 0 | 0 | 301 | 183 | 8 | 0 | 38 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 92 | 202 | 0 | 0 | 0.5 | 58 | 60 | 5 | 2 | 163 | 263 | 62 | 5 | 5 | 78 | 0 | 3 | 8 | 270 | 22 | 11 | 0 | 15 | 0 | 0 | 7 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 40 | 24 | 0 | 8 | 0 | 20 | 10 | 8 | 0 | 70 | 160 | 0 | 0 | 180 | 0 | 0 | 171 | 62 | 0 | 0 | 0 |  | 4521.5 | 1430 | 5951.5 | 2707 | 477 | 1327 | 362 | 230 | 158 | 598 | 92 | 0.5 | 0 | 103.8
17:00 | 30 | 120 | 0 | 0 | 220 | 14 | 35 | 340 | 281 | 0 | 20 | 350 | 0 | 7 | 0 | 15 | 152 | 0 | 120 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 7 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 195 | 0 | 60 | 0 | 8 | 17 | 0 | 68 | 45 | 12 | 0 | 0 | 80 | 0 | 0 | 0 | 272 | 184 | 8 | 0 | 20 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 88 | 184 | 0 | 0 | 0.3 | 58 | 60 | 5 | 2 | 100 | 266 | 50 | 5 | 5 | 79 | 0 | 3 | 8 | 265 | 22 | 11 | 0 | 15 | 0 | 0 | 7 |  | 476 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 15 | 8 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 18 | 24 | 0 | 8 | 0 | 20 | 10 | 8 | 0 | 70 | 160 | 0 | 0 | 177 | 0 | 0 | 170 | 30 | 0 | 0 | 0 |  | 4240.3 | 1400 | 5640.3 | 2588 | 476 | 1165 | 332 | 230 | 158 | 603 | 88 | 0.3 | 0 | 103.79
18:00 | 30 | 120 | 0 | 0 | 200 | 15 | 35 | 300 | 252 | 0 | 20 | 320 | 0 | 7 | 0 | 15 | 152 | 0 | 80 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 22 | 25 | 5 | 33 | 14 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 196 | 0 | 50 | 0 | 8 | 26 | 0 | 68 | 45 | 12 | 0 | 0 | 80 | 0 | 0 | 0 | 283 | 193 | 8 | 0 | 20 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 12 | 74 | 171 | 0 | 22 | 0.1 | 58 | 60 | 8 | 2 | 100 | 277 | 62 | 5 | 5 | 79 | 0 | 3 | 8 | 270 | 23 | 11 | 0 | 15 | 0 | 0 | 7 |  | 476 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 12 | 20 | 8 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 10 | 26 | 18 | 16 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 70 | 159 | 0 | 0 | 178 | 0 | 0 | 156 | 12 | 0 | 0 | 0 |  | 4157.1 | 1430 | 5587.1 | 2611 | 476 | 1099 | 324 | 229 | 158 | 616 | 74 | 0.1 | 0 | 103.77
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 30 | 120 | 0 | 0 | 260 | 54 | 40 | 320 | 302 | 0 | 20 | 350 | 0 | 13 | 4 | 15 | 182 | 0 | 120 | 0 | 7 | 10 | 19 | 10 | 34 | 0 | 8 | 36 | 18 | 36 | 22 | 25 | 5 | 33 | 14 | 10 | 0 | 78 | 78 | 0 | 0 | 19 | 0 | 205 | 0 | 50 | 0 | 11 | 40 | 68 | 68 | 75 | 14 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 202 | 8 | 0 | 39 | 0 | 3 | 6 | 41 | 0 | 0 | 0 | 0 | 14 | 12 | 98 | 200 | 32 | 19 | 0 | 58 | 60 | 22 | 13 | 100 | 288 | 63 | 30 | 10 | 80 | 0 | 10 | 8 | 320 | 23 | 11 | 0 | 25 | 0 | 0 | 100 |  | 476 | 32 | 0 | 102 | 99 | 120 | 0 | 0 | 42 | 36 | 32 | 68 | 22 | 14 | 0 | 0 | 0 | 43 | 38 | 26 | 25 | 16 | 47 | 8 | 40 | 20 | 10 | 11 | 0 | 70 | 160 | 17 | 18 | 192 | 0 | 0 | 140 | 54 | 0 | 0 | 0 |  | 5139 | 1978 | 7117 | 2912 | 476 | 1423 | 841 | 230 | 156 | 981 | 98 | 0 | 0 | 103.75
19:30 | 30 | 120 | 0 | 0 | 300 | 92 | 70 | 335 | 354 | 0 | 20 | 400 | 0 | 33 | 15 | 30 | 181 | 0 | 160 | 0 | 25 | 30 | 48 | 10 | 51 | 0 | 15 | 36 | 36 | 36 | 22 | 25 | 5 | 33 | 14 | 24 | 0 | 76 | 78 | 0 | 0 | 25 | 0 | 196 | 0 | 50 | 0 | 22 | 51 | 73 | 68 | 91 | 14 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 195 | 8 | 0 | 42 | 0 | 3 | 30 | 60 | 0 | 0 | 0 | 0 | 25 | 12 | 120 | 203 | 48 | 19 | 0 | 58 | 60 | 45 | 25 | 130 | 276 | 64 | 40 | 10 | 80 | 0 | 45 | 8 | 320 | 23 | 11 | 0 | 50 | 0 | 0 | 100 |  | 476 | 49 | 0 | 107 | 99 | 140 | 0 | 0 | 44 | 47 | 32 | 67 | 24 | 105 | 0 | 0 | 0 | 43 | 38 | 45 | 40 | 24 | 47 | 27 | 43 | 22 | 10 | 11 | 0 | 70 | 160 | 16 | 18 | 193 | 0 | 0 | 151 | 61 | 0 | 0 | 0 |  | 5825 | 2209 | 8034 | 3005 | 476 | 1757 | 1193 | 230 | 154 | 1099 | 120 | 0 | 0 | 103.75
20:00 | 30 | 120 | 0 | 0 | 300 | 102 | 70 | 335 | 354 | 0 | 20 | 400 | 0 | 32 | 15 | 30 | 181 | 0 | 160 | 0 | 25 | 7 | 40 | 10 | 51 | 0 | 24 | 36 | 36 | 36 | 22 | 25 | 5 | 33 | 14 | 24 | 0 | 79 | 78 | 0 | 0 | 25 | 0 | 196 | 0 | 50 | 0 | 0 | 51 | 73 | 68 | 93 | 17 | 0 | 0 | 120 | 0 | 0 | 0 | 290 | 183 | 55 | 0 | 42 | 0 | 3 | 35 | 62 | 0 | 0 | 0 | 0 | 25 | 14 | 110 | 204 | 48 | 22 | 0 | 58 | 60 | 53 | 45 | 130 | 265 | 55 | 60 | 47 | 79 | 0 | 43 | 8 | 275 | 23 | 11 | 0 | 50 | 0 | 0 | 100 |  | 476 | 48 | 0 | 108 | 99 | 150 | 0 | 0 | 43 | 56 | 32 | 64 | 25 | 110 | 0 | 0 | 0 | 43 | 38 | 51 | 40 | 43 | 47 | 43 | 43 | 22 | 10 | 11 | 0 | 70 | 160 | 16 | 18 | 187 | 0 | 0 | 161 | 72 | 0 | 0 | 0 |  | 5842 | 2286 | 8128 | 2958 | 476 | 1871 | 1202 | 230 | 157 | 1124 | 110 | 0 | 0 | 103.73
21:00 | 30 | 120 | 0 | 0 | 300 | 103 | 79 | 340 | 354 | 0 | 20 | 400 | 0 | 33 | 15 | 30 | 180 | 0 | 160 | 0 | 32 | 7 | 32 | 10 | 51 | 0 | 24 | 36 | 36 | 36 | 22 | 25 | 5 | 33 | 14 | 24 | 0 | 80 | 78 | 0 | 0 | 25 | 0 | 196 | 0 | 50 | 0 | 3 | 51 | 74 | 68 | 99 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 195 | 55 | 0 | 42 | 0 | 24 | 51 | 62 | 0 | 0 | 0 | 0 | 25 | 14 | 116 | 203 | 48 | 20 | 0 | 58 | 60 | 53 | 50 | 100 | 279 | 62 | 60 | 48 | 78 | 0 | 42 | 8 | 275 | 8 | 11 | 0 | 50 | 0 | 0 | 100 |  | 476 | 31 | 0 | 106 | 99 | 120 | 0 | 0 | 44 | 64 | 32 | 67 | 31 | 110 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 47 | 43 | 43 | 22 | 10 | 11 | 0 | 70 | 159 | 16 | 18 | 180 | 0 | 0 | 172 | 99 | 0 | 0 | 0 |  | 5893 | 2336 | 8229 | 2983 | 476 | 1926 | 1200 | 229 | 158 | 1141 | 116 | 0 | 0 | 103.71
22:00 | 30 | 120 | 0 | 0 | 300 | 109 | 79 | 345 | 353 | 0 | 20 | 400 | 0 | 32 | 15 | 30 | 180 | 0 | 160 | 0 | 32 | 7 | 32 | 10 | 51 | 0 | 24 | 36 | 36 | 36 | 22 | 25 | 9 | 33 | 14 | 25 | 0 | 80 | 78 | 0 | 0 | 26 | 0 | 199 | 0 | 50 | 0 | 29 | 51 | 75 | 80 | 99 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 323 | 196 | 55 | 0 | 42 | 0 | 24 | 51 | 60 | 0 | 0 | 0 | 0 | 33 | 14 | 138 | 202 | 48 | 20 | 0 | 58 | 60 | 53 | 50 | 100 | 278 | 64 | 60 | 48 | 78 | 0 | 44 | 8 | 315 | 8 | 11 | 0 | 50 | 0 | 0 | 100 |  | 477 | 16 | 0 | 107 | 99 | 120 | 0 | 0 | 44 | 65 | 32 | 67 | 33 | 110 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 45 | 43 | 42 | 22 | 10 | 11 | 0 | 70 | 159 | 16 | 18 | 186 | 0 | 0 | 179 | 99 | 0 | 0 | 0 |  | 6043 | 2336 | 8379 | 3029 | 477 | 1973 | 1240 | 229 | 158 | 1135 | 138 | 0 | 0 | 103.71
23:00 | 30 | 120 | 0 | 0 | 300 | 108 | 79 | 345 | 356 | 0 | 20 | 400 | 0 | 32 | 15 | 15 | 180 | 0 | 160 | 0 | 7 | 7 | 25 | 0 | 51 | 0 | 24 | 36 | 36 | 36 | 22 | 25 | 10 | 33 | 14 | 25 | 0 | 80 | 78 | 0 | 0 | 25 | 0 | 192 | 0 | 100 | 0 | 51 | 51 | 77 | 80 | 99 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 184 | 55 | 0 | 42 | 0 | 24 | 51 | 61 | 0 | 0 | 0 | 0 | 33 | 14 | 132 | 204 | 48 | 20 | 0 | 60 | 60 | 53 | 50 | 100 | 265 | 58 | 60 | 48 | 80 | 0 | 44 | 8 | 300 | 8 | 11 | 0 | 50 | 0 | 0 | 100 |  | 477 | 16 | 0 | 106 | 99 | 120 | 0 | 0 | 44 | 60 | 25 | 66 | 32 | 110 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 45 | 43 | 41 | 22 | 10 | 11 | 0 | 70 | 160 | 16 | 18 | 183 | 0 | 0 | 174 | 99 | 0 | 0 | 0 |  | 5988 | 2313 | 8301 | 2979 | 477 | 1960 | 1203 | 230 | 158 | 1162 | 132 | 0 | 0 | 103.71
24:00 | 30 | 120 | 0 | 0 | 300 | 109 | 79 | 345 | 354 | 0 | 20 | 400 | 0 | 10 | 15 | 15 | 182 | 0 | 160 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 24 | 18 | 18 | 18 | 22 | 25 | 10 | 33 | 14 | 8 | 0 | 80 | 78 | 0 | 0 | 26 | 0 | 193 | 0 | 100 | 0 | 51 | 51 | 67 | 80 | 99 | 4 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 186 | 55 | 0 | 42 | 0 | 24 | 51 | 21 | 0 | 0 | 0 | 0 | 33 | 0 | 134 | 202 | 8 | 20 | 0 | 60 | 60 | 53 | 50 | 130 | 264 | 64 | 30 | 48 | 80 | 0 | 44 | 8 | 290 | 8 | 11 | 0 | 15 | 0 | 0 | 100 |  | 476 | 16 | 0 | 106 | 99 | 120 | 0 | 0 | 42 | 60 | 25 | 67 | 32 | 110 | 0 | 0 | 0 | 43 | 0 | 102 | 40 | 43 | 45 | 8 | 40 | 22 | 10 | 8 | 0 | 70 | 160 | 16 | 18 | 181 | 0 | 0 | 173 | 99 | 0 | 0 | 0 |  | 5692 | 2231 | 7923 | 2968 | 476 | 1909 | 962 | 230 | 158 | 1086 | 134 | 0 | 0 | 103.71
KWH | 716000 | 2962575 | 0 | 0 | 5728790 | 1136932 | 1229312 | 8038400 | 6957000 | 0 | 496600 | 8145587 | 0 | 313920 | 248760 | 438960 | 4183910 | 0 | 3480000 | 0 | 295964 | 224496 | 283680 | 50089 | 358080 | 0 | 257424 | 270720 | 510930 | 518604 | 226656 | 600000 | 179640 | 673400 | 386200 | 145692 | 0 | 1815247 | 1832500 | 0 | 0 | 255420 | 0 | 4714032 | 0 | 1622670 | 0 | 545280 | 784544 | 1080904 | 1687680 | 1667520 | 577440 | 0 | 0 | 2540702 | 0 | 0 | 0 | 6765000 | 4590900 | 1338181 | 0 | 631944 | 0 | 298000 | 460424 | 248760 | 0 | 0 | 0 | 0 | 356300 | 307820 | 2616000 | 4246280 | 277428 | 209880 | 8842 | 1118000 | 1305363 | 504600 | 438000 | 3132707 | 6157995 | 1368000 | 655680 | 450360 | 1933080 | 0 | 427500 | 91800 | 7385870 | 453408 | 184800 | 0 | 632290 | 0 | 0 | 856800 |  | 11639272 | 191400 | 0 | 1102080 | 1456320 | 3060480 | 0 | 0 | 511200 | 651520 | 489750 | 1419990 | 545142 | 1467840 | 0 | 0 | 0 | 320112 | 263011 | 867906 | 723010 | 655392 | 461000 | 396480 | 358765 | 388080 | 185508 | 185526 | 0 | 1736290 | 3891800 | 118000 | 123000 | 4589982 | 0 | 0 | 4118936 | 1659204 | 430080 | 0 | 0 |  | 117634272 | 44007076 | 161641348 | 66037141 | 11639272 | 35678647 | 16854449 | 5628090 | 3647747 | 19531160 | 2616000 | 8842 | 0
Fuel Cost | 615760 | 2547814.5 | 0 | 0 | 4926759.4 | 920914.92 | 1155553.28 | 4903424 | 4243770 | 0 | 680342 | 5457543.29 | 0 | 1971417.6 | 1661716.8 | 2682045.6 | 2719541.5 | 0 | 3862800 | 0 | 1849775 | 1479428.64 | 2743185.6 | 319066.93 | 2144899.2 | 0 | 1717018.08 | 1930233.6 | 3193312.5 | 3251647.08 | 169992 | 450000 | 0 | 0 | 0 | 1378246.32 | 0 | 0 | 0 | 0 | 0 | 2418827.4 | 0 | 64346536.8 | 0 | 35552699.7 | 0 | 4793011.2 | 8449538.88 | 10517195.92 | 10446739.2 | 10772179.2 | 3776457.6 | 0 | 0 | 2312038.82 | 0 | 0 | 0 | 4667850 | 3213630 | 923344.89 | 0 | 423402.48 | 0 | 274160 | 377547.68 | 233834.4 | 0 | 0 | 0 | 0 | 274351 | 230865 | 17893440 | 3184710 | 2549563.32 | 161607.6 | 0 | 1162720 | 1357577.52 | 484416 | 394200 | 4041192.03 | 4310596.5 | 1559520 | 701577.6 | 495396 | 2203711.2 | 0 | 397575 | 85374 | 4726956.8 | 340056 | 140448 | 0 | 0 | 0 | 0 | 0 |  | 59360287.2 | 5579310 | 0 | 7273728 | 9757344 | 49212518.4 | 0 | 0 | 5756112 | 7674905.6 | 3119707.5 | 1405790.1 | 539690.58 | 9071251.2 | 0 | 0 | 0 | 3665282.4 | 2819477.92 | 7776437.76 | 6254036.5 | 5832988.8 | 4909650 | 3933081.6 | 3863899.05 | 426888 | 174377.52 | 140443.182 | 0 | 10539280.3 | 0 | 2722260 | 2637120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 269171055.58 | 214445867.612 | 483616923.192 | 47965750.802 | 59360287.2 | 26054311.99 | 103577722.87 | 10539280.3 | 0 | 218226130.03 | 17893440 | 0 | 0
Yesterday Day Peak | 30 | 120 | 0 | 0 | 180 | 13 | 30 | 350 | 212 | 0 | 20 | 260 | 0 | 7 | 0 | 15 | 205 | 0 | 170 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 0 | 25 | 6 | 33 | 7 | 0 | 0 | 80 | 78 | 0 | 0 | 8 | 0 | 226 | 0 | 60 | 0 | 11 | 0 | 0 | 68 | 45 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 261 | 204 | 8 | 0 | 10 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 3 | 62 | 156 | 0 | 0 | 2.1 | 30 | 44 | 5 | 2 | 130 | 286 | 64 | 5 | 5 | 78 | 0 | 3 | 0 | 310 | 23 | 8 | 0 | 15 | 0 | 0 | 0 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 5 | 0 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 24 | 0 | 8 | 0 | 21 | 10 | 5 | 0 | 72 | 160 | 0 | 0 | 193 | 0 | 0 | 150 | 14 | 0 | 0 | 0 |  | 5470.1 | DayPeak
Yesterday Evening Peak | 30 | 120 | 0 | 0 | 300 | 103 | 79 | 340 | 354 | 0 | 20 | 400 | 0 | 33 | 15 | 30 | 180 | 0 | 160 | 0 | 32 | 7 | 32 | 10 | 51 | 0 | 24 | 36 | 36 | 36 | 22 | 25 | 5 | 33 | 14 | 24 | 0 | 80 | 78 | 0 | 0 | 25 | 0 | 196 | 0 | 50 | 0 | 3 | 51 | 74 | 68 | 99 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 301 | 195 | 55 | 0 | 42 | 0 | 24 | 51 | 62 | 0 | 0 | 0 | 0 | 25 | 14 | 116 | 203 | 48 | 20 | 0 | 58 | 60 | 53 | 50 | 100 | 279 | 62 | 60 | 48 | 78 | 0 | 42 | 8 | 275 | 8 | 11 | 0 | 50 | 0 | 0 | 100 |  | 476 | 31 | 0 | 106 | 99 | 120 | 0 | 0 | 44 | 64 | 32 | 67 | 31 | 110 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 47 | 43 | 43 | 22 | 10 | 11 | 0 | 70 | 159 | 16 | 18 | 180 | 0 | 0 | 172 | 99 | 0 | 0 | 0 |  | 8229 | EvPeak
Forecast for Evening | 30 | 120 | 0 | 0 | 330 | 102 | 78 | 412 | 360 | 84 | 20 | 450 | 305 | 100 | 100 | 55 | 200 | 0 | 200 | 100 | 88 | 102 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 80 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 135 | 0 | 51 | 85 | 80 | 90 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 360 | 225 | 78 | 0 | 42 | 0 | 10 | 51 | 85 | 50 | 52 | 0 | 0 | 33 | 22 | 182 | 200 | 95 | 22 | 0 | 60 | 61 | 50 | 50 | 163 | 330 | 66 | 86 | 50 | 100 | 20 | 44 | 9 | 341 | 23 | 11 | 200 | 300 | 0 | 0 | 100 |  | 472 | 48 | 0 | 110 | 99 | 225 | 0 | 55 | 46 | 74 | 40 | 66 | 35 | 110 | 30 | 43 | 0 | 43 | 47 | 102 | 50 | 43 | 45 | 43 | 43 | 22 | 11 | 11 | 0 | 74 | 260 | 17 | 19 | 215 | 0 | 0 | 220 | 98 | 100
Forecast for Day | 30 | 120 | 0 | 0 | 260 | 102 | 40 | 412 | 350 | 84 | 20 | 450 | 0 | 100 | 100 | 55 | 180 | 0 | 150 | 100 | 84 | 94 | 100 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 40 | 0 | 80 | 80 | 0 | 0 | 25 | 0 | 215 | 0 | 52 | 0 | 51 | 85 | 62 | 90 | 98 | 44 | 0 | 0 | 120 | 0 | 0 | 0 | 360 | 225 | 78 | 0 | 42 | 0 | 10 | 51 | 85 | 0 | 52 | 0 | 0 | 33 | 22 | 136 | 165 | 95 | 0 | 2 | 60 | 61 | 50 | 50 | 163 | 310 | 54 | 86 | 50 | 80 | 0 | 44 | 9 | 341 | 23 | 0 | 0 | 300 | 0 | 0 | 100 |  | 472 | 0 | 0 | 110 | 99 | 225 | 0 | 0 | 0 | 50 | 40 | 66 | 35 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 45 | 43 | 0 | 22 | 11 | 11 | 0 | 70 | 250 |  | 0 | 215 | 0 | 0 | 220 | 96
Generation at 08:00(Today) | 30 | 120 | 0 | 0 | 240 | 15 | 40 | 345 | 248 | 0 | 20 | 320 | 0 | 7 | 0 | 15 | 120 | 0 | 80 | 0 | 7 | 7 | 0 | 0 | 8 | 0 | 6 | 0 | 18 | 17 | 22 | 25 | 10 | 33 | 14 | 0 | 0 | 76 | 78 | 0 | 0 | 0 | 0 | 208 | 0 | 50 | 0 | 24 | 8 | 17 | 80 | 13 | 18 | 0 | 0 | 120 | 0 | 0 | 0 | 327 | 201 | 8 | 0 | 39 | 0 | 5 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 15 | 102 | 201 | 0 | 0 | 0.4 | 58 | 60 | 5 | 5 | 100 | 280 | 62 | 10 | 5 | 80 | 0 | 5 | 8 | 280 | 23 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 462 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 9 | 8 | 66 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 0 | 0 | 19 | 10 | 5 | 0 | 70 | 160 | 0 | 0 | 182 | 0 | 0 | 141 | 52 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5197.1 | 8:00
| Highest Generation |  | 8788 | 1:00
| Day Peak Generation |  | 5470.1 | 12:00
| Evening Peak Generation |  | 8229 | 21:00
| HVDC Max Flow |  | 477 | 2:00
| HVDC EvPeak Flow |  | 476 | 21:00
| Load factor L.F |  | 76.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-20
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5470.1 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 5756.2 | MW
Evening Peak Generation : |  | 8229 | MW Hour : | 21:00 | Available Max Generation : |  | 11645 | MW
E.P. Demand (at gen end) : |  | 8229 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 9500 | MW
Maximum Generation : |  | 8788 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2145 | MW
Total Gen. (MKWH) : |  | 161.6413 | System Load Factor : | 76.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -820 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-20
Actual : | 103.35 | Ft.(MSL) , | Rule curve : | 20 | Ft.( MSL )
Gas Consumed : | Total = | 868.52 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 74020062.792
|  | Coal : | 10539280.3 | Oil : | 321803852.9 | Total : | 406363195.992
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3345.5862 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1133.3174 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1014.6366 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 916.5335 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 828.4104 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 668.4869 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 379.4047 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 172.2661 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 515.5434 |  |  | 0 | 0%
Total | 0 |  | 8974.1852 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,
|  |  |  | 3) Ghorasal Unit-1,4 |  | 12) Bheramara 360 MW
|  |  |  | 4) Baghabari 100 MW |  | 13) Ashuganj North 450 MW
|  |  |  | 5) Tongi GT |  | 14) Chandpur 163 MW
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Modunaghat-Chandraghona 132 kV Ckt-1 was under shut down from 08:56 to 10:17 for red hot maintenance at
Madunaghat end.
b) Bhola 225 MW tripped at 10:10 and GT2 & ST were synchronized at 11:04 & 12:46 respectively. Again tripped
at 13:36 and GT1 was synchronized at 16:22.
c) Tangail 132/33 kV T1,T2 & T3 transformers tripped at 11:15 due to 33 kV feeder fault and were switched on at 11:25. |  |  |  | About 87 MW power interruption occurred under Tangail S/S
area from 11:15 to 11:25.
d) Khulshi-Baraulia 132 kV Ckt-1 tripped at 10:33 from both end showing dist E/F L/O at Khulshi end and dist E/F
at Baraulia end and was switched on at 10:48.
e) Halishahar 132/33 kV T2 & T3 transformers tripped at 11:14 due to 33 kV EPZ feeder got fired showing E/F , O/C |  |  |  | About 93 MW power interruption occurred under Halishahar S/S
& differential relay and were switched on at 11:45 & 11:49 respectively. |  |  |  | area from 11:14 to 11:45.
f) Halishahar 132/33 kV T2 transformer was under shut down from 12:20 to 13:58 for red hot maintenance at |  |  |  | About 30 MW power interruption occurred under Halishahar S/S
33 kV side. |  |  |  | area from 12:20 to 13:58.
g) Magura 132/33 kV T1 transformer was under shut down from 12:50 to 13:28 for radiator valve problem.
h) Tangail 132/33 kV T1 & T2 transformers were under shut down from 14:33 to 17:28 for associated 33 kV bus |  |  |  | About 50 MW power interruption occurred under Tangail S/S
different point tightening & other works by distribution system. |  |  |  | area from 14:33 to 17:28.
i) Barapukuria-Rangpur 132 kV Ckt-2 was shut down at 07:28 (20/06/2018) for red hot at Barapukuria end T-connector
Y-phase and was switched on at 09:46.
j) Bottail 132/33 kV T2 transformer was under shut down from 07:07 to 08:48 (20/06/2018) due to red hot |  |  |  | About 35 MW power interruption occurred under Bottail S/S
at R-phase REB feeder. |  |  |  | area from 07:07 to 08:48(20/06/2018).
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 30 | 716000 | #1 Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2962575 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 5728790
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 79 | 1229312 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 103 | 1136932
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 20 | 496600 | #1 Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8038400 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 0 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 354 | 6957000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 8145587 | frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 33 | 313920 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 0 | 0 | Reserve
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 15 | 248760 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 438960 | Low demand
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 10 | 50089 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 226656
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 160 | 3480000
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 0 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 32 | 295964 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 180 | 4183910
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 0 | Reserve
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 7 | 224496 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 24 | 257424 | Low demand
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 36 | 270720 | Low demand
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 283680 | Low demand
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 36 | 510930 | Low demand
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 36 | 518604 | Low demand
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 51 | 358080 | Low demand
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 779640 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 673400
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 14 | 386200 | Low demand
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 24 | 145692 | Low demand
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 50 | 632290 | On test.
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5199 | 2601 | 49690611
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 255420
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 0 | 577440 | 33 kV fault.
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 158 | 3647747 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 196 | 4714032 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 50 | 1622670
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 3 | 545280 | tripped at 19:45.
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 51 | 784544
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 74 | 1080904
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 68 | 1687680 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | gas line problem.
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 0
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 1667520
| Chittagong area Total |  |  |  | 1561 | 724 | 16583237
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2540702 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Under maint.
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 195 | 4590900 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 301 | 6765000 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 42 | 631944
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 24 | 298000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 55 | 1338181 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 460424
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 62 | 248760 | frequency control.
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | gas line problem.
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | gas line problem.
** | Tripura |  | Imported power | 0 | 160 | 116 | 2616000
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 356300
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 0 | Reserve
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 14 | 307820
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | On test.
| Comilla Area Total |  |  |  | 2541 | 1005 | 20154031
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 203 | 4246280
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 209880
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 48 | 277428 | Low demand
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 8842
| United Mymensingh PPL |  | IPP | 200 | 0 | 100 | 856800 | On test.
| Mymensingh Area Total |  |  |  | 322 | 371 | 5599230
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1118000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1305363
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3132707 | frequency control.
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 279 | 6157995 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 504600
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 438000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 184800
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 62 | 1368000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 60 | 655680
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 450360
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1933080 | frequency control.
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 42 | 427500 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 8 | 453408
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 275 | 7385870 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 8 | 91800
| Sylhet Area Total |  |  |  | 1549 | 1192 | 25607163
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 31 | 191400
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 476 | 11639272
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 106 | 1102080
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1456320 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 44 | 511200
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3060480 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 64 | 651520
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 32 | 489750
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 0 | 0 | Reserve
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 430080 | On test.
| Khulna Area Total |  |  |  | 1769 | 972 | 19532102
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1467840
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 31 | 545142
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 67 | 1419990 | Machine problem.
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 99 | 1659204
| Barisal Area Total |  |  |  | 462 | 307 | 5092176
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 320112
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 38 | 263011
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 723010 | Low demand
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 655392 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 47 | 461000
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | FGMO
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 172 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 43 | 358765
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 388080
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 185508
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 185526
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 396480 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 867906
| Rajshahi Area Total |  |  |  | 1123 | 614 | 4804790
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 70 | 1736290
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 159 | 3891800
117 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 118000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 123000
| Rangpur Area Total |  |  |  | 484 | 263 | 5869090
| Total |  |  |  | 15010 | 8049 | 152932430
| Eastern Grid Total |  |  |  | 11172 | 5893 | 117634272
| Western Grid Total |  |  |  | 3838 | 2156 | 35298158
| National Grid Total |  |  |  | 15010 | 8049 | 152932430
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-19 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4899 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2863 | MW
i) Dhaka area |  |  | 2243 | MW | i) Khulna area |  |  | 1114 | MW
ii) Chittagong area |  |  | 798 | MW | ii) Rajshahi area |  |  | 935 | MW
iii) Comilla area |  |  | 799 | MW | iii) Barisal area |  |  | 233 | MW
iv) Mymensingh area |  |  | 667 | MW | iv) Rangpur area |  |  | 581 | MW
v) Sylhet area |  |  | 392 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7762 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 70 | 100 | Netrokona | 77 | 2000 | Central s/s | 62 | 2100
Munsiganj | 92 | 100 | Jamalpur | 103 | 2200 | Noapara | 73 | 100
Megnaghat | 22 | 1930 | Sherpur | 78 | 2200 | Jessore | 126 | 100
Shyampur | 80 | 100 | Srimongal | 31 | 1930 | Jhenida | 91 | 100
Bhulta | 84 | 100 | Shahjibazar | 81 | 2100 | Bottail | 106 | 400
Madanganj | 29 | 2300 | Fenchuganj | 41 | 1930 | G.K Project | 50 | 100
Shitalakhya | 52 | 100 | Kulawara | 39 | 2100 | Faridpur | 130 | 100
Rahim steel | 1 | 100 | Sylhet | 120 | 1930 | Madaripur | 130 | 100
Matuail | 44 | 100 | Chatak | 27 | 100 | Gopalganj | 76 | 100
Ghorasal | 58 | 100 | Sunamganj | 28 | 1930 | Bagerhat | 73 | 100
Narsingdi | 76 | 2200 | Biani Bazar | 40 | 2000 | Mongla | 26 | 1100
Haripur (SBU) | 32 | 600 | Comilla (S) | 138 | 2200 | Satkhira | 90 | 100
Ullon | 72 | 100 | Comilla(N) | 81 | 2100 | Gallamari | 38 | 100
Hasnabad | 143 | 100 | Chandpur | 106 | 2000 | Magura | 50 | 100
Magbazar | 79 | 1200 | Feni | 100 | 2200 | Chuadanga | 73 | 100
Maniknagar | 54 | 1700 | Chowmuhani | 168 | 2200 | Barisal | 108 | 2300
Bangabhaban | 30 | 1100 | Ashuganj | 49 | 1930 | Patuakhali | 90 | 100
Narinda | 46 | 100 | Daudkandi | 80 | 2100 | Bhandaria | 44 | 100
Dhanmondi | 60 | 1200 | B.Baria | 111 | 1930 | Ishurdi | 43 | 100
Lalbag | 43 | 100 | Ramganj | 31 | 1930 | Ruppur Paromanobik | 1 | 100
Madartek | 70 | 2200 | Madunaghat | 50 | 2100 | Natore | 106 | 100
Mirpur | 84 | 1900 | Hathazari | 79 | 2000 | Bogra | 199 | 2100
Kalyanpur | 92 | 1100 | Khulshi | 119 | 1400 | Noagaon | 97 | 100
Gulshan | 57 | 2000 | Halishahar | 104 | 1000 | Rajshahi | 125 | 2000
Uttara | 42 | 100 | Baraulia | 86 | 2100 | C.Nawabganj | 65 | 2100
Kamrangirchar | 94 | 100 | Sikalbaha | 31 | 2000 | Amnura | 36 | 2100
Savar | 100 | 1900 | Dohazari | 84 | 1930 | Pabna | 101 | 100
Bhasantec | 33 | 1000 | Cox'sbazar | 91 | 1930 | Shahjadpur | 65 | 100
Agargaon | 64 | 2000 | Chandraghona | 34 | 1930 | Serajganj | 71 | 100
Satmosjid | 76 | 100 | Kaptai | 4 | 1900 | Niyamatpur | 50 | 2100
Tongi | 98 | 2000 | A. Khaer Stl. | 10 | 1900 | Joypurhat | 43 | 2100
Kabirpur | 86 | 100 | Bakulia | 78 | 1900 | Rangpur | 104 | 2000
Basundhara | 82 | 100 | Julda | 11 | 2100 | Lalmonirhat | 84 | 2100
Manikganj | 148 | 1930 | TK chemical | 0.6 | 2100 | Saidpur | 107 | 2100
Joydevpur | 49 | 2100 | Modern Steel | 0.4 | 100 | Purbasadipur | 76 | 2100
New Tongi | 102 | 2000 | Shahmirpur | 23 | 100 | Thakurgaon | 62 | 2100
Korda | 212 | 100 | Abul Khair 230 | 183 | 500 | Palashbari | 83 | 100
Tangail | 162 | 2100 | BSRM | 104 | 1600 | Barapukuria | 41 | 2000
Mymensing | 189 | 2300 | Khagrachhari | 17 | 1930 | Panchagar | 39 | 2000
Kishorganj | 86 | 2300 | Goalpara | 34 | 100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-19
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 397 | 8:00 | 386 | 21:00 | Kaliakoir | 384 | 8:00 | 368 | 1:00
Bheramara | 401 | 6:00 | 392 | 24:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 227 | 7:00 | 223 | 1:00
Ishurdi | 235 | 10:00 | 220 | 1:00 | Comilla (N) | 235 | 11:00 | 225 | 1:00
Ashuganj | 235 | 7:00 | 230 | 1:00 | Hathazari | 221 | 11:00 | 210 | 1:00
Serajganj | 227 | 17:00 | 215 | 1:00 | Megnaghat | 230 | 7:00 | 228 | 1:00
Baghabari | 232 | 10:00 | 215 | 1:00 | Fenchuganj | 239 | 7:00 | 234 | 3:00
Barapukuria | 236 | 8:00 | 226 | 22:00 | Siddhirganj | 227 | 7:00 | 223 | 1:00
Bogra | 231 | 6:00 | 214 | 1:00 | Maniknagar | 226 | 8:00 | 221 | 1:00
Khulna South | 241 | 17:00 | 228 | 22:00 | Old Airport | 227 | 7:00 | 221 | 1:00
Rampura | 226 | 8:00 | 221 | 1:00 | Barisal | 242 | 14:00 | 210 | 10:00
Haripur | 225 | 10:00 | 222 | 2:00 | AKSML | 222 | 11:00 | 211 | 10:00
Hasnabad | 230 | 7:00 | 223 | 1:00 | BSRM | 225 | 11:00 | 214 | 1:00
Aminbazar | 229 | 8:00 | 221 | 1:00 | Bibiyana | 238 | 9:00 | 230 | 23:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 138 | 900 | 134 | 100 | Ramganj | 131 | 1300 | 111 | 1900
Munsiganj | 137 | 1000 | 133 | 100 | Madanhat | 133 | 1100 | 130 | 100
Megnaghat | 135 | 700 | 132 | 100 | Hathazari | 131 | 1100 | 126 | 100
Shyampur | 135 | 1200 | 132 | 200 | Khulshi | 128 | 1100 | 125 | 1400
Bhulta | 130 | 500 | 127 | 100 | Halishahar | 131 | 1100 | 126 | 1400
Madanganj | 139 | 900 | 133 | 1300 | Baraulia | 130 | 1000 | 125 | 1900
Shitalakhya | 139 | 900 | 134 | 100 | Sikalbaha | 131 | 1100 | 127 | 1900
Rahim steal | 137 | 1500 | 135 | 100 | Dohazari | 130 | 1100 | 125 | 1800
Matuail | 137 | 700 | 133 | 100 | Cox'sbazar | 122 | 1300 | 114 | 100
Ghorasal | 138 | 700 | 135 | 100 | Chandraghona | 131 | 900 | 129 | 1830
Narsinghdi | 137 | 1800 | 131 | 200 | Kaptai | 132 | 900 | 129 | 2100
Haripur (SBU) | 137 | 1500 | 133 | 600 | A. Khaer Stl. | 129 | 1200 | 125 | 1830
Ullon | 137 | 800 | 135 | 2000 | Bakulia | 128 | 1200 | 126 | 100
Hasnabad | 137 | 1830 | 134 | 600 | Julda | 131 | 1100 | 126 | 1600
Magbazar | 140 | 800 | 135 | 100 | TK Chemical | 132 | 800 | 130 | 1600
Maniknagar | 138 | 700 | 135 | 100 | Modern Steel | 129 | 1300 | 126 | 100
Bangabhaban | 138 | 700 | 135 | 100 | Shahmirpur | 130 | 1100 | 126 | 1830
Narinda | 138 | 700 | 135 | 100 | Khagrachhari | 132 | 1100 | 127 | 100
Dhanmondi | 137 | 800 | 135 | 2000 | Goalpara | 138 | 1830 | 133 | 100
Lalbag | 139 | 800 | 136 | 1600 | Central s/s | 137 | 700 | 132 | 200
Madartek | 138 | 800 | 135 | 1300 | Noapara | 136 | 1700 | 127 | 2200
Mirpur | 136 | 600 | 134 | 100 | Jessore | 131 | 1700 | 122 | 100
Kalyanpur | 136 | 500 | 134 | 100 | Jhenida | 133 | 1700 | 117 | 100
Gulshan | 136 | 600 | 133 | 100 | Bottail | 137 | 1700 | 136 | 100
Uttara | 134 | 700 | 130 | 100 | G.K.Project | 141 | 800 | 128 | 100
Kamrangirchar | 137 | 2000 | 132 | 100 | Faridpur | 136 | 1400 | 122 | 100
Savar | 135 | 2000 | 130 | 100 | Madaripur | 132 | 1400 | 125 | 100
Bhasantec | 136 | 800 | 131 | 100 | Gopalganj | 135 | 900 | 121 | 100
Agargaon | 136 | 700 | 132 | 100 | Bagerhat | 135 | 1400 | 129 | 2200
Satmosjid | 135 | 1800 | 131 | 100 | Mongla | 134 | 900 | 125 | 2100
Tongi | 139 | 800 | 135 | 100 | Satkhira | 134 | 1700 | 128 | 200
Kabirpur | 137 | 800 | 132 | 2100 | Gallamari | 137 | 1600 | 132 | 100
Basundhara | 135 | 900 | 131 | 100 | Magura | 132 | 1700 | 111 | 100
Manikganj | 142 | 800 | 135 | 100 | Chuadanga | 129 | 1600 | 108 | 100
Joydevpur | 141 | 800 | 133 | 100 | Barisal | 139 | 2000 | 130 | 1800
New Tongi | 140 | 800 | 134 | 100 | Patuakhali | 137 | 1400 | 125 | 1000
Kodda | 139 | 800 | 134 | 100 | Bhandaria | 137 | 1400 | 130 | 100
Tangail | 140 | 700 | 130 | 100 | Ishurdi | 141 | 900 | 130 | 100
Mymensing | 139 | 700 | 124 | 100 | Ruppur Paromanobik | 140 | 1600 | 129 | 100
Kishorganj | 135 | 600 | 123 | 100 | Natore | 137 | 1700 | 128 | 100
Netrokona | 139 | 600 | 122 | 100 | Bogra | 139 | 700 | 126 | 500
Jamalpur | 137 | 400 | 124 | 200 | Noagaon | 135 | 500 | 122 | 100
Sherpur | 137 | 600 | 121 | 200 | Rajshahi | 135 | 1700 | 127 | 1000
Srimongal | 140 | 600 | 135 | 1900 | C.Nawabganj | 133 | 1830 | 126 | 1930
Shahjibazar | 139 | 600 | 135 | 1830 | Amnura | 135 | 1500 | 128 | 400
Fenchuganj | 136 | 100 | 134 | 1900 | Pabna | 136 | 1700 | 125 | 100
Khulawara | 136 | 500 | 134 | 1700 | Shahjadpur | 143 | 1700 | 138 | 100
Sylhet | 135 | 200 | 133 | 1500 | Serajganj | 138 | 800 | 126 | 100
Chatak | 136 | 200 | 131 | 2100 | Niyamatpur | 136 | 600 | 119 | 2100
Sunamganj | 135 | 700 | 132 | 2300 | Joypurhat | 137 | 600 | 121 | 2100
Biani Bazar | 135 | 300 | 131 | 1830 | Rangpur | 134 | 600 | 111 | 100
Comilla(s) | 130 | 900 | 124 | 2200 | Lalmonirhat | 135 | 600 | 105 | 2100
Comilla(n) | 140 | 1200 | 133 | 2400 | Saidpur | 132 | 700 | 109 | 2000
Chandpur | 137 | 1100 | 112 | 2200 | Purbasadipur | 138 | 500 | 122 | 2000
Feni | 126 | 1100 | 114 | 2100 | Thakurgaon | 133 | 500 | 116 | 2000
Chowmuhani | 132 | 1600 | 108 | 100 | Palashbari | 135 | 600 | 115 | 100
Ashuganj | 140 | 400 | 135 | 100 | Barapukuria | 138 | 700 | 127 | 2000
Daudkandi | 135 | 900 | 129 | 2300 | Panchagar | 130 | 500 | 108 | 2000
B.Baria | 138 | 600 | 133 | 100

## L-Curve
Date | 2018-06-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 720 | 5692 | 2231 | 7923 |  |  |  | QF-LDC-12
0:30 | 770 | 6036 | 2319.5 | 8355.5 | Date: | 2018-06-19
1:00 | 820 | 6380 | 2408 | 8788
1:30 | 820 | 6203 | 2337.5 | 8540.5
2:00 | 820 | 6026 | 2267 | 8293
2:30 | 790 | 5765 | 2203.5 | 7968.5 | [5 empty] | Gen. at Eve. Peak | 8229 | 8229 MW (21:00 )
3:00 | 760 | 5504 | 2140 | 7644 | [6 empty] | 21:00
3:30 | 740 | 5356 | 2083.5 | 7439.5 | [5 empty] | Gen. at Day Peak | 5470.1 | 5470.1 MW (12:00 )
4:00 | 720 | 5208 | 2027 | 7235 | [6 empty] | 12:00
4:30 | 620 | 4990 | 2001 | 6991 | [5 empty] | Highest Generation | 8788
5:00 | 520 | 4772 | 1975 | 6747 | [6 empty] | 1:00
5:30 | 450 | 4455 | 1840 | 6295
6:00 | 380 | 4138 | 1705 | 5843
6:30 | 395 | 4021.05 | 1674.5 | 5695.55
7:00 | 410 | 3904.1 | 1644 | 5548.1
7:30 | 435 | 3795.6 | 1577 | 5372.6
8:00 | 460 | 3687.1 | 1510 | 5197.1
8:30 | 460 | 3750.8 | 1474.5 | 5225.3
9:00 | 460 | 3814.5 | 1439 | 5253.5
9:30 | 485 | 3873.7 | 1419 | 5292.7
10:00 | 510 | 3932.9 | 1399 | 5331.9
10:30 | 520 | 3953.4 | 1382 | 5335.4
11:00 | 530 | 3973.9 | 1365 | 5338.9
11:30 | 565 | 4056 | 1348.5 | 5404.5
12:00 | 600 | 4138.1 | 1332 | 5470.1
12:30 | 600 | 4240.15 | 1356 | 5596.15
13:00 | 600 | 4342.2 | 1380 | 5722.2
13:30 | 610 | 4477 | 1404 | 5881
14:00 | 620 | 4611.8 | 1428 | 6039.8
14:30 | 590 | 4590.75 | 1428 | 6018.75
15:00 | 560 | 4569.7 | 1428 | 5997.7
15:30 | 540 | 4545.6 | 1429 | 5974.6
16:00 | 520 | 4521.5 | 1430 | 5951.5
16:30 | 470 | 4380.9 | 1415 | 5795.9
17:00 | 420 | 4240.3 | 1400 | 5640.3
17:30 | 410 | 4198.7 | 1415 | 5613.7
18:00 | 400 | 4157.1 | 1430 | 5587.1
18:30 | 440 | 4648.05 | 1704 | 6352.05
19:00 | 480 | 5139 | 1978 | 7117
19:30 | 760 | 5825 | 2209 | 8034
20:00 | 780 | 5842 | 2286 | 8128 |  |  |  | Executive Engineer
20:30 | 770 | 5867.5 | 2311 | 8178.5 |  |  |  | Network Operation Division
21:00 | 760 | 5893 | 2336 | 8229
21:30 | 765 | 5968 | 2336 | 8304
22:00 | 770 | 6043 | 2336 | 8379 |  |  |  |  | Page 6 of 7
22:30 | 755 | 6015.5 | 2324.5 | 8340
23:00 | 740 | 5988 | 2313 | 8301
23:30 | 730 | 5840 | 2272 | 8112
24:00 | 720 | 5692 | 2231 | 7923
8229 MW (21:00 )
5470.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-19 |  | Energy | 161641348
[10 empty] | 2018-06-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2968 | 476 | 1909 | 962 | 230 | 158 | 1086 | 0 | 134
0:30 | 3030 | 476 | 2081.5 | 1095 | 231.5 | 157.5 | 1137 | 0 | 147 | Date: | 2018-06-19
1:00 | 3092 | 476 | 2254 | 1228 | 233 | 157 | 1188 | 0 | 160
1:30 | 3062 | 476.5 | 2229 | 1086 | 232.5 | 157 | 1137.5 | 0 | 160 | [7 empty] | Total Energy | 161.6413 | Total Energy Gen 161.641 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.641 MKWHr
2:00 | 3032 | 477 | 2204 | 944 | 232 | 157 | 1087 | 0 | 160 | [7 empty] | Energy not Served | 0
2:30 | 3011.5 | 477 | 1994.5 | 926.5 | 231.5 | 157 | 1011.5 | 0 | 159 | [7 empty] | Energy Requirement | 161.6413
3:00 | 2991 | 477 | 1785 | 909 | 231 | 157 | 936 | 0 | 158
3:30 | 2972 | 477 | 1662 | 892 | 231.5 | 157 | 892 | 0 | 156 | [6 empty] | Shortage
4:00 | 2953 | 477 | 1539 | 875 | 232 | 157 | 848 | 0 | 154
4:30 | 2832.5 | 477 | 1483 | 838 | 232.5 | 157 | 820 | 0 | 151
5:00 | 2712 | 477 | 1427 | 801 | 233 | 157 | 792 | 0 | 148
5:30 | 2558 | 477 | 1305.5 | 690.5 | 233.5 | 156.5 | 731 | 0 | 143
6:00 | 2404 | 477 | 1184 | 580 | 234 | 156 | 670 | 0 | 138
6:30 | 2367.5 | 477 | 1122 | 548 | 235 | 158 | 656 | 0 | 132 |  |  |  |  | Coal
7:00 | 2331 | 477 | 1060 | 516 | 236 | 160 | 642 | 0 | 126
7:30 | 2282 | 477 | 1024 | 468 | 235.5 | 160 | 641.5 | 0 | 84.5 |  |  |  | Oil |  |  |  | ,
8:00 | 2233 | 477 | 988 | 420 | 235 | 160 | 641 | 0 | 43
8:30 | 2267.5 | 477 | 1001.5 | 395.5 | 234.5 | 160 | 640.5 | 0 | 48.5
9:00 | 2302 | 477 | 1015 | 371 | 234 | 160 | 640 | 0 | 54
9:30 | 2384.5 | 476.5 | 1004.5 | 369 | 234 | 160 | 609.5 | 0 | 54
10:00 | 2467 | 476 | 994 | 367 | 234 | 160 | 579 | 0 | 54
10:30 | 2433 | 476 | 1011 | 384.5 | 234 | 159 | 574.5 | 0 | 62
11:00 | 2399 | 476 | 1028 | 402 | 234 | 158 | 570 | 0 | 70
11:30 | 2506.5 | 476.5 | 1036 | 361 | 233 | 158 | 565.5 | 0 | 66
12:00 | 2614 | 477 | 1044 | 320 | 232 | 158 | 561 | 0 | 62
12:30 | 2675.5 | 476.5 | 1079 | 324 | 232 | 158 | 581.5 | 0 | 68
13:00 | 2737 | 476 | 1114 | 328 | 232 | 158 | 602 | 0 | 74
13:30 | 2737 | 476 | 1114 | 328 | 232 | 158 | 602 | 0 | 74
14:00 | 2737 | 476 | 1114 | 328 | 232 | 158 | 602 | 0 | 74
14:30 | 2758.5 | 476 | 1218.5 | 344.5 | 231 | 158 | 588.5 | 0 | 84
15:00 | 2780 | 476 | 1323 | 361 | 230 | 158 | 575 | 0 | 94
15:30 | 2743.5 | 476.5 | 1325 | 361.5 | 230 | 158 | 586.5 | 0 | 93
16:00 | 2707 | 477 | 1327 | 362 | 230 | 158 | 598 | 0 | 92
16:30 | 2647.5 | 476.5 | 1246 | 347 | 230 | 158 | 600.5 | 0 | 90
17:00 | 2588 | 476 | 1165 | 332 | 230 | 158 | 603 | 0 | 88
17:30 | 2599.5 | 476 | 1132 | 328 | 229.5 | 158 | 609.5 | 0 | 81
18:00 | 2611 | 476 | 1099 | 324 | 229 | 158 | 616 | 0 | 74
18:30 | 2761.5 | 476 | 1261 | 582.5 | 229.5 | 157 | 798.5 | 0 | 86
19:00 | 2912 | 476 | 1423 | 841 | 230 | 156 | 981 | 0 | 98
19:30 | 3005 | 476 | 1757 | 1193 | 230 | 154 | 1099 | 0 | 120
20:00 | 2958 | 476 | 1871 | 1202 | 230 | 157 | 1124 | 0 | 110
20:30 | 2970.5 | 476 | 1898.5 | 1201 | 229.5 | 157.5 | 1132.5 | 0 | 113
21:00 | 2983 | 476 | 1926 | 1200 | 229 | 158 | 1141 | 0 | 116
21:30 | 3006 | 476.5 | 1949.5 | 1220 | 229 | 158 | 1138 | 0 | 127
22:00 | 3029 | 477 | 1973 | 1240 | 229 | 158 | 1135 | 0 | 138
22:30 | 3004 | 477 | 1966.5 | 1221.5 | 229.5 | 158 | 1148.5 | 0 | 135
23:00 | 2979 | 477 | 1960 | 1203 | 230 | 158 | 1162 | 0 | 132
23:30 | 2973.5 | 476.5 | 1934.5 | 1082.5 | 230 | 158 | 1124 | 0 | 133 | Max Temp. in Dhaka |  | 28.5° C
24:00 | 2968 | 476 | 1909 | 962 | 230 | 158 | 1086 | 0 | 134
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 161.641 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 161.641 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 77 | 77 | 77 | 77 | 77 | 76 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 78 | 76 | 79 | 80 | 80 | 80 | 80 | 1815247
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1832500
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 25 | 0 | [7 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 19 | 25 | 25 | 25 | 26 | 25 | 26 | 255420
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 221 | 221 | 222 | 221 | 169 | 169 | 169 | 169 | 196 | 196 | 195 | 226 | 214 | 195 | 195 | 196 | 195 | 196 |  | 205 | 196 | 196 | 196 | 199 | 192 | 193 | 4714032
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 115 | 100 | 50 | 50 | 51 | 51 | 52 | 52 | 50 | 80 | 80 | 60 | 100 | 80 | 60 | 60 | 60 | 50 |  | 50 | 50 | 50 | 50 | 50 | 100 | 100 | 1622670
| Dohazari Peaking | 74 | 74 | 74 | 74 | 74 | 60 | 60 | 59 | 59 | 27 | 16 | 0 | 0 | [6 empty] | 68 | 73 | 73 | 74 | 75 | 77 | 67 | 1080904
12 | Hathazari peaking | 57 | 57 | 57 | 57 | 57 | 40 | 40 | 40 | 40 | 0 | [5 empty] | 17 | 17 | 26 |  | 40 | 51 | 51 | 51 | 51 | 51 | 51 | 784544
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | 0
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 201 | 160 | 160 | 160 | 100 | 80 | 80 | 80 | 80 | 100 | 120 | 170 | 206 | 207 | 160 | 130 | 120 | 80 |  | 120 | 160 | 160 | 160 | 160 | 160 | 160 | 3480000
17 | Siddhirganj CCPP-335 MW | 198 | 198 | 170 | 170 | 172 | 172 | 170 | 120 | 120 | 120 | 120 | 205 | 202 | 207 | 223 | 180 | 152 | 152 |  | 182 | 181 | 181 | 180 | 180 | 180 | 182 | 4183910
18 | Summit Gazipur | 101 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 25 | 50 | 50 | 50 | 50 | 50 | 15 | 632290
19 | Ashuganj 195MW Modular | 186 | 186 | 186 | 148 | 102 | 72 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 55 | 55 | 55 | 55 | 55 | 1338181
20 | Ghorasal ST: Unit-1,2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 716000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2962575
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 250 | 165 | 162 | 131 | 184 | 184 | 190 | 180 | 180 | 250 | 250 | 250 | 220 | 200 |  | 260 | 300 | 300 | 300 | 300 | 300 | 300 | 5728790
26
28 | Ashuganj ST: Unit- 3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 105 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2540702
29 | Ashuganj ST: Unit- 4 | [5 empty] | 0
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 41 | 41 | 41 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 17 | 34 | 36 | 38 | 20 | 20 |  | 39 | 42 | 42 | 42 | 42 | 42 | 42 | 631944
33 | Ashuganj CCPP 225 MW | 184 | 183 | 184 | 184 | 183 | 183 | 182 | 184 | 183 | 225 | 184 | 204 | 206 | 185 | 183 | 183 | 184 | 193 |  | 202 | 195 | 183 | 195 | 196 | 184 | 186 | 4590900
34 | Ashuganj CCPP(South) | 301 | 301 | 301 | 301 | 287 | 250 | 250 | 257 | 228 | 231 | 228 | 261 | 261 | 264 | 301 | 301 | 272 | 283 |  | 301 | 301 | 290 | 301 | 323 | 301 | 301 | 6765000
Ashuganj CCPP(North)
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 496600
39 | Haripur 412 MW CCPP | 345 | 344 | 344 | 345 | 344 | 300 | 255 | 250 | 280 | 345 | 345 | 350 | 370 | 365 | 340 | 340 | 340 | 300 |  | 320 | 335 | 335 | 340 | 345 | 345 | 345 | 8038400
40 | Meghnaghat CCPP 450MW | 420 | 400 | 400 | 380 | 380 | 270 | 240 | 240 | 240 | 240 | 260 | 260 | 280 | 360 | 360 | 360 | 350 | 320 |  | 350 | 400 | 400 | 400 | 400 | 400 | 400 | 8145587
41 | Haripur Power CCPP 360MW | 351 | 350 | 351 | 348 | 321 | 231 | 202 | 212 | 212 | 212 | 212 | 212 | 212 | 314 | 331 | 331 | 281 | 252 |  | 302 | 354 | 354 | 354 | 353 | 356 | 354 | 6957000
42 | Mymensingh RPCL 210MW | 201 | 201 | 207 | 191 | 190 | 147 | 145 | 145 | 145 | 156 | 157 | 156 | 159 | 202 | 201 | 202 | 184 | 171 |  | 200 | 203 | 204 | 203 | 202 | 204 | 202 | 4246280
43 | Haripur NEPC 110MW
44 | Fenchugonj CCPP-1 | 60 | 60 | 60 | 60 | 60 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 1118000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1305363
46 | Shajibazar 330 MW | 292 | 292 | 297 | 299 | 240 | 239 | 240 | 242 | 265 | 280 | 266 | 286 | 296 | 268 | 262 | 263 | 266 | 277 |  | 288 | 276 | 265 | 279 | 278 | 265 | 264 | 6157995
47 | Shahjibazar GT: Unit- 8, 9 | 52 | 63 | 63 | 52 | 45 | 53 | 46 | 54 | 58 | 64 | 55 | 64 | 62 | 64 | 64 | 62 | 50 | 62 |  | 63 | 64 | 55 | 62 | 64 | 58 | 64 | 1368000
48 | Shahjibazar 86MW | 86 | 86 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 30 | 40 | 60 | 60 | 60 | 60 | 30 | 655680
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 10 | 10 | 47 | 48 | 48 | 48 | 48 | 450360
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 77 | 78 | 78 | 78 | 78 | 77 | 77 | 78 | 78 | 78 | 78 | 79 | 78 | 79 | 79 |  | 80 | 80 | 79 | 78 | 78 | 80 | 80 | 1933080
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 48 | 48 | 48 | 2 | 2 | 2 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 10 | 45 | 43 | 42 | 44 | 44 | 44 | 427500
53 | Sylhet (Desh) 10MW | 8 | 8 | 0 | [11 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 91800
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 0 | 0 |  |  | 2 | 3 | 2 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 184800
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 19 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 22 | 45 | 53 | 53 | 53 | 53 | 53 | 504600
56 | Shahjahanulla 25 MW | 23 | 0 | 8 | 15 | 21 | 0 | 15 | 21 | 21 | 21 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 23 |  | 23 | 23 | 23 | 8 | 8 | 8 | 8 | 453408
57 | Summit Bibiana- 2 | 310 | 280 | 280 | 290 | 270 | 280 | 280 | 260 | 300 | 300 | 290 | 310 | 320 | 305 | 270 | 270 | 265 | 270 |  | 320 | 320 | 275 | 275 | 315 | 300 | 290 | 7385870
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 36 | 36 | 36 | 36 | 36 | 36 | 18 | 518604
59 | Sikalbaha (Energis) | 51 | 51 | 51 | 51 | 24 | 8 | 8 | 8 | 8 | 8 | 0 | 11 | 16 | 16 | 16 | 16 | 8 | 8 |  | 11 | 22 | 0 | 3 | 29 | 51 | 51 | 545280
60 | Barabkunda (Regent)
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 0 | 0 | [10 empty] | 0 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 226656
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 0 | 0 | [11 empty] | 22 |  | 19 | 19 | 22 | 20 | 20 | 20 | 20 | 209880
63 | Tripura | 160 | 160 | 158 | 154 | 148 | 138 | 126 | 43 | 54 | 54 | 70 | 62 | 74 | 78 | 94 | 92 | 88 | 74 |  | 98 | 120 | 110 | 116 | 138 | 132 | 134 | 2616000
64 | Malancha, Ctg. EPZ (United)
65 | Feni (Doreen) 22MW
66 | Feni, Mohipal (Doreen)
67 | Jangalia (Summit) 33MW | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 14 | 25 | 25 | 25 | 33 | 33 | 33 | 356300
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 12 | 0 | 0 | 3 | 3 | 3 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 14 | 14 | 14 | 14 | 0 | 307820
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 10 | 10 | 10 | 10 | 10 | 10 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 |  | 5 | 5 | 5 | 5 | 9 | 10 | 10 | 179640
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 16 | 0 |  |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 673400
72 | Summit Rupganj | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 7 | 7 | 7 | 14 | 14 | 14 | 7 | 7 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 386200
73 | Ghorashal (Regent) | 105 | 106 | 106 | 23 | 23 | 25 | 25 | 15 | 14 | 13 | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 15 |  | 54 | 92 | 102 | 103 | 109 | 108 | 109 | 1136932
76 | Siddhirganj (Desh)
77 | Siddhirganj (Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 25 | 25 | 32 | 32 | 7 | 7 | 295964
78 | Gazipur (RPCL) | 24 | 0 | [17 empty] | 10 | 24 | 24 | 24 | 25 | 25 | 8 | 145692
79 | Kodda 150MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | [10 empty] | 19 | 48 | 40 | 32 | 32 | 25 | 0 | 283680
80 | Jamalpur 95MW | 8 | 8 | 8 | 8 | 8 | 0 | [13 empty] | 32 | 48 | 48 | 48 | 48 | 48 | 8 | 277428
81 | Lakdhanvi 52 MW
82 | Madanganj 102MW | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | [6 empty] | 4 | 15 | 15 | 15 | 15 | 15 | 15 | 248760
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 41 | 60 | 62 | 62 | 60 | 61 | 21 | 248760
85 | Keraniganj (Powerpac) 100MW | 0 | [18 empty] | 10 | 10 | 10 | 10 | 10 | 0 |  | 50089
86 | Meghnaghat CCPP(Summit)
87 | Meghnaghat (IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 7 | 7 | 7 | 7 | 7 |  | 13 | 33 | 32 | 33 | 32 | 32 | 10 | 313920
88 | Ghorashal 78MW (MAX) | 76 | 77 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 35 | 35 | 35 | 35 | 35 | 35 |  | 40 | 70 | 70 | 79 | 79 | 79 | 79 | 1229312
90 | Ashuganj (United) 53MW | 53 | 53 | 10 | 10 | 10 | 10 | 10 | 10 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 3 | 3 | 24 | 24 | 24 | 24 | 298000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 80 | 80 | 80 | 1687680
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 13 | 25 | 45 | 50 | 50 | 50 | 50 | 438000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 30 | 35 | 51 | 51 | 51 | 51 | 460424
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 10 | 30 | 7 | 7 | 7 | 7 | 7 | 224496
95 | Patenga 50MW | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 44 | 40 | 0 | 0 | 0 | 0 | 12 | 12 | 12 |  | 14 | 14 | 17 | 0 | 0 |  | 4 | 577440
96 | Chittagong ECPV 108 MW | 98 | 98 | 98 | 98 | 98 | 72 | 44 | 45 | 45 | 40 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 75 | 91 | 93 | 99 | 99 | 99 | 99 | 1667520
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 8 | 15 | 24 | 24 | 24 | 24 | 24 | 257424
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 51 | 51 | 51 | 51 | 51 | 8 | 358080
99 | Madanganj-55 MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 30 | 30 | 30 | 30 | 15 | 15 | 438960
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 36 | 36 | 36 | 36 | 36 | 18 | 510930
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 163 | 163 | 163 | 163 | 100 | 100 |  | 100 | 130 | 130 | 100 | 100 | 100 | 130 | 3132707
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.1 | 0.1 | 0.5 | 0.9 | 1.9 | 2.1 | 1.2 | 0.8 | 0.7 | 0.5 | 0.3 | 0.1 |  | 0 | 0 | 0 | 0 | 0 |  |  | 8842
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | [11 empty] | 36 | 36 | 36 | 36 | 36 | 36 | 18 | 270720
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 126 | 0 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 |  | 7 | 7 | 7 | 7 | 7 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 856800
112
113
114
115
116
117
118 | Eastern Zone Total | 6380 | 6026 | 5504 | 5208 | 4772 | 4138 | 3904.1 | 3687.1 | 3814.5 | 3932.9 | 3973.9 | 4138.1 | 4342.2 | 4611.8 | 4569.7 | 4521.5 | 4240.3 | 4157.1 | 0 | 5139 | 5825 | 5842 | 5893 | 6043 | 5988 | 5692 | 117634272
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 107 | 69 | 69 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 102 | 107 | 108 | 106 | 107 | 106 | 106 | 1102080
124 | Khulna (KPCL-2) | 100 | 100 | 100 | 84 | 100 | 66 | 66 | 32 | 32 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1456320
125
126 | Khulna (Aggreko) 55MW
127 | Faridpur Peaking | 45 | 45 | 45 | 45 | 45 | 26 | [11 empty] | 12 |  | 42 | 44 | 43 | 44 | 44 | 44 | 42 | 511200
128 | Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 140 | 150 | 120 | 120 | 120 | 120 | 3060480
129
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 48 | 16 | 16 | 16 | [8 empty] | 14 | 105 | 110 | 110 | 110 | 110 | 110 | 1467840
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 98 | 98 | 98 | 97 | 98 | 98 | 97 | 60 | 53 | 32 | 32 | 14 | 12 | 62 | 61 | 62 | 30 | 12 |  | 54 | 61 | 72 | 99 | 99 | 99 | 99 | 1659204
137 | Bhola CCPP 194MW | 90 | 89 | 87 | 90 | 89 | 89 | 89 | 90 | 85 | 90 |  | 15 | 43 |  |  |  | 24 | 68 |  | 68 | 67 | 64 | 67 | 67 | 66 | 67 | 1419990
| Bhola (Venture) 33MW | 34 | 33 | 37 | 36 | 36 | 35 | 26 | 28 | 27 | 26 | 1 | 2 | 6 | 6 | 9 | 12 | 10 | 14 |  | 22 | 24 | 25 | 31 | 33 | 32 | 32 | 545142
140 | Bangla Trak Noapara | 78 | 78 | 78 | 78 | 78 | [21 empty] | 430080
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 40 | 16 | 16 | [5 empty] | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 25 | 25 | 489750
142 | Gopalganj Peaking | 40 | 41 | 38 | 27 | 22 | 22 | 19 | 19 | 19 | 8 | 8 | 5 | 7 | 8 | 4 | 8 | 15 | 20 |  | 36 | 47 | 56 | 64 | 65 | 60 | 60 | 651520
143 | Bheramara GT-1,2,3 | 33 | [18 empty] | 32 | 49 | 48 | 31 | 16 | 16 | 16 | 191400
144
145 | Bheramara HVDC | 476 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 476 | 476 | 477 | 476 | 477 | 476 | 477 | 476 | 476 |  | 476 | 476 | 476 | 476 | 477 | 477 | 476 | 11639272
146 | Bheramara 360 MW
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 73 | 73 | 72 | 73 | 73 | 75 | 76 | 75 | 74 | 74 | 74 | 72 | 72 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1736290
151 | Barapukuria Unit-3 | 160 | 159 | 159 | 159 | 160 | 159 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 159 |  | 160 | 160 | 160 | 159 | 159 | 160 | 160 | 3891800
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | 43 | 43 | 0 | [14 empty] | 0 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 320112
| Sirajgonj Unit-1 225MW (Gas) | 180 | 176 | 170 | 178 | 177 | 175 | 175 | 177 | 170 | 165 | 190 | 193 | 196 | 193 | 177 | 180 | 177 | 178 |  | 192 | 193 | 187 | 180 | 186 | 183 | 181 | 4589982
157 | Sirajgonj Unit-1 225MW (Oil) | [6 empty] | 0 | 0 |  | 0 | 0 | [12 empty] | 0 |  |  | 0
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 167 | 165 | 162 | 168 | 168 | 167 | 167 | 167 | 156 | 148 | 151 | 150 | 161 | 179 | 170 | 171 | 170 | 156 |  | 140 | 151 | 161 | 172 | 179 | 174 | 173 | 4118936
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil) |  |  | 0
160 | Bera Peaking | 36 | 36 | 0 | [14 empty] | 10 |  | 38 | 38 | 38 | 38 | 38 | 38 | 0 | 263011
161 | Bogra (GBB) | 22 | 22 | 19 | 17 | 17 | 3 | 3 | 3 | 7 | 9 | 18 | 21 | 21 | 21 | 20 | 20 | 20 | 18 |  | 20 | 22 | 22 | 22 | 22 | 22 | 22 | 388080
162 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 185508
163 | Ullapara (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 185526
164 | Amnura 50MW | 33 | 40 | 40 | 40 | 12 | 12 | 12 | 12 | 12 | 12 | 30 | 30 | 30 | 40 | 40 | 40 | 18 | 18 |  | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 723010
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 35 | 24 | 24 | 16 |  | 16 | 24 | 43 | 43 | 43 | 43 | 43 | 655392
166 | Katakhali Peaking | 44 | 44 | 44 | 45 | 45 | 0 | 0 | 0 | [9 empty] | 0 |  | 47 | 47 | 47 | 47 | 45 | 45 | 45 | 461000
167 | Santahar Peaking | 42 | 42 | 42 | 0 | 0 | 0 | [11 empty] | 0 |  | 40 | 43 | 43 | 43 | 42 | 41 | 40 | 358765
168 | Rajlanka 52 MW | 43 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 8 | 8 | 8 | 8 |  | 8 | 27 | 43 | 43 | 43 | 43 | 8 | 396480
169 | Chapainawabganj-100 MW | 101 | 67 | 67 | 26 | 26 | 0 | 0 | [6 empty] | 0 | 26 | 26 | 26 | 26 |  | 26 | 45 | 51 | 102 | 102 | 102 | 102 | 867906
170
171
172 | Rangpur GT | 17 | 17 | 0 | [14 empty] | 0 |  | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 118000
173 | Saidpur GT | 18 | 0 | [15 empty] | 0 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 123000
175
176
177
178 | Western Zone Total | 2408 | 2267 | 2140 | 2027 | 1975 | 1705 | 1644 | 1510 | 1439 | 1399 | 1365 | 1332 | 1380 | 1428 | 1428 | 1430 | 1400 | 1430 | 0 | 1978 | 2209 | 2286 | 2336 | 2336 | 2313 | 2231 | 44007076
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953