## Daily Gen
Hourly Generation & Demand
Date: | 2016-11-30
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 4966 | 4966 | 0
2:00 | 4712 | 4712 | 0
3:00 | 4512 | 4512 | 0
4:00 | 4341 | 4341 | 0
5:00 | 4382 | 4382 | 0
6:00 | 4637 | 4637 | 0
7:00 | 4857 | 4857 | 0
8:00 | 5211 | 5211 | 0
9:00 | 5497 | 5497 | 0
10:00 | 5560 | 5560 | 0
11:00 | 5638 | 5638 | 0
12:00 | 5735 | 5735 | 0 | Day peak
13:00 | 5766 | 5766 | 0
14:00 | 5462 | 5462 | 0
15:00 | 5585 | 5585 | 0
16:00 | 5703 | 5703 | 0
17:00 | 6106 | 6106 | 0
18:00 | 7477 | 7477 | 0
18:30 | 0 | 0 | 0
19:00 | 7601 | 7601 | 0 | Evening peak
19:30 | 7532 | 7532 | 0
20:00 | 7363 | 7363 | 0
21:00 | 7047 | 7047 | 0
22:00 | 6395 | 6395 | 0
23:00 | 5872 | 5872 | 0
24:00 | 5359 | 5359 | 0

## forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [7 empty] | 2016-12-01 | Thursday
|  | Date (day): | 2016-12-01 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8190 | MW |  |  | (b) At Evening Peak Hour : |  | 9074 | MW
Sl. No. | Name of the Power Stations |  | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[8 empty] | On | 2016-11-30 | 2016-12-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Nos. of Unit X Capacity (MW) | MW | MW | MW | MW | MW | MW | MW | MW
1 | a) Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 38 | 38 | 38 | 38 |  |  | # 2 under maint.
| b) Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 100 | 100 | 110 | 110 |  | 60
| c) Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 190 | 190 | 190 | 190
| d) Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | 1/10/2016 |  | Long term maint.
| e) Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6(18/07/10)(18/07/2010) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 90 | 97 | 85 | 97
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 40 | 42 | 41 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 40 | 81 | 85 | 85
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 96 | 100 | 100
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3*32 | 96 | 60 | 0 | 0 | 0 | 0 |  | 60 | Under maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 382 | 402 | 412 | 412
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 40 | 95 | 96 |  |  | Engine problem
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 311 | 323 | 360 | 360
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 7 | 91 | 80 | 90 |  | 9 | Engine problem
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 305 | 305
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 65 | 81 | 80 | 81 |  |  | Engine problem
14 | Madanganj-55 MW |  | HFO | IPP | 5*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
15 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 70 | 50 | 80 | 93 |  | 50 | Engine problem
16 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
17 | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 105 | 110 | 110 | 110 | 40
18 | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
19 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 96 | 98 | 0 | 20 | 98 | 98
20 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 60 | 92 | 90 | 90 |  |  | Engine problem
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 60 | 92 | 92 | 92 |  | 10 | Engine problem
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 30 | 42 | 42 | 42 |  | 9 | Engine problem
24 | Kodda Peaking |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 117 | 150 | 149 | 149
25 | Northern 55 MW |  | HFO | RPP |  | 55 | 55 | 0 | 37 | 55 | 55
26 | Southern Power |  | HFO | RPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
| CLCPC Keranigonj 108 MW |  | HFO | RPP |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 6*3.67+7*8.73 | 80 | 80 | 57 | 57 | 57 | 57 |  | 23 | Engine problem
28 | Summit Power, Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Summit Power, Rupganj |  | Gas | SIPP,REB | 4*8.74 | 33 | 33 | 31 | 33 | 31 | 32
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 26 | 34 | 35 | 35 |  | 18 | Engine problem
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| Dhaka Area Total |  |  |  |  | 4774 | 4543 | 2437 | 2911 | 3482 | 3524 | 250 | 727
32 | a) Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Under maint.
| b) Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 170 | 150 | 160 | 160 |  |  | Gas shortage
33 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 26 | 26 | 25 | 25
34 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 52 | 51 | 35 | 50
35 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 70 | 168 | 92 | 120 |  | 50 | Unit-5 Under maint.
36 | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under Maintenance
37 | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | under maint for 7 days.
38 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 43 | 43 | 25 | 38 | 42 | 42
39 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 9 | 80
40 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 51 | 16 | 85
41 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 85 | 101 | 80 | 94 |  |  | Engine problem
42 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 19 | 18 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 2 | 5 | 3 | 5
43 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 91 | 98 | 90 | 98 |  | 10
| Chittagong area Total |  |  |  |  | 1408 | 1328 | 556 | 706 | 571 | 778 | 180 | 250
44 | a) Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 128 | 97 | 52 | 52 | 52 | 52 |  | 45 | #1 Under maint.
| b) Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 132 | 132 | 132 | 132
| c) Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 150 | 150
| d) Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
| e) Ashuganj : GT-2 |  |  | APSCL | 1*56 | 56 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
45 | Ashuganj CCPP 225 MW |  |  | APSCL | 1*142+1*75 | 217 | 217 | 200 | 220 | 225 | 225
46 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
47 | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 29 | 29 |  | 16 | Engine problem
48 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 20 | 20 | 20 | 35 |  | Gas shortage
49 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Date expired.
50 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 20 | 10 | 10 | 33 |  | Gas shortage
51 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.7+1*16 | 195 | 195 | 67 | 86 | 106 | 100 | 109 |  | Gas shortage
52 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 45 | 45 | 45 | 45 |  | 6 | Engine problem
53 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 10 | 86 | 52 | 85
54 | Titas (Daudkandi) Peaking |  |  | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 40
55 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST under maint.
56 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
57 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
** | Tripura |  |  | Imported Power |  | 100 | 100 | 50 | 72 | 56 | 80
58 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 29 | 31 | 30 | 30
59 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
60 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.6+2*6.9 | 25 | 25 | 13 | 16 | 22 | 21 |  | 9 | Engine problem
| Comilla Area Total |  |  |  |  | 2256 | 2149 | 1044 | 1254 | 1230 | 1320 | 177 | 558
61 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 122 | 130 | 152 | 152 | 72
62 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| Jamalpur IPP |  | HFO | IPP | 12*8.9 |  |  | 8 | 70 | 102 | 75 |  |  | On test
| Mymensingh Area Total |  |  |  |  | 232 | 224 | 150 | 220 | 276 | 249 | 72 | 0
63 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 60 | 60 | 65 | 60
64 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 30 | Under maint.
65 | Shahjibazar 330 MW |  | Gas | PDB | 2*110 | 220 | 220 | 0 | 0 | 0 | 0 |  |  | Under maint.
66 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 10 | 50 | 47 | 50
67 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 11 | 45 | 48 | 48
68 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 8 | 8 |  |  | Engine problem
69 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
70 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 79 | 78 | 79 |  | 7 | Engine problem
71 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 10 | 25 | 50 | 50
72 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 68 | 80 | 100 | 120
73 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 20 | 0 | 20
74 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 6 | 43 | 44 | 44 |  | 7 | Engine problem
75 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 5 | 16 | 12 | 25
76 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 235 | 230 | 341 | 341 |  |  | FGMO
77 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 7 | 8 |  |  | Engine problem
| Sylhet Area Total |  |  |  |  | 1321 | 1286 | 425 | 668 | 800 | 853 | 66 | 44
78 | Bheramara GT: Unit- 1,2,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 0 | 0 | 30
79 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105
** | Bheramara Interconnector(HVDC ) |  |  | Imported Power |  | 500 | 500 | 503 | 503 | 496 | 496
80 | a) Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11
| b) Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
81 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 5 | 110 | 110 | 110
82 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 99 | 115 |  | 0
83 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 37 | 0 | 43
84 | Khulna 150 MW GT |  | HSD | NWZPGCL | 1*158+1*72 | 230 | 230 | 0 | 0 | 230 | 230 |  |  | FGMO
85 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 0 | 70
Fuel shortage
86 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 32 | 32 | 32 |  |  | Engine problem
87 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 32 | 55 | 55
| Khulna Area Total |  |  |  |  | 1488 | 1419 | 532 | 889 | 1022 | 1181 | 0 | 160
88 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 96 | 16 | 110
89 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 25
90 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 11 | 12 | 9 | 13 |  | 20 | Engine problem
91 | Bhola CCPP GT-1,2,ST |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 173 | 187 | 197 | 193
| Barisal Area Total |  |  |  |  | 377 | 367 | 200 | 295 | 222 | 341 | 0 | 20
92 | a) Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 68 | 45 | 71 | 71 |  |  | FGMO
| b) Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
93 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 40 | 0 | 40
94 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 57
95 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 50 | 45 | 50
96 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 0 | 25 | 50 | 50
97 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 0 | 44
98 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 185 | 225 | 225 |  |  | FGMO
99 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 45
100 | Bogra (GBB) |  | Gas | RPP | 6*4 | 20 | 22 | 22 | 22 | 22 | 22
101 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 20 | 7 | 11 | 12 | 12 |  | 9 | Engine problem
102 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 5 | 11 | 6 | 11
103 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 807 | 809 | 302 | 510 | 483 | 679 | 0 | 109
104 | a) Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 89 | 89 | 90 | 90
| b) Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 0 | 0 | 0 | 0 |  |  | Under maint.
105 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 19 | 0 | 19
106 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 20 | 0 | 20
107 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 40 | 0 | 20 | 14 | 20 |  | 20 | Engine problem
| Rangpur Area Total |  |  |  |  | 337 | 280 | 89 | 148 | 104 | 149 | 0 | 20
| Total |  |  |  |  | 13000 | 12405 | 5735 | 7601 | 8190 | 9074 | 745 | 1888
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5325.3032 | 7058 | 7604.923 | 8425.7719
A. |  | 2016-11-30 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 7601 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 4341 | MW at | 4:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7601 | MW
3 | Day peak Generation : |  |  | 5735 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7058 | MW
4 | Evening peak Generation : |  |  | 7601 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 137.492 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 95.6725 | MKWHr |  | By Oil: | 25.119 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 2.1177 | MKWHr |  | By Hydro: | 2.1072 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 745 | For Oil: | 0 | MW | Dhaka | 2746 | 2746 | 0
|  |  | For Water Shortage: |  |  | 50 | MW | Chittagong | 767 | 767 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 1888 | MW | Khulna | 855 | 855 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 866.04 | MMCFD |  |  | Rajshahi | 723 | 723 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 65146721.409 | ii) Oil : | Taka | 194023583.683 | Comilla | 610 | 610 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 8241979.424 | Total | Taka | 267412284.516 | Mymensingh | 484 | 484 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 272 | 272 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -540 | MW at | 19:00 | hrs | Barisal | 147 | 147 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -280 | MW at | 15:00 | hrs | Rangpur | 454 | 454 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 29.2° C |  |  | Total | 7058 | 7058 | 0
B. |  | 2016-12-01 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 7650 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 9074 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 5850 | MW
4 | Reserve (Generation end) |  |  |  | 1424 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 137.49 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4422 | MW at | 4:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.6276 | MKWHr. | ii) During Peak demand: |  | 503 | MW at | 19:00 | hrs. | iii)Maximum: | 504 | 17:00
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.848 | MKWHr.
*Cost for HVDC & Tripura energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.22 |  | (b) Today: | 103.11 |  | (c) Rule Curve: |  | 106
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2016-12-01
Till now the maximum generation is : - |  |  | 9036 MW | 21:00 | Hrs on | 2016-06-30
The Summary of Yesterday's |  | 2016-11-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5735 | MW Hour : | 12:00 | Min. Gen. at | 4:00 | 4422 | MW
Evening Peak Generation : |  | 7601 | MW Hour : | 19:00 | Max Generation : |  | 9074 | MW
E.P. Demand (at gen end) : |  | 7601 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 7650 | MW
Maximum Generation : |  | 7601 | MW Hour : | 19:00 | Reserve (Generation end) |  | 1424 | MW
Total Gen. (MKWH) : |  | 137.492 | System L/ Factor : | 75.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -280 | MW at | 15:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2016-12-01
Actual : | (c) Rule Curve: | Ft.(MSL) , | Rule curve : | 0 | Ft.( MSL )
Gas Consumed : | Total | 866.04 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 65146721.409
|  | Coal : | 8241979.424 | Oil : | 194023583.683 | Total : | 267412284.516
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2838 |  |  | - | -
Chittagong Area | 0 | 0:00 | 794 |  |  | - | -
Khulna Area | 0 | 0:00 | 792 |  |  | - | -
Rajshahi Area | 0 | 0:00 | 770 |  |  | - | -
Comilla Area | 0 | 0:00 | 589 |  |  | - | -
Mymensingh Area | 0 | 0:00 | 449 |  |  | - | -
Sylhet Area | 0 | 0:00 | 279 |  |  | - | -
Barisal Area | 0 | 0:00 | 157 |  |  | - | -
Rangpur Area | 0 | 0:00 | 434 |  |  | - | -
Total | 0 |  | 7102 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010) |  | 10) Ghorasal Unit-2
| Nil |  |  | 2) Kaptai Unit-5 |  | 11) Tongi GT
|  |  |  | 3) Ashuganj ST: Unit- 1 |  | 12) Sikalbaha Peaking GT
|  |  |  | 4) Khulna ST 110 MW (04/11/2014) |  | 13) Siddhirgonj GT: Unit-1,2
|  |  |  | 5) Ghorasal Unit-5 |  | 14) Sikalbaha ST
|  |  |  | 6) Baghabari 100 MW |  | 15) Barapukuria unit-2
7) Haripur SBU GT- 3
8) Ashugonj CCPP South
9) Chittagong Unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Comments on Power Interruption
a) Shahmirpur-Sikalbaha 132 kV Ckt-2 was under shut down from 08:40 to 14:57 for A/M.
b) Khulshi-AKSML 132 kV Ckt was under shut down from 09:21 to 14:36 for A/M.
c) Comilla(N)-Daudkandi 132 kV Ckt-2 was under shut down from 08:35 to 16:08 for A/M.
d) Tongi(old) 132/33 kV T2 transformer was under shut down from 09:20 to 15:43 for A/M.
e) Haripur 230 kV bus-2 was under shut down from 09:51 to 15:57 for A/M.
f) Netrokona 132/33 kV T3 transformer was under shut down from 08:10 to 14:50 for A/M.
g) Jamalpur 132/33 kV T3 transformer was under shut down from 08:58 to 16:53 for A/M.
h) Kishoreganj-Mymensingh 132 kV Ckt-2 was under shut down from 08:42 to 14:44 for A/M.
i) Mirpur 132/33 kV T1 transformer was shut down at 09:05 for A/M.
j) Hasnabad-Aminbazar 132 kV Ckt-2 was under shut down from 09:24 to 16:58 for A/M.
k) Sylhet-Chattak 132 kV Ckt-1 was under shut down from 08:34 to 14:47 for A/M.
l) Kabirpur-Manikganj 132 kV Ckt-1 and associated T3 & T4 transformers were under shut down
from 09:30 to 16:39 for A/M.
m) Sirajganj-Shahjadpur 132 kV Ckt was under shut down from 08:28 to 15:39 for A/M.
n) Bogra-Polashbari 132 kV Ckt-2 was under shut down from 08:26 to 16:20 for A/M.
o) Rajshahi-Chapainawabganj 132 kV Ckt-2 was under shut down from 09:23 to 14:32 for A/M.
p) Rangpur-Lalmonirhat 132 kV Ckt was under shut down from 08:40 to 16:05 for A/M. |  |  |  | About 30 MW power interruption occurred under Lalmonirhat S/S area
from 08:40 to 16:05.
q) Aminbazar-Hasnabad 132 kV Ckt-1 & 2 was shut down at 08:20 from Aminbazar end to limit flow
of Hasnabad -Meghnaghat Ckt-1 and Ckt-1 was switched on at 16:48.
r) Shyampur-Hasnabad 132 kV Ckt tripped t 10:05 from Hasnabad end only showing dist Z1 B-phase |  |  |  | About 60 MW power interruption occurred under Shyampur S/S area
and was switched on at 10:15. |  |  |  | from 10:05 to 10:15.
s) Bheramara HVDC 11 kV auxiliary transformer was under shut down from 10:08 to 14:05 for A/M.
t) Ghorasal-Rampura 230 kV Ckt-1 tripped at 15:32 from both ends showing dist 87 TEF1, AB-phase
at Rampura end and no relay at Ghorasal end and was switched on at 15:55.
u) Kabirpur 132/33 kV T3 transformer was under shut down from 16:20 to 16:44 for Red hot maintenance |  |  |  | About 25 MW power interruption occurred under Kabirpur S/S area
at 33 kV Noyerhat feeder. |  |  |  | from 16:20 to 16:44.
v) Hasnabad-Meghnaghat 230 kV Ckt-1 was shut down since 07:32 (01/12/2016) for A/M.
.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2016-11-30 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1a | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 38 | 929000 | #2 Unde maint.
[6 empty] | 0 |  | 0
1b | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 100 | 2485035 | 0
1c | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 190 | 4559310 | 0
1d | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 0 | 0 | Under maint.
1e | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 |  | Long term maint.
2 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 97 | 1756410 | 0
3 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 42 | 929520 | 0
4 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 81 | 1411200 | 0
5 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 96 | 1892273 | Engine problem
6 |  |  | 1*32 | PDB | 20 | 0 | 289700 | Under maint.
| Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 0 |  | Under maint.
|  |  | 1*32 | PDB | 20 | 0 |  | Under maint.
7 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 402 | 9222580 | 0
8 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 40 | 103100 | Low demand.
9 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 323 | 7300000 | Low demand.
10 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 400 | 9214000 | Low demand.
11 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 91 | 570240 | Engine problem
12 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 305 | 0 | 0 | Reserve
13 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 81 | 1191528 | Engine problem
14 | Madanganj-55 MW |  | 5*17.08+1*11.3 | IPP | 55 | 55 | 496570 | 0
15 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 50 | 918615 | Low demand.
16 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 19 | 442620 | Engine problem
17 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 110 | 2627100 | Gas shortage
18 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 0 | 0 | Gas shortage.
19 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 98 | 20 | 60480 | Low demand.
20 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 92 | 1167360 | Engine problem
21 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 51 | 67210 | 0
22 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 92 | 1270224 | Engine problem
23 | Katpotti 52 MW |  |  | RPP | 51 | 42 | 535872 | Engine problem
24 | Kodda Peaking |  | 9*17.06 | BPDB-RPCL | 149 | 150 | 1509600 | 0
| Northern 55 MW |  |  | RPP | 55 | 37 | 238703 | Low demand.
25 | Southern Power |  |  | RPP | 55 | 55 | 726090 | 0
| CLCPC Keranigonj 108 MW |  |  |  |  | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | 6*3.67+7*8.73 | SIPP, REB | 80 | 57 | 1226360 | Engine problem
27 | Summit Power, Maona |  | 4*8.73 | SIPP, REB | 33 | 33 | 808300 | 0
28 | Summit Power, Rupganj |  | 4*8.74 | SIPP, REB | 33 | 33 | 784000 | 0
29 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 34 | 465444 | Engine problem
30 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Under maintenance.
| Dhaka Area Total |  |  |  | 4543 | 2911 | 55198444
31 | a) Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
| b) Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 150 | 3400000
32 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 26 | 262080
33 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 51 | 794400 | 0
34 | Chittagong ECPV 108 MW |  |  | IPP | 108 | 98 | 1296000 | Engine problem
35 |  |  | 1*40 | PDB | 40 | 44 | 1217658
|  |  | 1*40 | PDB | 40 | 44
| Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 50
|  |  | 1*50 | PDB | 50 | 30 | 889500
|  |  | 1*50 | PDB | 50 | 0 |  | Under maint.
36 | Shikalbaha ST |  | 1*60 | PDB | 40 | 0 | 0 | Under maintenance.
37 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 0 | 0 | FGMO
38 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 0 | 0 | Reserve
39 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 51 | 506605 | Low demand.
40 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 101 | 1568280 | 0
41 | Shikalbaha (Energis) |  |  | RPP | 43 | 38 | 332160
42 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 18 | 447648 | Engine problem
* | Malancha, Ctg EPZ(United) |  |  |  |  | 5 | 75120 | 0
| Chittagong Area Total |  |  |  | 1328 | 706 | 10789451
43 | a) Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 97 | 0 | 1260610 | # 1 Under maint.
|  |  | 1*64 | APSCL |  | 52
| b) Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 132 | 3094318 | 0
| c) Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 150 | 3512725 | 0
| d) Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 135 | 3175706 | 0
| Ashuganj : GT-2 |  | 1*56 | APSCL | 40 | 0 | 0 | Under maint.
44 | Ashuganj CCPP 225 MW |  | 1*142+1*75 | APSCL | 217 | 220 | 0 | 0
45 | Ashuganj CCPP(South) |  |  | APSCL | 360 | 0 | 5223800 | Under maint.
46 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 29 | 676296 | Gas shortage due to fertilizer.
47 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 20 | 236640 | Gas shortage due to fertilizer.
48 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 0 | 0 | Date expired.
49 | Ashuganj (United) |  | 14*4 | RPP | 53 | 20 | 310000 | Gas shortage due to fertilizer.
50 | Ashuganj Modular 200 MW |  | 20*9.7+1*16 | IPP | 195 | 86 | 1856727 | Gas shortage due to fertilizer.
51 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 45 | 801016 | Engine problem
52 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 86 | 828613 | 0
53 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 0 | 0 | Reserve
54 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 90 | 2092550 | 0
55 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 19 | 468756 | 0
56 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 8 | 183240 | Engine problem
** | Tripura |  |  |  | 100 | 72 | 1848000
57 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 31 | 456900 | 0
58 | Lakdanavi-52 MW |  |  | IPP | 52 | 43 | 114965 | Low demand.
59 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 16 | 408640 | Engine problem
| Comilla Area Total |  |  |  | 2149 | 1254 | 26549502
60 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 130 | 3119000 | FGMO
61 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 20 | 391068 | 0
| Jamalpur RPP |  |  | RPP |  | 70 | 406650 | 0
| Mymensingh Area Total |  |  |  | 224 | 220 | 3916718
62 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 60 | 1322000 | 0
63 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 0 | 0 | Under maint.
| Shahjibazar CCPP 330 MW |  | 2*110 | PDB | 220 | 0 | 0 | Under maint.
64 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 50 | 641400
65 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 45 | 604000 | 0
66 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 10 | 234624 | 0
0
67 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 0 | 0 | Gas shortage
68 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 79 | 823680 | 0
69 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 25 | 310680 | Engine problem
70 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 80 | 2202730 | 0
71 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 20 | 134000 | 0
72 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 43 | 486580 | Engine problem
73 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 16 | 191088 | 0
74 | Summit Bibiana-2 |  | 1*222+1*119 | IPP | 341 | 230 | 5897125 | FGMO
75 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 10 | 61200 | 0
| Sylhet Area Total |  |  |  | 1286 | 668 | 12909107
|  |  | 1*20 | PDB | 16 | 0 | 169856 | Reserve
76 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 0 |  | Reserve
|  |  | 1*20 | PDB | 16 | 0 |  | Long term maint.
Reserve
** | Bheramara Interconnector(HVDC) |  |  | Imported Power | 500 | 503 | 10627636
77 | a) Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint.
| b) Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
78 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 110 | 631200 | 0
79 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 115 | 745920 | 0
80 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 37 | 127680 | 0
81 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 230 | 0 | 0 | Reserve
82 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 60 | 0 | Low demand.
83 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
84 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 32 | 259125 | Engine problem
85 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 32 | 40800 | Low demand.
| Khulna Area Total |  |  |  | 1419 | 889 | 12602217
86 | Summit Barisal 110MW |  | 7*17.076 | IPP | 110 | 96 | 811200 | Low demand.
87 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 0 | 0 | Reserve
|  |  | 1*20 | PDB | 14 | 0 |  | Reserve.
88 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 12 | 237861 | Engine problem
89 | Bhola CCPP GT-1,2,ST |  | 2*63+1*68 | PDB | 194 | 187 | 4190729 | 0
| Barisal Area Total |  |  |  | 367 | 295 | 5239790
90 | a) Baghabari GT |  | 1*71 | PDB | 71 | 45 | 1350000 | FGMO
| b) Baghabari GT |  | 1*100 | PDB | 100 | 0 | 0 | Under maint.
91 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 40 | 120507 | Low demand.
92 | Bera Peaking |  | 9*8.29 | PDB | 71 | 0 | 0 | Reserve
93 | Amnura |  | 7*7.79 | QRPP | 50 | 50 | 164860 | 0
94 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 25 | 50880 | Low demand.
95 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 42 | 176202 | 0
96 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 185 | 4977745 | FGMO
97 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 36 | 169084 | Low demand.
98 | Bogra (GBB) |  | 6*4 | RPP | 22 | 22 | 454200 | 0
99 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 20 | 11 | 208240 | Engine problem
100 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 163980 | 0
101 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 43 | 97440 | Low demand.
| Rajshahi Area Total |  |  |  | 809 | 510 | 7933138
102 | a) Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 89 | 2117672 | 0
| b) Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 0 | 0 | Under maint.
103 | Rangpur GT |  | 1*20 | PDB | 20 | 19 | 67500 | 0
104 | Saidpur GT |  | 1*20 | PDB | 20 | 20 | 80000 | 0
105 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 40 | 20 | 88500 | Engine problem
| Rangpur Area Total |  |  |  | 280 | 148 | 2353672
| Total |  |  |  | 12405 | 7601 | 137492039
| Eastern Grid Total |  |  |  | 8488 | 5759 | 109363222
| Western Grid Total |  |  |  | 2600 | 1842 | 28128817
| National Grid Total |  |  |  | 11088 | 7601 | 137492039
*Data collected from respective power station over telephone.

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2016-11-30 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4879 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2179 | MW
i) Dhaka area |  |  | 2746 | MW | i) Khulna area |  |  | 855 | MW
ii) Chittagong area |  |  | 767 | MW | ii) Rajshahi area |  |  | 723 | MW
iii) Comilla area |  |  | 610 | MW | iii) Barisal area |  |  | 147 | MW
iv) Mymensingh area |  |  | 484 | MW | iv) Rangpur area |  |  | 454 | MW
v) Sylhet area |  |  | 272 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7058 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 100 | 1100 | Kishorganj | 53 | 1900 | Jessore | 100 | 1800
Munsiganj | 74 | 1930 | Netrokona | 51 | 1800 | Jhenida | 63 | 1830
Megnaghat | 38 | 1830 | Jamalpur | 74 | 1830 | Bottail | 74 | 1800
Shyampur | 135 | 1700 | Sherpur | 51 | 1930 | G.K Project | 28 | 1800
Bhulta | 123 | 1830 | Srimongal | 22 | 1800 | Faridpur | 104 | 1800
Madanganj | 49 | 600 | Shahjibazar | 48 | 2000 | Madaripur | 84 | 2000
Shitalakhya | 83 | 1200 | Fenchuganj | 32 | 1800 | Gopalganj | 47 | 1800
Rahim steel | 9 | 1000 | Khulawara | 28 | 1800 | Bagerhat | 56 | 1800
Matuail | 58 | 900 | Sylhet | 110 | 1800 | Mongla | 25 | 1600
Ghorasal | 79 | 1930 | Chatak | 38 | 1800 | Satkhira | 58 | 1830
Narsingdi | 67 | 1900 | Comilla (S) | 74 | 1830 | Gallamari | 35 | 1300
Haripur (SBU) | 62 | 1900 | Comilla(N) | 100 | 1930 | Magura | 29 | 1800
Ullon | 67 | 1800 | Chandpur | 78 | 2000 | Chuadanga | 48 | 1800
Hasnabad | 134 | 1830 | Feni | 71 | 1830 | Barisal | 76 | 1800
Magbazar | 94 | 1200 | Chowmuhani | 130 | 1800 | Patuakhali | 43 | 2000
Maniknagar | 76 | 1100 | Ashuganj | 40 | 1830 | Bhandaria | 30 | 1800
Bangabhaban | 30 | 1300 | Daudkandi | 70 | 1930 | Ishurdi | 34 | 1900
Narinda | 76 | 1500 | B.Baria | 72 | 1830 | Natore | 72 | 1900
Dhanmondi | 80 | 1300 | Madanhat | 40 | 1800 | Bogra | 160 | 1800
Lalbag | 76 | 1300 | Hathazari | 80 | 1800 | Noagaon | 77 | 2000
Madartek | 44 | 2000 | Khulshi | 148 | 1300 | Rajshahi | 93 | 1800
Mirpur | 83 | 1800 | Halishahar | 106 | 1800 | C.Nawabganj | 42 | 1900
Kalyanpur | 81 | 1800 | Baraulia | 109 | 1800 | Amnura | 15 | 2000
Gulshan | 95 | 1300 | Sikalbaha | 26 | 1800 | Pabna | 67 | 1800
Uttara | 70 | 1830 | Dohazari | 66 | 1930 | Shahjadpur | 56 | 2000
Kamrangirchar | 57 | 1800 | Cox'sbazar | 54 | 1830 | Serajganj | 61 | 1900
Savar | 96 | 1800 | Chandraghona | 25 | 1900 | Niyamatpur | 40 | 2000
Bhasantec | 83 | 1800 | Kaptai | 40 | 2000 | Joypurhat | 30 | 1830
Agargaon | 34 | 1800 | A. Khaer Stl. | 15 | 2200 | Rangpur | 80 | 1900
Satmosjid | 51 | 1800 | Bakulia | 90 | 1800 | Lalmonirhat | 72 | 1800
Tongi | 89 | 1100 | Julda | 14 | 1600 | Saidpur | 82 | 1800
Kabirpur | 165 | 1800 | TK chemical | 7 | 2200 | Purbasadipur | 64 | 1900
Basundhara | 78 | 1800 | Modern Steel | 18 | 100 | Thakurgaon | 46 | 1800
Manikganj | 60 | 1900 | Shahmirpur | 20 | 1900 | Palashbari | 66 | 1800
Joydevpur | 176 | 1800 | Abul Khair 230 | 181 | 200 | Barapukuria | 31 | 1800
New Tongi | 92 | 1200 | BSRM | 73 | 900 | Panchagar | 27 | 1800
Korda | 54 | 1800 | Goalpara | 17 | 1930
Tangail | 118 | 1900 | Central s/s | 68 | 1800
Mymensing | 145 | 1930 | Noapara | 51 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## L.curve
Date | 2016-11-30 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -680 | 4335 | 1097 | 5432 | -680 | 5432 | 0:00 | DAILY LOAD CURVE | 2016-11-30
0:30 | -560 | 4160.5 | 1038.5 | 5199 | -440 | 5199 | 1:00
1:00 | -440 | 3986 | 980 | 4966 | -440 | 4966 | 2:00
1:30 | -440 | 3888.5 | 950.5 | 4839 | -380 | 4839 | 3:00
2:00 | -440 | 3791 | 921 | 4712 | -360 | 4712 | 4:00
2:30 | -410 | 3707 | 905 | 4612 | -380 | 4612 | 5:00
3:00 | -380 | 3623 | 889 | 4512 | -420 | 4512 | 6:00
3:30 | -370 | 3536.5 | 890 | 4426.5 | -460 | 4426.5 | 7:00
4:00 | -360 | 3450 | 891 | 4341 | -520 | 4341 | 8:00
4:30 | -370 | 3457.5 | 904 | 4361.5 | -500 | 4361.5 | 9:00
5:00 | -380 | 3465 | 917 | 4382 | -440 | 4382 | 10:00
5:30 | -400 | 3588 | 921.5 | 4509.5 | -350 | 4509.5 | 11:00
6:00 | -420 | 3711 | 926 | 4637 | -380 | 4637 | 12:00
6:30 | -440 | 3825 | 922 | 4747 | -430 | 4747 | 13:00
7:00 | -460 | 3939 | 918 | 4857 | -340 | 4857 | 14:00 |  |  |  | 7601 | 19:00
7:30 | -490 | 4085 | 949 | 5034 | -280 | 5034 | 15:00 |  |  |  | 5735 | 12:00
8:00 | -520 | 4231 | 980 | 5211 | -290 | 5211 | 16:00
8:30 | -510 | 4369.5 | 984.5 | 5354 | -350 | 5354 | 17:00
9:00 | -500 | 4508 | 989 | 5497 | -540 | 5497 | 18:00
9:30 | -470 | 4550 | 978.5 | 5528.5 | -560 | 5528.5 | 18:30
10:00 | -440 | 4592 | 968 | 5560 | -540 | 5560 | 19:00
10:30 | -395 | 4563.5 | 1035.5 | 5599 | -590 | 5599 | 19:30
11:00 | -350 | 4535 | 1103 | 5638 | -610 | 5638 | 20:00
11:30 | -365 | 4573.5 | 1113 | 5686.5 | -620 | 5686.5 | 21:00
12:00 | -380 | 4612 | 1123 | 5735 | -600 | 5735 | 22:00
12:30 | -405 | 4626.5 | 1124 | 5750.5 | -560 | 5750.5 | 23:00
13:00 | -430 | 4641 | 1125 | 5766 | -480 | 5766 | 24:00
13:30 | -385 | 4560 | 1103 | 5663 |  | 5663
14:00 | -340 | 4479 | 1081 | 5560 | 128.92 | 5560
14:30 | -310 | 4539.5 | 1093.5 | 5633 | 86.5 | 5633
15:00 | -280 | 4600 | 1106 | 5706 |  | 5706
15:30 | -285 | 4600 | 1104.5 | 5704.5 | 7867500 | 5704.5
16:00 | -290 | 4600 | 1103 | 5703 |  | 5703
16:30 | -320 | 4734 | 1170.5 | 5904.5 |  | 5904.5
17:00 | -350 | 4868 | 1238 | 6106 | 700 | 6106
17:30 | -350 | 5267 | 1524.5 | 6791.5 | 1800 | 6791.5
18:00 | -350 | 5666 | 1811 | 7477 | 100 | 7477
18:30 | -560 | 5712.5 | 1826.5 | 7539 | 1400 | 7539
19:00 | -540 | 5759 | 1842 | 7601 | 100 | 7601
19:30 | -590 | 5706 | 1826 | 7532 | 1800 | 7532
20:00 | -610 | 5635 | 1728 | 7363 | 1800 | 7363
20:30 | -615 | 5548.5 | 1656.5 | 7205 | 1800 | 7205
21:00 | -620 | 5462 | 1585 | 7047 | 2100 | 7047
21:30 | -610 | 5270 | 1451 | 6721 | 1900 | 6721
22:00 | -600 | 5078 | 1317 | 6395 | 1900 | 6395
22:30 | -580 | 4908 | 1225.5 | 6133.5 |  | 6133.5
23:00 | -560 | 4738 | 1134 | 5872 |  | 5872
23:30 | -520 | 4509 | 1106.5 | 5615.5 |  | 5615.5
24:00 | -480 | 4280 | 1079 | 5359 |  | 5359
*MAX.GEN.(E.P.) |  | 7601 |  | 19:00
*MAX.GEN.(D.P.) |  | 5735 |  | 12:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
7601 MW (19:00)
5735 MW (12:00)

## En.Curve
QF-LDC-12
Date | 2016-11-30 |  | Energy | 137492039 | 0
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | Tripura |  | DAILY ENERGY CURVE |  | 2016-11-30
0:00 | 870 | 499 | 3314 | 230 | 89 | 90 | 16 | 0 | 90
0:30 | 879 | 460.5 | 3178.5 | 184 | 89 | 80 | 16 | 0 | 87
1:00 | 888 | 422 | 3043 | 138 | 89 | 70 | 16 | 0 | 84
1:30 | 877.5 | 390 | 2981.5 | 115.5 | 88.5 | 70 | 16 | 0 | 83 | [5 empty] | 137.492
2:00 | 867 | 358 | 2920 | 93 | 88 | 70 | 16 | 0 | 82 | [5 empty] | 0
2:30 | 867 | 358 | 2847 | 78 | 88 | 70 | 16 | 0 | 81 | [5 empty] | 137.492
3:00 | 867 | 358 | 2774 | 63 | 88 | 70 | 16 | 0 | 80
3:30 | 867 | 358 | 2684 | 66.5 | 88 | 70 | 16 | 0 | 74
4:00 | 867 | 358 | 2594 | 70 | 88 | 70 | 16 | 0 | 68
4:30 | 856.5 | 358 | 2615.5 | 70 | 88.5 | 70 | 16 | 0 | 69
5:00 | 846 | 358 | 2637 | 70 | 89 | 70 | 16 | 0 | 70
5:30 | 855.5 | 358 | 2757.5 | 70 | 89.5 | 67.5 | 16 | 0 | 68
6:00 | 865 | 358 | 2878 | 70 | 90 | 65 | 16 | 0 | 66
6:30 | 865 | 358 | 2974.5 | 78.5 | 90 | 65 | 16 | 0 | 63
7:00 | 865 | 358 | 3071 | 87 | 90 | 65 | 16 | 0 | 60
7:30 | 846 | 358 | 3170.5 | 161.5 | 89.5 | 65 | 16 | 0 | 61
8:00 | 827 | 358 | 3270 | 236 | 89 | 65 | 16 | 0 | 62
8:30 | 841.5 | 358 | 3252.5 | 380 | 89 | 65 | 16 | 0 | 62
9:00 | 856 | 358 | 3235 | 524 | 89 | 65 | 16 | 0 | 62
9:30 | 853 | 363 | 3225 | 577.5 | 89.5 | 65 | 16 | 0 | 67
10:00 | 850 | 368 | 3215 | 631 | 90 | 65 | 16 | 0 | 72
10:30 | 843.5 | 435.5 | 3133.5 | 688 | 89 | 67.5 | 16 | 0 | 73
11:00 | 837 | 503 | 3052 | 745 | 88 | 70 | 16 | 0 | 74
11:30 | 834.5 | 503 | 3073 | 769.5 | 88.5 | 70 | 16 | 0 | 74
12:00 | 832 | 503 | 3094 | 794 | 89 | 70 | 16 | 0 | 74
12:30 | 834.5 | 503 | 3083 | 825.5 | 88.5 | 70 | 16 | 0 | 75
13:00 | 837 | 503 | 3072 | 857 | 88 | 70 | 16 | 0 | 76
13:30 | 831.5 | 503 | 2953.5 | 831 | 88.5 | 66 | 16 | 0 | 77
14:00 | 826 | 503 | 2835 | 805 | 89 | 62 | 16 | 0 | 78
14:30 | 836.5 | 503 | 2883 | 792 | 89.5 | 74.5 | 16 | 0 | 77
15:00 | 847 | 503 | 2931 | 779 | 90 | 87 | 16 | 0 | 76
15:30 | 835.5 | 503 | 3006.5 | 774 | 89.5 | 87 | 16 | 0 | 77
16:00 | 824 | 503 | 3082 | 769 | 89 | 87 | 16 | 0 | 78 | Max Temp. in Dhaka |  | i) Energy
16:30 | 823 | 503 | 3160.5 | 817 | 89.5 | 106.5 | 41.5 | 0 | 75
17:00 | 822 | 503 | 3239 | 865 | 90 | 126 | 67 | 0 | 72
17:30 | 853.5 | 503 | 3397.5 | 1176 | 89.5 | 157 | 185 | 0 | 73
18:00 | 885 | 503 | 3556 | 1487 | 89 | 188 | 303 | 0 | 74
18:30 | 887.5 | 503 | 3563 | 1562 | 89 | 178 | 304 | 0 | 92
19:00 | 890 | 503 | 3570 | 1637 | 89 | 168 | 305 | 0 | 90
19:30 | 890 | 502 | 3592 | 1543 | 90 | 150 | 301 | 0 | 92
20:00 | 891 | 503 | 3586 | 1418 | 89 | 150 | 275 | 0 | 92
20:30 | 871.5 | 503 | 3576.5 | 1331.5 | 89.5 | 150 | 207.5 | 0 | 92
21:00 | 852 | 503 | 3567 | 1245 | 90 | 150 | 140 | 0 | 92
21:30 | 846 | 503.5 | 3558 | 1058.5 | 90.5 | 110 | 84 | 0 | 91
22:00 | 840 | 504 | 3549 | 872 | 91 | 70 | 28 | 0 | 90
22:30 | 840 | 503.5 | 3504 | 695 | 89 | 80 | 22 | 0 | 87
23:00 | 840 | 503 | 3459 | 518 | 87 | 90 | 16 | 0 | 84
23:30 | 820.5 | 503 | 3411.5 | 361 | 87.5 | 77.5 | 16 | 0 | 81
24:00 | 801 | 503 | 3364 | 204 | 88 | 65 | 16 | 0 | 78
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Tripura

## volt
Date: | 2016-11-30
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 222 | 1:00 | 220 | 8:00 | Tongi | 214 | 1:00 | 206 | 11:00
Ishurdi | 234 | 2:00 | 225 | 12:00 | Comilla (N) | 225 | 1:00 | 220 | 16:00
Ashuganj | 230 | 1:00 | 225 | 8:00 | Hathazari | 220 | 20:00 | 213 | 24:00
Serajganj | 225 | 1:00 | 217 | 20:00 | Megnaghat | 218 | 13:00 | 214 | 15:00
Baghabari | 223 | 1:00 | 218 | 12:00 | Fenchuganj | 241 | 24:00 | 234 | 6:00
Barapukuria | 226 | 1:00 | 220 | 18:00 | Siddhirganj | 233 | 3:00 | 224 | 12:00
Bogra | 225 | 2:00 | 215 | 18:00 | Maniknagar | 232 | 3:00 | 222 | 11:00
Khulna South | 233 | 14:00 | 214 | 12:00 | Old Airport | 215 | 3:00 | 207 | 12:00
Rampura | 215 | 2:00 | 210 | 11:00 | Barisal | 237 | 3:00 | 228 | 12:00
Haripur | 213 | 23:00 | 210 | 11:00 | AKSML | 220 | 19:30 | 211 | 12:00
Hasnabad | 216 | 6:00 | 208 | 12:00 | BSRM | 221 | 3:00 | 212 | 9:00
Aminbazar | 215 | 3:00 | 208 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 1900 | 132 | 1100 | Madanhat | 137 | 1400 | 131 | 1000
Munsiganj | 137 | 2200 | 132 | 100 | Hathazari | 132 | 2000 | 129 | 200
Megnaghat | 133 | 1800 | 130 | 300 | Khulshi | 137 | 1400 | 130 | 700
Shyampur | 133 | 1900 | 126 | 1200 | Halishahar | 133 | 2000 | 127 | 600
Bhulta | 125 | 600 | 122 | 1000 | Baraulia | 131 | 1400 | 125 | 800
Madanganj | 132 | 1800 | 128 | 2400 | Sikalbaha | 134 | 1400 | 128 | 800
Shitalakhya | 137 | 2100 | 129 | 1200 | Dohazari | 134 | 1400 | 126 | 800
Rahim steal | 134 | 100 | 132 | 900 | Cox'sbazar | 133 | 1400 | 124 | 1700
Matuail | 134 | 300 | 130 | 1000 | Chandraghona | 134 | 1400 | 130 | 1700
Ghorasal | 135 | 100 | 133 | 1200 | Kaptai | 132 | 2000 | 130 | 700
Narsinghdi | 134 | 400 | 129 | 1200 | A. Khaer Stl. | 131 | 1400 | 127 | 700
Haripur (SBU) | 135 | 2000 | 131 | 1300 | Bakulia | 132 | 1400 | 126 | 900
Ullon | 136 | 1900 | 131 | 1700 | Julda | 132 | 2000 | 128 | 900
Hasnabad | 134 | 600 | 128 | 1600 | TK Chemical | 135 | 1400 | 130 | 600
Magbazar | 131 | 500 | 123 | 1200 | Modern Steel | 132 | 2000 | 126 | 600
Maniknagar | 136 | 600 | 130 | 1200 | Shahmirpur | 132 | 1400 | 126 | 700
Bangabhaban | 131 | 600 | 130 | 1200 | Goalpara | 136 | 1700 | 126 | 700
Narinda | 131 | 600 | 130 | 1300 | Central s/s | 137 | 1700 | 122 | 1200
Dhanmondi | 136 | 1900 | 131 | 1700 | Noapara | 135 | 100 | 120 | 1200
Lalbag | 131 | 600 | 124 | 1200 | Jessore | 130 | 1400 | 115 | 1200
Madartek | 131 | 600 | 125 | 1300 | Jhenida | 130 | 100 | 114 | 1200
Mirpur | 133 | 400 | 124 | 1100 | Bottail | 135 | 100 | 125 | 1200
Kalyanpur | 136 | 300 | 130 | 1200 | G.K.Project | 137 | 200 | 129 | 1200
Gulshan | 132 | 300 | 123 | 1200 | Faridpur | 133 | 400 | 126 | 2100
Uttara | 134 | 400 | 126 | 1200 | Madaripur | 133 | 400 | 126 | 1200
Kamrangirchar | 133 | 400 | 129 | 1200 | Gopalganj | 137 | 1800 | 127 | 1200
Savar | 133 | 400 | 126 | 1200 | Bagerhat | 136 | 100 | 124 | 1200
Bhasantec | 136 | 300 | 130 | 1100 | Mongla | 132 | 200 | 121 | 1200
Agargaon | 136 | 300 | 130 | 1800 | Satkhira | 136 | 1400 | 122 | 1200
Satmosjid | 136 | 200 | 130 | 1200 | Gallamari | 137 | 1400 | 127 | 1100
Tongi | 137 | 100 | 130 | 1800 | Magura | 135 | 300 | 126 | 1800
Kabirpur | 135 | 1300 | 126 | 800 | Chuadanga | 130 | 100 | 115 | 1200
Basundhara | 127 | 400 | 121 | 1300 | Barisal | 136 | 1700 | 131 | 1200
Manikganj | 137 | 100 | 128 | 1800 | Patuakhali | 136 | 1700 | 131 | 1200
Joydevpur | 133 | 1300 | 127 | 800 | Bhandaria | 135 | 300 | 126 | 2300
New Tongi | 135 | 400 | 126 | 1800 | Ishurdi | 136 | 200 | 128 | 1200
Kodda | 135 | 1400 | 127 | 800 | Natore | 135 | 100 | 127 | 1200
Tangail | 133 | 200 | 120 | 1800 | Bogra | 134 | 300 | 127 | 1800
Mymensing | 133 | 600 | 128 | 2100 | Noagaon | 131 | 200 | 124 | 1200
Kishorganj | 135 | 300 | 131 | 2100 | Rajshahi | 134 | 200 | 125 | 1200
Netrokona | 134 | 300 | 130 | 2100 | C.Nawabganj | 131 | 1900 | 120 | 1200
Jamalpur | 132 | 1830 | 125 | 2200 | Amnura | 137 | 1900 | 132 | 1700
Sherpur | 131 | 1700 | 122 | 2100 | Pabna | 131 | 200 | 125 | 1200
Srimongal | 143 | 2400 | 140 | 200 | Shahjadpur | 139 | 100 | 134 | 1300
Shahjibazar | 140 | 100 | 137 | 1100 | Serajganj | 133 | 1400 | 126 | 1900
Fenchuganj | 142 | 900 | 139 | 700 | Niyamatpur | 131 | 400 | 120 | 1200
Khulawara | 141 | 2400 | 139 | 100 | Joypurhat | 134 | 600 | 124 | 1830
Sylhet | 139 | 2400 | 136 | 1100 | Rangpur | 127 | 200 | 117 | 1800
Chatak | 139 | 100 | 135 | 900 | Lalmonirhat | 124 | 400 | 117 | 1700
Comilla(s) | 134 | 100 | 131 | 1800 | Saidpur | 125 | 400 | 114 | 1800
Comilla(n) | 135 | 700 | 133 | 1100 | Purbasadipur | 126 | 100 | 118 | 1830
Chandpur | 135 | 900 | 130 | 1800 | Thakurgaon | 122 | 200 | 114 | 1800
Feni | 123 | 700 | 121 | 1200 | Palashbari | 130 | 300 | 119 | 1800
Chowmuhani | 128 | 700 | 125 | 1800 | Barapukuria | 126 | 100 | 120 | 1800
Ashuganj | 138 | 2300 | 136 | 1300 | Panchagar | 118 | 100 | 105 | 1800
Daudkandi | 134 | 300 | 128 | 1200
B.Baria | 138 | 1800 | 135 | 100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7