## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-11-14 | Sunday
|  |  | Date (day): | 2021-11-14 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12127.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13624 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-11-13 | 2021-11-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 0 | 0 |  | 190 | Under maint.
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 100 | 100 | 8 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 397 | 400 | 400
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 326 | 270 | 300 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 250 | 250 | 250 | 250 | 200 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 295 | 260 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 25 | 25 |  | 75 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 16 | 19 | 19 |  | 3 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 263 | 260 | 0 | 0 | 335 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 0 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 56 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 45 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 70 | 80 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 9 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5560 | 2173 | 2187 | 2986 | 3416 | 753 | 1338
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 24 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 70 | 70 | 70 |  | 160 | Unit 2 & 5 under maint.
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 51 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 60 | 90 | 80 | 80 |  | 20 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 13 | 5 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 242 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 40 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 554 | 993 | 1396 | 1441 | 65 | 868
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 135 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 215 | 221 | 200 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 300 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint.
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 29 | 29 |  | 16 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 35 | 30 | 30 | 25 |  | Gas shortage
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 45 | 16 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 100 | 130 | 130 |  | 20 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 135 | 136 | 138 |  | 25 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 51 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 68 | 102 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 22 | 22
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1037 | 1415 | 1757 | 2042 | 493 | 467
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 156 | 190 | 160 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 0 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 8 | 0 | 0 | 0 | 0 |  | 8 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 120 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 3 | 8 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 622 | 332 | 318 | 570.6 | 559 | 0 | 8
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 163 | 160 | 162 |  | 168 | GT-1 S/D
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 62 | 60 | 65
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 80 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 70 | 50 | 80 | 80 |  | 20 | Engine problem
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 205 | 205 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 389 | 353 | 324 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint.
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1548 | 1492 | 1571 | 1658 | 0 | 701
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 732 | 726 | 741 | 741
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 30 |  | 24 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 350 | 350 | 370 | 40 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 70 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 0 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1032 | 1146 | 1246 | 1706 | 40 | 93
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 21 | 28 | 30
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 93 | 90 | 90 |  | 104 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 12 | 12 | 83 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 280 | 340 | 620 | 620
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 151 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 538 | 685 | 1080 | 1232 | 83 | 104
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 9 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 18 | 18 | 32 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 0 | 8 | 42 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 7 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 140 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 177 | 190 | 190 | 30 |  | Gas shortage
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 421 | 322 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 20 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 42 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 70 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 636 | 744 | 1320 | 1375 | 634 | 68
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 82 | 81 | 80 | 82
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 88 | 194 | 201 | 195 | 0 | 399
|  | Total |  |  |  |  | 22031 | 20934 | 7938 | 9174 | 12127.6 | 13624 | 2068 | 4046
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7607.4663 | 8792 | 11622.6138 | 13056.7046
| A. |  | 2021-11-13 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 9174 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 6283 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9174 | MW
| 3 | Day peak Generation : |  |  | 7938 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8792 | MW
| 4 | Evening peak Generation : |  |  | 9174 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 186.4646 | MKWHr | By Solar | 0.36963 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 132.8729 | MKWHr |  | By Oil: | 24.0644 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 10.126 | MKWHr |  | By Hydro: | 1.6459 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2068 | MW | Dhaka | 3244 | 3244 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 4046 | MW | Chittagong | 1095 | 1095 |  | 0 |  | 18:00 |  | 104
|  |  |  | Total = |  |  | 6114 | MW | Khulna | 1009 | 1009 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 987.29 | MMCFD |  |  | Rajshahi | 838 | 838 |  | 0 |  | 19:00 |  | 102
| 8 | Fuel Cost : | i) Gas : | Taka | 142104299.178 | ii) Oil : | Taka | 172372134.56 | Comilla | 762 | 762 |  | 0 |  | 19:30 |  | 100
|  |  | iii) Coal : |  | 47646112.65 | Total | Taka | 362122546.388 | Mymensingh | 678 | 678 |  | 0 |  | 20:00 |  | 98
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.106 | MKWHr. | Sylhet | 351 | 351 |  | 0 |  | 21:00 |  | 96
|  | ii) During Peak Demand : |  |  | -6 | MW (E to W) at | 19:00 | hrs | Barisal | 253 | 253 |  | 0 |  | 22:00 |  | 92
|  | iii) Maximum : |  |  | -124 | MW at | 18:00 | hrs | Rangpur | 562 | 562 |  | 0 |  | 23:00 |  | 88
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.2° C |  |  | Total | 8792 | 8792 |  | 0
| B. |  | 2021-11-14 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 25.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 9800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 13624 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3824 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 199.1883 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6147 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.3804 | MKWHr. | ii) HVDC Flow at Peak Time |  | 726 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.0054 | MKWHr. | iii) Maximum HVDC Flow : |  | 732 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.56 |  | (b) Today: | 102.49 |  | (c) Rule Curve: |  | 107.7
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-11-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Private(HSD) | Private(HFO) | Coal | Hydro | Public(HSD) | Public(HFO) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 393 | 337 |  | 0 | 250 | 285 | 0 | 0 | 15 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 29 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 37 | 120 | 0 | 0 | 280 | 0 | 180 | 70 | 138 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 92 | 217 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 110 | 161 | 55 | 10 | 0 | 212 | 0 | 0 | 10 | 275 | 24 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 60 | 0 | 0 | 369 | 0 | 0 | 17 | 0 | 231 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 70 | 17 | 0 |  | 732 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 221 | 0 | 0 | 0 |  | 5229 | 2297 | 7526 | 3616 | 732 | 2006 | 0 | 544 | 382 | 69 | 0 | 85 | 92 | 0 | 0 | 102.57
2:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 378 | 289 |  | 0 | 250 | 290 | 0 | 0 | 15 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 30 | 33 | 33 | 0 | 0 | 29 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 32 | 120 | 0 | 0 | 280 | 0 | 181 | 8 | 137 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 90 | 219 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 110 | 162 | 51 | 10 | 0 | 178 | 0 | 0 | 10 | 280 | 23 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 60 | 0 | 0 | 369 | 0 | 0 | 17 | 0 | 233 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 70 | 17 | 0 |  | 646 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 12 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 220 | 0 | 0 | 0 |  | 5047 | 2140 | 7187 | 3538 | 646 | 1862 | 0 | 546 | 351 | 69 | 0 | 85 | 90 | 0 | 0 | 102.57
3:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 327 | 287 |  | 0 | 250 | 280 | 0 | 0 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 17 | 25 | 30 | 33 | 33 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 32 | 80 | 0 | 0 | 280 | 0 | 180 | 8 | 138 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 88 | 218 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 110 | 161 | 40 | 10 | 0 | 178 | 0 | 0 | 10 | 290 | 23 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 60 | 0 | 0 | 368 | 0 | 0 | 17 | 0 | 232 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 70 | 17 | 0 |  | 638 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 12 | 0 | 0 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 172 | 0 | 0 | 0 |  | 4922 | 2076 | 6998 | 3429 | 638 | 1826 | 0 | 530 | 332 | 70 | 0 | 85 | 88 | 0 | 0 | 102.57
4:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 324 | 288 |  | 0 | 250 | 290 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 18 | 25 | 30 | 33 | 33 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 38 | 80 | 0 | 0 | 280 | 0 | 180 | 8 | 139 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 86 | 218 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 110 | 161 | 40 | 10 | 0 | 178 | 0 | 0 | 10 | 300 | 23 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 30 | 0 | 0 | 370 | 0 | 0 | 17 | 0 | 214 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 12 | 0 | 0 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 172 | 0 | 0 | 0 |  | 4853 | 1915 | 6768 | 3430 | 494 | 1837 | 0 | 435 | 331 | 70 | 0 | 85 | 86 | 0 | 0 | 102.56
5:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 257 |  | 0 | 250 | 305 | 0 | 0 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 25 | 25 | 33 | 33 | 0 | 0 | 31 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 38 | 80 | 0 | 0 | 305 | 0 | 196 | 8 | 138 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 86 | 218 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 110 | 160 | 40 | 10 | 0 | 151 | 0 | 0 | 10 | 290 | 23 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 0 | 332 | 0 | 0 | 17 | 0 | 158 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 12 | 0 | 0 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 150 | 0 | 0 | 0 |  | 4356 | 1927 | 6283 | 3068 | 494 | 1816 | 0 | 321 | 342 | 71 | 0 | 85 | 86 | 0 | 0 | 102.56
6:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 304 | 302 |  | 0 | 250 | 275 | 0 | 0 | 0 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 25 | 25 | 33 | 33 | 0 | 0 | 31 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 37 | 80 | 0 | 0 | 310 | 0 | 180 | 8 | 136 | 23 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 82 | 219 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 140 | 163 | 40 | 10 | 0 | 152 | 0 | 0 | 10 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 0 | 316 | 0 | 0 | 17 | 0 | 158 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 151 | 0 | 0 | 0 |  | 4676 | 2003 | 6679 | 3351 | 494 | 1883 | 0 | 321 | 392 | 71 | 0 | 85 | 82 | 0 | 0 | 102.56
7:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 304 | 303 |  | 0 | 250 | 305 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 25 | 25 | 33 | 33 | 0 | 0 | 31 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 21 | 35 | 80 | 0 | 0 | 330 | 0 | 193 | 8 | 138 | 23 | 5 | 0 | 11 | 0 | 0 | 0 | 22 | 11 | 8 | 21 | 78 | 218 | 0 | 22 | 0 | 30 | 0 | 8 | 0 | 163 | 161 | 40 | 10 | 0 | 176 | 0 | 0 | 10 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 32 | 0 | 50 | 4 | 10 | 0 | 0 | 340 | 0 | 50 | 17 | 0 | 123 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 70 | 17 | 0 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 12 | 0 | 0 | 0 | 399 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 151 | 0 | 0 | 0 |  | 4889 | 2047 | 6936 | 3429 | 494 | 1993 | 0 | 386 | 393 | 71 | 0 | 85 | 78 | 7 | 0 | 102.55
8:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 340 | 303 |  | 0 | 250 | 295 | 0 | 0 | 0 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 18 | 25 | 25 | 33 | 16 | 0 | 0 | 31 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 345 | 0 | 182 | 8 | 137 | 23 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 82 | 217 | 0 | 22 | 0 | 30 | 0 | 39 | 0 | 163 | 162 | 20 | 70 | 0 | 212 | 0 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 70 | 0 | 10 | 0 | 0 | 371 | 0 | 70 | 17 | 2 | 122 | 35 | 17 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 70 | 17 | 2 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 12 | 0 | 0 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 310 | 151 | 0 | 0 | 0 |  | 5124 | 2054 | 7178 | 3494 | 494 | 2091 | 0 | 453 | 392 | 71 | 0 | 85 | 82 | 16 | 0 | 102.63
9:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 352 | 300 |  | 0 | 250 | 285 | 0 | 0 | 20 | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 17 | 18 | 25 | 25 | 33 | 16 | 0 | 0 | 30 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 300 | 0 | 186 | 16 | 137 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 70 | 213 | 0 | 19 | 1 | 30 | 0 | 39 | 0 | 163 | 160 | 50 | 81 | 0 | 212 | 0 | 0 | 10 | 295 | 21 | 0 | 0 | 0 | 0 | 0 | 67 | 0 | 70 | 0 | 40 | 0 | 0 | 387 | 0 | 70 | 17 | 2 | 157 | 48 | 17 | 0 | 0 | 0 | 0 | 0 | 36 | 24 | 0 | 70 | 17 | 3 |  | 494 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 310 | 151 | 0 | 0 | 2 |  | 5259 | 1993 | 7252 | 3493 | 494 | 2031 | 0 | 601 | 391 | 70 | 0 | 55 | 70 | 47 | 0 | 0
10:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 352 | 300 |  | 0 | 250 | 295 | 0 | 0 | 42 | 265 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 29 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 290 | 0 | 181 | 16 | 137 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 70 | 159 | 0 | 19 | 1 | 30 | 0 | 39 | 0 | 163 | 162 | 60 | 78 | 0 | 205 | 0 | 0 | 10 | 295 | 21 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 70 | 0 | 40 | 0 | 0 | 387 | 0 | 70 | 17 | 4 | 159 | 54 | 17 | 0 | 0 | 0 | 0 | 0 | 48 | 35 | 0 | 70 | 17 | 7 |  | 495 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 280 | 151 | 0 | 0 | 2 |  | 5282 | 1959 | 7241 | 3456 | 495 | 2028 | 0 | 696 | 361 | 69 | 0 | 0 | 70 | 66 | 0 | 0
11:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 352 | 308 |  | 0 | 250 | 265 | 0 | 0 | 55 | 262 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 38 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 80 | 0 | 0 | 290 | 0 | 181 | 16 | 138 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 72 | 157 | 0 | 19 | 2 | 30 | 0 | 42 | 0 | 163 | 164 | 61 | 78 | 0 | 205 | 0 | 0 | 10 | 305 | 21 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 70 | 0 | 60 | 0 | 1 | 386 | 0 | 70 | 17 | 3 | 209 | 54 | 17 | 0 | 0 | 10 | 0 | 1 | 44 | 42 | 0 | 70 | 17 | 8 |  | 664 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 280 | 151 | 0 | 0 | 2 |  | 5395 | 2133 | 7528 | 3455 | 664 | 2020 | 0 | 814 | 360 | 78 | 0 | 0 | 72 | 65 | 0 | 0
12:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 352 | 326 |  | 0 | 250 | 295 | 0 | 0 | 55 | 263 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 80 | 0 | 0 | 330 | 0 | 215 | 16 | 136 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 68 | 156 | 0 | 19 | 2 | 30 | 0 | 50 | 0 | 163 | 162 | 61 | 81 | 0 | 205 | 0 | 0 | 10 | 300 | 22 | 5 | 0 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 60 | 0 | 10 | 389 | 3 | 70 | 17 | 2 | 242 | 54 | 17 | 0 | 8 | 10 | 0 | 17 | 52 | 108 | 0 | 70 | 17 | 9 |  | 732 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 280 | 151 | 0 | 0 | 2 |  | 5644 | 2294 | 7938 | 3529 | 732 | 2165 | 0 | 969 | 362 | 40 | 0 | 0 | 68 | 73 | 0 | 0
13:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 384 | 0 |  | 0 | 250 | 295 | 0 | 0 | 55 | 260 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 135 | 0 | 0 | 310 | 0 | 219 | 45 | 136 | 26 | 17 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 72 | 156 | 0 | 19 | 2 | 30 | 0 | 47 | 0 | 163 | 160 | 64 | 83 | 0 | 205 | 0 | 0 | 10 | 310 | 22 | 5 | 0 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 90 | 0 | 10 | 388 | 8 | 70 | 22 | 3 | 287 | 54 | 40 | 0 | 15 | 40 | 0 | 24 | 22 | 115 | 0 | 70 | 17 | 4 |  | 732 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 11 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 280 | 171 | 0 | 0 | 1 |  | 5607 | 2320 | 7927 | 3649 | 732 | 1875 | 0 | 1128 | 363 | 70 | 0 | 0 | 72 | 38 | 0 | 0
14:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 |  | 0 | 250 | 270 | 0 | 0 | 55 | 263 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 135 | 0 | 0 | 280 | 0 | 179 | 45 | 136 | 26 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 15 | 72 | 158 | 0 | 22 | 1 | 30 | 0 | 50 | 0 | 110 | 162 | 64 | 80 | 0 | 205 | 0 | 0 | 10 | 290 | 22 | 5 | 0 | 0 | 0 | 0 | 100 | 0 | 58 | 0 | 90 | 0 | 10 | 403 | 8 | 35 | 51 | 3 | 251 | 54 | 68 | 0 | 8 | 40 | 0 | 34 | 16 | 54 | 0 | 50 | 17 | 3 |  | 731 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 280 | 171 | 0 | 0 | 0 |  | 5340 | 2241 | 7581 | 3538 | 731 | 1742 | 0 | 1036 | 364 | 70 | 0 | 0 | 72 | 28 | 0 | 102.53
15:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 400 | 0 |  | 0 | 250 | 300 | 0 | 0 | 30 | 263 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 135 | 0 | 0 | 280 | 0 | 179 | 45 | 136 | 23 | 35 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 20 | 15 | 40 | 158 | 0 | 22 | 0 | 30 | 0 | 53 | 0 | 163 | 163 | 40 | 81 | 0 | 198 | 0 | 0 | 10 | 290 | 22 | 5 | 0 | 0 | 0 | 0 | 100 | 0 | 50 | 0 | 90 | 0 | 10 | 402 | 8 | 17 | 51 | 1 | 250 | 54 | 68 | 0 | 8 | 40 | 0 | 35 | 8 | 54 | 0 | 50 | 17 | 5 |  | 732 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 11 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 280 | 171 | 0 | 0 | 0 |  | 5288 | 2259 | 7547 | 3474 | 732 | 1865 | 0 | 985 | 363 | 70 | 0 | 0 | 40 | 18 | 0 | 102.53
16:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 363 | 0 |  | 0 | 250 | 290 | 0 | 0 | 30 | 262 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 18 | 25 | 28 | 33 | 17 | 0 | 0 | 0 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 135 | 0 | 0 | 290 | 0 | 187 | 45 | 137 | 26 | 35 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 64 | 158 | 0 | 22 | 0 | 30 | 0 | 53 | 0 | 130 | 160 | 40 | 83 | 0 | 199 | 0 | 0 | 10 | 280 | 22 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 50 | 0 | 60 | 0 | 13 | 403 | 8 | 17 | 34 | 0 | 250 | 54 | 68 | 0 | 9 | 10 | 0 | 35 | 3 | 54 | 0 | 50 | 17 | 1 |  | 732 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 0 | 0 | 361 | 3 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 280 | 171 | 0 | 0 | 0 |  | 5152 | 2238 | 7390 | 3472 | 732 | 1807 | 0 | 876 | 363 | 70 | 0 | 0 | 64 | 6 | 0 | 102.53
17:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 337 | 90 |  | 0 | 250 | 230 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 25 | 28 | 33 | 17 | 0 | 0 | 0 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 6 | 135 | 0 | 0 | 305 | 0 | 187 | 45 | 134 | 23 | 35 | 0 | 51 | 0 | 0 | 1 | 22 | 11 | 33 | 15 | 88 | 158 | 0 | 22 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 40 | 40 | 0 | 178 | 0 | 0 | 10 | 310 | 24 | 5 | 0 | 32 | 0 | 0 | 96 | 0 | 50 | 0 | 60 | 30 | 51 | 353 | 15 | 17 | 57 | 0 | 270 | 54 | 80 | 0 | 46 | 40 | 0 | 56 | 0 | 68 | 6 | 50 | 17 | 0 |  | 732 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 6 | 0 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 0 | 0 | 362 | 25 | 0 | 8 | 0 | 34 | 0 | 0 | 7 | 280 | 171 | 0 | 0 | 0 |  | 5384 | 2324 | 7708 | 3366 | 732 | 1802 | 0 | 1278 | 362 | 70 | 0 | 10 | 88 | 0 | 0 | 102.53
18:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 349 | 100 |  | 0 | 250 | 260 | 0 | 0 | 45 | 264 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 20 | 55 | 0 | 25 | 18 | 33 | 17 | 0 | 0 | 33 | 70 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7 | 0 | 68 | 8 | 0 | 39 | 0 | 11 | 135 | 0 | 0 | 295 | 0 | 221 | 45 | 136 | 26 | 35 | 0 | 51 | 0 | 0 | 8 | 22 | 11 | 33 | 19 | 104 | 165 | 0 | 22 | 0 | 30 | 0 | 50 | 0 | 163 | 164 | 62 | 84 | 0 | 204 | 0 | 0 | 10 | 285 | 24 | 11 | 0 | 135 | 0 | 0 | 130 | 0 | 56 | 0 | 60 | 66 | 120 | 353 | 8 | 0 | 105 | 0 | 304 | 54 | 110 | 0 | 113 | 40 | 0 | 104 | 0 | 156 | 17 | 50 | 17 | 0 |  | 726 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 20 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 12 | 8 | 8 | 0 | 33 | 21 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 0 | 0 | 344 | 83 | 0 | 47 | 0 | 108 | 0 | 0 | 35 | 340 | 200 | 0 | 0 | 0 |  | 6391 | 2740 | 9131 | 3523 | 726 | 1940 | 0 | 2156 | 422 | 103 | 0 | 157 | 104 | 0 | 0 | 102.53
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 397 | 270 |  | 0 | 250 | 260 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 24 | 0 | 13 | 135 | 0 | 0 | 300 | 0 | 221 | 45 | 135 | 23 | 35 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 190 | 0 | 0 | 0 | 30 | 0 | 53 | 0 | 163 | 163 | 62 | 84 | 0 | 205 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 45 | 0 | 0 | 120 | 0 | 80 | 0 | 90 | 51 | 100 | 353 | 8 | 0 | 105 | 0 | 304 | 54 | 110 | 0 | 113 | 40 | 0 | 104 | 0 | 162 | 0 | 50 | 17 | 0 |  | 726 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 21 | 0 | 0 | 0 | 0 | 9 | 0 | 42 | 12 | 8 | 7 | 0 | 33 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 0 | 0 | 322 | 70 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 340 | 220 | 0 | 0 | 0 |  | 6405 | 2769 | 9174 | 3631 | 726 | 2119 | 0 | 1946 | 421 | 70 | 0 | 159 | 102 | 0 | 0 | 102.52
19:30 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 399 | 302 |  | 0 | 250 | 300 | 0 | 0 | 30 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 18 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 18 | 17 | 135 | 0 | 0 | 340 | 0 | 218 | 45 | 136 | 26 | 35 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 185 | 0 | 22 | 0 | 30 | 0 | 53 | 0 | 163 | 162 | 62 | 84 | 0 | 205 | 0 | 0 | 10 | 325 | 24 | 5 | 0 | 45 | 0 | 0 | 120 | 0 | 80 | 0 | 90 | 0 | 50 | 373 | 0 | 0 | 68 | 0 | 302 | 54 | 110 | 0 | 75 | 40 | 0 | 53 | 0 | 162 | 0 | 50 | 17 | 0 |  | 726 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 11 | 0 | 0 | 0 | 404 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 340 | 220 | 0 | 0 | 0 |  | 6329 | 2763 | 9092 | 3775 | 726 | 2312 | 0 | 1578 | 421 | 70 | 0 | 110 | 100 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 398 | 300 |  | 0 | 250 | 260 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 18 | 17 | 135 | 0 | 0 | 300 | 0 | 221 | 45 | 133 | 26 | 42 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 98 | 185 | 0 | 17 | 0 | 30 | 0 | 50 | 0 | 163 | 162 | 62 | 84 | 0 | 205 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 45 | 0 | 0 | 120 | 0 | 80 | 0 | 90 | 0 | 50 | 404 | 0 | 0 | 68 | 0 | 302 | 54 | 110 | 0 | 75 | 40 | 0 | 53 | 0 | 162 | 0 | 50 | 17 | 0 |  | 726 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 0 | 0 | 0 | 384 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 350 | 220 | 0 | 0 | 0 |  | 6246 | 2779 | 9025 | 3782 | 726 | 2230 | 0 | 1578 | 431 | 70 | 0 | 110 | 98 | 0 | 0 | 102.52
21:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 398 | 332 |  | 0 | 250 | 270 | 0 | 0 | 30 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 16 | 30 | 135 | 0 | 0 | 300 | 0 | 221 | 45 | 136 | 26 | 52 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 96 | 170 | 0 | 12 | 0 | 30 | 0 | 50 | 0 | 163 | 160 | 62 | 84 | 0 | 205 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 80 | 0 | 90 | 0 | 0 | 405 | 0 | 0 | 34 | 0 | 303 | 54 | 110 | 0 | 46 | 40 | 0 | 53 | 0 | 162 | 0 | 50 | 17 | 0 |  | 725 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 0 | 0 | 417 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 370 | 221 | 0 | 0 | 0 |  | 6065 | 2620 | 8685 | 3759 | 725 | 2309 | 0 | 1242 | 450 | 70 | 0 | 34 | 96 | 0 | 0 | 102.52
22:00 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 398 | 336 |  | 0 | 250 | 260 | 0 | 0 | 30 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 37 | 135 | 0 | 0 | 270 | 0 | 178 | 45 | 136 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 92 | 175 | 0 | 22 | 0 | 30 | 0 | 53 | 0 | 163 | 161 | 62 | 81 | 0 | 205 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 65 | 0 | 90 | 0 | 0 | 405 | 0 | 0 | 34 | 0 | 303 | 54 | 68 | 0 | 26 | 40 | 0 | 17 | 0 | 162 | 0 | 50 | 17 | 0 |  | 726 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 0 | 0 | 336 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 370 | 221 | 0 | 0 | 0 |  | 5868 | 2485 | 8353 | 3646 | 726 | 2240 | 0 | 1129 | 450 | 70 | 0 | 0 | 92 | 0 | 0 | 102.51
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 397 | 329 |  | 0 | 250 | 290 | 0 | 0 | 15 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 38 | 135 | 0 | 0 | 280 | 0 | 186 | 45 | 137 | 26 | 53 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 88 | 176 | 0 | 22 | 0 | 30 | 0 | 53 | 0 | 130 | 160 | 40 | 40 | 0 | 178 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 43 | 0 | 90 | 0 | 0 | 410 | 0 | 0 | 34 | 0 | 303 | 54 | 68 | 0 | 0 | 10 | 0 | 0 | 0 | 54 | 0 | 100 | 17 | 0 |  | 726 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 0 | 0 | 354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 221 | 0 | 0 | 0 |  | 5454 | 2371 | 7825 | 3529 | 726 | 2197 | 0 | 792 | 423 | 70 | 0 | 0 | 88 | 0 | 0 | 102.51
24:00 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 395 | 326 |  | 0 | 250 | 250 | 0 | 0 | 15 | 261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 135 | 0 | 0 | 280 | 0 | 181 | 45 | 132 | 26 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 28 | 21 | 84 | 176 | 0 | 22 | 0 | 30 | 0 | 52 | 0 | 130 | 161 | 40 | 5 | 0 | 178 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 17 | 0 | 90 | 0 | 0 | 410 | 0 | 0 | 34 | 0 | 303 | 54 | 51 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 0 |  | 726 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 180 | 0 | 0 | 0 |  | 5165 | 2305 | 7470 | 3454 | 726 | 2037 | 0 | 676 | 423 | 70 | 0 | 0 | 84 | 0 | 0 | 102.51
KWH | 0 | 0 | 0 | 2551500 | 0 | 8363 | 0 | 8847360 | 5530000 |  | 0 | 6164750 | 6767185 | 0 | 0 | 681620 | 6339012 | 0 | 0 | 0 | 329328 | 0 | 0 | 0 | 0 | 0 | 1161720 | 40682 | 309457 | 365328 | 600000 | 654120 | 828900 | 741500 | 0 | 0 | 321856 | 1324000 | 2700000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 15360 | 0 | 1043352 | 15120 | 0 | 85440 | 254928 | 481440 | 2679106 | 0 | 0 | 7527300 | 0 | 3106000 | 752727 | 3261340 | 551088 | 603360 | 0 | 990830 | 0 | 0 | 17170 | 457632 | 210960 | 625500 | 465700 | 2005440 | 4358240 | 0 | 456228 | 10700 | 717000 | 0 | 853200 | 0 | 3643200 | 3588000 | 1195968 | 1333440 | 0 | 4619280 | 0 | 0 | 251460 | 7267000 | 536928 | 181488 | 0 | 373854 | 0 | 0 | 1977600 | 0 | 1132416 | 4590 | 1462080 | 166080 | 448290 | 9090000 | 96000 | 630000 | 906618 | 21000 | 5650473 | 1237324 | 1241158 | 0 | 550200 | 411840 | 0 | 597120 | 245800 | 1582560 | 26345 | 1529927 | 443520 | 36343 |  | 15380363 | 0 | 8222112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2105108 | 399000 | 0 | 0 | 0 | 0 | 9664 | 0 | 119192 | 26190 | 15822 | 12162 | 21120 | 60095 | 386880 | 0 | 198684 | 1947055 | 0 | 0 | 0 | 0 | 0 | 0 | 4521736 | 0 | 286036 | 0 | 0 | 0 | 8711563 | 323040 | 0 | 333792 | 0 | 395510 | 0 | 37874 | 115104 | 8178900 | 4354527 | 0 | 0 | 13320 |  | 130289744 | 56174849 | 186464593 | 84087973 | 15380363 | 48784961 | 0 | 22819953 | 10125955 | 1645856 | 0 | 1244465 | 2005440 | 369627 | 0
Fuel Cost | 0 | 0 | 0 | 3750705 | 0 | 11039.16 | 0 | 8935833.6 | 5695900 |  | 0 | 6719577.5 | 7511575.35 | 0 | 0 | 5766505.2 | 6592572.48 | 0 | 0 | 0 | 3003471.36 | 0 | 0 | 0 | 0 | 0 | 8480556 | 314471.86 | 3051246.02 | 273996 | 450000 | 0 | 0 | 0 | 0 | 0 | 86901.12 | 357480 | 4887000 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10120514.4 | 144396 | 0 | 676684.8 | 321209.28 | 1429876.8 | 3965076.88 | 0 | 0 | 5570202 | 0 | 2857520 | 971017.83 | 3750541 | 622729.44 | 844704 | 0 | 1694319.3 | 0 | 0 | 163973.5 | 581192.64 | 158220 | 1094625 | 349275 | 15040800 | 4619734.4 | 0 | 579409.56 | 170558 | 1175880 | 0 | 1518696 | 0 | 4153248 | 3731520 | 2356056.96 | 2546870.4 | 0 | 7991354.4 | 0 | 0 | 512978.4 | 7339670 | 402696 | 137930.88 | 0 | 2826336.24 | 0 | 0 | 10283520 | 0 | 11142973.44 | 53657.1 | 11915952 | 1801968 | 3160444.5 | 8453700 | 875520 | 5953500 | 7896642.78 | 0 | 42717575.88 | 10777092.04 | 10909778.82 | 0 | 4715214 | 2742854.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 88590890.88 | 0 | 8633217.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2378772.04 | 618450 | 0 | 0 | 0 | 0 | 95093.76 | 0 | 1054849.2 | 201663 | 213913.44 | 117849.78 | 204652.8 | 582921.5 | 742809.6 | 0 | 150403.788 | 11740741.65 | 0 | 0 | 0 | 0 | 0 | 0 | 5968691.52 | 0 | 429054 | 0 | 0 | 0 | 8624447.37 | 3372537.6 | 0 | 3167686.08 | 0 | 3069157.6 | 0 | 418507.7 | 850618.56 | 35905371 | 0 | 0 | 0 | 0 |  | 289709040.72 | 177132300.468 | 466841341.188 | 90740065.468 | 88590890.88 | 51364233.71 | 0 | 160400905.92 | 47646112.65 | 444381.12 | 0 | 11971228.64 | 15040800 | 642722.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 352 | 326 |  | 0 | 250 | 295 | 0 | 0 | 55 | 263 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 40 | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 80 | 0 | 0 | 330 | 0 | 215 | 16 | 136 | 20 | 5 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 68 | 156 | 0 | 19 | 2 | 30 | 0 | 50 | 0 | 163 | 162 | 61 | 81 | 0 | 205 | 0 | 0 | 10 | 300 | 22 | 5 | 0 | 0 | 0 | 0 | 100 | 0 | 70 | 0 | 60 | 0 | 10 | 389 | 3 | 70 | 17 | 2 | 242 | 54 | 17 | 0 | 8 | 10 | 0 | 17 | 52 | 108 | 0 | 70 | 17 | 9 |  | 732 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 0 | 0 | 0 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 280 | 151 | 0 | 0 | 2 |  | 7938 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 397 | 270 | 0 | 0 | 250 | 260 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 16 | 25 | 31 | 33 | 33 | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 24 | 0 | 13 | 135 | 0 | 0 | 300 | 0 | 221 | 45 | 135 | 23 | 35 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 190 | 0 | 0 | 0 | 30 | 0 | 53 | 0 | 163 | 163 | 62 | 84 | 0 | 205 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 45 | 0 | 0 | 120 | 0 | 80 | 0 | 90 | 51 | 100 | 353 | 8 | 0 | 105 | 0 | 304 | 54 | 110 | 0 | 113 | 40 | 0 | 104 | 0 | 162 | 0 | 50 | 17 | 0 |  | 726 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 21 | 0 | 0 | 0 | 0 | 9 | 0 | 42 | 12 | 8 | 7 | 0 | 33 | 21 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 0 | 0 | 0 | 322 | 70 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 340 | 220 | 0 | 0 | 0 |  | 9174 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 400 | 360 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 30 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 90 | 50 | 21 | 20 | 80 | 0 | 0 | 330 | 0 | 220 | 45 | 138 | 29 | 30 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 22 | 164 | 200 | 0 | 22 | 0 | 30 | 0 | 50 | 0 | 163 | 162 | 65 | 84 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 80 | 200 | 130 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 0 | 162 | 116 | 80 | 17 |  |  | 741 | 0 | 370 | 0 | 0 | 220 | 0 | 0 | 30 | 40 | 0 | 90 | 30 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 18 | 8 | 40 | 52 | 33 | 22 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 12 | 100 | 0 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 620 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 400 | 300 | 0 | 0 | 250 | 300 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 102 | 149 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 30 | 40 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 80 | 90 | 50 | 20 | 5 | 80 | 0 | 0 | 330 | 0 | 200 | 16 | 136 | 29 | 30 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 25 | 22 | 138 | 160 | 0 | 22 | 1.6 | 30 | 0 | 50 | 0 | 163 | 160 | 60 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 24 | 11 | 0 | 250 | 0 | 100 | 200 | 50 | 149 | 20 | 80 | 200 | 130 | 324 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 104 | 50 | 162 | 116 | 80 | 17 | 30 |  | 741 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 28 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 18 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 12 | 50 | 0 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 8 | 113 | 620 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 398 | 340 | 0 | 0 | 250 | 265 | 0 | 0 | 0 | 262 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 25 | 33 |  | 0 | 0 | 0 | 70 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 5 | 80 | 0 | 0 | 280 | 0 | 179 | 8 | 135 | 26 | 30 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 78 | 217 | 0 | 22 | 1 | 30 | 0 | 50 | 0 | 163 | 163 | 62 | 78 | 0 | 191 | 0 | 0 | 9 | 300 | 8 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 67 | 9 | 30 | 0 | 0 | 399 | 0 | 0 | 0 | 1 | 195 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 10 | 0 | 50 | 17 | 3 | 0 | 536 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 0 | 0 | 0 | 377 | 0 | 0 | 0 | 0 | 20 | 0 | 1 | 0 | 250 | 222 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6283 | 5:00
| Highest Generation |  | 9174 | 19:00
| Day Peak Generation |  | 7938 | 12:00
| Evening Peak Generation |  | 9174 | 19:00
| HVDC Max Flow |  | 732 | 1:00
| HVDC EvPeak Flow |  | 726 | 19:00
| Load factor L.F |  | 84.69%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-11-14
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-11-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7938 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6147 | MW
Evening Peak Generation : |  | 9174 | MW Hour : | 19:00 | Available Max Generation : |  | 13624 | MW
E.P. Demand (at gen end) : |  | 9174 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 9800 | MW
Maximum Generation : |  | 9174 | MW Hour : | 19:00 | Reserve(Generation end) |  | 3824 | MW
Total Gen. (MKWH) : |  | 186.4646 | System Load Factor : | 84.69% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -124 | MW at | 18:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-11-14
Actual : | 102.49 | Ft.(MSL) , | Rule curve : | 107.7 | Ft.( MSL )
Gas Consumed : | Total = | 987.29 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 142104299.178
: |  | Coal : | 47646112.65 | Oil : | 172372134.56 | Total : | 362122546.388
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3502.571 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1187.839 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1063.689 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 960.9285 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 868.4898 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 700.8324 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 396.0262 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 180.5555 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 540.4969 |  |  | 0 | 0%
Total | 0 |  | 9401.4283 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Baghabari-71 MW & 100 MW
5) Shajibazar 330 Mw GT-1
6) Raozan #02
7) Sirajganj-1,3
8) Siddhirganj 335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barapukuria 132/33 KV T-4 transformer was under shut down from 08:37 to 16:12 for A/M.
b) Barishal(N) 132/33 KV T-4 transformer was under shut down from 08:35 to 16:51 for A/M.
c) Baroirhat 132/33 KV T-1 transformer is under shut down since 09:20 for C/M.
d) Mirsharai EPZ-BSRM 230 KV Ckt-1 was under shut down from 10:25 to 17:11 for D/W.
e) Meghnaghat-Comilla(N) 230 KV Ckt-1 was under shut down from 11:52 to 17:31 for A/M.
f) Comilla (N)-Kachua 132 KV Ckt-1 was under shut down from 08:27 to 14:50 for A/M.
g) Sikalbaha-Dohazari 132 KV Ckt-1 was under shut down from 08:56 to 15:45 for A/M.
h) Goalpara 132 KV Busbar-A was under shut down from 09:50 to 16:52 for A/M.
i) Halishahar 132/33 KV T-3 transformer was under shut down from 07:50 to 13:15 for A/M.
j) Hathazari-Baroiarhat 132 KV Ckt-1 was under shut down from 09:05 to 19:28 for A/M.
k) HVDC-Bheramara 230 KV Ckt-1 was under shut down from 09:33 to 15:59 for A/M.
l) Khulna South 230/132 KV T-03 transformer was under shut down from 08:30 to 17:07 for A/M.
m) Mithapukur-Palashbari 132 kV Ckt-2 was under shut down from 08:18 to 15:33 for A/M.
n) RPCL-Mymensing 132 KV Ckt-2 was under shut down from 09:53 to 17:10 for A/M.
o) Natore 132/33 KV T-2 transformer was under shut down from 08:02 to 16:13 for A/M.
p) Netrokona 132/33 KV T-3 transformer was under shut down from 09:18 to 16:07 for A/M.
q) Purbasadipur 132/33 KV T-3 transformer was under shut down from 08:14 to 16:42 for A/M.
r) Bheramara HVDC-Rajshahi 230 KV Ckt-1 was under shut down from 09:24 to 17:38 for D/W.
s) Rajshahi(Old) 132/33 KV T-3 transformer was under shut down from 08:01 to 17:01 for C/M.
t) Rajshahi 230 KV Busbar-1 was under shut down from 10:50 to 14:29 for D/W.
u) Rampura-Bhulta 230 KV Ckt-1 was under shut down from 08:19 to 16:32 for A/M.
v) Sirajganj 230 KV BUS-1 was under shut down from 09:48 to 16:40 for A/M.
w) Sreemangal 132/33 KV T-1 transformer was under shut down from 08:21 to 16:20 for A/M.
x) Sunamganj 132/33 KV T-1 transformer was under shut down from 08:57 to 16:46 for A/M.
y) Kallyanpur 132/33 KV GT-3 transformer was under shut down from 09:17 to 17:37 for C/M.
z) Haripur-Madanganj 132 KV Ckt was under shut down from 09:52 to 14:32 for A/M.
aa) Rampur 230/132 KV MTR-02 transformer was under shut down from 10:28 to 17:28 for D/W.
ab) Jamalpur-UMPL 132 KV Ckt was under shut down from 09:12 to 16:56 for A/M.
ac) Bheramara HVDC-Bahrampur 400 KV Ckt-1 was switched on at 12:36 & Ckt-2 at 14:06..
ad) Haripur 360 MW CCPP tripped at 12:12 and GT was synchronized at 16:49 & ST at 18:08.
ae) Barishal-Bhandaria 132 kV Ckt tripped at 14:14 from Barishal end showing Dist. C-phase and was switched on at | [5 empty] | About 22 MW power interruption occurred under
14:22. | [5 empty] | Bhandaria S/S area from 14:14 to 14:22.
af) Haripur-Sonargaon 132 kV Ckt-1 tripped at 18:59 from Haripur end showing Dist. Z1, A-phase and was switched
on at 9:11.
ag) Ghorashal Unit-5 was shutdown at 22:57 due to Water feed pump problem.
ah) Baroaulia 132/33 kV T-2 transformer was switched on at 05:07.
ai) Mongla 132/33 kV T-1 transformer is under shut down since 07:35(14-11-2021) for A/M.
aj) Mongla 33 kV Bus of 132/33 kV T-2 transformer is under shut down since 07:37(14-11-2021) for C/M by WZPDCO. | [5 empty] | About 35 MW power interruption has been running
under Mongla S/S area since 07:37(14-11-2021).
| Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-11-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2551500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 8363 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 8847360
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 270 | 5530000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 250 | 6164750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6767185 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 681620 | Low demand.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 365328
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 260 | 6339012 | Machine problem
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 329328 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1161720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 40682 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 309457 | 33 kV feeder problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1254120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 828900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 741500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 373854 | Low demand.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 80 | 1132416 | Low demand.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 630000 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 597120 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1582560
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 36343
| Dhaka area Total |  |  |  | 5560 | 2187 | 46273118
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 0 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 4590
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 24 | 85440 | Low demand.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1645856 | Low water level & #2 Under maint.
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 906618
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1043352 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 15120 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1462080 | Low demand.
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 254928 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 481440
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21000
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 5650473
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1237324
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1241158
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 40 | 411840 | Low demand.
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 26345 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 993 | 17187564
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2679106 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 221 | 3106000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7527300 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 551088 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 35 | 603360 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 752727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 990830
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 100 | 448290 | Low demand.
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3261340 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 51 | 166080 | Low demand.
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 457632
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 2005440
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 625500
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 17170 | Reserve.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 465700
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 550200
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1415 | 24862243
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 190 | 4358240 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 456228
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 8 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10700
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 120 | 1977600 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 8 | 96000 | Low demand.
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 245800
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 15360 | Reserve.
| Mymensingh Area Total |  |  |  | 622 | 318 | 7159928
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3643200
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 163 | 3588000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 853200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 181488
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1195968
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1333440
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 1529927
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 205 | 4619280
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 536928
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7267000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 353 | 9090000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 251460
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1492 | 34806891
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 726 | 15380363
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8222112 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 323040 | Low demand.
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1146 | 23925515
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 21 | 399000 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 93 | 2105108 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 286036 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 340 | 8178900 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4354527
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 2046 | 685 | 15323571
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 9 | 9664 | Low demand.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 26190 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 15822 | Low demand.
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 7 | 12162 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 177 | 4521736 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 322 | 8711563 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 60095
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 386880
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 198684
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 21120 | Reserve.
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 42 | 119192 | Low demand.
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 70 | 333792 | Low demand.
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 115104 | Low demand.
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 13320
| Rajshahi Area Total |  |  |  | 2179 | 744 | 14545324
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 81 | 1947055
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 395510
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37874
| Rangpur Area Total |  |  |  | 605 | 194 | 2380439
| Total |  |  |  | 20934 | 9174 | 186464593
| Eastern Grid Total |  |  |  | 13975 | 6405 | 130289744
| Western Grid Total |  |  |  | 6959 | 2769 | 56174849
| National Grid Total |  |  |  | 20934 | 9174 | 186464593
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-11-13
(a) ENTIRE EASTERN GRID : |  | 6130 | MW | (b) ENTIRE WESTERN GRID : |  | 2662 | MW
i) Dhaka area |  | 3244 | MW | i) Khulna area |  | 1009 | MW
ii) Chittagong area |  | 1095 | MW | ii) Rajshahi area |  | 838 | MW
iii) Comilla area |  | 762 | MW | iii) Barisal area |  | 253 | MW
iv) Mymensingh area |  | 678 | MW | iv) Rangpur area |  | 562 | MW
v) Sylhet area |  | 351 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 8792 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 10:00 | Mymensing | 158 | 18:00 | Jessore | 76 | 18:00
Munsiganj | 68 | 1:00 | Kishoreganj | 90 | 19:00 | Benapol | 36 | 18:00
Sonargaon | 68 | 18:30 | Netrokona | 78 | 18:30 | Jhenida(Old) | 78 | 18:00
Shyampur | 178 | 10:00 | Jamalpur | 92 | 18:00 | Bottail | 88 | 18:00
Bhulta | 167 | 12:00 | Sherpur | 86 | 18:00 | G.K Project | 36 | 18:00
Madanganj | 37 | 12:00 | Srimongal | 35 | 18:00 | Faridpur | 100 | 18:00
Shitalakhya | 101 | 12:00 | Shahjibazar | 82 | 20:00 | Rajbari | 32 | 18:00
Rahim steel | 11 | 13:00 | Fenchuganj | 29 | 17:00 | Madaripur | 62 | 19:30
Matuail | 56 | 10:00 | Kulawara | 30 | 18:00 | Sariatpur | 42 | 20:00
Ghorasal | 54 | 11:00 | Sylhet | 110 | 20:00 | Gopalganj | 63 | 18:30
Narsingdi | 126 | 23:00 | Chatak | 16 | 18:30 | Bagerhat | 75 | 18:00
Haripur (SBU) | 104 | 10:00 | Sunamganj | 32 | 18:00 | 43 | 33 | 8:00
Sreenagar | 26 | 18:30 | Biani Bazar | 41 | 18:00 | Satkhira | 70 | 18:30
Ullon | 48 | 17:00 | Comilla (S) | 104 | 18:00 | Gallamari | 29 | 13:00
Hasnabad | 52 | 1:00 | Comilla(N) | 74 | 2:00 | Magura | 38 | 18:30
Magbazar | 68 | 14:00 | Chandpur | 46 | 19:00 | Norail | 35 | 18:00
Maniknagar | 44 | 11:00 | Feni | 84 | 18:30 | Chuadanga | 57 | 18:30
Bangabhaban | 5 | 11:00 | Chowmuhani | 130 | 19:30 | Barisal(N) | 27 | 19:00
Motijheel | 18 | 16:00 | Ashuganj | 30 | 1:00 | Barisal (S) | 80 | 12:00
Narinda | 66 | 13:00 | Daudkandi | 96 | 18:30 | Patuakhali | 75 | 20:00
Kazla | 68 | 12:00 | B.Baria | 106 | 1:00 | Bhandaria | 40 | 20:00
Dhanmondi | 133 | 13:00 | Ramganj | 52 | 19:00 | Borguna | 12 | 19:00
Lalbag | 64 | 13:00 | Chaddagram | 28 | 19:00 | Borhan Uddin | 30 | 21:00
Madartek | 46 | 1:00 | PHP | 6 | 1:00 | Ishurdi | 49 | 18:00
Dhaka University | 22 | 12:00 | Kochua | 38 | 18:00 | Ruppur Paromanobik | 3 | 12:00
Aftabnagar | 10 | 13:00 | Madunaghat | 50 | 18:30 | Natore | 88 | 19:00
Fatullah | 52 | 10:00 | Hathazari | 71 | 18:30 | Bogra | 111 | 19:30
Nawabganj | 32 | 21:00 | Khulshi | 163 | 18:30 | Noagaon | 72 | 19:30
Keraniganj | 53 | 18:30 | Halishahar | 78 | 13:00 | Rajshahi | 95 | 19:00
Banani | 34 | 11:00 | Baraulia | 121 | 8:00 | Rajshahi New | 12 | 10:00
Mirpur | 87 | 18:30 | Sikalbaha | 32 | 20:00 | C.Nawabganj | 39 | 19:00
Kalyanpur | 72 | 12:00 | Dohazari | 86 | 19:00 | Amnura | 29 | 18:30
Gulshan | 72 | 13:00 | Cox'sbazar | 101 | 18:00 | Pabna | 68 | 18:00
Uttara | 62 | 13:00 | Chandraghona | 26 | 18:00 | Shahjadpur | 69 | 18:00
Uttara New | 8 | 18:30 | Kaptai | 3.8 | 18:00 | Serajganj | 54 | 18:30
Kamrangirchar | 75 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 43 | 19:00
Savar | 128 | 17:00 | Bakulia | 102 | 15:00 | Joypurhat | 38 | 20:00
Bhasantec | 78 | 22:00 | Julda | 17 | 1:00 | Sherpur(Bogura) | 46 | 18:00
Agargaon | 72 | 14:00 | TK chemical | 21.9 | 1:00 | Mohastangor | 42 | 18:00
Satmosjid | 78 | 13:00 | Modern Steel | 9 | 14:00 | Bhangura | 20 | 18:00
Tongi | 97 | 10:00 | Shahmirpur | 28 | 18:30 | Rangpur | 94 | 18:00
Kabirpur | 174 | 0:00 | Khagrachhari | 18 | 18:00 | Lalmonirhat | 43 | 18:00
Basundhara | 140 | 18:00 | Matarbari | 28 | 17:00 | Saidpur | 82 | 18:30
Purbachal | 11 | 17:00 | Baroiar Hat | 54 | 23:00 | Purbasadipur | 75 | 19:00
Manikganj | 54 | 0:00 | Rangamati | 10 | 18:00 | Thakurgaon | 62 | 18:30
Joydevpur | 136 | 0:00 | Abul Khair 230 | 123 | 13:00 | Palashbari | 77 | 18:00
New Tongi | 69 | 11:00 | BSRM | 154 | 5:00 | Barapukuria | 38 | 18:00
Kodda | 198 | 9:00 | GPH Ispat | 94 | 9:00 | Panchagar | 43 | 18:00
Dhamrai | 74 | 11:00 | Agrabad | 68 | 19:00 | Joldhaka | 26 | 18:00
Rajendrapur | 80 | 3312:00 | Goalpara | 21 | 13:00 | Kurigram | 42 | 18:00
Valuka | 88 | 12:00 | Central S/S | 72 | 18:00 | Mithapukur | 23 | 18:00
Tangail | 143 | 18:00 | Noapara | 36 | 18:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-11-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 18:00 | 404 | 12:00 | Kaliakoir | 402 | 0.125 | 395 | 0.041667
| Bheramara | 408 | 18:30 | 396 | 12:00 | Bhulta | 391 | 0.75 | 381 | 0.5
| Ashuganj(N) | 398 | 13:00 | 387 | 12:00 | Gopalganj | 415 | 0.625 | 407 | 0.875
| Payra | 416 | 18:00 | 410 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 236 | 1:00 | 235 | 14:00 | Hathazari | 234 | 20:00 | 219 | 12:00
| Ishurdi | 241 | 5:00 | 230 | 12:00 | Megnaghat | 241 | 20:00 | 233 | 10:00
| Ashuganj | 241 | 18:00 | 235 | 12:00 | Fenchuganj | 246 | 18:00 | 242 | 2:00
| Serajganj | 236 | 5:00 | 232 | 8:00 | Siddhirganj | 237 | 18:00 | 230 | 12:00
| Baghabari | 237 | 4:00 | 230 | 12:00 | Maniknagar | 235 | 18:00 | 223 | 11:00
| Barapukuria | 234 | 4:00 | 228 | 13:00 | Agargaon | 234 | 10:00 | 227 | 12:00
| Bogra | 231 | 17:00 | 223 | 12:00 | Barisal | 244 | 18:00 | 238 | 20:00
| Rajshahi | 235 | 5:00 | 222 | 12:00 | Bhola 225 MW | 246 | 4:00 | 242 | 19:30
| Khulna South | 242 | 19:00 | 226 | 12:00 | AKSML | 232 | 18:00 | 218 | 12:00
| Rampura | 234 | 17:00 | 229 | 12:00 | BSRM | 233 | 17:00 | 217 | 12:00
| Haripur | 235 | 18:00 | 228 | 12:00 | Bibiyana | 244 | 18:30 | 239 | 12:00
| Hasnabad | 234 | 17:00 | 227 | 12:00 | Bhulta | 238 | 18:00 | 229 | 12:00
| Shyampur | 233 | 18:00 | 227 | 12:00 | Ashuganj (S) | 239 | 18:30 | 231 | 12:00
| Aminbazar | 236 | 1:00 | 229 | 2:00 | Kaliakoir | 231 | 18:30 | 225 | 3:00
| Tongi | 230 | 18:00 | 221 | 12:00 | GPH | 233 | 18:00 | 217 | 12:00
| Comilla (N) | 236 | 18:00 | 225 | 12:00 | Jhenaidah | 2533 | 7:00 | 226 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 138 | 18:00 | 133 | 11:00 | Kochua | 138 | 0.75 | 134 | 0.58333
| Munsiganj | 140 | 18:00 | 135 | 16:00 | Madanhat | 137 | 0.79167 | 129 | 0.45833
| Sonargaon | 137 | 18:00 | 132 | 11:00 | Hathazari | 137 | 0.54167 | 128 | 0.5
| Shyampur | 140 | 18:00 | 136 | 12:00 | Khulshi | 135 | 0.54167 | 124 | 0.5
| Bhulta | 133 | 18:00 | 129 | 11:00 | Halishahar | 135 | 0.54167 | 125 | 0.20833
| Madanganj | 139 | 14:00 | 134 | 1:00 | Baraulia | 138 | 0.79167 | 127 | 0.41667
| Shitalakhya | 140 | 18:00 | 135 | 16:00 | Sikalbaha | 136 | 0.83333 | 125 | 0.5
| Rahim steal | 138 | 18:00 | 134 | 10:00 | Dohazari | 131 | 0.8125 | 120 | 0.5
| Matuail | 138 | 18:00 | 133 | 11:00 | Cox'sbazar | 120 | 0.33333 | 105 | 0.5
| Ghorasal | 140 | 1:00 | 139 | 23:00 | Chandraghona | 136 | 0.70833 | 128 | 0.41667
| Narsinghdi | 134 | 4:00 | 132 | 12:00 | Kaptai | 133 | 0.75 | 130 | 0.375
| Haripur (SBU) | 138 | 18:00 | 134 | 11:00 | A. Khaer Stl. | 135 | 0.77083 | 125 | 0.5
| Sreenagar | 139 | 18:00 | 135 | 12:00 | Bakulia | 134 | 0.75 | 124 | 0.5
| Ullon | 136 | 6:00 | 132 | 12:00 | Julda | 134 | 0.54167 | 127 | 0.41667
| Hasnabad | 140 | 19:00 | 135 | 9:00 | TK Chemical | 135 | 0.75 | 126 | 0.125
| Magbazar | 136 | 1:00 | 133 | 12:00 | Modern Steel | 136 | 0.83333 | 125 | 0.5
| Maniknagar | 137 | 3:00 | 132 | 12:00 | Shahmirpur | 136 | 0.83333 | 128 | 0.041667
| Bangabhaban | 137 | 3:00 | 132 | 12:00 | Khagrachhari | 135 | 0.75 | 126 | 0.5
| Motijheel | 137 | 3:00 | 132 | 12:00 | Matarbari | 130 | 0.041667 | 115 | 0.5
| Narinda | 137 | 3:00 | 132 | 12:00 | Baroiar Hat | 136 | 17:00 | 129 | 1:00
| Kazla | 137 | 3:00 | 132 | 12:00 | Rangamati | 135 | 18:00 | 126 | 12:00
| Dhanmondi | 139 | 18:00 | 135 | 12:00 | Agrabad | 136 | 13:00 | 125 | 0.5
| Lalbag | 135 | 22:00 | 128 | 12:00 | Goalpara S/S | 135 | 4:00 | 125 | 0.5
| Madartek | 136 | 3:00 | 133 | 9:00 | Khulna Central S/S | 134 | 5:00 | 1126 | 0.5
| Dhaka University | 136 | 2:00 | 132 | 12:00 | Noapara | 135 | 6:00 | 128 | 0.875
| Aftabnagar | 136 | 4:00 | 132 | 12:00 | Jessore | 134 | 0.16667 | 127 | 0.5
| Fatullah | 140 | 18:00 | 136 | 12:00 | Benapol | 135 | 2:00 | 127 | 0.5
| Nawabganj | 139 | 18:00 | 134 | 12:00 | Jhenida(Old) | 138 | 0.20833 | 131 | 0.5
| Keraniganj | 139 | 18:00 | 134 | 12:00 | Bottail | 139 | 0.20833 | 134 | 0.5
| Banani | 136 | 2:00 | 132 | 12:00 | G.K Project | 142 | 0.375 | 129 | 0.5
| Mirpur | 135 | 18:00 | 128 | 10:00 | Faridpur | 140 | 0.125 | 135 | 0.8125
| Kalyanpur | 135 | 18:00 | 130 | 9:00 | Rajbari | 140 | 0.125 | 136 | 0.5
| Gulshan | 136 | 6:00 | 132 | 11:00 | Madaripur | 142 | 6:00 | 139 | 0.77083
| Uttara | 135 | 18:00 | 129 | 11:00 | Shariyatpur S/S | 142 | 0.16667 | 138 | 0.875
| Uttara New | 135 | 22:00 | 129 | 10:00 | Gopalganj | 145 | 3:00 | 139 | 0.41667
| Kamrangirchar | 139 | 18:00 | 135 | 9:00 | Bagerhat | 134 | 19:00 | 122 | 0.5
| Savar | 137 | 22:00 | 128 | 15:00 | Mongla | 133 | 19:00 | 119 | 12:00
| Bhasantec | 136 | 5:00 | 131 | 11:00 | Satkhira | 133 | 0.16667 | 124 | 12:00
| Agargaon | 136 | 2:00 | 132 | 12:00 | Gallamari | 141 | 2:00 | 136 | 0.29167
| Satmosjid | 136 | 2:00 | 131 | 11:00 | Magura | 138 | 0.041667 | 132 | 0.5
| Tongi | 140 | 4:00 | 133 | 10:00 | Narail | 137 | 3:00 | 131 | 0.5
| Kabirpur | 139 | 22:00 | 135 | 18:29 | Chuadanga | 137 | 4:00 | 129 | 0.5
| Basundhara | 138 | 18:30 | 133 | 16:00 | Barisal(N) | 142 | 5:00 | 138 | 21:00
| Purbachal | 137 | 7:00 | 132 | 12:00 | Barisal (S) | 141 | 0.20833 | 137 | 0.875
| Manikganj | 141 | 9:00 | 138 | 8:00 | Patuakhali(S) | 140 | 0.16667 | 135 | 0.77083
| Joydevpur | 139 | 4:00 | 133 | 12:00 | Bhandaria | 141 | 0.625 | 135 | 0.77083
| New Tongi | 140 | 7:00 | 133 | 16:00 | Borguna | 142 | 4:00 | 136 | 19:30
| Kodda | 138 | 7:00 | 127 | 16:00 | Jhenaidah(New) | 138 | 6:00 | 131 | 12:00
| Dhamrai | 136 | 18:00 | 130 | 19:00 | Ishurdi | 140 | 3:00 | 134 | 12:00
| Rajendrapur | 138 | 8:00 | 128 | 16:00 | Ruppur Paromanobik | 139 | 6:00 | 134 | 12:00
| Valuka | 131 | 19:00 | 122 | 12:00 | Natore | 138 | 6:00 | 132 | 12:00
| Tangail | 138 | 0:00 | 132 | 16:00 | Bogra | 136 | 6:00 | 132 | 12:00
| Mymensing | 133 | 6:00 | 124 | 14:00 | Noagaon | 135 | 6:00 | 128 | 13:00
| Kishorganj | 134 | 9:00 | 129 | 12:00 | Rajshahi | 137 | 18:30 | 130 | 12:00
| Netrokona | 131 | 4:00 | 124 | 12:00 | Rajshahi New | 139 | 6:00 | 131 | 12:00
| Jamalpur | 137 | 18:30 | 128 | 7:00 | C.Nawabganj | 138 | 18:00 | 130 | 12:00
| Sherpur | 137 | 18:30 | 126 | 7:00 | Amnura | 139 | 19:00 | 129 | 12:00
| Srimongal | 138 | 8:00 | 136 | 1:00 | Pabna | 139 | 3:00 | 133 | 12:00
| Shahjibazar | 137 | 8:00 | 134 | 5:00 | Shahjadpur | 140 | 18:00 | 135 | 12:00
| Fenchuganj | 138 | 8:00 | 135 | 2:00 | Serajganj | 136 | 5:00 | 133 | 12:00
| Khulawara | 137 | 19:00 | 136 | 1:00 | Niyamatpur | 134 | 6:00 | 127 | 12:00
| Sylhet | 135 | 7:00 | 133 | 1:00 | Joypurhat | 136 | 19:00 | 130 | 12:00
| Chatak | 136 | 3:00 | 135 | 1:00 | Sherpur(Bogura) | 138 | 3:00 | 132 | 12:00
| Sunamganj | 135 | 6:00 | 132 | 16:00 | Mohastangor | 137 | 19:00 | 131 | 12:00
| Biani Bazar | 135 | 03:00 | 133 | 12:00 | Bangura | 140 | 6:00 | 134 | 12:00
| Comilla(s) | 130 | 15:00 | 126 | 18:00 | Rangpur | 131 | 17:00 | 125 | 12:00
| Comilla(n) | 141 | 17:00 | 135 | 12:00 | Lalmonirhat | 132 | 6:00 | 125 | 12:00
| Chandpur | 140 | 15:00 | 132 | 1:00 | Saidpur | 132 | 6:00 | 125 | 12:00
| Feni | 137 | 18:00 | 128 | 1:00 | Purbasadipur | 131 | 17:00 | 122 | 18:00
| Chowmuhani | 135 | 18:00 | 127 | 1:00 | Thakurgaon | 130 | 11:00 | 125 | 19:00
| Ashuganj | 139 | 19:00 | 136 | 12:00 | Palashbari | 134 | 6:00 | 128 | 12:00
| Daudkandi | 139 | 17:00 | 133 | 3:00 | Barapukuria | 134 | 0.25 | 128 | 0.54167
| B.Baria | 135 | 14:00 | 133 | 19:30 | Panchagar | 131 | 0.125 | 121 | 0.75
| Ramganj | 137 | 17:00 | 129 | 1:00 | Joldhaka | 131 | 0.25 | 123 | 0.75
| Chaddagram | 139 | 18:00 | 132 | 1:00 | Kurigram | 132 | 0.70833 | 123 | 0.29167
| PHP | 136 | 18:00 | 128 | 1:00 | Mithapukur | 135 | 0.125 | 128 | 0.54167

## L-Curve
Date | 2021-11-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 210 | 5165 | 2305 | 7470 |  |  |  | QF-LDC-11
0:30 | 282 | 5197 | 2301 | 7498 | Date: | 2021-11-13
1:00 | 354 | 5229 | 2297 | 7526
1:30 | 317 | 5138 | 2218.5 | 7356.5
2:00 | 280 | 5047 | 2140 | 7187
2:30 | 303 | 4984.5 | 2108 | 7092.5 | [5 empty] | Gen. at Eve. Peak | 9174 | 9174 MW (19:00 )
3:00 | 326 | 4922 | 2076 | 6998 | [6 empty] | 19:00
3:30 | 294 | 4887.5 | 1995.5 | 6883 | [5 empty] | Gen. at Day Peak | 7938 | 7938 MW (12:00 )
4:00 | 262 | 4853 | 1915 | 6768 | [6 empty] | 12:00
4:30 | 271 | 4604.5 | 1921 | 6525.5 | [5 empty] | Highest Generation | 9174
5:00 | 280 | 4356 | 1927 | 6283 | [6 empty] | 19:00
5:30 | 266 | 4516 | 1965 | 6481
6:00 | 252 | 4676 | 2003 | 6679
6:30 | 153 | 4782.5 | 2025 | 6807.5
7:00 | 54 | 4889 | 2047 | 6936
7:30 | 36 | 5006.5 | 2050.5 | 7057
8:00 | 18 | 5124 | 2054 | 7178
8:30 | 68 | 5191.5 | 2023.5 | 7215
9:00 | 118 | 5259 | 1993 | 7252
9:30 | 146 | 5270.5 | 1976 | 7246.5
10:00 | 174 | 5282 | 1959 | 7241
10:30 | 220 | 5338.5 | 2046 | 7384.5
11:00 | 266 | 5395 | 2133 | 7528
11:30 | 285 | 5519.5 | 2213.5 | 7733
12:00 | 304 | 5644 | 2294 | 7938
12:30 | 266 | 5625.5 | 2307 | 7932.5
13:00 | 228 | 5607 | 2320 | 7927
13:30 | 244 | 5473.5 | 2280.5 | 7754
14:00 | 260 | 5340 | 2241 | 7581
14:30 | 335 | 5314 | 2250 | 7564
15:00 | 410 | 5288 | 2259 | 7547
15:30 | 416 | 5220 | 2248.5 | 7468.5
16:00 | 422 | 5152 | 2238 | 7390
16:30 | 355 | 5268 | 2281 | 7549
17:00 | 288 | 5384 | 2324 | 7708
17:30 | 206 | 5887.5 | 2532 | 8419.5
18:00 | 124 | 6391 | 2740 | 9131
18:30 | 65 | 6398 | 2754.5 | 9152.5
19:00 | 6 | 6405 | 2769 | 9174
19:30 | 50 | 6329 | 2763 | 9092
20:00 | 52 | 6246 | 2779 | 9025 |  |  |  | Executive Engineer
20:30 | 37 | 6155.5 | 2699.5 | 8855 |  |  |  | Network Operation Division
21:00 | 22 | 6065 | 2620 | 8685
21:30 | 39 | 5966.5 | 2552.5 | 8519
22:00 | 56 | 5868 | 2485 | 8353 |  |  |  |  | Page 6 of 7
22:30 | 115 | 5661 | 2428 | 8089
23:00 | 174 | 5454 | 2371 | 7825
23:30 | 192 | 5309.5 | 2338 | 7647.5
24:00 | 210 | 5165 | 2305 | 7470
9174 MW (19:00 )
7938 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-11-13 |  | Energy |  | 186464593
[13 empty] | 2021-11-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3454 | 726 | 2037 | 0 | 676 | 423 | 70 | 0 | 0 | 84 | 0 | 0
0:30 | 3535 | 729 | 2021.5 | 0 | 610 | 402.5 | 69.5 | 0 | 42.5 | 88 | 0 | 0 | Date: | 2021-11-13
1:00 | 3616 | 732 | 2006 | 0 | 544 | 382 | 69 | 0 | 85 | 92 | 0 | 0
1:30 | 3577 | 689 | 1934 | 0 | 545 | 366.5 | 69 | 0 | 85 | 91 | 0 | 0 | [8 empty] | Total Energy | 186.4646 | Total Energy Gen 186.465 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 186.465 MKWHr
2:00 | 3538 | 646 | 1862 | 0 | 546 | 351 | 69 | 0 | 85 | 90 | 0 | 0 | [8 empty] | Energy not Served | 0
2:30 | 3483.5 | 642 | 1844 | 0 | 538 | 341.5 | 69.5 | 0 | 85 | 89 | 0 | 0 | [8 empty] | Energy Requirement | 186.4646
3:00 | 3429 | 638 | 1826 | 0 | 530 | 332 | 70 | 0 | 85 | 88 | 0 | 0
3:30 | 3429.5 | 566 | 1831.5 | 0 | 482.5 | 331.5 | 70 | 0 | 85 | 87 | 0 | 0 | [6 empty] | Shortage
4:00 | 3430 | 494 | 1837 | 0 | 435 | 331 | 70 | 0 | 85 | 86 | 0 | 0
4:30 | 3249 | 494 | 1826.5 | 0 | 378 | 336.5 | 70.5 | 0 | 85 | 86 | 0 | 0
5:00 | 3068 | 494 | 1816 | 0 | 321 | 342 | 71 | 0 | 85 | 86 | 0 | 0
5:30 | 3209.5 | 494 | 1849.5 | 0 | 321 | 367 | 71 | 0 | 85 | 84 | 0 | 0
6:00 | 3351 | 494 | 1883 | 0 | 321 | 392 | 71 | 0 | 85 | 82 | 0 | 0
6:30 | 3390 | 494 | 1938 | 0 | 353.5 | 392.5 | 71 | 0 | 85 | 80 | 3.5 | 0 |  |  |  |  | Coal
7:00 | 3429 | 494 | 1993 | 0 | 386 | 393 | 71 | 0 | 85 | 78 | 7 | 0
7:30 | 3461.5 | 494 | 2042 | 0 | 419.5 | 392.5 | 71 | 0 | 85 | 80 | 11.5 | 0 |  |  |  | Oil |  |  |  | ,
8:00 | 3494 | 494 | 2091 | 0 | 453 | 392 | 71 | 0 | 85 | 82 | 16 | 0
8:30 | 3493.5 | 494 | 2061 | 0 | 527 | 391.5 | 70.5 | 0 | 70 | 76 | 31.5 | 0
9:00 | 3493 | 494 | 2031 | 0 | 601 | 391 | 70 | 0 | 55 | 70 | 47 | 0
9:30 | 3474.5 | 494.5 | 2029.5 | 0 | 648.5 | 376 | 69.5 | 0 | 27.5 | 70 | 56.5 | 0
10:00 | 3456 | 495 | 2028 | 0 | 696 | 361 | 69 | 0 | 0 | 70 | 66 | 0
10:30 | 3455.5 | 579.5 | 2024 | 0 | 755 | 360.5 | 73.5 | 0 | 0 | 71 | 65.5 | 0
11:00 | 3455 | 664 | 2020 | 0 | 814 | 360 | 78 | 0 | 0 | 72 | 65 | 0
11:30 | 3492 | 698 | 2092.5 | 0 | 891.5 | 361 | 59 | 0 | 0 | 70 | 69 | 0
12:00 | 3529 | 732 | 2165 | 0 | 969 | 362 | 40 | 0 | 0 | 68 | 73 | 0
12:30 | 3589 | 732 | 2020 | 0 | 1048.5 | 362.5 | 55 | 0 | 0 | 70 | 55.5 | 0
13:00 | 3649 | 732 | 1875 | 0 | 1128 | 363 | 70 | 0 | 0 | 72 | 38 | 0
13:30 | 3649 | 732 | 1875 | 0 | 1128 | 363 | 70 | 0 | 0 | 72 | 38 | 0
14:00 | 3649 | 732 | 1875 | 0 | 1128 | 363 | 70 | 0 | 0 | 72 | 38 | 0
14:30 | 3561.5 | 732 | 1870 | 0 | 1056.5 | 363 | 70 | 0 | 0 | 56 | 28 | 0
15:00 | 3474 | 732 | 1865 | 0 | 985 | 363 | 70 | 0 | 0 | 40 | 18 | 0
15:30 | 3473 | 732 | 1836 | 0 | 930.5 | 363 | 70 | 0 | 0 | 52 | 12 | 0
16:00 | 3472 | 732 | 1807 | 0 | 876 | 363 | 70 | 0 | 0 | 64 | 6 | 0
16:30 | 3419 | 732 | 1804.5 | 0 | 1077 | 362.5 | 70 | 0 | 5 | 76 | 3 | 0
17:00 | 3366 | 732 | 1802 | 0 | 1278 | 362 | 70 | 0 | 10 | 88 | 0 | 0
17:30 | 3444.5 | 729 | 1871 | 0 | 1717 | 392 | 86.5 | 0 | 83.5 | 96 | 0 | 0
18:00 | 3523 | 726 | 1940 | 0 | 2156 | 422 | 103 | 0 | 157 | 104 | 0 | 0
18:30 | 3577 | 726 | 2029.5 | 0 | 2051 | 421.5 | 86.5 | 0 | 158 | 103 | 0 | 0
19:00 | 3631 | 726 | 2119 | 0 | 1946 | 421 | 70 | 0 | 159 | 102 | 0 | 0
19:30 | 3775 | 726 | 2312 | 0 | 1578 | 421 | 70 | 0 | 110 | 100 | 0 | 0
20:00 | 3782 | 726 | 2230 | 0 | 1578 | 431 | 70 | 0 | 110 | 98 | 0 | 0
20:30 | 3770.5 | 725.5 | 2269.5 | 0 | 1410 | 440.5 | 70 | 0 | 72 | 97 | 0 | 0
21:00 | 3759 | 725 | 2309 | 0 | 1242 | 450 | 70 | 0 | 34 | 96 | 0 | 0
21:30 | 3702.5 | 725.5 | 2274.5 | 0 | 1185.5 | 450 | 70 | 0 | 17 | 94 | 0 | 0
22:00 | 3646 | 726 | 2240 | 0 | 1129 | 450 | 70 | 0 | 0 | 92 | 0 | 0
22:30 | 3587.5 | 726 | 2218.5 | 0 | 960.5 | 436.5 | 70 | 0 | 0 | 90 | 0 | 0
23:00 | 3529 | 726 | 2197 | 0 | 792 | 423 | 70 | 0 | 0 | 88 | 0 | 0
23:30 | 3491.5 | 726 | 2117 | 0 | 734 | 423 | 70 | 0 | 0 | 86 | 0 | 0 | Max Temp. in Dhaka |  | 24.7° C | 29.2° C
24:00 | 3454 | 726 | 2037 | 0 | 676 | 423 | 70 | 0 | 0 | 84 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 186.465 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 186.465 MKWHr
Note on W13: Author:

## Generation
g | 2021-11-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 29 | 29 | 30 | 30 | 31 | 31 | 31 | 31 | 30 | 29 | 38 | 0 | 0 | 0 |  |  |  | 33 |  | 0 | [6 empty] | 321856
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1324000
3 | Chattogram TPP-1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | [19 empty] | 4590
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 55 | [8 empty] | 68 |  | 68 | 68 | 68 | 34 |  |  | 0 | 1043352
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 51 | 51 | 34 | 57 | 105 |  | 105 | 68 | 68 | 34 | 34 | 34 | 34 | 906618
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 264 | 263 | 261 | 262 | 261 | 261 | 263 | 263 | 262 | 265 | 262 | 263 | 260 | 263 | 263 | 262 | 260 | 264 |  | 260 | 264 | 260 | 261 | 260 | 264 | 261 | 6339012
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 32 | 135 |  | 45 | 45 | 45 |  |  |  |  | 373854
19 | Ashuganj 195MW PP (APSCL-United) | 70 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 752727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 |  | 0 | 2551500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 120 | 120 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2679106
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 26 | 26 | 23 | 26 | 23 | 26 |  | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 551088
33 | Ashuganj 225 MW CCPP | 180 | 181 | 180 | 180 | 196 | 180 | 193 | 182 | 186 | 181 | 181 | 215 | 219 | 179 | 179 | 187 | 187 | 221 |  | 221 | 218 | 221 | 221 | 178 | 186 | 181 | 3106000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 305 | 310 | 330 | 345 | 300 | 290 | 290 | 330 | 310 | 280 | 280 | 290 | 305 | 295 |  | 300 | 340 | 300 | 300 | 270 | 280 | 280 | 7527300
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 17 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 42 | 52 | 53 | 53 | 53 | 603360
36 | Chandpur 150 MW CCPP | 138 | 137 | 138 | 139 | 138 | 136 | 138 | 137 | 137 | 137 | 138 | 136 | 136 | 136 | 136 | 137 | 134 | 136 |  | 135 | 136 | 133 | 136 | 136 | 137 | 132 | 3261340
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 393 | 378 | 327 | 324 |  | 304 | 304 | 340 | 352 | 352 | 352 | 352 | 384 | 400 | 400 | 363 | 337 | 349 |  | 397 | 399 | 398 | 398 | 398 | 397 | 395 | 8847360
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6164750
41 | Haripur 360MW CCPP(HPL) | 337 | 289 | 287 | 288 | 257 | 302 | 303 | 303 | 300 | 300 | 308 | 326 |  |  |  |  | 90 | 100 |  | 270 | 302 | 300 | 332 | 336 | 329 | 326 | 5530000
42 | RPCL 210MW CCPP | 217 | 219 | 218 | 218 | 218 | 219 | 218 | 217 | 213 | 159 | 157 | 156 | 156 | 158 | 158 | 158 | 158 | 165 |  | 190 | 185 | 185 | 170 | 175 | 176 | 176 | 4358240
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 3 | 11 | 36 | 48 | 44 | 52 | 22 | 16 | 8 | 3 | 0 | [9 empty] | 245800
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 161 | 162 | 161 | 161 | 160 | 163 | 161 | 162 | 160 | 162 | 164 | 162 | 160 | 162 | 163 | 160 | 161 | 164 |  | 163 | 162 | 162 | 160 | 161 | 160 | 161 | 3588000
47 | Shahjibazar GTPP Unit- 8 & 9 | 55 | 51 | 40 | 40 | 40 | 40 | 40 | 20 | 50 | 60 | 61 | 61 | 64 | 64 | 40 | 40 | 40 | 62 |  | 62 | 62 | 62 | 62 | 62 | 40 | 40 | 1195968
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 81 | 78 | 78 | 81 | 83 | 80 | 81 | 83 | 40 | 84 |  | 84 | 84 | 84 | 84 | 81 | 40 | 5 | 1333440
| Shahjibazar 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 100 | 100 | 1529927
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 178 | 178 | 178 | 151 | 152 | 176 | 212 | 212 | 205 | 205 | 205 | 205 | 205 | 198 | 199 | 178 | 204 |  | 205 | 205 | 205 | 205 | 205 | 178 | 178 | 4619280
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251460
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 10 | 8 | 8 | 8 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 5 | 5 | 5 | 11 | 11 | 11 | 0 | 181488
55 | Fenchugonj 51 MW PP (Barakatullah) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 39 | 39 | 39 | 42 | 50 | 47 | 50 | 53 | 53 | 25 | 50 |  | 53 | 53 | 50 | 50 | 53 | 53 | 52 | 853200
56 | Shahjahanulla 25 MW PP | 24 | 23 | 23 | 23 | 23 | 16 | 16 | 16 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 536928
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 290 | 300 | 290 | 300 | 305 | 300 | 295 | 295 | 305 | 300 | 310 | 290 | 290 | 280 | 310 | 285 |  | 290 | 325 | 300 | 280 | 290 | 280 | 300 | 7267000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 |  | 17 | [5 empty] | 0 | 309457
59 | Tangail Palli Power Gen 22 MW | [16 empty] | 0 | 7 | [7 empty] | 0 | 15360
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [13 empty] | 18 | 18 | 16 | 16 | 16 | 16 | 254928
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  |  |  | 16 | 18 | 19 | 19 | 19 | 19 | 0 | 365328
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 17 | 12 | 22 | 22 | 22 | 456228
63 | Impoprt (Tripura) | 92 | 90 | 88 | 86 | 86 | 82 | 78 | 82 | 70 | 70 | 72 | 68 | 72 | 72 | 40 | 64 | 88 | 104 |  | 102 | 100 | 98 | 96 | 92 | 88 | 84 | 2005440
64 | Malancha, Ctg. EPZ (United) | 37 | 32 | 32 | 38 | 38 | 37 | 35 | 4 | 4 | 4 | 2 | 2 | 8 | 6 | 3 | 3 | 6 | 11 |  | 13 | 17 | 17 | 30 | 37 | 38 | 5 | 481440
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 457632
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 210960
67 | Jangalia 33MW PP (Summit) | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 20 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 625500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 465700
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 28 | 28 | 25 | 28 | 28 | 28 | 18 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 654120
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 828900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 17 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 741500
73 | Ghorashal 108MW PP (Regent) | [25 empty] | 53 | 8363
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [11 empty] | 8 | 15 | 8 | 8 | 9 | 46 | 113 |  | 113 | 75 | 75 | 46 | 26 |  | 0 | 550200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | [5 empty] | 24 | 35 | 42 | 108 | 115 | 54 | 54 | 54 | 68 | 156 |  | 162 | 162 | 162 | 162 | 162 | 54 | 0 | 1582560
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [25 empty] | 0 | 0
79 | Kodda 150MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 1 | 8 | [8 empty] | 17170
| Gazipur 100 MW PP | [6 empty] | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 17 | 17 | 17 | [8 empty] | 0 | 630000
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 2 | 4 | 3 | 2 | 3 | 3 | 1 | 0 | [10 empty] | 21000
| Jodiac Power | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 48 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1237324
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 68 | 68 | 68 | 80 | 110 |  | 110 | 110 | 110 | 110 | 68 | 68 | 51 | 1241158
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 285 | 290 | 280 | 290 | 305 | 275 | 305 | 295 | 285 | 295 | 265 | 295 | 295 | 270 | 300 | 290 | 230 | 260 |  | 260 | 300 | 260 | 270 | 260 | 290 | 250 | 6767185
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [10 empty] | 1 | 17 | 24 | 34 | 35 | 35 | 56 | 104 |  | 104 | 53 | 53 | 53 | 17 |  | 0 | 597120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [16 empty] | 10 | 8 | [7 empty] | 0 | 15120
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 5 | 990830
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 24 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 32 | [7 empty] | 0 | 329328
95 | Patenga 50MW PP (Baraka) | [16 empty] | 10 | 39 |  | 24 | [5 empty] | 0 | 85440
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | [6 empty] | 20 | 42 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 45 |  | 40 | 30 | 30 | 30 | 30 | 15 | 15 | 681620
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 20 | [7 empty] | 0 | 40682
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 140 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 163 | 130 | 130 | 163 |  | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 3643200
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [9 empty] | 10700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 37 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 1161720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 45 | 45 | 45 | 32 | 32 | 32 | 32 | 60 | 67 | 80 | 80 | 100 | 100 | 100 | 100 | 80 | 96 | 130 |  | 120 | 120 | 120 | 100 | 100 | 50 | 50 | 1977600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 50 | 70 | 70 | 70 | 70 | 70 | 70 | 58 | 50 | 50 | 50 | 56 |  | 80 | 80 | 80 | 80 | 65 | 43 | 17 | 1132416
115 | Juldah 100 MW PP Unit-3 (Acorn) | 60 | 60 | 60 | 30 | 10 | 10 | 10 | 10 | 40 | 40 | 60 | 60 | 90 | 90 | 90 | 60 | 60 | 60 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1462080
116 | Chandpur 200MW (Desh energy) | [16 empty] | 30 | 66 |  | 51 | [5 empty] | 0 | 166080
117 | Ashuganj 150MW PP (Midland) | [10 empty] | 1 | 10 | 10 | 10 | 10 | 13 | 51 | 120 |  | 100 | 50 | 50 |  |  |  | 0 | 448290
118 | Bibiyana-III 400 MW CCPP | 369 | 369 | 368 | 370 | 332 | 316 | 340 | 371 | 387 | 387 | 386 | 389 | 388 | 403 | 402 | 403 | 353 | 353 |  | 353 | 373 | 404 | 405 | 405 | 410 | 410 | 9090000
| Jamalpur 115 MW PP (United) | [11 empty] | 3 | 8 | 8 | 8 | 8 | 15 | 8 |  | 8 | [5 empty] | 0 | 96000
| Anwara 300 MW PP (United) | 231 | 233 | 232 | 214 | 158 | 158 | 123 | 122 | 157 | 159 | 209 | 242 | 287 | 251 | 250 | 250 | 270 | 304 |  | 304 | 302 | 302 | 303 | 303 | 303 | 303 | 5650473
| Juldah unit-2 (Acorn) | [10 empty] | 10 | 10 | 40 | 40 | 40 | 10 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 10 | 10 | 411840
| Anlima Energy Ltd. | [16 empty] | 6 | 17 | [7 empty] | 0 | 26345
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 2 | 3 | 7 | 8 | 9 | 4 | 3 | 5 | 1 | 0 | [9 empty] | 36343
120 | Eastern Zone Total | 5229 | 5047 | 4922 | 4853 | 4356 | 4676 | 4889 | 5124 | 5259 | 5282 | 5395 | 5644 | 5607 | 5340 | 5288 | 5152 | 5384 | 6391 |  | 6405 | 6329 | 6246 | 6065 | 5868 | 5454 | 5165 | 130289744
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [15 empty] | 3 | 25 | 83 |  | 70 | 53 | 53 |  |  |  | 0 | 323040
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 220 | 172 | 172 | 150 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 171 | 171 | 171 | 171 | 171 | 200 |  | 220 | 220 | 220 | 221 | 221 | 221 | 180 | 4354527
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 286036
| Bhola 225 MW CCPP | 91 | 91 | 90 | 90 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 83 | 83 | 83 | 83 | 83 | 83 | 92 |  | 93 | 93 | 93 | 93 | 92 | 92 | 92 | 2105108
140 | Bhola 33 MW PP (Venture) | 20 | 19 | 18 | 16 | 16 | 17 | 15 | 14 | 13 | 13 | 12 | 13 | 15 | 14 | 12 | 14 | 15 | 20 |  | 21 | 21 | 22 | 22 | 22 | 21 | 21 | 399000
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 732 | 646 | 638 | 494 | 494 | 494 | 494 | 494 | 494 | 495 | 664 | 732 | 732 | 731 | 732 | 732 | 732 | 726 |  | 726 | 726 | 726 | 725 | 726 | 726 | 726 | 15380363
147 | Bheramara 410 MW CCPP | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 325 | 325 | 325 | 300 | 300 | 350 |  | 350 | 380 | 410 | 410 | 360 | 330 | 330 | 8222112
148 | Payra 1320 MW | 300 | 270 | 250 | 250 | 260 | 310 | 310 | 310 | 310 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 340 |  | 340 | 340 | 350 | 370 | 370 | 340 | 340 | 8178900
149
150 | Barapukuria TPP Unit-1 | 82 | 81 | 82 | 81 | 82 | 82 | 83 | 82 | 81 | 81 | 80 | 82 | 83 | 84 | 83 | 83 | 82 | 82 |  | 81 | 81 | 81 | 80 | 80 | 83 | 83 | 1947055
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 8 |  | 9 | [6 empty] | 9664
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [10 empty] | 13320
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 180 | 179 | 177 | 177 | 181 | 194 | 190 | 184 | 181 | 185 | 186 | 185 | 206 | 180 | 160 | 170 | 169 | 164 |  | 177 | 188 | 183 | 173 | 169 | 164 | 173 | 4521736
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 330 | 296 | 326 | 312 | 339 | 350 | 399 | 395 | 336 | 330 | 330 | 421 | 380 | 330 | 370 | 361 | 362 | 344 |  | 322 | 404 | 384 | 417 | 336 | 354 | 320 | 8711563
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 18 | 3 | 3 | 3 | 3 | 3 | 21 | 21 | 17 | 21 | 20 | 19 | 19 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 386880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 198684
165 | Amnura 50 MW PP(Sinha) | [17 empty] | 12 |  | 12 | 0 |  |  |  |  | 0 | 26190
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 8 | [5 empty] | 0 | 15822
167 | Katakhali 50 MW Peaking PP | [17 empty] | 8 |  | 7 | [6 empty] | 12162
168 | Santahar 50 MW Peaking PP | [17 empty] | 33 |  | 33 | [6 empty] | 60095
169 | Natore 52 MW PP (Rajlanka) | [16 empty] | 6 | [8 empty] | 0 | 21120
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 10 | 40 |  | 42 | 42 | 42 |  |  |  | 0 | 119192
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [16 empty] | 8 | 47 |  | 70 | 70 | 70 | 35 | 35 |  | 0 | 333792
172 | Confidence Power Bogura Unit-1 113 MW | [16 empty] | 7 | 35 |  | 35 | 35 | 35 |  |  |  | 0 | 115104
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 34 | 108 |  | 113 | 70 | 70 | 34 | 34 |  | 0 | 395510
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 3 | 4 | 6 | 6 | 6 | 5 | 4 | 2 | 0 | [9 empty] | 37874
178
178