## Daily Gen
Hourly Generation & Demand
Date: | 2015-06-07
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 7358 | 7358 | 0
2:00 | 7124 | 7124 | 0
3:00 | 7026 | 7026 | 0
4:00 | 6868 | 6868 | 0
5:00 | 6649 | 6649 | 0
6:00 | 6161 | 6161 | 0
7:00 | 6092 | 6092 | 0
8:00 | 6237 | 6237 | 0
9:00 | 6443 | 6443 | 0
10:00 | 6531 | 6531 | 0
11:00 | 6678 | 6678 | 0
12:00 | 6861 | 6861 | 0 | Day peak
13:00 | 6862 | 6862 | 0
14:00 | 6828 | 6828 | 0
15:00 | 6909 | 6909 | 0
16:00 | 6942 | 6942 | 0
17:00 | 6833 | 6833 | 0
18:00 | 6581 | 6581 | 0
18:30 | 6660 | 6660 | 0
19:00 | 7184 | 7184 | 0
19:30 | 7394 | 7394 | 0
20:00 | 7459 | 7459 | 0
21:00 | 7496 | 7496 | 0 | Evening peak
22:00 | 7454 | 7454 | 0
23:00 | 7334 | 7334 | 0
24:00 | 7319 | 7319 | 0

## forecast
[7 empty] | POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-07
SUMMARY OF DAILY ELECTRICITY GENERATION
|  | Month : |  | 2015-06-08 |  |  | Day : | Monday |  |  |  | Date : | 2015-06-08
| Probable Maximum Generation : |  |  |  | (a) At Day Peak Hour : |  | 6409 | MW |  | (b) At Evening Peak Hour : |  |  | 7780 | MW
| Water Level of Kaptai Lake at 06:00 AM (ft) |  |  |  | (a) Yesterday : |  | 77.36 |  |  | (b) Today: | 76.9 | (c) Rule Curve: |  | 77.82
Sl. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  |  | Actual Generation |  | Available Geneneration |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[7 empty] | Present | On | 2015-06-07 | On | 2015-06-08 | for Fuel | for Plants S/D | Shut down (Date) / |  | Start up
[7 empty] | Capacity | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | or M/C prob. | Remarks |  | Date
[6 empty] | MW | MW | MW | MW | MW | MW | MW | MW
1a | Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 42 | 42 | 42 | 42 |  |  | #1(6/6/15) |  | 2015-10-06
1b | Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 170 | 170 | 170 | 170
1c | Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 2015-05-01 |  | Unknown
1d | Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
1e | Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6 (18/07/2010) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 94 | 102 | 100 | 100
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 40 | 41 | 42 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract date expired 26/05/2014
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 51 | 55 | 54 | 55 |  | 54 | Machine problem
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3*32 | 96 | 60 | 37 | 45 | 37 | 45 |  | 15 | #3 |  | Unknown
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | 25/5/15 |  | Unknown
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 68 | 81 | 68 | 82 |  | 29 | 2 Engine problem
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 344 | 342 | 343 | 342
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | 24/5/15 |  | Unknown
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 78 | 86 | 86 | 86 |  | 14 | 1 Engine problem
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 135 | 151 | 310 | 305 | 154
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 81 | 84 | 65 | 84 |  | 17 | 1 Engine problem
14 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 102 | 101 | 102 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 16 | 18 | 18 | 18 |  | 4 | 1 Machine problem
16a | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 105 | 105 | 110 | 110 |  | 45 | Machine problem
16b | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 201 | 203 | 197 | 210
17 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 96 | 98 | 74 | 80 | 0 | 80 |  | 18 | Engine problem
18 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 92 | 92 | 92 | 92 |  | 7 | 1 Engine problem
19 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 48 | 49 | 49 | 50
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 76 | 102 | 102 | 102
21 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 45 | 52 | 52 | 52
22 | Kodda Peaking |  | Gas | BPDB-RPCL |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
23 | Summit Power, Dhaka |  | Gas | SIPP,REB | 6*3.67+2*6.97+14*8.73 | 146 | 146 | 104 | 104 | 106 | 105
24 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 43 | 43 | 34 | 43 |  | 9 | 1 Engine problem
25 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | gas shortage.
| Dhaka Area Total |  |  |  |  | 4460 | 4229 | 2236 | 2338 | 2369 | 2508 | 259 | 1444
26a | Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | 2015-06-06 |  | Unknown
26b | Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 80 | 70 | 80 | 100
27 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 26 | 17 | 25
28 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 54 | 54 | 51 | 50
29 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 84 | 80 | 62 | 100
30a | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 37 | 40 | 40 | 40
30b | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 | 75 |  | 2015-06-06 |  | Unknown
31 | Sikalbaha (Energis) |  | HFO | RPP |  | 40 | 40 | 35 | 35 | 26 | 35
32 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 96 | 0 | 96
33 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 0 | 102
34 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 81 | 100 | 69 | 100
35 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 16 | 18 | 18 | 18 |  | 4 | 2 Machine problem
36 | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 3 | 5 | 1 | 5
37 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 83 | 86 | 88 | 100 |  | 22 | Engine problem
| Chittagong area Total |  |  |  |  | 1405 | 1325 | 510 | 722 | 442 | 751 | 355 | 26
38a | Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 128 | 97 | 50 | 50 | 50 | 50 |  | 47 | #1(28/04/2015) |  | Unknown
38b | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 130 | 130 | 130 | 130
38c | Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 150 | 150
38d | Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
38e | Ashuganj 225 MW(GT) |  | Gas | APSCL | 1*140 | 140 | 140 | 65 | 145 | 146 | 140
38f | Ashuganj : GT-2 |  | Gas | APSCL | 1*56 | 56 | 40 | 25 | 0 | 0 | 0 |  | 40 | 2015-07-06 |  | Unknown
38g | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 32 | 32 | 32 |  | 13 | Machine problem
39 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 55 | 56 | 55
40 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 100 | 22 | 95
41 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 53 | 53 | 10 | 53
42 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 177 | 188 | 103 | 188 |  | 7
43 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 8 | 51
44 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 82 | 86 | 61 | 85
45 | Titas (Daudkandi) Peaking |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 0 | 41 |  | 11
46 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 153 | 156 | 153 | 158
47 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 14 | 17 | 15 | 18 |  | 5 | Machine problem
48 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
49 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 30 | 32 | 33 | 33
50 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 52 | 52 | 0 | 52
51 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21 |  | 5 | Machine problem
| Comilla Area Total |  |  |  |  | 1719 | 1612 | 1371 | 1501 | 1133 | 1498 | 0 | 128
52 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 95 | 97 | 95 | 100 |  |  | gas shortage.
53 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 14 | 14 |  | 8 | Machine problem
| Mymensingh Area Total |  |  |  |  | 232 | 224 | 109 | 111 | 109 | 114 | 0 | 0
54a | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 61 | 62 | 69 | 69 |  | 18 | ST (27/05/15) |  | Unknown
54b | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 44 | 44 | 44 | 44 |  | 90 | GT-3 (21/5/15) |  | Unknown
55 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 46 | 49 | 50 | 50
56 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 43 | 46 | 46
57 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 8 | 11 |  |  | Machine problem
58 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 64 | 63 | 64 | 66
59 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 60 | 86
60 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 46 | 46 | 50
61 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 98 | 140 | 136 | 142
62 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 19 | 20
63 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 48 | 50 | 49 | 50
64 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 20 | 24 | 20 | 24
65 | Summit Bibiana- 2 |  | Gas | IPP | 1*222 | 222 | 222 | 230 | 233 | 228 | 222
66 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 982 | 947 | 830 | 880 | 849 | 890 | 0 | 108
67 | Bheramara GT: Unit- 1, 2 ,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 24 | 14 | 30 |  | 16 | # 3 under maint.
68 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | contract date experid 31/12/2013
69 | Bheramara HVDC Interconnector |  |  | India |  | 500 | 500 | 453 | 448 | 453 | 447
70a | Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11 |  | Unknown
70b | Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
71 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 105 | 105 | 35 | 107
72 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115 |  | 0
73 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 35 | 41 |  | 13 | 3 Engine problem
74 | Khulna 150MW GT |  | HSD | NWZPGCL | 1*150 | 158 | 158 | 153 | 144 | 120 | 158
75 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 44 | 65 | 0 | 72 |  | 29 | 3 Engine problem
76 | Noapara (Quantam) |  | HFO | RPP | 5*9.9+6*9.5+2*9.2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | Long term maint.
77 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 32 | 32 | 32 |  | 8 | 1 Engine problem
78 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 40 | 48 | 37 | 48
| Khulna Area Total |  |  |  |  | 1517 | 1448 | 942 | 1022 | 841 | 1050 | 0 | 327
79 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 13 | 26 | 0 | 26
80 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 28 | 34 | 29 | 33
| Barisal Area Total |  |  |  |  | 73 | 63 | 41 | 60 | 29 | 59 | 0 | 0
81a | Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 63 | 67 | 65 | 67
81b | Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 100 | 71 | 90 | 100
82 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 40 | 40 | 0 | 40
83 | Westmont GT, Baghabari |  | Gas | IPP |  |  |  | 0 | 0 | 0 | 0 |  |  | Plant Retired in FY 2013-2014
84 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 50 | 57 | 0 | 57 |  | 14 | 2 Engine problem
85 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 35 | 42 | 42 | 42 |  | 8 | 1 Engine problem
86 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 42 | 42 | 34 | 42 |  | 8 | 1 Engine problem
87 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 43 | 44 | 0 | 45 |  | 6 | Engine problem
88 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 134 | 135 | 134 | 140 |  |  | ST (3/6/15) |  | 17/6/15
89 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 25 | 43 | 0 | 45 |  | 7 | Engine problem
90 | Bogra (GBB) |  | Gas | RPP | 6*4 | 20 | 22 | 18 | 18 | 22 | 18
91 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 20 | 10 | 11 | 11 | 11 |  | 9 | 3 Machine problem
92 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
93 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 807 | 809 | 614 | 633 | 461 | 670 | 0 | 52
94a | Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 68 | 89 | 89 | 89
94b | Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 86 | 90 | 87 | 90 |  | 14 | Machine problem
95 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 15 | 12 | 0 | 17
96 | Syedpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 17 | 15 | 0 | 18
97 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 40 | 22 | 23 | 0 | 26 |  | 15 | Engine problem
| Rangpur Area Total |  |  |  |  | 337 | 280 | 208 | 229 | 176 | 240 | 0 | 29
| Total |  |  |  |  | 11532 | 10937 | 6861 | 7496 | 6409 | 7780 | 614 | 2114
| Useable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6323.7259 | 6909 | 5907.1213 | 7170
A. |  | 2015-06-07 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 7496 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6092 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7496 | MW
3 | Day peak Generation : |  |  | 6861 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6909 | MW
4 | Evening peak Generation : |  |  | 7496 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 170.66 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 109.6695 | MKWHr |  | By Oil: | 44.5664 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.0948 | MKWHr |  | By Hydro: | 1.4972 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 614 | For Oil: | 0 | MW | Dhaka | 2923 | 2923 | 0 |  |  | Hour |  | MW
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 705 | 705 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 2114 | MW | Khulna | 781 | 781 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1015.44 | MMCFD |  |  |  | Rajshahi | 773 | 773 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : |  | 81404566.281 | ii) Oil : Taka |  | 586189707.968 | Comilla | 540 | 540 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 15937101.712 | Total | Taka | 683531375.961 | Mymensingh | 389 | 389 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 276 | 276 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -260 | MW at | 21:00 | hrs | Barisal | 150 | 150 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -60 | MW at | 13:00 | hrs | Rangpur | 372 | 372 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.6° C |  |  | Total | 6909 | 6909 | 0
B. |  | 2015-06-08 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
1 | Maximum Demand* (Generation end) |  |  |  | 7750 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 7780 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Shortage (Generation end) |  |  |  | -30 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
4 | Total Energy Generation |  |  |  | 171 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
5 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6313 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.832 | MKWHr.
ii) During peak Demand : |  |  | 448 | MW at | 21:00 | hrs
iii) Maximum : |  |  | 453 | MW at | 2:00 | hrs
*Cost for HVDC energy is not usaually included in the total fuel cost.
*Demand may vary depending on the weather condition &other factors.

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2015-06-08
Till now the maximum generation is : - |  |  | 7817 MW | 21:00 | Hrs on | 2015-05-31
The Summary of Yesterday's ( |  | 2015-06-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6861 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6313 | MW
Evening Peak Generation : |  | 7496 | MW Hour : | 21:00 | Max Generation : |  | 7780 | MW
E.P. Demand (at gen end) : |  | 7496 | MW Hour : | 21:00 | Max Demand : |  | 7750 | MW
Maximum Generation : |  | 7496 | MW Hour : | 21:00 | Shortage : |  | -30 | MW
Total Gen. (MKWH) : |  | 170.66 | System L/ Factor : | 94.86% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -60 | MW at | 13:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2015-06-08
Actual : | 87.64 | Ft.(MSL) , | Rule curve : | 77.82 | Ft.( MSL )
Gas Consumed : | Total | 1015.44 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : Gas : |  |  | 81404566.281
|  | Coal : | 15937101.712 | Oil : | 586189707.968 | Total : | 683531375.961
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | - | 0:00 | 2865 |  |  | - | -
Chittagong Area | - | 0:00 | 736 |  |  | - | -
Khulna Area | - | 0:00 | 821 |  |  | - | -
Rajshahi Area | - | 0:00 | 768 |  |  | - | -
Comilla Area | - | 0:00 | 594 |  |  | - | -
Mymensingh Area | - | 0:00 | 453 |  |  | - | -
Sylhet Area | - | 0:00 | 337 |  |  | - | -
Barisal Area | - | 0:00 | 158 |  |  | - | -
Rangpur Area | - | 0:00 | 438 |  |  | - | -
-
Total | 0 |  | 7170 |  |  | 0
Information of the Generating machines under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
| 1) Meghanaghat GT-2 (24/05/2015) |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010) |  | 9) Fenchuganj GT3 & ST(31/5/15)
| 2) Meghanaghat GT-1 (29/05/2015) |  |  | 2) Ashuganj ST: Unit-1(28/04/2015) |  | 10) Haripur-412 MW (25/5/15)
|  |  |  | 3) Khulna ST 110 MW (04/11/2014) |  | 11) Sikalbaha GT (06/06/2015)
4) Ghorasal ST: Unit-4 (05/01/2015)
5) Haripur GT1,3( 24/05/2015)
6) Meghnaghat CCPP-ST:(21/04/2015)
7) Fenchuganj CCPP-2:ST(08/4/15)
8) Bheramara GT:Unit-3(10/04/2015)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Forced load shaded / Interrupted Areas
a) Jessore 132/33 kV T-2 transformer tripped at 08:58 showing instantaneous earth fault 67 ,lock out and was switched on
at 09:28.
b) Meghnaghat-Hasnabad 230 kV Ckt-2 was shut down from 01:10 to 03:11(08/06/15) due to red hot maintenance .
c) Cox'sbazar 132/33 kV T1 & T2 transformer tripped at 01:57 showing PRD relay at T2 transformer & O/C relay at T1 |  |  |  | About 30 MW power interruption occurred under Cox'sbazar S/S areas
transformer and were switched on at 02:54(8/6/15) |  |  |  | from 01:57 to 02:54
d) Meghnaghat-Comilla(N) 230 kV Ckt-2 was shut down from 03:13 to 05:59(08/06/15) due to red hot maintenance .
e) Aminbazar 230/132 kV T-3 transformer was shut down from 05:18 to 07:35(08/06/15) due to red hot maintenance .
f) Ashuganj-Ghorasal 230 kV Ckt-1 was under shut down since 07:31 (8/6/2015) due to 450 MW project work.

## P2
POWER GRID COMPANY OF BANGLADESH LTD.
Description of the generation of various Power Stations
| Date : | 2015-06-07 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1 | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 42 | 1005000
2 | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 170 | 3942225
3 | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint
4 | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 190 | 4299750
5 | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 | 0 | Long term maint.
6 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 102 | 2394930
7 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 41 | 1007230
8 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 0 | 0 | Contract Date Expired, Long term maint
9 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 55 | 1258727 | Machine problem
|  |  | 1*32 | PDB | 20 | 20 | 907600
10 | Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 25 | 0
|  |  | 1*32 | PDB | 20 |  | 0 | Under maint. since 18/06/09, Long term maint
11 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 0 | 0 | Under maint.
12 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 81 | 1579100 | Engine problem.
13 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 342 | 8132000 | gas shortage.
14 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 0 | 0 | Under maint.
15 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 86 | 1872960 | Engine problem.
16 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 203 | 151 | 3334080 | Engine problem.
17 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 84 | 1965888 | Engine problem.
18 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 101 | 2183940
19 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 18 | 415548 | Machine problem
20 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 105 | 2554650 | Machine problem
21 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 203 | 4884000
22 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 98 | 80 | 833280 | Engine problem.
23 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 92 | 2021208 | Engine problem.
24 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 49 | 853470
25 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 102 | 2160000
26 | Katpotti 52 MW |  |  | RPP | 52 | 52 | 1090080
27 | Kodda Peaking |  |  | BPDB-RPCL |  | 0 | 0
28
29
30 | Summit Power,Dhaka |  | 6*3.67+2*6.97+14*8.73 | SIPP, REB | 146 | 104 | 2535471 | Machine problem
31 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 43 | 986880 | 1 Engine problem.
32 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Gas Shortage
| Dhaka Area Total |  |  |  | 4128 | 2338 | 52218017
33 | Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 0 | 0 | Gas Shortage
34 | Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 80 | 2400000
35 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 26 | 542700 | Engine problem
36 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 54 | 1279200
37 | Chittagong ECPV 108 MW |  |  | IPP |  | 86 | 2047680 | Engine problem
|  |  | 1*40 | PDB | 40 | 32 | 1250000
|  |  | 1*40 | PDB | 40 | 31 | 0
38 | Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 0 | 0
|  |  | 1*50 | PDB | 50 | 17 | 247200
|  |  | 1*50 | PDB | 50 | 0 | 0
39 | Shikalbaha ST |  | 1*60 | PDB | 40 | 40 | 864050
40 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 0 | 0 | Gas Shortage
41 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 96 | 828924
42 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 102 | 813226
43 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 100 | 1943400
44 | Shikalbaha (Energis) |  |  | RPP | 26 | 35 | 781440
45 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 18 | 392640 | Machine problem
46 | Malancha, Ctg EPZ(United) |  |  |  |  | 5 | 305760
| Chittagong Area Total |  |  |  | 1203 | 722 | 13696220
47 | Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 97 | 0 | 1240714 | #1 under maint.
|  |  | 1*64 | APSCL |  | 50 | 0
48 | Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 130 | 3015230
49 | Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 150 | 3502830
50 | Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 135 | 3235814
| Ashuganj CCPP 225 MW |  | 1*140 | APSCL | 140 | 145 | 2438000
51 | Ashuganj : GT-2 |  | 1*56 | APSCL | 40 | 0 | 347293 | Machine problem
52 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 32 | 727200 | Machine problem
53 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 55 | 1294080
54 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 100 | 2292900
55 | Ashuganj (United) |  | 14*4 | RPP | 53 | 53 | 1272000
56 | Ashuganj Modular 200 MW |  |  | IPP | 195 | 188 | 4399272
57 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 51 | 1186800
58 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 86 | 2040080
59 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 41 | 618816
60 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 156 | 3409567
61 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 17 | 391572 | Machine problem
62 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 8 | 195840
63 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 32 | 775000
64 | Lakdamavi-52 MW |  |  | IPP | 52 | 52 | 983242
65 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 20 | 463670 | Machine problem
| Comilla Area Total |  |  |  | 1612 | 1501 | 33829920
66 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 97 | 5249000 | Gas Shortage
67 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 14 | 299232 | Machine problem
| Mymensingh Area Total |  |  |  | 224 | 111 | 5548232
68 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 62 | 1442000 | Machine problem
69 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 44 | 6064400 | Machine problem
70 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 49 | 1159200
71 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 43 | 441000
72 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 11 | 230352 | Machine problem
[5 empty] | 0 | 0 | 0
73 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 63 | 1457000
74 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 86 | 2026560
75 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 46 | 1021320
76 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 140 | 3069580
77 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 19 | 466000
78 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 50 | 1151140
79 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 24 | 459288
80 | Summit Bibiana-2 |  | 1*222 | IPP | 222 | 233 | 5292500
81 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 10 | 247500
| Sylhet Area Total |  |  |  | 947 | 880 | 24527840
|  |  | 1*20 | PDB | 16 | 12 | 0
82 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 12 | 248800
|  |  | 1*20 | PDB | 16 | 0 | 0 | Under maint
83 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
84 | Bheramara HVDC Interconnector |  |  | India | 500 | 448 | 10832000
85 | Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint
86 | Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
87 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 105 | 2323680
88 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 115 | 2714880
89 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 41 | 417600 | Engine problem
90 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 158 | 144 | 2755200
91 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 65 | 1275456 | Engine problem
92 | Noapara (Quantam) |  | 9.9*5+9.5*6+9.2*2 | RPP | 101 | 0 | 0 | All Engine problem, Long term maint
93 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 32 | 696750 | Engine problem
94 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 48 | 694500
| Khulna Area Total |  |  |  | 1448 | 1022 | 21958866
95 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 14 | 0
96 |  |  | 1*20 | PDB | 14 | 12 | 472393
97 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 34 | 722500
| Barisal Area Total |  |  |  | 63 | 60 | 1194893
98 | Baghabari GT |  | 1*71 | PDB | 71 | 67 | 1533000
99 | Baghabari GT |  | 1*100 | PDB | 100 | 71 | 2097000
100 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 40 | 627112 | Engine problem
101 | Westmont GT, Baghabari |  |  | IPP |  | 0 | 0 | Plant Retired in FY 2013-2014
102 | Bera Peaking |  | 9*8.29 | PDB | 71 | 57 | 783407 | Engine problem
103 | Amnura |  | 7*7.79 | QRPP | 50 | 42 | 777790 | Engine problem
104 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 42 | 830481 | Engine problem
105 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 44 | 704558 | Engine problem
106 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 135 | 3275500 | ST under maint
107 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 43 | 585691 | Engine problem
108 | Bogra (GBB) |  | 6*4 | RPP | 22 | 18 | 457530
109 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 20 | 11 | 257904 | Machine problem
110 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 261846
111 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 52 | 890400 | Engine problem
| Rajshahi Area Total |  |  |  | 809 | 633 | 13082219
112 | Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 89 | 2017309 | Machine problem
113 | Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 90 | 2077527 | Machine problem
114 | Rangpur GT |  | 1*20 | PDB | 20 | 12 | 74500 | Machine problem
115 | Saidpur GT |  | 1*20 | PDB | 20 | 15 | 110000
116 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 40 | 23 | 324410 | Engine problem
| Rangpur Area Total |  |  |  | 280 | 229 | 4603746
| Total |  |  |  | 10714 | 7496 | 170659953
| Eastern Grid Total |  |  |  | 8114 | 5552 | 129820229
| Western Grid Total |  |  |  | 2600 | 1944 | 40839724
| National Grid Total |  |  |  | 10714 | 7496 | 170659953
*Data collected from respective power station over telephone.

## P3
| POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-09
NATIONAL LOAD DESPATCH CENTER
PEAK HOUR DEMAND (AT S/S END) OF DIFFERENT AREAS
Date: | 2015-06-07
(a) ENTIRE EASTERN GRID : |  |  | 4833 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2076 | MW
i) Dhaka area |  |  | 2923 | MW | i) Khulna area |  |  | 781 | MW
ii) Chittagong area |  |  | 705 | MW | ii) Rajshahi area |  |  | 773 | MW
iii) Comilla area |  |  | 540 | MW | iii) Barisal area |  |  | 150 | MW
iv) Mymensingh area |  |  | 389 | MW | iv) Rangpur area |  |  | 372 | MW
v) Sylhet area |  |  | 276 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6909 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 110 | 900 | Kishorganj | 45 | 1900 | Noapara | 49 | 2100
Munsiganj | 108 | 2000 | Netrokona | 43 | 1900 | Jessore | 106 | 2000
Megnaghat | 134 | 2100 | Jamalpur | 88 | 1900 | Jhenida | 57 | 2400
Shyampur | 138 | 2400 | Sherpur | 20 | 100 | Bottail | 74 | 1930
Bhulta | 126 | 2100 | Srimongal | 34 | 1930 | G.K Project | 31 | 1930
Madanganj | 140 | 2300 | Shahjibazar | 48 | 2100 | Faridpur | 84 | 100
Shitalakhya | 86 | 1000 | Fenchuganj | 22 | 2200 | Madaripur | 71 | 500
Rahim steel | 4 | 1100 | Khulawara | 31 | 2100 | Gopalganj | 38.6 | 2400
Matuail | 55 | 2400 | Sylhet | 129 | 1930 | Bagerhat | 53 | 2100
Ghorasal | 82 | 2400 | Chatak | 39 | 2200 | Mongla | 23.6 | 1100
Narsingdi | 70 | 2000 | Comilla(S) | 156 | 2200 | Satkhira | 54.2 | 2200
Haripur (SBU) | 59 | 2200 | Comilla(N) | 40 | 1900 | Gallamari | 45.2 | 1300
Ullon | 101 | 2000 | Chandpur | 72 | 1500 | Magura | 26 | 100
Hasnabad | 136 | 2000 | Feni | 71 | 2100 | Chuadanga | 40 | 400
Magbazar | 155 | 1600 | Chowmuhani | 112 | 1700 | Barisal | 80 | 100
Maniknagar | 106 | 1500 | Ashuganj | 53 | 1930 | Patuakhali | 52 | 100
Bangabhaban | 44 | 1500 | Daudkandi | 42 | 2200 | Bhandaria | 28 | 2000
Narinda | 86 | 1200 | B.Baria | 81 | 2400 | Ishurdi | 39 | 1900
Dhanmondi | 170 | 1200 | Madanhat 32305 | 40.5 | 1200 | Natore | 70 | 2000
Lalbag | 72 | 1700 | Hathazari | 88 | 2200 | Bogra | 177 | 100
Mirpur | 24 | 1900 | Khulshi | 148 | 23 | Noagaon | 79 | 2000
Kalyanpur | 84.5 | 2000 | Halishahar | 124 | 2300 | Rajshahi | 114 | 2000
Gulshan | 156 | 2100 | Baraulia | 118 | 200 | C.Nawabganj | 63 | 100
Uttara | 150 | 1500 | Sikalbaha | 29 | 100 | Pabna | 71 | 100
Kamrangirchar | 98 | 1830 | Dohazari | 60 | 100 | Shahjadpur | 53 | 2000
Savar | 97 | 1200 | Cox'sbazar | 52 | 1900 | Serajganj | 60 | 2000
Bhasantec | 94 | 2100 | Chandraghona | 28 | 2200 | Niyamatpur | 55 | 2000
Agargaon | 109 | 1830 | Kaptai | 4 | 1830 | Joypurhat | 24 | 1930
Tongi | 94 | 1100 | A. Khaer Stl. | 23.5 | 1300 | Rangpur | 81 | 2000
Kabirpur | 183 | 300 | Bakulia | 97 | 1900 | Lalmonirhat | 58 | 1930
Basundhara | 137 | 1400 | Julda | 20 | 100 | Saidpur | 68 | 1900
Manikganj | 70 | 2200 | TK chemical | 2.4 | 100 | Purbasadipur | 66 | 1200
Joydevpur | 210 | 600 | Modern Steel | 16 | 1000 | Thakurgaon | 48 | 1930
New Tongi | 97 | 900 | Shahmirpur | 15.3 | 1900 | Palashbari | 50 | 100
Tangail | 98 | 2400 | Goalpara | 33 | 1930 | Barapukuria | 31 | 2000
Mymensing | 130 | 2100 | Central s/s | 69 | 2200 | Panchagar | 16 | 1900
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## L.curve
Date | 2015-06-07 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -350 | 5479 | 1956 | 7435 | -350 | 7435 | 0:00 | DAILY LOAD CURVE | 2015-06-07
0:30 | -350 | 5512.5 | 1884 | 7396.5 | -350 | 7396.5 | 1:00
1:00 | -350 | 5546 | 1812 | 7358 | -410 | 7358 | 2:00
1:30 | -380 | 5491 | 1750 | 7241 | -440 | 7241 | 3:00
2:00 | -410 | 5436 | 1688 | 7124 | -400 | 7124 | 4:00
2:30 | -425 | 5420 | 1655 | 7075 | -380 | 7075 | 5:00
3:00 | -440 | 5404 | 1622 | 7026 | -340 | 7026 | 6:00
3:30 | -420 | 5319.5 | 1627.5 | 6947 | -330 | 6947 | 7:00
4:00 | -400 | 5235 | 1633 | 6868 | -330 | 6868 | 8:00
4:30 | -390 | 5158 | 1600.5 | 6758.5 | -270 | 6758.5 | 9:00
5:00 | -380 | 5081 | 1568 | 6649 | -160 | 6649 | 10:00
5:30 | -360 | 4872 | 1533 | 6405 | -150 | 6405 | 11:00
6:00 | -340 | 4663 | 1498 | 6161 | -80 | 6161 | 12:00
6:30 | -335 | 4662 | 1464.5 | 6126.5 | -60 | 6126.5 | 13:00
7:00 | -330 | 4661 | 1431 | 6092 | -100 | 6092 | 14:00 |  |  |  | 7496 | 21:00
7:30 | -330 | 4734 | 1430.5 | 6164.5 | -80 | 6164.5 | 15:00 |  |  |  | 6861 | 12:00
8:00 | -330 | 4807 | 1430 | 6237 | -70 | 6237 | 16:00
8:30 | -300 | 4905.5 | 1434.5 | 6340 | -100 | 6340 | 17:00
9:00 | -270 | 5004 | 1439 | 6443 | -150 | 6443 | 18:00
9:30 | -215 | 5004 | 1483 | 6487 | -110 | 6487 | 18:30
10:00 | -160 | 5004 | 1527 | 6531 | -120 | 6531 | 19:00
10:30 | -155 | 5029 | 1575.5 | 6604.5 | -220 | 6604.5 | 19:30
11:00 | -150 | 5054 | 1624 | 6678 | -240 | 6678 | 20:00
11:30 | -115 | 5055 | 1714.5 | 6769.5 | -260 | 6769.5 | 21:00
12:00 | -80 | 5056 | 1805 | 6861 | -260 | 6861 | 22:00
12:30 | -70 | 5033.5 | 1828 | 6861.5 | -260 | 6861.5 | 23:00
13:00 | -60 | 5011 | 1851 | 6862 | -280 | 6862 | 24:00
13:30 | -80 | 5035 | 1810 | 6845 |  | 6845
14:00 | -100 | 5059 | 1769 | 6828 | 128.92 | 6828
14:30 | -90 | 5084 | 1784.5 | 6868.5 | 86.5 | 6868.5
15:00 | -80 | 5109 | 1800 | 6909 |  | 6909
15:30 | -75 | 5126.5 | 1799 | 6925.5 | 7867500 | 6925.5
16:00 | -70 | 5144 | 1798 | 6942 |  | 6942
16:30 | -85 | 5127 | 1760.5 | 6887.5 |  | 6887.5
17:00 | -100 | 5110 | 1723 | 6833 | 700 | 6833
17:30 | -100 | 5043.5 | 1663.5 | 6707 | 1800 | 6707
18:00 | -100 | 4977 | 1604 | 6581 | 100 | 6581
18:30 | -110 | 5013 | 1647 | 6660 | 1400 | 6660
19:00 | -120 | 5380 | 1804 | 7184 | 100 | 7184
19:30 | -220 | 5489 | 1905 | 7394 | 1800 | 7394
20:00 | -240 | 5541 | 1918 | 7459 | 1800 | 7459
20:30 | -250 | 5546.5 | 1931 | 7477.5 | 1800 | 7477.5
21:00 | -260 | 5552 | 1944 | 7496 | 2100 | 7496
21:30 | -260 | 5551 | 1924 | 7475 | 1900 | 7475
22:00 | -260 | 5550 | 1904 | 7454 | 1900 | 7454
22:30 | -260 | 5524.5 | 1869.5 | 7394 |  | 7394
23:00 | -260 | 5499 | 1835 | 7334 |  | 7334
23:30 | -270 | 5507 | 1819.5 | 7326.5 |  | 7326.5
24:00 | -280 | 5515 | 1804 | 7319 |  | 7319
*MAX.GEN.(E.P.) |  | 7496 |  | 21:00
*MAX.GEN.(D.P.) |  | 6861 |  | 12:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
7496MW (21:00)
6861MW (12:00)

## En.Curve
QF-LDC-12
Date | 2015-06-07 |  | Energy | 170659953
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE |  | DAILY ENERGY CURVE |  | 2015-06-07
0:00 | 1364 | 449 | 2813 | 1708 | 177 | 66 | 595 | 0
0:30 | 1368 | 450.5 | 2818.5 | 1702.5 | 175 | 66.5 | 548.5 | 0
1:00 | 1372 | 452 | 2824 | 1697 | 173 | 67 | 502 | 0
1:30 | 1371 | 452.5 | 2821 | 1651.5 | 172 | 67 | 423 | 0 | [5 empty] | 170.66
2:00 | 1370 | 453 | 2818 | 1606 | 171 | 67 | 344 | 0 | [5 empty] | 0
2:30 | 1371 | 453 | 2819 | 1559.5 | 173.5 | 67 | 335.5 | 0 | [5 empty] | 170.66
3:00 | 1372 | 453 | 2820 | 1513 | 176 | 67 | 327 | 0
3:30 | 1370.5 | 452.5 | 2820 | 1540.5 | 177 | 52.5 | 237.5 | 0
4:00 | 1369 | 452 | 2820 | 1568 | 178 | 38 | 148 | 0
4:30 | 1370 | 452.5 | 2819.5 | 1487.5 | 176 | 37 | 123 | 0
5:00 | 1371 | 453 | 2819 | 1407 | 174 | 36 | 98 | 0
5:30 | 1367.5 | 453 | 2812 | 1177.5 | 174.5 | 36 | 92 | 0
6:00 | 1364 | 453 | 2805 | 948 | 175 | 36 | 86 | 0
6:30 | 1356.5 | 452.5 | 2783.5 | 965 | 175 | 36 | 86 | 0
7:00 | 1349 | 452 | 2762 | 982 | 175 | 36 | 86 | 0
7:30 | 1336 | 452 | 2703 | 1131 | 175 | 36 | 86 | 0
8:00 | 1323 | 452 | 2644 | 1280 | 175 | 36 | 86 | 0
8:30 | 1321 | 452.5 | 2663.5 | 1368.5 | 175 | 37 | 74 | 0
9:00 | 1319 | 453 | 2683 | 1457 | 175 | 38 | 62 | 0
9:30 | 1314 | 452.5 | 2664.5 | 1532.5 | 176.5 | 38 | 85 | 0
10:00 | 1309 | 452 | 2646 | 1608 | 178 | 38 | 108 | 0
10:30 | 1302 | 452.5 | 2652 | 1650.5 | 164 | 51 | 136.5 | 0
11:00 | 1295 | 453 | 2658 | 1693 | 150 | 64 | 165 | 0
11:30 | 1289 | 453 | 2658.5 | 1704.5 | 152 | 74 | 235.5 | 0
12:00 | 1283 | 453 | 2659 | 1716 | 154 | 84 | 306 | 0
12:30 | 1277.5 | 452.5 | 2656.5 | 1697 | 165.5 | 84 | 322 | 0
13:00 | 1272 | 452 | 2654 | 1678 | 177 | 84 | 338 | 0
13:30 | 1254.5 | 452 | 2664 | 1657 | 175.5 | 84.5 | 340.5 | 0
14:00 | 1237 | 452 | 2674 | 1636 | 174 | 85 | 343 | 0
14:30 | 1260 | 452 | 2680.5 | 1650.5 | 176.5 | 85 | 342 | 0
15:00 | 1283 | 452 | 2687 | 1665 | 179 | 85 | 341 | 0
15:30 | 1284 | 451.5 | 2699 | 1660.5 | 180 | 84.5 | 340.5 | 0 | Max Temp. in Dhaka |  | 35.6° C
16:00 | 1285 | 451 | 2711 | 1656 | 181 | 84 | 340 | 0
16:30 | 1263 | 451.5 | 2703 | 1634.5 | 180.5 | 82 | 341 | 0
17:00 | 1241 | 452 | 2695 | 1613 | 180 | 80 | 342 | 0
17:30 | 1229.5 | 452 | 2638.5 | 1542.5 | 178.5 | 77.5 | 323 | 0
18:00 | 1218 | 452 | 2582 | 1472 | 177 | 75 | 304 | 0
18:30 | 1237 | 448 | 2582 | 1489 | 173 | 74 | 343 | 0
19:00 | 1273 | 448 | 2704 | 1694 | 178 | 74 | 540 | 0
19:30 | 1292 | 448 | 2746 | 1806 | 174 | 76 | 585 | 0
20:00 | 1285 | 448 | 2792 | 1799 | 178 | 77 | 607 | 0
20:30 | 1289.5 | 448 | 2785.5 | 1820.5 | 178.5 | 78.5 | 601 | 0
21:00 | 1294 | 448 | 2779 | 1842 | 179 | 80 | 595 | 0
21:30 | 1287 | 448 | 2788.5 | 1832.5 | 178.5 | 80 | 586.5 | 0
22:00 | 1280 | 448 | 2798 | 1823 | 178 | 80 | 578 | 0
22:30 | 1277.5 | 448 | 2798 | 1769.5 | 179 | 81 | 573.5 | 0
23:00 | 1275 | 448 | 2798 | 1716 | 180 | 82 | 569 | 0
23:30 | 1269.5 | 448 | 2804 | 1711 | 179 | 82 | 568 | 0
24:00 | 1264 | 448 | 2810 | 1706 | 178 | 82 | 567 | 0
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Gas

## volt
NATIONAL LOAD DESPATCH CENTER
The Maximum & Minimum Voltages of different Sub-Stations.
Date : | 2015-06-07
| Maxm |  | Minm |  |  | Maxm |  | Minm
Sub-Station | Voltage | Hour | Voltage | Hour | Sub-Station | Voltage | Hour | Voltage | Hour
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 225 | 100 | 210 | 1500 | Hasnabad | 210 | 800 | 196 | 1600
Ishurdi | 236 | 1100 | 227 | 400 | Aminbazar | 209 | 500 | 192 | 1500
Ashuganj | 230 | 100 | 224 | 1700 | Tongi | 210 | 400 | 195 | 1600
Serajganj | 228 | 1830 | 221 | 400 | Comilla (N) | 222 | 700 | 215 | 900
Baghabari | 226 | 1830 | 220 | 800 | Hathazari | 221 | 200 | 212 | 1600
Barapukuria | 226 | 1800 | 220 | 100 | Megnaghat | 214 | 400 | 200 | 1600
Bogra | 228 | 1900 | 221 | 300 | Fenchuganj | 232 | 2000 | 222 | 100
Khulna South | 232 | 1100 | 223 | 200 | Siddhirganj | 237 | 500 | 212 | 1500
Rampura | 213 | 200 | 200 | 1300 | Maniknagar | 231 | 600 | 209 | 1600
Haripur | 210 | 100 | 200 | 1600 | Old Airport | 211 | 500 | 193 | 1600
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 140 | 100 | 128 | 1500 | Madanhat | 136 | 100 | 130 | 1000
Munsiganj | 137 | 100 | 128 | 1600 | Hathazari | 132 | 100 | 128 | 1000
Megnaghat | 136 | 400 | 130 | 1300 | Khulshi | 135 | 200 | 131 | 1600
Shyampur | 135 | 100 | 125 | 1600 | Halishahar | 135 | 200 | 128 | 900
Bhulta | 117 | 300 | 112 | 1000 | Baraulia | 133 | 2000 | 125 | 1600
Madanganj | 130 | 800 | 124 | 700 | Sikalbaha | 134 | 300 | 128 | 1400
Shitalakhya | 135 | 400 | 123 | 1300 | Dohazari | 134 | 2000 | 126 | 1700
Rahim steal | 137 | 200 | 128 | 1600 | Cox'sbazar | 131 | 500 | 125 | 1600
Matuail | 136 | 300 | 126 | 1500 | Chandraghona | 135 | 200 | 128 | 1000
Ghorasal | 132 | 100 | 128 | 1600 | Kaptai | 134 | 2000 | 130 | 1700
Narsinghdi | 132 | 500 | 126 | 1500 | A. Khaer Stl. | 133 | 2000 | 126 | 1500
Haripur (SBU) | 137 | 100 | 128 | 1600 | Bakulia | 133 | 300 | 125 | 1000
Ullon | 135 | 700 | 128 | 1600 | Julda | 133 | 100 | 126 | 1500
Hasnabad | 128 | 600 | 122 | 1600 | TK Chemical | 135 | 100 | 129 | 1600
Magbazar | 132 | 600 | 116 | 1600 | Modern Steel | 132 | 2000 | 125 | 1100
Maniknagar | 132 | 600 | 124 | 1700 | Shahmirpur | 134 | 2000 | 127 | 1000
Bangabhaban | 132 | 600 | 124 | 1700 | Goalpara | 137 | 1100 | 134 | 100
Narinda | 132 | 600 | 124 | 1700 | Central s/s | 138 | 1300 | 134 | 100
Dhanmondi | 132 | 600 | 124 | 1700 | Noapara | 135 | 1830 | 128 | 200
Lalbag | 130 | 600 | 117 | 1300 | Jessore | 138 | 1830 | 122 | 300
Mirpur | 127 | 300 | 117 | 1500 | Jhenida | 128 | 1830 | 118 | 100
Kalyanpur | 124 | 500 | 111 | 1500 | Bottail | 135 | 1100 | 131 | 900
Gulshan | 128 | 600 | 118 | 1600 | G.K.Project | 137 | 1830 | 132 | 700
Uttara | 132 | 500 | 116 | 1500 | Faridpur | 131 | 2300 | 124 | 1700
Kamrangirchar | 124 | 700 | 112 | 1400 | Madaripur | 132 | 1100 | 121 | 1000
Savar | 128 | 100 | 120 | 1000 | Gopalganj | 136 | 600 | 124 | 2100
Bhasantec | 129 | 600 | 118 | 1300 | Bagerhat | 131 | 1100 | 124 | 100
Agargaon | 127 | 300 | 115 | 1600 | Mongla | 128 | 1500 | 124 | 100
Tongi | 130 | 400 | 120 | 1500 | Satkhira | 135 | 1830 | 129 | 100
Kabirpur | 129 | 500 | 122 | 1900 | Gallamari | 138 | 1830 | 133 | 100
Basundhara | 130 | 400 | 119 | 1600 | Magura | 126 | 1830 | 120 | 100
Manikganj | 123 | 300 | 111 | 1600 | Chuadanga | 124 | 1800 | 114 | 100
Joydevpur | 132 | 600 | 125 | 1930 | Barisal | 133 | 700 | 122 | 2000
New Tongi | 125 | 300 | 115 | 1500 | Patuakhali | 120 | 1700 | 113 | 100
Tangail | 122 | 200 | 110 | 1500 | Bhandaria | 125 | 600 | 118 | 300
Mymensing | 126 | 700 | 117 | 2200 | Ishurdi | 136 | 1400 | 132 | 100
Kishorganj | 130 | 800 | 123 | 1900 | Natore | 132 | 1400 | 129 | 700
Netrokona | 125 | 600 | 117 | 2200 | Bogra | 132 | 1800 | 126 | 200
Jamalpur | 124 | 600 | 115 | 2200 | Noagaon | 130 | 1830 | 123 | 900
Sherpur | 124 | 200 | 113 | 1700 | Rajshahi | 137 | 1830 | 126 | 700
Srimongal | 141 | 800 | 138 | 1500 | C.Nawabganj | 134 | 1800 | 123 | 1000
Shahjibazar | 140 | 600 | 137 | 100 | Pabna | 130 | 1100 | 126 | 1000
Fenchuganj | 138 | 200 | 137 | 100 | Shahjadpur | 138 | 1800 | 130 | 900
Khulawara | 137 | 100 | 135 | 1500 | Serajganj | 138 | 1900 | 128 | 900
Sylhet | 138 | 300 | 135 | 1900 | Niyamatpur | 131 | 1830 | 120 | 700
Chatak | 136 | 200 | 134 | 1900 | Joypurhat | 131 | 1830 | 123 | 1000
Comilla(s) | 136 | 600 | 131 | 1000 | Rangpur | 123 | 1800 | 116 | 2000
Comilla(n) | 130 | 2000 | 125 | 1000 | Lalmonirhat | 120 | 1600 | 112 | 300
Chandpur | 132 | 800 | 1127 | 2200 | Saidpur | 130 | 1830 | 116 | 2000
Feni | 128 | 700 | 124 | 1200 | Purbasadipur | 125 | 1700 | 119 | 200
Chowmuhani | 122 | 2100 | 118 | 1300 | Thakurgaon | 123 | 1830 | 109 | 100
Ashuganj | 125 | 2000 | 122 | 1200 | Palashbari | 118 | 1300 | 110 | 2000
Daudkandi | 135 | 800 | 131 | 1000 | Barapukuria | 126 | 1800 | 120 | 2000
B.Baria | 131 | 2000 | 24 | 1000 | Panchagar | 121 | 1800 | 112 | 400