## Daily Gen
Hourly Generation & Demand
Date: | 2017-02-03
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 5369 | 5369 | 0
2:00 | 5050 | 5050 | 0
3:00 | 4811 | 4811 | 0
4:00 | 4714 | 4714 | 0
5:00 | 4637 | 4637 | 0
6:00 | 4696 | 4696 | 0
7:00 | 5017 | 5017 | 0
8:00 | 5286 | 5286 | 0
9:00 | 5404 | 5404 | 0 | Day peak
10:00 | 5274 | 5274 | 0
11:00 | 5164 | 5164 | 0
12:00 | 5251 | 5251 | 0
13:00 | 5325 | 5325 | 0
14:00 | 4860 | 4860 | 0
15:00 | 4859 | 4859 | 0
16:00 | 4817 | 4817 | 0
17:00 | 4879 | 4879 | 0
18:00 | 5995 | 5995 | 0
18:30 | 0 | 0 | 0
19:00 | 6807 | 6807 | 0
19:30 | 6834 | 6834 | 0
20:00 | 6870 | 6870 | 0 | Evening peak
21:00 | 6646 | 6646 | 0
22:00 | 6233 | 6233 | 0
23:00 | 5746 | 5746 | 0
24:00 | 5332 | 5332 | 0

## forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [7 empty] | 2017-02-04 | Saturday
|  | Date (day): | 2017-02-04 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 7535 | MW |  |  | (b) At Evening Peak Hour : |  | 8870 | MW
Sl. No. | Name of the Power Stations |  | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[8 empty] | On | 2017-02-03 | 2017-02-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Nos. of Unit X Capacity (MW) | MW | MW | MW | MW | MW | MW | MW | MW
1 | a) Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70 |  | 15
| b) Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 170 | 170 | 170 | 170
| c) Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 30/01/17
| d) Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | 1/10/2016 |  | Long term maint.
| e) Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | (18/07/10) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 97 | 97 | 83 | 100
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 45 | 45 | 46 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 44 | 84 | 78 | 78
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 101 | 99 | 98 | 100 |  | 9 | Engine problem
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3*32 | 96 | 60 | 20 | 20 | 20 | 20 |  | 60 | # 1 & 3 Under maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 315 | 380 | 360 | 412 |  |  | Low demand
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 95 | 95 |  | 14 | Engine problem
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under Maintenance.
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 370 | 380 | 400 | 450
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 7 | 66 | 90 | 100 |  |  | Low demand
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 0 | 305 |  |  | Reserve
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 95 | 100 | 100
14 | Madanganj-55 MW |  | HFO | IPP | 5*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55 |  |  | Low demand
15 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 0 | 30 | 93 | 93
16 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 19
17 | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
18 | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 197 | 145 | 171 | 100 | 65 |  | Gas shortage
19 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 96 | 98 | 0 | 0 | 98 | 98 |  |  | Reserve
20 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 7 | 100 | 90 | 100
| Siddhirganj CCPP-335 MW |  | Gas | EGCB |  |  |  | 0 | 0 | 0 | 0
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 0 | 50 | 50 |  |  | Reserve
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 50 | 90 | 102 |  | 52 | Low demand
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 41 | 42 |  |  | Reserve
24 | Kodda Peaking |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 90 | 149 | 149
25 | Northern 55 MW |  | HFO | RPP |  | 55 | 55 | 0 | 37 | 55 | 55 |  |  | Low demand
26 | Southern Power |  | HFO | RPP | 3*19.3 | 55 | 55 | 0 | 36 | 55 | 55 |  |  | Low demand
| CLCPC Keranigonj 108 MW |  | HFO | RPP |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 6*3.67+7*8.73 | 80 | 80 | 24 | 47 | 51 | 55 |  | 33 | Engine problem
28 | Summit Power, Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Summit Power, Rupganj |  | Gas | SIPP,REB | 4*8.74 | 33 | 33 | 22 | 26 | 22 | 33
30 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 26 | 43 | 43 |  | 26 | Engine problem
31 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| Dhaka Area Total |  |  |  |  | 4774 | 4543 | 1564 | 2175 | 2726 | 3127 | 170 | 1279
32 | a) Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| b) Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
33 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 26 | 9 | 26 | 25 |  |  | Low demand
34 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 49 | 50 | 49 | 50
35 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 96 | 76 | 96 | 100 |  | 100 | Unit-2 & 5 Under maint.
36 | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under Maintenance
37 | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 0 | 0 | 150 | 150
38 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 25 | 34 | 51 | 51 |  |  | Low demand
39 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 75
40 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 95 | 16 | 102
41 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 88 | 80 | 100
42 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 30 | 40 | 10 | 20
43 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 52 | 51 | 52 | 51 |  | 57 | Engine problem
| Chittagong area Total |  |  |  |  | 1416 | 1336 | 424 | 458 | 545 | 739 | 0 | 564
44 | a) Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 64 | 53 | 52 | 52 | 52 | 52 |  |  | #1 Under maint.
| b) Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 132 | 132 | 132 | 132
| c) Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 150 | 150
| d) Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 100 | 134
| e) Ashuganj : GT-2 |  | Gas | APSCL | 1*56 | 56 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under Maintenance
45 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 217 | 217 | 200 | 120 | 130 | 142 |  | 75 | ST Under maint.
| Ashuganj CCPP(North) |  | Gas | APSCL |  |  |  | 225 | 283 | 289 | 280 |  |  | On test
46 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 383 | 330 | 360
47 | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 29 | 26 | 29 | 16 |  | Gas shortage
48 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 10 | 10 | 10 | 45 |  | Gas shortage
49 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Date expired
50 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 30 | 10 | 10 | 10 | 43 |  | Gas shortage
51 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.7+1*16 | 195 | 195 | 198 | 100 | 100 | 100 | 95 |  | Gas shortage
52 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 40 | 51
53 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 10 | 85 | 85 | 85
54 | Titas (Daudkandi) Peaking |  |  | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50 |  |  | Reserve
55 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 140 | 140
56 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 22 | 21 | 22 | 21
57 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8
** | Tripura |  |  | Imported Power |  | 100 | 100 | 70 | 100 | 80 | 100
58 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 0 | 25 | 25 | 25 |  | 8 | Engine problem
59 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 0 | 0 | 52 | 52 |  |  | Reserve
60 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.6+2*6.9 | 25 | 25 | 22 | 21 | 22 | 21 |  |  | Engine problem
| Comilla Area Total |  |  |  |  | 2192 | 2105 | 1711 | 1720 | 1803 | 1952 | 199 | 123
61 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 75 | 73 | 75 | 73 | 129 |  | Gas shortage
62 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
63 | Jamalpur IPP |  | HFO | IPP | 12*8.9 | 95 | 95 | 93 | 93 | 50 | 50
| Mymensingh Area Total |  |  |  |  | 327 | 319 | 168 | 188 | 147 | 145 | 129 | 0
64 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 60 | 60 | 50 | 60
65 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 50 | 60 | 50
66 | Shahjibazar 330 MW |  | Gas | PDB | 2*110 | 330 | 330 | 100 | 80 | 120 | 120
67 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 47 | 50 | 47
68 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 26 | 26 | 36 | 26 |  | 18 | Engine problem
69 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
70 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Under maint.
71 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 84 | 82 | 84
72 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Gas shortage
73 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 69 | 122 | 35 | 142
74 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 20 | 0 | 20
75 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 45 | 47 | 46 | 47
76 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 5 | 23 | 5 | 23
77 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint.
78 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 8 | 8
| Sylhet Area Total |  |  |  |  | 1431 | 1396 | 433 | 575 | 500 | 635 | 116 | 362
79 | Bheramara GT: Unit- 1,2,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 0 | 0 | 15 |  | 30 | # 1 & 2 under maint.
80 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Long term maintenance
** | Bheramara Interconnector(HVDC ) |  |  | Imported Power |  | 500 | 500 | 394 | 490 | 490 | 490
81 | a) Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11
| b) Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
82 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 5 | 51 | 105 | 110 |  |  | Low demand
83 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 115 | 115 | 115
84 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 45 | 0 | 45
85 | Khulna CCPP |  | HSD | NWZPGCL | 1*158+1*72 | 230 | 230 | 50 | 50 | 158 | 158 |  | 72 | ST Under maint.
86 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 0 | 70
Fuel shortage
87 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 8 | 40
88 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 40 | 40 |  |  | Reserve
| Khulna Area Total |  |  |  |  | 1488 | 1419 | 449 | 831 | 916 | 1083 | 0 | 262
89 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 98 | 100 | 110
90 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 24 |  |  | Reserve
91 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 9 | 11 | 9 | 14 |  | 22 | Engine problem
92 | Bhola CCPP GT-1,2,ST |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 188 | 180 | 194
| Barisal Area Total |  |  |  |  | 377 | 367 | 214 | 297 | 289 | 342 | 0 | 22
93 | a) Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 60 | 60 | 60 |  |  | FGMO
| b) Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
94 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 48 |  |  | Reserve
95 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 56 |  |  | Reserve
96 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 25 | 43 | 50 |  |  | Low demand
97 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 0 | 16 | 43 | 50 |  |  | Low demand
98 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 46 | 0 | 50
99 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 200 | 190 | 210 | 210 |  |  | FGMO
100 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  |  | Low demand
101 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
102 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 6 | 6 | 6 | 6 |  | 4 | Engine problem
103 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8 | 11 | 10 | 11
104 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 809 | 799 | 282 | 443 | 442 | 648 | 0 | 108
105 | a) Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 77 | 77 | 77 | 77
| b) Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 82 | 86 | 80 | 86
106 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 16
107 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 20 | 0 | 20
108 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 23 | 0 | 0 | 0 | 0 |  | 23 | Under maint.
| Rangpur Area Total |  |  |  |  | 337 | 263 | 159 | 183 | 167 | 199 | 0 | 23
| Total |  |  |  |  | 13151 | 12547 | 5404 | 6870 | 7535 | 8870 | 614 | 2743
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 4928.1019 | 6265 | 6871.4374 | 8088.8719
A. |  | 2017-02-03 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 6870 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 4637 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6870 | MW
3 | Day peak Generation : |  |  | 5404 | MW at | 9:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6265 | MW
4 | Evening peak Generation : |  |  | 6870 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 129.9785 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 92.0471 | MKWHr |  | By Oil: | 20.7304 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.8038 | MKWHr |  | By Hydro: | 1.8328 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 614 | For Oil: | 0 | MW | Dhaka | 2098 | 2098 | 0
|  |  | For Water Shortage: |  |  | 100 | MW | Chittagong | 690 | 690 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 2743 | MW | Khulna | 788 | 788 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 847.44 | MMCFD |  |  | Rajshahi | 775 | 775 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 54165226.655 | ii) Oil : | Taka | 151036547.705 | Comilla | 589 | 589 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14804315.652 | Total | Taka | 220006090.012 | Mymensingh | 478 | 478 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 237 | 237 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -590 | MW at | 20:00 | hrs | Barisal | 132 | 132 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -360 | MW at | 16:00 | hrs | Rangpur | 478 | 478 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25.2° C |  |  | Total | 6265 | 6265 | 0
B. |  | 2017-02-04 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 25.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 7600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 8870 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6000 | MW
4 | Reserve (Generation end) |  |  |  | 2870 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 130 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4229 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.7942 | MKWHr. | ii) During Peak demand: |  | 490 | MW at | 20:00 | hrs. | iii)Maximum: | 490 | 21:00
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.7702 | MKWHr.
*Cost for HVDC & Tripura energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 97.87 |  | (b) Today: | 97.73 |  | (c) Rule Curve: |  | 96.58

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2017-02-04
Till now the maximum generation is : - |  |  | 9036 MW | 21:00 | Hrs on | 2016-06-30
The Summary of Yesterday's |  | 2017-02-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5404 | MW Hour : | 9:00 | Min. Gen. at | 5:00 | 4229 | MW
Evening Peak Generation : |  | 6870 | MW Hour : | 20:00 | Max Generation : |  | 8870 | MW
E.P. Demand (at gen end) : |  | 6870 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 7600 | MW
Maximum Generation : |  | 6870 | MW Hour : | 20:00 | Reserve (Generation end) |  | 2870 | MW
Total Gen. (MKWH) : |  | 129.9785 | System L/ Factor : | 78.83% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -360 | MW at | 16:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2017-02-04
Actual : | 97.73 | Ft.(MSL) , | Rule curve : | 96.58 | Ft.( MSL )
Gas Consumed : | Total | 847.44 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 54165226.655
|  | Coal : | 14804315.652 | Oil : | 151036547.705 | Total : | 220006090.012
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 2770 |  |  | - | -
Chittagong Area | 0 | 0:00 | 775 |  |  | - | -
Khulna Area | 0 | 0:00 | 771 |  |  | - | -
Rajshahi Area | 0 | 0:00 | 751 |  |  | - | -
Comilla Area | 0 | 0:00 | 576 |  |  | - | -
Mymensingh Area | 0 | 0:00 | 439 |  |  | - | -
Sylhet Area | 0 | 0:00 | 271 |  |  | - | -
Barisal Area | 0 | 0:00 | 153 |  |  | - | -
Rangpur Area | 0 | 0:00 | 424 |  |  | - | -
Total | 0 |  | 6930 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010) |  | 10) Ghorasal Unit- 2
| Nil |  |  | 2) Kaptai Unit-2 & 5 |  | 11) Ghorasal Unit- 4(30/01/17)
|  |  |  | 3) Ashuganj ST: Unit- 1, 5 & GT-2 |  | 10)Thakurgaon (RZ)
|  |  |  | 4) Khulna ST 110 MW (04/11/2014) |  | 13) Sikalbaha ST
|  |  |  | 5) Ghorasal Unit-5 |  | 14) Shahjibazar(Energyprima)
|  |  |  | 6) Baghabari 100 MW |  | 15) Shahjibazar GT: Unit- 8, 9
7) Haripur SBU GT- 1,2,3
8) Summit Bibiana- 2
9) Chittagong Unit-1 & 2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Comments on Power Interruption
a) Feni 132/33 kV T-2 transformer was under shut down from 07:15 to 14:36 for A/M.
b) B.Pukuria 132/33 kV T-1 transformer was shut down at 09:10 for red hot maintenance at B-phase
132 kV CT connector and was switched on at 11:10.
c) Ashuganj-225 MW CCPP ST was shut down at 10:22 for steam leakage from degenerator.
d) Aminbazar-Mirpur 132 kV Ckt-2 tripped at 13:47 showing dist.RST at Mirpur end & dist.RST,SOTF
at Aminbazar end and was switched on at 21:01.
e) Kaliakoir-Aminbazar 230 kV Ckt-2 tripped at 16:20 due to LA burst at Aminbazar end.
f) After maintenance Ashuganj #5 was synchronized at 01:33 (4/2/17).
g) After maintenance Sikalbaha-150 MW GT was synchronized at 05:48 (4/2/17).
h) Mymensing 132/33 kV T-2 transformer was shut down at 07:40 (4/2/17) for A/M.
i) Ishurdi-Ghorasal 230 kV Ckt-2 & 1 tripped at 04:30 & 05:51 (4/2/17) showing dist.R-phase at Ishurdi
end & primary & secondary protection at Ghorasal end and were switched on at 05:42 & 07:16
(4/2/17) respectively.
j) Jessore 132/33 kV T-3 transformer tripped at 23:26 showing E/F relay at 132 kV end & CB tripped
at 33 kV end and was switched on at 04:04 (4/2/17).
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2017-02-03 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1a | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 70 | 1504000
0
1b | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 170 | 4227615 | 0
1c | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
1d | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 0 | 0 | Under maint.
1e | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 |  | Long term maint.
2 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 97 | 1967587 | 0
3 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 45 | 1019910 | 0
4 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 84 | 1116416 | 0
5 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 99 | 2383636 | Engine problem
6 |  |  | 1*32 | PDB | 20 | 20 | 483400
| Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 0 |  | Gas shortage
|  |  | 1*32 | PDB | 20 | 0 |  | Under maint.
7 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 380 | 8192376 | Low demand
8 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 0 | 27500 | Reserve
9 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 0 | 0 | Annual Maintenance.
10 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 380 | 8524000 | Low demand
11 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 66 | 407040 | Low demand
12 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 305 | 0 | 0 | Reserve
13 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 95 | 694610
14 | Madanganj-55 MW |  | 5*17.08+1*11.3 | IPP | 55 | 30 | 113715 | Low demand
15 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 30 | 124599 | Low demand
16 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 19 | 461481 | Engine problem
17 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 0 | 0 | Gas shortage
18 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 145 | 3572000 | Gas shortage
19 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 98 | 0 | 0 | Reserve
20 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 100 | 728640 | 0
| Siddhirganj CCPP-335 MW |  |  | EGCB |  | 0 | 0 | 0
21 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 0 | 0 | Reserve
22 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 50 | 351936 | Low demand
23 | Katpotti 52 MW |  |  | RPP | 51 | 0 | 0 | Reserve
24 | Kodda Peaking |  | 9*17.06 | BPDB-RPCL | 149 | 90 | 530400 | Low demand
| Northern 55 MW |  |  | RPP | 55 | 37 | 182254 | Low demand
25 | Southern Power |  |  | RPP | 55 | 36 | 302000 | Low demand
| CLCPC Keranigonj 108 MW |  |  |  |  | 0 | 0 | On test
26 | Summit Power,(Madhabdi+Ashulia) |  | 6*3.67+7*8.73 | SIPP, REB | 80 | 47 | 959460 | Engine problem
27 | Summit Power, Maona |  | 4*8.73 | SIPP, REB | 33 | 33 | 792700 | 0
28 | Summit Power, Rupganj |  | 4*8.74 | SIPP, REB | 33 | 26 | 623600 | Engine problem
29 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 26 | 260820 | Low demand
30 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Under maintenance.
| Dhaka Area Total |  |  |  | 4543 | 2175 | 39551695
31 | a) Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
| b) Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
32 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 9 | 153360 | Low demand
33 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 50 | 602880 | 0
34 | Chittagong ECPV 108 MW |  |  | IPP | 108 | 51 | 663360 | Engine problem
35 |  |  | 1*40 | PDB | 40 | 46 | 927000
|  |  | 1*40 | PDB | 40 | 0
| Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 0
|  |  | 1*50 | PDB | 50 | 30 | 905800
|  |  | 1*50 | PDB | 50 | 0 |  | Under maint.
36 | Shikalbaha ST |  | 1*60 | PDB | 40 | 0 | 0 | Under maint.
37 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 0 | 25959 | Under maint.
38 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 0 | 53538 | Reserve
39 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 95 | 865647
40 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 88 | 1311360 | Engine problem
41 | Shikalbaha (Energis) |  |  | RPP | 51 | 34 | 603360 | Low demand
42 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 15 | 363840 | Engine problem
* | Malancha, Ctg EPZ(United) |  |  |  |  | 40 | 853440
| Chittagong Area Total |  |  |  | 1336 | 458 | 7329544
43 | a) Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 53 | 0 | 1259814 | #1 under maint
|  |  | 1*64 | APSCL |  | 52
| b) Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 132 | 3173406 | 0
| c) Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 150 | 3621570 | 0
| d) Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 0 | 0 | Under maint.
| Ashuganj : GT-2 |  | 1*56 | APSCL | 40 | 0 | 0 | Under maint.
44 | Ashuganj CCPP 225 MW |  | 1*142+1*75 | APSCL | 217 | 120 | 8453750 | Low demand
| Ashuganj CCPP(North) |  |  | APSCL |  | 283 | 4352000 | On test
45 | Ashuganj CCPP(South) |  |  | APSCL | 360 | 383 | 3786500 | 0
46 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 29 | 573408 | Engine problem
47 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 10 | 559680 | Gas shortage
48 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 0 | 0 | Date expired
49 | Ashuganj (United) |  | 14*4 | RPP | 53 | 10 | 509000 | Gas shortage
50 | Ashuganj Modular 200 MW |  | 20*9.7+1*16 | IPP | 195 | 100 | 3696727 | Gas shortage
51 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 51 | 1106480 | 0
52 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 85 | 800979 | 0
53 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 0 | 0 | Reserve
54 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 140 | 3297600 | 0
55 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 21 | 508572 | 0
56 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 8 | 116460 | Engine problem
** | Tripura |  |  |  | 100 | 100 | 1770240 | 0
57 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 25 | 404500 | Engine problem
58 | Lakdanavi-52 MW |  |  | IPP | 52 | 0 | 0 | Reserve
59 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 21 | 504210 | Engine problem
| Comilla Area Total |  |  |  | 2105 | 1720 | 38494896
60 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 73 | 1738000 | Gas shortage
61 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 22 | 189900 | 0
62 | Jamalpur RPP |  |  | IPP | 95 | 93 | 2069037 | 0
| Mymensingh Area Total |  |  |  | 319 | 188 | 3996937
63 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 60 | 1295000 | 0
64 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 50 | 1372280 | 0
| Shahjibazar CCPP 330 MW |  | 2*110 | PDB | 330 | 80 | 1580796 | 0
65 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 47 | 1027200
66 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 26 | 624000 | Engine problem
67 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 8 | 142416 | Engine problem
Engine problem
68 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 0 | 0 | Under maint.
69 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 84 | 854400 | 0
70 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 0 | 0 | Gas shortage
71 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 122 | 2171490 | Low demand
72 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 20 | 113000 | 0
73 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 47 | 825240 | 0
74 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 23 | 305664 | 0
75 | Summit Bibiana-2 |  | 1*222+1*119 | IPP | 341 | 0 | 0 | Under maint.
76 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 8 | 192240 | Engine problem
| Sylhet Area Total |  |  |  | 1396 | 575 | 10503726
|  |  | 1*20 | PDB | 16 | 0 | 93440
77 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 0 |  | Reserve
|  |  | 1*20 | PDB | 16 | 0 |  | Long term maint.
** | Bheramara Interconnector(HVDC) |  |  | Imported Power | 500 | 490 | 9794181 | 0
78 | a) Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint.
| b) Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
79 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 51 | 311040 | Low demand
80 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 115 | 601920 | 0
81 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 45 | 138880 | 0
82 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 230 | 50 | 1274880 | Low demand
83 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 40 | 0 | 0
84 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
85 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 40 | 140625 | 0
86 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 1419 | 831 | 12354966
87 | Summit Barisal 110MW |  | 7*17.076 | IPP | 110 | 98 | 797760 | 0
88 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 0 | 0 | Reserve
|  |  | 1*20 | PDB | 14 | 0 |  | Reserve
89 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 11 | 225874 | Engine problem
90 | Bhola CCPP GT-1,2,ST |  | 2*63+1*68 | PDB | 194 | 188 | 4596852 | 0
| Barisal Area Total |  |  |  | 367 | 297 | 5620486
91 | a) Baghabari GT |  | 1*71 | PDB | 71 | 60 | 1420000 | FGMO
| b) Baghabari GT |  | 1*100 | PDB | 100 | 0 | 0 | Under maint.
92 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 0 | 8978 | Reserve.
93 | Bera Peaking |  | 9*8.29 | PDB | 71 | 0 | 0 | Reserve.
94 | Amnura |  | 7*7.79 | QRPP | 50 | 25 | 241700 | Low demand
95 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 16 | 154176 | Low demand
96 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 46 | 203607 | 0
97 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 190 | 4988509 | FGMO
98 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 37 | 182689 | Low demand
99 | Bogra (GBB) |  | 6*4 | RPP | 22 | 18 | 428190 | Engine problem
100 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 10 | 6 | 132264 | Engine problem
101 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 188902 | 0
102 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 34 | 217440 | Low demand
| Rajshahi Area Total |  |  |  | 799 | 443 | 8166455
103 | a) Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 77 | 1836654 | 0
| b) Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 86 | 1967127 | 0
104 | Rangpur GT |  | 1*20 | PDB | 20 | 0 | 31000 | Reserve.
105 | Saidpur GT |  | 1*20 | PDB | 20 | 20 | 125000 | 0
106 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 23 | 0 | 0 | Under maint.
| Rangpur Area Total |  |  |  | 263 | 183 | 3959781
| Total |  |  |  | 12547 | 6870 | 129978486
| Eastern Grid Total |  |  |  | 8488 | 5116 | 99876798
| Western Grid Total |  |  |  | 2600 | 1754 | 30101688
| National Grid Total |  |  |  | 11088 | 6870 | 129978486
*Data collected from respective power station over telephone.

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2017-02-03 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4092 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2173 | MW
i) Dhaka area |  |  | 2098 | MW | i) Khulna area |  |  | 788 | MW
ii) Chittagong area |  |  | 690 | MW | ii) Rajshahi area |  |  | 775 | MW
iii) Comilla area |  |  | 589 | MW | iii) Barisal area |  |  | 132 | MW
iv) Mymensingh area |  |  | 478 | MW | iv) Rangpur area |  |  | 478 | MW
v) Sylhet area |  |  | 237 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6265 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 62 | 200 | Kishorganj | 49 | 2300 | Jessore | 96 | 1900
Munsiganj | 70 | 1930 | Netrokona | 64 | 700 | Jhenida | 64 | 1900
Megnaghat | 49 | 2000 | Jamalpur | 79 | 800 | Bottail | 64 | 1830
Shyampur | 111 | 100 | Sherpur | 55 | 900 | G.K Project | 29 | 1900
Bhulta | 104 | 100 | Srimongal | 28 | 1930 | Faridpur | 100 | 300
Madanganj | 34 | 100 | Shahjibazar | 58 | 1830 | Madaripur | 64 | 1930
Shitalakhya | 67 | 1000 | Fenchuganj | 24 | 2200 | Gopalganj | 47 | 1930
Rahim steel | 1 | 100 | Khulawara | 15 | 1830 | Bagerhat | 54 | 1830
Matuail | 54 | 100 | Sylhet | 94 | 1830 | Mongla | 16 | 100
Ghorasal | 63 | 1830 | Chatak | 38 | 1830 | Satkhira | 58 | 1900
Narsingdi | 75 | 1900 | Comilla (S) | 98 | 2000 | Gallamari | 24 | 1200
Haripur (SBU) | 37 | 1900 | Comilla(N) | 77 | 1800 | Magura | 30 | 1830
Ullon | 38 | 1800 | Chandpur | 72 | 1830 | Chuadanga | 50 | 1830
Hasnabad | 110 | 2000 | Feni | 71 | 2000 | Barisal | 70 | 1930
Magbazar | 67 | 1830 | Chowmuhani | 130 | 2000 | Patuakhali | 40 | 1900
Maniknagar | 44 | 2000 | Ashuganj | 37 | 2000 | Bhandaria | 32 | 1930
Bangabhaban | 12 | 2000 | Daudkandi | 52 | 1900 | Ishurdi | 32 | 1830
Narinda | 56 | 1900 | B.Baria | 78 | 1900 | Natore | 73 | 1930
Dhanmondi | 54 | 1800 | Madanhat | 42 | 1930 | Bogra | 160 | 1900
Lalbag | 50 | 2000 | Hathazari | 74 | 1900 | Noagaon | 93 | 1900
Madartek | 39 | 2000 | Khulshi | 134 | 1200 | Rajshahi | 88 | 1930
Mirpur | 65 | 1800 | Halishahar | 88 | 1830 | C.Nawabganj | 57 | 1900
Kalyanpur | 75 | 1830 | Baraulia | 93 | 100 | Amnura | 21 | 1830
Gulshan | 56 | 1830 | Sikalbaha | 27 | 1800 | Pabna | 62 | 2000
Uttara | 64 | 1900 | Dohazari | 70 | 1900 | Shahjadpur | 52 | 2000
Kamrangirchar | 35 | 1900 | Cox'sbazar | 52 | 2000 | Serajganj | 51 | 1900
Savar | 64 | 1900 | Chandraghona | 24 | 1830 | Niyamatpur | 76 | 1830
Bhasantec | 63 | 1900 | Kaptai | 3 | 1830 | Joypurhat | 32 | 1830
Agargaon | 28 | 1800 | A. Khaer Stl. | 22 | 400 | Rangpur | 70 | 1900
Satmosjid | 48 | 1800 | Bakulia | 64 | 1830 | Lalmonirhat | 68 | 1900
Tongi | 45 | 1830 | Julda | 17 | 500 | Saidpur | 88 | 1900
Kabirpur | 101 | 2000 | TK chemical | 5 | 100 | Purbasadipur | 76 | 2000
Basundhara | 80 | 1930 | Modern Steel | 9 | 100 | Thakurgaon | 48 | 1930
Manikganj | 60 | 1900 | Shahmirpur | 18 | 1830 | Palashbari | 79 | 1830
Joydevpur | 146 | 1830 | Abul Khair 230 | 192 | 100 | Barapukuria | 40 | 900
New Tongi | 67 | 1200 | BSRM | 69 | 800 | Panchagar | 26 | 1830
Korda | 56 | 1000 | Goalpara | 7 | 1900
Tangail | 132 | 2100 | Central s/s | 63 | 1900
Mymensing | 145 | 2000 | Noapara | 49 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## L.curve
Date | 2017-02-03 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -550 | 4498 | 1346 | 5844 | -550 | 5844 | 0:00 | DAILY LOAD CURVE | 2017-02-03
0:30 | -550 | 4405.5 | 1201 | 5606.5 | -550 | 5606.5 | 1:00
1:00 | -550 | 4313 | 1056 | 5369 | -510 | 5369 | 2:00
1:30 | -530 | 4139 | 1070.5 | 5209.5 | -480 | 5209.5 | 3:00
2:00 | -510 | 3965 | 1085 | 5050 | -460 | 5050 | 4:00
2:30 | -495 | 3845 | 1085.5 | 4930.5 | -490 | 4930.5 | 5:00
3:00 | -480 | 3725 | 1086 | 4811 | -440 | 4811 | 6:00
3:30 | -470 | 3681.5 | 1081 | 4762.5 | -670 | 4762.5 | 7:00
4:00 | -460 | 3638 | 1076 | 4714 | -710 | 4714 | 8:00
4:30 | -475 | 3609 | 1066.5 | 4675.5 | -740 | 4675.5 | 9:00
5:00 | -490 | 3580 | 1057 | 4637 | -660 | 4637 | 10:00
5:30 | -465 | 3598 | 1068.5 | 4666.5 | -600 | 4666.5 | 11:00
6:00 | -440 | 3616 | 1080 | 4696 | -600 | 4696 | 12:00
6:30 | -555 | 3785.5 | 1071 | 4856.5 | -620 | 4856.5 | 13:00
7:00 | -670 | 3955 | 1062 | 5017 | -440 | 5017 | 14:00 |  |  |  | 6870 | 20:00
7:30 | -690 | 4057 | 1094.5 | 5151.5 | -400 | 5151.5 | 15:00 |  |  |  | 5404 | 9:00
8:00 | -710 | 4159 | 1127 | 5286 | -360 | 5286 | 16:00
8:30 | -725 | 4229.5 | 1115.5 | 5345 | -360 | 5345 | 17:00
9:00 | -740 | 4300 | 1104 | 5404 | -360 | 5404 | 18:00
9:30 | -700 | 4240.5 | 1098.5 | 5339 | -610 | 5339 | 18:30
10:00 | -660 | 4181 | 1093 | 5274 | -690 | 5274 | 19:00
10:30 | -630 | 4086.5 | 1132.5 | 5219 | -690 | 5219 | 19:30
11:00 | -600 | 3992 | 1172 | 5164 | -680 | 5164 | 20:00
11:30 | -600 | 4042 | 1165.5 | 5207.5 | -640 | 5207.5 | 21:00
12:00 | -600 | 4092 | 1159 | 5251 | -590 | 5251 | 22:00
12:30 | -610 | 4127.5 | 1160.5 | 5288 | -540 | 5288 | 23:00
13:00 | -620 | 4163 | 1162 | 5325 | -440 | 5325 | 24:00
13:30 | -530 | 3961 | 1130 | 5091 |  | 5091
14:00 | -440 | 3759 | 1098 | 4857 | 128.92 | 4857
14:30 | -420 | 3727 | 1099 | 4826 | 86.5 | 4826
15:00 | -400 | 3695 | 1100 | 4795 |  | 4795
15:30 | -380 | 3695 | 1111 | 4806 | 7867500 | 4806
16:00 | -360 | 3695 | 1122 | 4817 |  | 4817
16:30 | -360 | 3722 | 1126 | 4848 |  | 4848
17:00 | -360 | 3749 | 1130 | 4879 | 700 | 4879
17:30 | -360 | 4033.5 | 1403.5 | 5437 | 1800 | 5437
18:00 | -360 | 4318 | 1677 | 5995 | 100 | 5995
18:30 | -610 | 4687.5 | 1713.5 | 6401 | 1400 | 6401
19:00 | -690 | 5057 | 1750 | 6807 | 100 | 6807
19:30 | -690 | 5091 | 1743 | 6834 | 1800 | 6834
20:00 | -680 | 5116 | 1754 | 6870 | 1800 | 6870
20:30 | -660 | 5050 | 1708 | 6758 | 1800 | 6758
21:00 | -640 | 4984 | 1662 | 6646 | 2100 | 6646
21:30 | -615 | 4876.5 | 1563 | 6439.5 | 1900 | 6439.5
22:00 | -590 | 4769 | 1464 | 6233 | 1900 | 6233
22:30 | -565 | 4630.5 | 1359 | 5989.5 |  | 5989.5
23:00 | -540 | 4492 | 1254 | 5746 |  | 5746
23:30 | -490 | 4308 | 1231 | 5539 |  | 5539
24:00 | -440 | 4124 | 1208 | 5332 |  | 5332
*MAX.GEN.(E.P.) |  | 6870 |  | 20:00
*MAX.GEN.(D.P.) |  | 5404 |  | 9:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
6870 MW (20:00)
5404 MW (09:00)

## En.Curve
QF-LDC-12
Date | 2017-02-03 |  | Energy | 129978486 | 0
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | Tripura |  | DAILY ENERGY CURVE |  | 2017-02-03
0:00 | 563 | 487 | 3046 | 469 | 164 | 85 | 16 | 0 | 90
0:30 | 563 | 416.5 | 3058 | 337 | 154 | 87.5 | 16 | 0 | 87
1:00 | 563 | 346 | 3070 | 205 | 144 | 90 | 16 | 0 | 84
1:30 | 563 | 346 | 2942.5 | 178 | 153.5 | 80 | 16 | 0 | 83 | [5 empty] | 129.9785
2:00 | 563 | 346 | 2815 | 151 | 163 | 70 | 16 | 0 | 82 | [5 empty] | 0
2:30 | 562 | 345.5 | 2721.5 | 150.5 | 162 | 80 | 16 | 0 | 81 | [5 empty] | 129.9785
3:00 | 561 | 345 | 2628 | 150 | 161 | 90 | 16 | 0 | 80
3:30 | 561 | 345 | 2604 | 140.5 | 160.5 | 90 | 16 | 0 | 74
4:00 | 561 | 345 | 2580 | 131 | 160 | 90 | 16 | 0 | 68
4:30 | 561 | 345.5 | 2543 | 132 | 160.5 | 90 | 16 | 0 | 69
5:00 | 561 | 346 | 2506 | 133 | 161 | 90 | 16 | 0 | 70
5:30 | 561 | 346 | 2512 | 134.5 | 161 | 90 | 16 | 0 | 68
6:00 | 561 | 346 | 2518 | 136 | 161 | 90 | 16 | 0 | 66
6:30 | 561 | 345.5 | 2578.5 | 207.5 | 159.5 | 77.5 | 33.5 | 0 | 63
7:00 | 561 | 345 | 2639 | 279 | 158 | 65 | 51 | 0 | 60
7:30 | 536.5 | 369.5 | 2654 | 314.5 | 159 | 80.5 | 51 | 0 | 61
8:00 | 512 | 394 | 2669 | 350 | 160 | 96 | 51 | 0 | 62
8:30 | 555 | 394 | 2670 | 337 | 159.5 | 96 | 51 | 0 | 62
9:00 | 598 | 394 | 2671 | 324 | 159 | 96 | 51 | 0 | 62
9:30 | 618.5 | 394 | 2606.5 | 344 | 159.5 | 96 | 51 | 0 | 67
10:00 | 639 | 394 | 2542 | 364 | 160 | 96 | 51 | 0 | 72
10:30 | 649 | 394 | 2493.5 | 363.5 | 158 | 86 | 37 | 0 | 73
11:00 | 659 | 394 | 2445 | 363 | 156 | 76 | 23 | 0 | 74
11:30 | 650 | 394 | 2535 | 322.5 | 156 | 83 | 19.5 | 0 | 74
12:00 | 641 | 394 | 2625 | 282 | 156 | 90 | 16 | 0 | 74
12:30 | 646.5 | 394 | 2653 | 281.5 | 157 | 80 | 16 | 0 | 75
13:00 | 652 | 394 | 2681 | 281 | 158 | 70 | 16 | 0 | 76
13:30 | 652.5 | 394 | 2465 | 295 | 156.5 | 66 | 16 | 0 | 77
14:00 | 653 | 394 | 2249 | 309 | 155 | 62 | 16 | 0 | 78
14:30 | 651 | 394.5 | 2243 | 306.5 | 155.5 | 63 | 25 | 0 | 77
15:00 | 649 | 395 | 2237 | 304 | 156 | 64 | 34 | 0 | 76
15:30 | 649 | 394.5 | 2211 | 294 | 157.5 | 65 | 36.5 | 0 | 77
16:00 | 649 | 394 | 2185 | 284 | 159 | 66 | 39 | 0 | 78
16:30 | 644.5 | 394 | 2202.5 | 292 | 159.5 | 68 | 44.5 | 0 | 75
17:00 | 640 | 394 | 2220 | 300 | 160 | 70 | 50 | 0 | 72
17:30 | 646.5 | 441.5 | 2281 | 588.5 | 161 | 70 | 133.5 | 0 | 73 | Max Temp. in Dhaka |  | 25.2° C
18:00 | 653 | 489 | 2342 | 877 | 162 | 70 | 217 | 0 | 74
18:30 | 662.5 | 489 | 2551 | 965 | 162 | 73 | 263.5 | 0 | 92
19:00 | 672 | 489 | 2760 | 1053 | 162 | 76 | 310 | 0 | 90
19:30 | 663 | 489 | 2785 | 1094 | 162 | 76 | 257 | 0 | 92
20:00 | 663 | 490 | 2794 | 1086 | 163 | 76 | 263 | 0 | 92
20:30 | 663 | 490 | 2799.5 | 1021 | 163 | 76 | 202.5 | 0 | 92
21:00 | 663 | 490 | 2805 | 956 | 163 | 76 | 142 | 0 | 92
21:30 | 668.5 | 490 | 2792.5 | 795.5 | 164 | 76 | 102 | 0 | 91
22:00 | 674 | 490 | 2780 | 635 | 165 | 76 | 62 | 0 | 90
22:30 | 674 | 490 | 2770.5 | 467.5 | 165.5 | 76 | 62 | 0 | 87
23:00 | 674 | 490 | 2761 | 300 | 166 | 76 | 62 | 0 | 84
23:30 | 654 | 489.5 | 2636 | 283.5 | 164.5 | 73 | 39 | 0 | 81
24:00 | 634 | 489 | 2511 | 267 | 163 | 70 | 16 | 0 | 78
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Tripura

## volt
Date: | 2017-02-03
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 232 | 8:00 | 230 | 0:00 | Tongi | 228 | 23:00 | 220 | 18:00
Ishurdi | 232 | 7:00 | 227 | 8:00 | Comilla (N) | 230 | 7:00 | 226 | 17:00
Ashuganj | 241 | 1:00 | 235 | 23:00 | Hathazari | 226 | 8:00 | 213 | 0:00
Serajganj | 225 | 1:00 | 218 | 18:30 | Megnaghat | 224 | 4:00 | 222 | 0:00
Baghabari | 227 | 3:00 | 220 | 21:00 | Fenchuganj | 240 | 5:00 | 234 | 9:00
Barapukuria | 227 | 3:00 | 219 | 9:00 | Siddhirganj | 239 | 5:00 | 230 | 0:00
Bogra | 225 | 5:00 | 212 | 9:00 | Maniknagar | 237 | 5:00 | 230 | 10:00
Khulna South | 234 | 5:00 | 225 | 8:00 | Old Airport | 223 | 5:00 | 216 | 12:00
Rampura | 224 | 3:00 | 220 | 11:00 | Barisal | 241 | 14:00 | 233 | 9:00
Haripur | 222 | 4:00 | 219 | 11:00 | AKSML | 226 | 10:00 | 206 | 9:00
Hasnabad | 225 | 5:00 | 219 | 12:00 | BSRM | 226 | 8:00 | 210 | 0:00
Aminbazar | 223 | 5:00 | 217 | 12:00 | Bibiyana | 0 | 1:00 | 0 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 139 | 100 | 137 | 1700 | Madanhat | 137 | 700 | 132 | 1100
Munsiganj | 138 | 1830 | 134 | 100 | Hathazari | 135 | 800 | 128 | 1700
Megnaghat | 135 | 800 | 133 | 300 | Khulshi | 133 | 700 | 126 | 1200
Shyampur | 133 | 700 | 130 | 1200 | Halishahar | 135 | 800 | 127 | 100
Bhulta | 128 | 2000 | 124 | 100 | Baraulia | 134 | 700 | 127 | 1600
Madanganj | 134 | 1800 | 130 | 1200 | Sikalbaha | 136 | 700 | 124 | 200
Shitalakhya | 140 | 1830 | 132 | 1200 | Dohazari | 136 | 800 | 128 | 100
Rahim steal | 137 | 1800 | 135 | 900 | Cox'sbazar | 132 | 700 | 121 | 200
Matuail | 136 | 700 | 134 | 100 | Chandraghona | 136 | 800 | 130 | 1200
Ghorasal | 140 | 100 | 140 | 100 | Kaptai | 135 | 1830 | 130 | 100
Narsinghdi | 137 | 1500 | 134 | 2000 | A. Khaer Stl. | 132 | 900 | 128 | 100
Haripur (SBU) | 137 | 1900 | 135 | 100 | Bakulia | 134 | 800 | 125 | 100
Ullon | 138 | 600 | 136 | 1200 | Julda | 135 | 800 | 125 | 300
Hasnabad | 135 | 600 | 134 | 1700 | TK Chemical | 135 | 600 | 130 | 1200
Magbazar | 136 | 600 | 132 | 1200 | Modern Steel | 135 | 700 | 128 | 1600
Maniknagar | 135 | 600 | 132 | 1200 | Shahmirpur | 135 | 800 | 127 | 1200
Bangabhaban | 134 | 500 | 132 | 1200 | Goalpara | 137 | 100 | 131 | 900
Narinda | 135 | 600 | 132 | 1200 | Central s/s | 138 | 1700 | 131 | 800
Dhanmondi | 135 | 600 | 132 | 1200 | Noapara | 136 | 300 | 127 | 800
Lalbag | 134 | 500 | 130 | 1200 | Jessore | 130 | 100 | 120 | 800
Madartek | 135 | 600 | 131 | 1200 | Jhenida | 132 | 300 | 121 | 800
Mirpur | 134 | 400 | 128 | 1200 | Bottail | 133 | 100 | 126 | 2100
Kalyanpur | 136 | 200 | 132 | 1200 | G.K.Project | 137 | 100 | 130 | 2100
Gulshan | 136 | 300 | 131 | 1200 | Faridpur | 134 | 500 | 127 | 2100
Uttara | 133 | 200 | 128 | 1200 | Madaripur | 134 | 500 | 127 | 2100
Kamrangirchar | 138 | 600 | 132 | 1200 | Gopalganj | 136 | 1400 | 126 | 2100
Savar | 135 | 400 | 128 | 1200 | Bagerhat | 138 | 1600 | 132 | 700
Bhasantec | 137 | 400 | 132 | 1200 | Mongla | 135 | 1400 | 130 | 700
Agargaon | 138 | 400 | 133 | 1200 | Satkhira | 137 | 300 | 128 | 800
Satmosjid | 138 | 300 | 133 | 1200 | Gallamari | 138 | 400 | 132 | 800
Tongi | 138 | 900 | 133 | 1800 | Magura | 133 | 300 | 120 | 1830
Kabirpur | 139 | 1800 | 133 | 900 | Chuadanga | 135 | 900 | 123 | 2000
Basundhara | 130 | 800 | 127 | 1830 | Barisal | 136 | 200 | 133 | 900
Manikganj | 145 | 100 | 136 | 1830 | Patuakhali | 136 | 200 | 133 | 900
Joydevpur | 140 | 1400 | 134 | 1200 | Bhandaria | 135 | 100 | 130 | 800
New Tongi | 139 | 100 | 133 | 1800 | Ishurdi | 137 | 300 | 130 | 800
Kodda | 140 | 1800 | 135 | 1700 | Natore | 135 | 1400 | 124 | 900
Tangail | 140 | 100 | 130 | 1800 | Bogra | 134 | 200 | 122 | 800
Mymensing | 123 | 100 | 116 | 1700 | Noagaon | 129 | 100 | 117 | 800
Kishorganj | 130 | 100 | 124 | 1300 | Rajshahi | 132 | 200 | 121 | 800
Netrokona | 122 | 300 | 112 | 1600 | C.Nawabganj | 133 | 1400 | 120 | 800
Jamalpur | 123 | 200 | 114 | 800 | Amnura | 135 | 1400 | 122 | 800
Sherpur | 125 | 200 | 114 | 1300 | Pabna | 132 | 300 | 126 | 800
Srimongal | 140 | 100 | 138 | 1200 | Shahjadpur | 138 | 1300 | 132 | 800
Shahjibazar | 141 | 200 | 136 | 1300 | Serajganj | 132 | 100 | 125 | 900
Fenchuganj | 138 | 100 | 136 | 1200 | Niyamatpur | 125 | 300 | 113 | 900
Khulawara | 138 | 100 | 136 | 800 | Joypurhat | 129 | 100 | 115 | 800
Sylhet | 137 | 100 | 135 | 1100 | Rangpur | 126 | 300 | 116 | 800
Chatak | 138 | 500 | 135 | 1300 | Lalmonirhat | 125 | 400 | 109 | 1200
Comilla(s) | 133 | 2300 | 128 | 1600 | Saidpur | 124 | 300 | 112 | 1830
Comilla(n) | 140 | 700 | 137 | 900 | Purbasadipur | 125 | 200 | 114 | 900
Chandpur | 138 | 600 | 134 | 1900 | Thakurgaon | 122 | 500 | 110 | 800
Feni | 127 | 900 | 122 | 2100 | Palashbari | 127 | 300 | 116 | 900
Chowmuhani | 132 | 700 | 127 | 1830 | Barapukuria | 127 | 300 | 119 | 900
Ashuganj | 140 | 100 | 136 | 1300 | Panchagar | 118 | 400 | 101 | 900
Daudkandi | 137 | 700 | 134 | 1200
B.Baria | 142 | 100 | 134 | 1300
Page 7 of 7