## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-12 | Tuesday
|  | Date (day): | 2018-06-12 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11120 | MW |  |  | (b) At Evening Peak Hour : |  | 12406 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-11 | 2018-06-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 65 | 65 | 65 | 65 |  | 20
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 |  | 50
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120 | 70
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 340 | 340 | 340
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 30 | 30 | 78 |  |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 35 | 35 | 102 | 6 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 344 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 55 | 84 | 84 |  | 26 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 286 | 261 | 350 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 410 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 240 | 200 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 65 | 81 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 50 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 17 | 50 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 87 | 88 | 84 | 88 |  | 12 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 195 | 210 | 190 | 210 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 20 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 94 | 102 |  | 0
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 48 | 47 | 49 | 49
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 36 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 100 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 90 | 90 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 53 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 49 | 51 | 51
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 279 | 270 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 12 | 0 | 100 |  |  | On test
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 3461 | 3674 | 4124 | 4400 | 441 | 415
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 25 | 44 | 44 |  | 5 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 113 | 123 | 132 | 132 |  | 98 | #4, Under maint.
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 195 | 215 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 60 | 50 | 100 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 12 | 51 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 75 | 85 | 85
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 81 | 62 | 80
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 90 | 90 | 90 |  |  | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 1 | 23 | 6 | 20
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 34 | 98 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 508 | 819 | 927 | 1004 | 360 | 153
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 80 | 100 |  |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100 |  |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint.
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 182 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 302 | 300 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 338 | 301 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 42 | 42 | 42
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 78 | 78 | 117 |  | Gas shortage
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 153 | 152 | 153 | 153
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 128 | 172 | 142 | 180
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 20 | 8 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 22 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 10 | 0 | 200 |  |  | On test
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1614 | 1621 | 1763 | 2131 | 160 | 189
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 85 | 69 | 80 | 100 | 102 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 82 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.6 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 205 | 205 | 205 | 205
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 320.6 | 376 | 404 | 422 | 102 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 56 | 58 | 58
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 61 | 61 | 61 | 61
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 178 | 306 | 260 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 45 | 53 | 50 | 50
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 47 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 63 | 66 | 66
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 89 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 49 | 50 | 49 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 55 | 70 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 43 | 44 | 44
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 285 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1110 | 1251 | 1341 | 1442 | 0 | 0
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 49 | 0 | 49
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 50 | 481 | 483 | 483
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 27 | 102 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 93 | 99 | 99 |  |  | Engine problem
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 41 | 46
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 160 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 14 | 74 | 50 | 74
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27/06/2018
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 40 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 53 | 0 | 55
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 88 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 309 | 1180 | 1048 | 1281 | 0 | 360
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 96 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 34 | 33 | 34
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 190 | 191 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 97 | 96 | 98
| Barisal Area Total |  |  |  |  | 472 | 462 | 356 | 418 | 433 | 466 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 37 | 0 | 47
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 45 | 47
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 194 | 173 | 215 | 215
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 170 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 0 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 11 | 11
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 22 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 51 | 102 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 582 | 782 | 760 | 897 | 71 | 116
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 68 | 67 | 70 | 70
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 195 | 260 | 250 | 260
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 15
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 263 | 359 | 320 | 363 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 8523.6 | 10480 | 11120 | 12406 | 1134 | 1318
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8142.1526 | 10011 | 10622.3588 | 11850.8078
A. |  | 2018-06-11 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10480 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7242.6 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10480 | MW
3 | Day peak Generation : |  |  | 8523.6 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10011 | MW
4 | Evening peak Generation : |  |  | 10480 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 212.4287 | MKWHr | By Solar | 0.01287 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 124.2029 | MKWHr |  | By Oil: | 66.9556 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 6.6879 | MKWHr |  | By Hydro: | 2.597 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1134 | MW | Dhaka | 3932 | 3932 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1318 | MW | Chittagong | 730 | 730 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2452 | MW | Khulna | 1284 | 1284 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1058.54 | MMCFD |  |  | Rajshahi | 1136 | 1136 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 91111427.274 | ii) Oil : | Taka | 540481914.81 | Comilla | 902 | 902 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 9869158.37 | Total | Taka | 641462500.454 | Mymensingh | 758 | 758 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 10.647 | MKWHr. | Sylhet | 408 | 408 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -720 | MW at | 21:00 | hrs | Barisal | 233 | 233 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -940 | MW at | 15:00 | hrs | Rangpur | 628 | 628 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 10011 | 10011 |  | 0
B. |  | 2018-06-12 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12406 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 1406 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 222.9691 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7596 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 8.5731 | MKWHr. | ii) HVDC Flow at Peak Time |  | 481 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3994 | MKWHr. | iii) Maximum HVDC Flow : |  | 481 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.38 |  | (b) Today: | 78.38 |  | (c) Rule Curve: |  | 76.26
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-06-11
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 370 | 301 | 0 | 0 | 450 | 250 | 41 | 81 | 55 | 208 | 0 | 0 | 0 | 40 | 7 | 149 | 30 | 90 | 10 | 45 | 36 | 56 | 55 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 75 | 26 | 0 | 0 | 25 | 0 | 193 | 0 | 70 | 0 | 8 | 0 | 17 | 40 | 0 | 6 | 19 | 26 | 0 | 100 | 100 | 15 | 292 | 194 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 152 | 89 | 24 | 20 | 0 | 57 | 61 | 50 | 50 | 163 | 255 | 64 | 84 | 49 | 0 | 0 | 42 | 9 | 320 | 23 | 11 | 0 | 302 | 0 | 0 | 205 |  | 477 | 0 | 0 | 108 | 99 | 160 | 0 | 0 | 40 | 50 | 40 | 195 | 31 | 80 | 0 | 0 | 0 | 0 | 0 | 101 | 50 | 43 | 45 | 43 | 41 | 22 | 6 | 11 | 0 | 67 | 185 | 15 | 18 | 194 | 0 | 0 | 187 | 96 | 22 | 0 | 0 |  | 6867 | 2426 | 9293 | 3366 | 477 | 1918 | 1941 | 252 | 101 | 1086 | 152 | 0 | 0 | 78.23
2:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 345 | 302 | 0 | 0 | 400 | 200 | 7 | 81 | 55 | 208 | 0 | 0 | 0 | 40 | 7 | 149 | 30 | 90 | 11 | 48 | 36 | 56 | 55 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 75 | 27 | 0 | 0 | 26 | 0 | 194 | 0 | 70 | 0 | 0 | 0 | 17 | 40 | 12 | 6 | 19 | 0 | 0 | 100 | 100 | 15 | 290 | 186 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 144 | 89 | 24 | 20 | 0 | 54 | 61 | 50 | 50 | 100 | 252 | 63 | 84 | 49 | 0 | 0 | 42 | 9 | 300 | 23 | 11 | 0 | 302 | 0 | 0 | 205 |  | 477 | 0 | 0 | 51 | 99 | 160 | 0 | 0 | 40 | 46 | 40 | 195 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 101 | 50 | 43 | 45 | 43 | 41 | 22 | 6 | 11 | 0 | 68 | 185 | 14 | 18 | 179 | 0 | 0 | 172 | 97 | 0 | 0 | 0 |  | 6586 | 2280 | 8866 | 3309 | 477 | 1759 | 1755 | 253 | 102 | 1067 | 144 | 0 | 0 | 78.26
3:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 350 | 331 | 0 | 0 | 400 | 200 | 7 | 81 | 55 | 208 | 0 | 0 | 0 | 40 | 7 | 149 | 30 | 90 | 11 | 47 | 36 | 55 | 13 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 76 | 28 | 0 | 0 | 26 | 0 | 195 | 0 | 70 | 0 | 0 | 0 | 17 | 40 | 12 | 4 | 0 | 16 | 0 | 100 | 100 | 20 | 301 | 193 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 146 | 87 | 24 | 20 | 0 | 56 | 61 | 50 | 50 | 100 | 250 | 62 | 84 | 49 | 0 | 0 | 42 | 9 | 320 | 23 | 11 | 0 | 302 | 0 | 0 | 205 |  | 463 | 0 | 0 | 51 | 99 | 160 | 0 | 0 | 40 | 50 | 40 | 194 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 101 | 50 | 43 | 45 | 43 | 41 | 22 | 6 | 11 | 0 | 68 | 185 | 14 | 18 | 186 | 0 | 0 | 179 | 95 | 0 | 0 | 0 |  | 6616 | 2280 | 8896 | 3321 | 463 | 1821 | 1709 | 253 | 104 | 1079 | 146 | 0 | 0 | 78.29
4:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 345 | 341 | 0 | 0 | 400 | 200 | 7 | 70 | 15 | 200 | 0 | 0 | 0 | 15 | 7 | 149 | 10 | 90 | 10 | 48 | 36 | 56 | 17 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 76 | 28 | 0 | 0 | 25 | 0 | 195 | 0 | 70 | 0 | 0 | 0 | 17 | 40 | 12 | 6 | 19 | 26 | 0 | 100 | 100 | 84 | 290 | 182 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 134 | 90 | 8 | 20 | 0 | 55 | 61 | 50 | 50 | 100 | 241 | 61 | 84 | 49 | 0 | 0 | 42 | 9 | 310 | 23 | 11 | 0 | 302 | 0 | 0 | 205 |  | 462 | 0 | 0 | 10 | 68 | 160 | 0 | 0 | 40 | 50 | 40 | 195 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 101 | 50 | 43 | 45 | 43 | 41 | 22 | 6 | 11 | 0 | 69 | 185 | 0 | 0 | 182 | 0 | 0 | 175 | 96 | 0 | 0 | 0 |  | 6548 | 2169 | 8717 | 3358 | 462 | 1831 | 1531 | 254 | 104 | 1043 | 134 | 0 | 0 | 78.32
5:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 340 | 350 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 199 | 0 | 0 | 0 | 7 | 7 | 130 | 10 | 16 | 10 | 12 | 18 | 56 | 36 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 77 | 28 | 0 | 0 | 8 | 0 | 195 | 0 | 70 | 0 | 0 | 0 | 17 | 40 | 12 | 6 | 19 | 16 | 0 | 100 | 100 | 104 | 309 | 187 | 78 | 153 | 42 | 0 | 5 | 51 | 10 | 0 | 0 | 19 | 11 | 33 | 19 | 116 | 103 | 8 | 20 | 0 | 54 | 61 | 50 | 50 | 100 | 250 | 62 | 10 | 49 | 0 | 0 | 42 | 9 | 300 | 23 | 11 | 0 | 150 | 0 | 0 | 205 |  | 462 | 0 | 0 | 10 | 18 | 130 | 0 | 0 | 40 | 40 | 8 | 193 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 26 | 43 | 0 | 22 | 6 | 8 | 0 | 69 | 185 | 0 | 0 | 178 | 0 | 0 | 172 | 96 | 0 | 0 | 0 |  | 6068 | 1893 | 7961 | 3406 | 462 | 1671 | 1076 | 254 | 105 | 871 | 116 | 0 | 0 | 78.35
6:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 340 | 352 | 0 | 0 | 350 | 200 | 7 | 15 | 15 | 200 | 0 | 0 | 0 | 7 | 7 | 84 | 10 | 8 | 10 | 12 | 18 | 36 | 55 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 80 | 28 | 0 | 0 | 8 | 0 | 195 | 0 | 60 | 0 | 0 | 0 | 0 | 15 | 12 | 5 | 19 | 15 | 0 | 100 | 100 | 120 | 301 | 182 | 78 | 153 | 42 | 0 | 5 | 5 | 10 | 0 | 0 | 19 | 11 | 8 | 19 | 110 | 103 | 8 | 20 | 0.1 | 54 | 61 | 11 | 10 | 100 | 244 | 64 | 10 | 10 | 0 | 0 | 11 | 9 | 290 | 23 | 11 | 0 | 100 | 0 | 0 | 205 |  | 462 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 40 | 35 | 8 | 190 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 0 | 16 | 0 | 22 | 6 | 8 | 0 | 68 | 185 | 0 | 0 | 175 | 0 | 0 | 169 | 95 | 0 | 0 | 0 |  | 5628.1 | 1810 | 7438.1 | 3375 | 462 | 1414 | 962 | 253 | 108 | 754 | 110 | 0.1 | 0 | 78.38
7:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 345 | 301 | 0 | 0 | 350 | 200 | 7 | 15 | 15 | 200 | 0 | 0 | 0 | 7 | 7 | 84 | 10 | 8 | 10 | 12 | 18 | 36 | 55 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 79 | 29 | 0 | 0 | 8 | 0 | 195 | 0 | 60 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 19 | 5 | 0 | 100 | 0 | 188 | 320 | 183 | 78 | 153 | 42 | 0 | 5 | 5 | 10 | 0 | 0 | 19 | 8 | 8 | 15 | 108 | 102 | 8 | 20 | 0.6 | 54 | 61 | 11 | 10 | 100 | 259 | 63 | 10 | 10 | 0 | 0 | 11 | 9 | 300 | 23 | 5 | 0 | 49 | 0 | 0 | 205 |  | 462 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 3 | 35 | 8 | 192 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 43 | 0 | 16 | 0 | 22 | 6 | 8 | 0 | 67 | 185 | 0 | 0 | 179 | 0 | 0 | 173 | 50 | 0 | 0 | 0 |  | 5518.6 | 1724 | 7242.6 | 3374 | 462 | 1315 | 902 | 252 | 108 | 721 | 108 | 0.6 | 0 | 78.4
8:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 365 | 332 | 0 | 0 | 370 | 200 | 7 | 16 | 15 | 190 | 0 | 0 | 0 | 7 | 7 | 84 | 10 | 8 | 11 | 12 | 18 | 36 | 50 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 80 | 29 | 0 | 0 | 8 | 0 | 207 | 0 | 60 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 19 | 6 | 0 | 100 | 0 | 255 | 334 | 205 | 78 | 152 | 42 | 0 | 5 | 5 | 11 | 0 | 0 | 19 | 8 | 8 | 15 | 108 | 88 | 8 | 20 | 0.7 | 55 | 61 | 11 | 10 | 100 | 259 | 62 | 10 | 10 | 0 | 0 | 11 | 9 | 320 | 23 | 5 | 0 | 49 | 0 | 0 | 205 |  | 463 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 14 | 8 | 196 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 40 | 43 | 0 | 16 | 0 | 22 | 6 | 8 | 0 | 69 | 185 | 0 | 0 | 195 | 0 | 0 | 187 | 50 | 0 | 0 | 0 |  | 5699.7 | 1735 | 7434.7 | 3492 | 463 | 1386 | 899 | 254 | 109 | 723 | 108 | 0.7 | 0 | 78.42
9:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 380 | 330 | 0 | 0 | 420 | 200 | 7 | 16 | 15 | 190 | 0 | 0 | 0 | 7 | 7 | 84 | 10 | 8 | 10 | 12 | 18 | 36 | 50 | 22 | 25 | 25 | 33 | 33 | 50 | 0 | 81 | 30 | 0 | 0 | 8 | 0 | 207 | 0 | 60 | 0 | 0 | 0 | 0 | 15 | 12 | 6 | 19 | 3 | 0 | 100 | 0 | 305 | 334 | 205 | 78 | 152 | 42 | 0 | 5 | 5 | 42 | 0 | 0 | 19 | 8 | 8 | 15 | 102 | 88 | 8 | 20 | 1.1 | 55 | 61 | 11 | 10 | 130 | 266 | 62 | 10 | 10 | 0 | 0 | 38 | 9 | 330 | 23 | 11 | 0 | 49 | 0 | 0 | 205 |  | 462 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 14 | 8 | 194 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 0 | 16 | 0 | 22 | 6 | 8 | 0 | 69 | 195 | 0 | 0 | 196 | 0 | 0 | 192 | 95 | 0 | 0 | 0 |  | 5916.1 | 1802 | 7718.1 | 3569 | 462 | 1573 | 908 | 264 | 111 | 728 | 102 | 1.1 | 0 | 0
10:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 370 | 308 | 8 | 0 | 450 | 200 | 17 | 25 | 23 | 190 | 0 | 0 | 0 | 10 | 15 | 100 | 50 | 77 | 17 | 24 | 18 | 56 | 55 | 22 | 25 | 25 | 25 | 33 | 41 | 0 | 83 | 30 | 0 | 0 | 8 | 0 | 195 | 0 | 60 | 0 | 0 | 0 | 0 | 50 | 15 | 6 | 19 | 3 | 0 | 100 | 0 | 308 | 301 | 185 | 78 | 152 | 39 | 0 | 5 | 12 | 85 | 0 | 0 | 19 | 8 | 33 | 15 | 114 | 87 | 8 | 20 | 0.5 | 55 | 61 | 45 | 10 | 163 | 146 | 62 | 70 | 48 | 0 | 0 | 37 | 9 | 310 | 23 | 11 | 0 | 80 | 0 | 0 | 205 |  | 384 | 0 | 0 | 27 | 49 | 120 | 0 | 0 | 0 | 14 | 40 | 193 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 0 | 16 | 0 | 22 | 6 | 8 | 0 | 69 | 195 | 0 | 0 | 195 | 0 | 0 | 185 | 95 | 0 | 0 | 0 |  | 6227.5 | 1831 | 8058.5 | 3400 | 384 | 1777 | 1281 | 264 | 113 | 725 | 114 | 0.5 | 0 | 0
11:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 345 | 300 | 13 | 0 | 450 | 200 | 82 | 45 | 48 | 190 | 0 | 0 | 10 | 65 | 48 | 100 | 50 | 90 | 21 | 48 | 36 | 56 | 55 | 22 | 25 | 22 | 25 | 33 | 41 | 0 | 84 | 31 | 0 | 0 | 8 | 0 | 195 | 0 | 60 | 0 | 20 | 0 | 0 | 50 | 42 | 13 | 19 | 5 | 0 | 100 | 0 | 315 | 316 | 193 | 78 | 152 | 36 | 0 | 5 | 51 | 85 | 0 | 13 | 19 | 8 | 33 | 15 | 116 | 87 | 8 | 20 | 0.7 | 56 | 61 | 45 | 10 | 163 | 153 | 62 | 81 | 48 | 0 | 0 | 42 | 9 | 290 | 23 | 11 | 0 | 195 | 0 | 0 | 205 |  | 100 | 0 | 0 | 27 | 58 | 120 | 0 | 0 | 0 | 14 | 32 | 193 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 0 | 16 | 0 | 22 | 10 | 8 | 0 | 69 | 195 | 0 | 0 | 188 | 0 | 0 | 177 | 94 | 0 | 0 | 0 |  | 6721.7 | 1536 | 8257.7 | 3400 | 100 | 1809 | 1736 | 264 | 115 | 717 | 116 | 0.7 | 0 | 0
12:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 365 | 286 | 13 | 0 | 450 | 240 | 90 | 48 | 42 | 195 | 0 | 0 | 17 | 87 | 48 | 100 | 50 | 90 | 20 | 48 | 36 | 56 | 55 | 22 | 25 | 22 | 33 | 33 | 41 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 209 | 0 | 60 | 0 | 12 | 0 | 0 | 60 | 34 | 19 | 0 | 1 | 0 | 100 | 0 | 340 | 338 | 205 | 78 | 153 | 36 | 0 | 5 | 51 | 85 | 0 | 20 | 19 | 8 | 33 | 15 | 128 | 85 | 8 | 20 | 2.6 | 56 | 61 | 45 | 10 | 163 | 178 | 62 | 84 | 49 | 0 | 0 | 42 | 9 | 320 | 23 | 8 | 0 | 279 | 0 | 0 | 205 |  | 50 | 0 | 0 | 27 | 66 | 120 | 0 | 0 | 0 | 14 | 32 | 190 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 0 | 22 | 0 | 18 | 10 | 8 | 0 | 68 | 195 | 0 | 0 | 194 | 0 | 0 | 186 | 96 | 0 | 0 | 0 |  | 7013.6 | 1510 | 8523.6 | 3497 | 50 | 1824 | 1906 | 263 | 113 | 740 | 128 | 2.6 | 0 | 0
13:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 390 | 272 | 14 | 0 | 430 | 240 | 91 | 38 | 55 | 205 | 0 | 0 | 10 | 65 | 48 | 100 | 50 | 85 | 20 | 48 | 36 | 56 | 55 | 22 | 25 | 22 | 33 | 33 | 33 | 0 | 83 | 30 | 0 | 0 | 8 | 0 | 210 | 0 | 80 | 0 | 24 | 0 | 0 | 80 | 45 | 24 | 19 | 3 | 0 | 100 | 0 | 320 | 320 | 197 | 78 | 153 | 36 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 8 | 33 | 15 | 124 | 84 | 8 | 20 | 2.3 | 56 | 61 | 45 | 37 | 163 | 273 | 62 | 84 | 50 | 0 | 0 | 42 | 9 | 320 | 23 | 8 | 0 | 300 | 0 | 0 | 205 |  | 54 | 0 | 0 | 51 | 66 | 120 | 0 | 0 | 0 | 14 | 40 | 188 | 21 | 48 | 0 | 0 | 0 | 30 | 0 | 85 | 50 | 43 | 0 | 34 | 0 | 22 | 10 | 8 | 0 | 55 | 195 | 0 | 0 | 198 | 0 | 0 | 192 | 95 | 0 | 0 | 0 |  | 7173.3 | 1619 | 8792.3 | 3601 | 54 | 1822 | 1995 | 250 | 113 | 831 | 124 | 2.3 | 0 | 0
14:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 365 | 267 | 13 | 0 | 430 | 240 | 93 | 48 | 55 | 210 | 0 | 0 | 17 | 78 | 48 | 100 | 50 | 90 | 20 | 47 | 36 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 33 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 211 | 0 | 80 | 0 | 24 | 0 | 0 | 80 | 40 | 24 | 19 | 5 | 0 | 100 | 0 | 330 | 331 | 202 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 15 | 134 | 79 | 8 | 20 | 1.8 | 56 | 61 | 45 | 47 | 163 | 312 | 62 | 84 | 50 | 0 | 0 | 42 | 9 | 320 | 23 | 8 | 0 | 294 | 0 | 0 | 205 |  | 113 | 0 | 0 | 51 | 66 | 120 | 0 | 0 | 0 | 14 | 40 | 190 | 26 | 64 | 0 | 0 | 0 | 43 | 0 | 85 | 50 | 43 | 0 | 34 | 0 | 22 | 10 | 5 | 0 | 54 | 195 | 0 | 0 | 191 | 0 | 0 | 184 | 95 | 30 | 0 | 0 |  | 7254.8 | 1725 | 8979.8 | 3642 | 113 | 1834 | 2056 | 249 | 113 | 837 | 134 | 1.8 | 0 | 0
15:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 360 | 257 | 13 | 0 | 430 | 240 | 100 | 50 | 55 | 203 | 0 | 0 | 17 | 86 | 94 | 100 | 90 | 90 | 21 | 48 | 36 | 55 | 55 | 0 | 25 | 22 | 33 | 33 | 33 | 0 | 84 | 30 | 0 | 0 | 8 | 0 | 203 | 0 | 80 | 0 | 38 | 0 | 0 | 80 | 40 | 26 | 19 | 2 | 0 | 100 | 0 | 323 | 320 | 195 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 15 | 138 | 78 | 8 | 20 | 0.6 | 56 | 60 | 49 | 47 | 163 | 310 | 62 | 84 | 49 | 0 | 0 | 42 | 9 | 335 | 23 | 8 | 10 | 301 | 0 | 12 | 205 |  | 93 | 0 | 0 | 105 | 66 | 120 | 0 | 0 | 0 | 14 | 40 | 189 | 25 | 64 | 0 | 0 | 0 | 43 | 0 | 85 | 50 | 43 | 27 | 43 | 0 | 22 | 10 | 8 | 0 | 67 | 195 | 0 | 0 | 191 | 0 | 0 | 184 | 95 | 30 | 0 | 0 |  | 7350.6 | 1809 | 9159.6 | 3581 | 93 | 1838 | 2277 | 262 | 114 | 856 | 138 | 0.6 | 0 | 0
16:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 345 | 257 | 13 | 0 | 430 | 200 | 100 | 70 | 55 | 210 | 0 | 0 | 17 | 84 | 94 | 115 | 50 | 28 | 21 | 47 | 54 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 37 | 0 | 84 | 30 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 0 | 0 | 0 | 80 | 44 | 31 | 19 | 2 | 0 | 100 | 0 | 300 | 301 | 181 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 2 | 25 | 19 | 11 | 33 | 15 | 146 | 78 | 8 | 20 | 0 | 56 | 61 | 50 | 47 | 163 | 376 | 58 | 84 | 49 | 0 | 0 | 40 | 9 | 280 | 23 | 11 | 10 | 300 | 0 | 11 | 205 |  | 204 | 0 | 0 | 107 | 66 | 120 | 0 | 0 | 0 | 31 | 40 | 183 | 26 | 64 | 0 | 0 | 0 | 43 | 9 | 85 | 50 | 43 | 42 | 43 | 35 | 18 | 10 | 8 | 0 | 67 | 209 | 0 | 0 | 179 | 0 | 0 | 172 | 95 | 30 | 0 | 0 |  | 7180 | 1979 | 9159 | 3590 | 204 | 1779 | 2145 | 276 | 114 | 905 | 146 | 0 | 0 | 0
17:00 | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 350 | 250 | 13 | 0 | 350 | 200 | 80 | 56 | 40 | 210 | 0 | 0 | 17 | 50 | 50 | 115 | 10 | 8 | 10 | 48 | 36 | 56 | 55 | 22 | 25 | 25 | 33 | 33 | 24 | 0 | 85 | 31 | 0 | 0 | 0 | 0 | 215 | 0 | 50 | 0 | 6 | 0 | 0 | 80 | 44 | 26 | 19 | 3 | 0 | 100 | 0 | 336 | 334 | 204 | 78 | 153 | 42 | 0 | 5 | 51 | 22 | 49 | 8 | 19 | 11 | 33 | 15 | 132 | 68 | 16 | 20 | 0.7 | 56 | 61 | 53 | 47 | 100 | 323 | 62 | 20 | 50 | 0 | 0 | 41 | 9 | 270 | 23 | 11 | 10 | 165 | 0 | 10 | 205 |  | 210 | 0 | 0 | 33 | 69 | 120 | 0 | 0 | 0 | 32 | 40 | 190 | 26 | 64 | 0 | 0 | 0 | 43 | 9 | 85 | 25 | 43 | 43 | 8 | 41 | 18 | 10 | 8 | 0 | 66 | 222 | 0 | 0 | 181 | 0 | 0 | 175 | 48 | 30 | 0 | 0 |  | 6607.7 | 1839 | 8446.7 | 3637 | 210 | 1451 | 1635 | 288 | 116 | 977 | 132 | 0.7 | 0 | 0
18:00 | 65 | 120 | 0 | 120 | 335 | 32 | 10 | 370 | 250 | 13 | 0 | 350 | 200 | 30 | 32 | 30 | 210 | 0 | 0 | 17 | 50 | 50 | 115 | 10 | 8 | 10 | 47 | 36 | 37 | 55 | 22 | 25 | 31 | 33 | 33 | 24 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 204 | 0 | 50 | 0 | 8 | 15 | 0 | 90 | 44 | 30 | 19 | 3 | 0 | 100 | 0 | 317 | 320 | 194 | 78 | 153 | 42 | 0 | 5 | 51 | 22 | 49 | 8 | 19 | 11 | 33 | 15 | 154 | 63 | 16 | 20 | 0 | 56 | 61 | 53 | 47 | 100 | 311 | 62 | 20 | 50 | 0 | 0 | 42 | 9 | 320 | 23 | 11 | 10 | 117 | 0 | 12 | 205 |  | 366 | 0 | 0 | 33 | 87 | 120 | 0 | 0 | 27 | 52 | 40 | 191 | 23 | 64 | 0 | 0 | 0 | 43 | 9 | 85 | 25 | 43 | 43 | 8 | 41 | 22 | 10 | 8 | 0 | 66 | 240 | 0 | 0 | 193 | 0 | 0 | 186 | 98 | 10 | 0 | 0 |  | 6531 | 2133 | 8664 | 3586 | 366 | 1595 | 1499 | 306 | 119 | 1039 | 154 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 65 | 120 | 0 | 120 | 335 | 35 | 30 | 348 | 260 | 13 | 0 | 330 | 200 | 37 | 32 | 38 | 210 | 0 | 0 | 17 | 50 | 50 | 115 | 10 | 8 | 10 | 48 | 54 | 37 | 55 | 22 | 25 | 17 | 33 | 33 | 24 | 0 | 90 | 32 | 0 | 0 | 8 | 0 | 204 | 0 | 50 | 0 | 8 | 81 | 82 | 90 | 44 | 36 | 19 | 13 | 0 | 100 | 0 | 323 | 320 | 195 | 78 | 152 | 42 | 0 | 5 | 51 | 22 | 49 | 8 | 19 | 11 | 33 | 22 | 168 | 62 | 16 | 20 | 0 | 56 | 61 | 53 | 47 | 100 | 329 | 62 | 20 | 50 | 0 | 0 | 42 | 9 | 315 | 23 | 11 | 10 | 122 | 0 | 12 | 205 |  | 453 | 49 | 0 | 51 | 90 | 120 | 0 | 12 | 47 | 84 | 40 | 187 | 28 | 64 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 47 | 8 | 42 | 22 | 10 | 11 | 0 | 67 | 250 | 0 | 18 | 185 | 0 | 0 | 178 | 97 | 10 | 0 | 0 |  | 6761 | 2445 | 9206 | 3571 | 453 | 1617 | 1610 | 317 | 122 | 1348 | 168 | 0 | 0 | 78.29
19:30 | 65 | 120 | 0 | 120 | 365 | 35 | 30 | 347 | 271 | 32 | 0 | 430 | 250 | 100 | 55 | 55 | 210 | 0 | 0 | 20 | 85 | 102 | 125 | 50 | 28 | 51 | 48 | 54 | 55 | 55 | 0 | 25 | 17 | 33 | 33 | 26 | 0 | 90 | 32 | 0 | 0 | 8 | 0 | 204 | 0 | 110 | 0 | 24 | 81 | 81 | 90 | 76 | 28 | 19 | 13 | 0 | 100 | 0 | 300 | 301 | 182 | 78 | 152 | 42 | 0 | 5 | 51 | 50 | 48 | 8 | 19 | 11 | 33 | 22 | 176 | 67 | 48 | 20 | 0 | 56 | 61 | 53 | 47 | 163 | 303 | 63 | 20 | 50 | 0 | 0 | 43 | 9 | 295 | 23 | 11 | 10 | 150 | 0 | 12 | 205 |  | 453 | 49 | 0 | 107 | 87 | 140 | 0 | 48 | 46 | 73 | 40 | 191 | 30 | 96 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 47 | 43 | 42 | 22 | 10 | 11 | 0 | 67 | 250 | 17 | 17 | 191 | 0 | 0 | 185 | 96 | 89 | 0 | 0 |  | 7435 | 2722 | 10157 | 3513 | 453 | 1801 | 2328 | 317 | 122 | 1447 | 176 | 0 | 0 | 78.29
20:00 | 65 | 120 | 0 | 120 | 340 | 35 | 30 | 355 | 262 | 55 | 0 | 360 | 200 | 100 | 45 | 55 | 210 | 0 | 0 | 30 | 80 | 102 | 149 | 50 | 86 | 51 | 47 | 7 | 56 | 55 | 0 | 25 | 32 | 33 | 33 | 40 | 0 | 91 | 32 | 0 | 0 | 8 | 0 | 194 | 0 | 80 | 0 | 41 | 81 | 81 | 90 | 90 | 31 | 19 | 18 | 0 | 100 | 0 | 300 | 301 | 180 | 78 | 152 | 42 | 0 | 5 | 51 | 85 | 48 | 8 | 19 | 11 | 33 | 22 | 166 | 72 | 48 | 20 | 0 | 56 | 61 | 53 | 47 | 100 | 298 | 54 | 89 | 50 | 15 | 0 | 43 | 9 | 240 | 23 | 11 | 10 | 168 | 0 | 12 | 205 |  | 453 | 49 | 0 | 107 | 87 | 140 | 0 | 48 | 46 | 73 | 40 | 191 | 30 | 96 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 47 | 43 | 42 | 22 | 10 | 11 | 0 | 67 | 250 | 15 | 17 | 183 | 0 | 0 | 176 | 96 | 89 | 0 | 0 |  | 7369 | 2703 | 10072 | 3507 | 453 | 1713 | 2373 | 317 | 123 | 1420 | 166 | 0 | 0 | 78.3
21:00 | 65 | 120 | 0 | 120 | 340 | 35 | 30 | 344 | 261 | 55 | 0 | 410 | 200 | 100 | 65 | 55 | 210 | 0 | 0 | 50 | 88 | 102 | 149 | 50 | 90 | 51 | 47 | 54 | 56 | 55 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 91 | 32 | 0 | 0 | 8 | 0 | 195 | 0 | 50 | 0 | 51 | 75 | 81 | 90 | 98 | 25 | 0 | 23 | 0 | 100 | 0 | 302 | 301 | 182 | 78 | 152 | 42 | 0 | 5 | 51 | 85 | 48 | 8 | 19 | 11 | 33 | 22 | 172 | 69 | 82 | 20 | 0 | 56 | 61 | 53 | 47 | 100 | 306 | 63 | 89 | 50 | 55 | 0 | 43 | 9 | 285 | 23 | 11 | 10 | 270 | 0 | 12 | 205 |  | 481 | 49 | 0 | 102 | 93 | 160 | 0 | 53 | 40 | 74 | 40 | 191 | 34 | 96 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 47 | 43 | 42 | 22 | 10 | 0 | 0 | 67 | 260 | 15 | 17 | 173 | 0 | 0 | 170 | 97 | 88 | 0 | 0 |  | 7741 | 2739 | 10480 | 3532 | 481 | 1817 | 2634 | 327 | 123 | 1394 | 172 | 0 | 0 | 78.3
22:00 | 65 | 120 | 0 | 120 | 340 | 35 | 30 | 345 | 251 | 13 | 0 | 410 | 200 | 100 | 65 | 55 | 195 | 0 | 0 | 17 | 88 | 102 | 149 | 20 | 90 | 50 | 47 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 91 | 32 | 0 | 0 | 8 | 0 | 196 | 0 | 50 | 0 | 51 | 75 | 81 | 80 | 98 | 26 | 0 | 23 | 0 | 100 | 0 | 300 | 301 | 181 | 78 | 153 | 42 | 0 | 5 | 51 | 85 | 49 | 8 | 19 | 11 | 33 | 22 | 175 | 69 | 91 | 20 | 0 | 56 | 61 | 53 | 47 | 163 | 301 | 63 | 89 | 50 | 54 | 0 | 43 | 9 | 285 | 23 | 11 | 10 | 288 | 0 | 0 | 205 |  | 479 | 49 | 0 | 101 | 89 | 190 | 0 | 53 | 40 | 71 | 40 | 182 | 34 | 96 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 43 | 43 | 42 | 22 | 10 | 10 | 0 | 67 | 260 | 15 | 17 | 182 | 0 | 0 | 165 | 98 | 83 | 0 | 0 |  | 7627 | 2756 | 10383 | 3520 | 479 | 1871 | 2474 | 327 | 123 | 1414 | 175 | 0 | 0 | 78.3
23:00 | 65 | 120 | 0 | 120 | 340 | 34 | 30 | 342 | 181 | 13 | 0 | 410 | 200 | 100 | 64 | 55 | 190 | 0 | 0 | 17 | 88 | 102 | 149 | 20 | 90 | 10 | 47 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 0 | 0 | 91 | 32 | 0 | 0 | 25 | 0 | 194 | 0 | 50 | 0 | 51 | 49 | 77 | 80 | 98 | 27 | 0 | 27 | 0 | 100 | 0 | 300 | 301 | 181 | 78 | 152 | 42 | 0 | 5 | 51 | 85 | 48 | 8 | 19 | 8 | 33 | 22 | 170 | 70 | 91 | 20 | 0 | 28 | 61 | 53 | 47 | 163 | 297 | 62 | 89 | 50 | 68 | 0 | 43 | 9 | 275 | 23 | 11 | 0 | 288 | 0 | 0 | 205 |  | 480 | 33 | 0 | 101 | 97 | 210 | 0 | 23 | 40 | 71 | 40 | 189 | 37 | 80 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 43 | 43 | 42 | 22 | 12 | 11 | 0 | 68 | 260 | 13 | 18 | 175 | 0 | 0 | 165 | 98 | 85 | 0 | 0 |  | 7449 | 2731 | 10180 | 3491 | 480 | 1799 | 2405 | 328 | 123 | 1384 | 170 | 0 | 0 | 78.3
24:00 | 65 | 120 | 0 | 120 | 340 | 34 | 30 | 342 | 251 | 0 | 0 | 410 | 200 | 100 | 64 | 55 | 190 | 0 | 0 | 0 | 88 | 50 | 149 | 20 | 90 | 10 | 47 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 19 | 0 | 91 | 31 | 0 | 0 | 25 | 0 | 195 | 0 | 70 | 0 | 51 | 49 | 50 | 80 | 98 | 21 | 0 | 27 | 0 | 100 | 0 | 300 | 301 | 181 | 78 | 152 | 42 | 0 | 5 | 51 | 86 | 0 | 8 | 0 | 0 | 33 | 22 | 166 | 71 | 95 | 20 | 0 | 60 | 61 | 53 | 47 | 163 | 302 | 51 | 89 | 50 | 68 | 0 | 43 | 9 | 280 | 23 | 11 | 0 | 301 | 0 | 0 | 205 |  | 479 | 33 | 0 | 101 | 87 | 210 | 0 | 13 | 40 | 71 | 40 | 194 | 31 | 64 | 0 | 0 | 0 | 43 | 0 | 102 | 50 | 43 | 43 | 43 | 41 | 22 | 12 | 11 | 0 | 67 | 260 | 13 | 17 | 175 | 0 | 0 | 163 | 98 | 86 | 0 | 0 |  | 7414 | 2652 | 10066 | 3496 | 479 | 1869 | 2318 | 327 | 122 | 1289 | 166 | 0 | 0 | 78.3
KWH | 1364000 | 2754045 | 0 | 2677500 | 8635218 | 214841 | 221088 | 8574970 | 6912000 | 243900 | 0 | 9218537 | 5359418 | 1373760 | 1185144 | 1036173 | 4920750 | 0 | 0 | 312000 | 1366080 | 1143504 | 2910720 | 782164 | 1416960 | 418610 | 972720 | 833040 | 1233253 | 1185035 | 425376 | 600000 | 590940 | 791900 | 831000 | 922068 | 0 | 1883632 | 713400 | 0 | 0 | 268740 | 0 | 4763492 | 0 | 1538196 | 0 | 432000 | 408664 | 504427 | 1381080 | 939840 | 411840 | 357168 | 242400 | 0 | 2384695 | 671206 | 6014000 | 7597750 | 4655000 | 1890182 | 3465982 | 948672 | 0 | 120000 | 974267 | 1185144 | 361773 | 220867 | 437688 | 228420 | 709900 | 443720 | 3399360 | 1901120 | 617932 | 461880 | 12870 | 1241000 | 1456360 | 1047000 | 874000 | 3263072 | 6049260 | 1457000 | 1528320 | 1037160 | 224780 | 0 | 906800 | 213120 | 7620250 | 554472 | 246144 | 88320 | 5181271 | 0 | 89840 | 4831200 |  | 8573091 | 259300 | 0 | 1329600 | 1594560 | 3472320 | 0 | 205530 | 494400 | 915456 | 776625 | 4631307 | 626960 | 1343040 | 0 | 0 | 0 | 473033 | 199968 | 1827232 | 1082170 | 998304 | 611600 | 756480 | 539651 | 498720 | 191448 | 211842 | 0 | 1625891 | 5062000 | 117000 | 160000 | 4716918 | 0 | 0 | 4445127 | 2185595 | 620160 | 0 | 0 |  | 161883390 | 50545328 | 212428718 | 83231983 | 8573091 | 40970904 | 42953228 | 6687891 | 2597032 | 24002359 | 3399360 | 12870 | 0
Fuel Cost | 1173040 | 2368478.7 | 0 | 2302650 | 7426287.48 | 174021.21 | 207822.72 | 5230731.7 | 4216320 | 2343879 | 0 | 6176419.79 | 81409559.42 | 8627212.8 | 7916761.92 | 6331017.03 | 3198487.5 | 0 | 0 | 4854720 | 8538000 | 7535691.36 | 28146662.4 | 4982384.68 | 8487590.4 | 6693573.9 | 6488042.4 | 5939575.2 | 7707831.25 | 7430169.45 | 319032 | 450000 | 0 | 0 | 0 | 8722763.28 | 0 | 0 | 0 | 0 | 0 | 2544967.8 | 0 | 65021665.8 | 0 | 33701874.36 | 0 | 3797280 | 4401311.28 | 4908074.71 | 8548885.2 | 6071366.4 | 2693433.6 | 303592.8 | 0 | 0 | 2170072.45 | 610797.46 | 5472740 | 5242447.5 | 3258500 | 1304225.58 | 3327342.72 | 635610.24 | 0 | 110400 | 798898.94 | 1114035.36 | 3921619.32 | 1638833.14 | 337019.76 | 171315 | 546623 | 332790 | 23251622.4 | 1425840 | 5678795.08 | 355647.6 | 0 | 1290640 | 1514614.4 | 1005120 | 786600 | 4209362.88 | 4234482 | 1660980 | 1635302.4 | 1140876 | 256249.2 | 0 | 843324 | 198201.6 | 4876960 | 415854 | 187069.44 | 1530585.6 | 0 | 0 | 0 | 0 |  | 43722764.1 | 7558595 | 0 | 8775360 | 10683552 | 55834905.6 | 0 | 3280258.8 | 5566944 | 10784071.68 | 4947101.25 | 4584993.93 | 620690.4 | 8299987.2 | 0 | 0 | 0 | 5416227.85 | 2143656.96 | 16371998.72 | 9360770.5 | 8884905.6 | 6513540 | 7504281.6 | 5812041.27 | 548592 | 179961.12 | 160364.394 | 0 | 9869158.37 | 0 | 2699190 | 3430400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 464882574.61 | 243554312.344 | 708436886.954 | 60964293.274 | 43722764.1 | 30147134 | 278249135.86 | 9869158.37 | 0 | 262232778.95 | 23251622.4 | 0 | 0
Yesterday Day Peak | 65 | 120 | 0 | 120 | 365 | 0 | 0 | 365 | 286 | 13 | 0 | 450 | 240 | 90 | 48 | 42 | 195 | 0 | 0 | 17 | 87 | 48 | 100 | 50 | 90 | 20 | 48 | 36 | 56 | 55 | 22 | 25 | 22 | 33 | 33 | 41 | 0 | 83 | 30 | 0 | 0 | 0 | 0 | 209 | 0 | 60 | 0 | 12 | 0 | 0 | 60 | 34 | 19 | 0 | 1 | 0 | 100 | 0 | 340 | 338 | 205 | 78 | 153 | 36 | 0 | 5 | 51 | 85 | 0 | 20 | 19 | 8 | 33 | 15 | 128 | 85 | 8 | 20 | 2.6 | 56 | 61 | 45 | 10 | 163 | 178 | 62 | 84 | 49 | 0 | 0 | 42 | 9 | 320 | 23 | 8 | 0 | 279 | 0 | 0 | 205 |  | 50 | 0 | 0 | 27 | 66 | 120 | 0 | 0 | 0 | 14 | 32 | 190 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 51 | 50 | 43 | 0 | 22 | 0 | 18 | 10 | 8 | 0 | 68 | 195 | 0 | 0 | 194 | 0 | 0 | 186 | 96 | 0 | 0 | 0 |  | 8523.6 | DayPeak
Yesterday Evening Peak | 65 | 120 | 0 | 120 | 340 | 35 | 30 | 344 | 261 | 55 | 0 | 410 | 200 | 100 | 65 | 55 | 210 | 0 | 0 | 50 | 88 | 102 | 149 | 50 | 90 | 51 | 47 | 54 | 56 | 55 | 22 | 25 | 28 | 33 | 33 | 49 | 0 | 91 | 32 | 0 | 0 | 8 | 0 | 195 | 0 | 50 | 0 | 51 | 75 | 81 | 90 | 98 | 25 | 0 | 23 | 0 | 100 | 0 | 302 | 301 | 182 | 78 | 152 | 42 | 0 | 5 | 51 | 85 | 48 | 8 | 19 | 11 | 33 | 22 | 172 | 69 | 82 | 20 | 0 | 56 | 61 | 53 | 47 | 100 | 306 | 63 | 89 | 50 | 55 | 0 | 43 | 9 | 285 | 23 | 11 | 10 | 270 | 0 | 12 | 205 |  | 481 | 49 | 0 | 102 | 93 | 160 | 0 | 53 | 40 | 74 | 40 | 191 | 34 | 96 | 0 | 0 | 0 | 43 | 37 | 102 | 50 | 43 | 47 | 43 | 42 | 22 | 10 | 0 | 0 | 67 | 260 | 15 | 17 | 173 | 0 | 0 | 170 | 97 | 88 | 0 | 0 |  | 10480 | EvPeak
Forecast for Evening | 65 | 120 | 0 | 120 | 340 | 102 | 78 | 412 | 360 | 84 | 0 | 450 | 305 | 100 | 100 | 55 | 210 | 0 | 0 | 100 | 88 | 102 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 98 | 34 | 0 | 0 | 25 | 0 | 225 | 0 | 135 | 0 | 51 | 85 | 80 | 90 | 98 | 44 | 19 | 20 | 100 | 100 | 0 | 360 | 360 | 225 | 78 | 153 | 42 | 0 | 10 | 51 | 85 | 50 | 52 | 19 | 11 | 33 | 22 | 180 | 100 | 95 | 22 | 0 | 58 | 61 | 50 | 50 | 163 | 330 | 66 | 86 | 50 | 100 | 0 | 44 | 9 | 341 | 23 | 11 | 200 | 300 | 0 | 100 | 205 |  | 483 | 49 | 0 | 110 | 99 | 225 | 0 | 55 | 46 | 74 | 40 | 194 | 34 | 110 | 30 | 0 | 0 | 43 | 47 | 102 | 50 | 43 | 47 | 43 | 43 | 22 | 11 | 11 | 0 | 70 | 260 | 15 | 18 | 215 | 0 | 0 | 220 | 98 | 100
Forecast for Day | 65 | 120 | 0 | 120 | 340 | 35 | 30 | 412 | 350 | 84 | 0 | 450 | 305 | 100 | 81 | 55 | 190 | 0 | 0 | 100 | 84 | 94 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 98 | 34 | 0 | 0 | 25 | 0 | 215 | 0 | 100 | 0 | 51 | 85 | 62 | 90 | 98 | 44 | 19 | 6 | 80 | 100 | 0 | 300 | 360 | 225 | 78 | 153 | 42 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 11 | 33 | 22 | 142 | 80 | 95 | 22 | 2 | 58 | 61 | 50 | 50 | 163 | 260 | 66 | 86 | 49 | 70 | 0 | 44 | 9 | 341 | 23 | 11 | 0 | 300 | 0 | 0 | 205 |  | 483 | 0 | 0 | 110 | 99 | 225 | 0 | 0 | 41 | 50 | 40 | 194 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 45 | 43 | 0 | 22 | 11 | 11 | 0 | 70 | 250 |  | 0 | 215 | 0 | 0 | 220 | 96
Generation at 08:00(Today) | 65 | 120 | 0 | 120 | 340 | 35 | 30 | 343 | 293 | 0 | 0 | 450 | 200 | 7 | 15 | 15 | 120 | 0 | 0 | 0 | 7 | 7 | 65 | 10 | 24 | 0 | 12 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 98 | 34 | 0 | 0 | 8 | 0 | 195 | 0 | 50 | 0 | 8 | 0 | 0 | 32 | 19 | 12 | 19 | 5 | 80 | 100 | 0 | 300 | 301 | 182 | 78 | 152 | 39 | 0 | 5 | 51 | 30 | 0 | 0 | 16 | 5 | 8 | 16 | 112 | 72 | 8 | 20 | 0 | 58 | 61 | 11 | 25 | 100 | 298 | 56 | 10 | 20 | 67 | 0 | 39 | 9 | 300 | 23 | 0 | 0 | 72 | 0 | 0 | 205 | 0 | 374 | 0 | 0 | 10 | 19 | 120 | 0 | 0 | 0 | 20 | 8 | 191 | 19 | 44 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 35 | 0 | 25 | 0 | 22 | 12 | 8 | 0 | 64 | 250 | 0 | 0 | 180 | 0 | 0 | 162 | 96 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7242.6 | 7:00
| Highest Generation |  | 10480 | 21:00
| Day Peak Generation |  | 8523.6 | 12:00
| Evening Peak Generation |  | 10480 | 21:00
| HVDC Max Flow |  | 481 | 21:00
| HVDC EvPeak Flow |  | 481 | 21:00
| Load factor L.F |  | 84.46%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-12
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8523.6 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7596 | MW
Evening Peak Generation : |  | 10480 | MW Hour : | 21:00 | Available Max Generation : |  | 12406 | MW
E.P. Demand (at gen end) : |  | 10480 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10480 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1406 | MW
Total Gen. (MKWH) : |  | 212.4287 | System Load Factor : | 84.46% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -940 | MW at | 15:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-12
Actual : | 78.38 | Ft.(MSL) , | Rule curve : | 76.26 | Ft.( MSL )
Gas Consumed : | Total = | 1058.54 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 91111427.274
|  | Coal : | 9869158.37 | Oil : | 540481914.81 | Total : | 641462500.454
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3912.8001 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1330.3138 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1191.8717 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1076.9405 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 973.2244 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 785.357 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 439.4609 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 202.217 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 605.7048 |  |  | 0 | 0%
Total | 0 |  | 10517.8901 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Sylhet-150 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Haripur GT-1,2
|  |  |  | 3) Ghorasal Unit-4 |  | 11) Bheramara 360 MW
|  |  |  | 4) Baghabari 100 MW |  | 12) Ashuganj 55 MW
|  |  |  | 5) Tongi GT |  | 13) Ashuganj unit-5
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Haripur-Madanganj 132 kV Ckt was under shut down from 10:37 to 11:57 for C/M at Haripur end.
b) Hathazari-Madunaghat 132 kV Ckt-1 tripped at 11:18 from both end showing Dist Z3 ABC only and was |  |  |  | About 16 MW Power interruption occurred under Hathazari S/S
switched on at 11:40. |  |  |  | area from 11:18 to 11:40.
c) Hathazari-Madunaghat 132 kV Ckt-2 tripped at 11:18 from both end showing Dist Z3 ABC only.
d) Modunaghat-Chandragona 132 kV Ckt-1 & 2 tripped at 11:18 from Chandragona end of Ckt-1 & both end of Ckt-2 |  |  |  | About 42 MW Power interruption occurred under Madunaghat S/S
showing Dist Z3 ABC due to CB loop turn at Chandragona Ckt from Madunaghat end and Ckt-1 |  |  |  | area from 11:18 to 11:45.
was switched on at 11:45.
e) Madunaghat-Khulshi 132 kV Ckt-1 & 2 tripped at 11:18 from Khulshi end showing Dist Z3 and were switched |  |  |  | About 34 MW Power interruption occurred under Khulshi S/S
on at 11:45. |  |  |  | area from 11:18 to 11:45.
f) Haripur-Siddhirganj 132 kV Ckt-1 & 2 tripped at 12:16 from Siddhirganj end showing inst E/F and were
switched on at 12:22.
g) Haripur-Rahim steel 132 kV Ckt tripped at 12:16 from Haripur end showing Dist Z1 ,aided trip due to LA burst |  |  |  | About 6 MW Power interruption occurred under Rahim steel S/S
at Rahim steel feeder and was switched on at 17:20. |  |  |  | area from 12:16 to 17:20.
h) Ishurdi 132 kV bus-1 & 2 was under shut down from 10:30 to 12:02 for D/W.
i) Savar-Aminbazar 132 kV Ckt-2 was under shut down from 08:03 to 18:31 for D/W.
j) After maintenance Mymensingh-Jamalpur 132 kV Ckt-1 was switched on at 17:25.
k) Sikalbaha-Madunaghat 132 kV Ckt tripped at 15:44 from Sikalbaha end showing Dist Z3 and was
switched on at 16:08.
l) Barishal-Bhandaria 132 kV Ckt tripped at 16:40 from both end showing Dist B-phase Z1 at Barishal end & Dist
Z1 at Bhandaria end and was switched on at 16:46.
m) Sylhet 150 MW GT was synchronized at 19:58.
n) Bheramara HVDC pole-2 was De-blocked at 11:02 and was blocked at 17:45.
o) Bheramara HVDC pole-1 was blocked at 11:21 was De-blocked at 16:57.
p) Saidpur-Purbasadipur 132 kV Ckt-1 & 2 tripped at 19:49 from Saidpur end of Ckt-1 & Purbasadipur end of |  |  |  | About 200MW Power interruption occurred under Purbosadipur,Thakurgaon
Ckt-2 showing O/C Ckt-1 only and were switched on at 19:53 & 19:54 respectively. |  |  |  | & Panchagar S/S area from 19:49 to 19:53.
q) After maintenance Ashuganj ST Unit-3 was synchronized at 00:20(12/06/2018).
r) Ramganj 132/33 kV T1 transformer was energized at 01:25(12/06/2018).
s) Rampura 230/132 kV auto transformer was under shut down from 05:06 to 07:42 (12/06/2018) for C/M. |  |  |  | About 85 MW Power interruption occurred under Rampura S/S
area from 05:06 to 07:42(12/06/2018).
t) Jamalpur 33 kV bus & T1,T2 transformers were shut down at 05:15 (12/06/2018) for C/M.
u) Faridpur 132/33 kV T1 transformer was shut down at 07:15(12/06/2018) for C/M.
v) Ghorasal-Tongi 230 kV Ckt-1 was shut down at 07:57 (12/06/2018) for C/M.
w) Saidpur 132/33 kV T3 transformer was under shut down from 07:15 to 08:15 for red hot maintenance. |  |  |  | About 5 MW Power interruption occurred under Saidpur S/S
area from 07:15 to 08:15(12/06/2018).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 65 | 1364000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2754045 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 120 | 2677500 | Gas shortage
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 340 | 8635218
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 30 | 221088 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 35 | 214841 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 344 | 8574970 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 55 | 243900 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 261 | 6912000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 410 | 9218537 | frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1373760
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 200 | 5359418 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 65 | 1185144 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1036173
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 50 | 782164 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 425376
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 50 | 312000 | Low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 88 | 1366080 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 210 | 4920750 | On test.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 418610
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1143504
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 47 | 972720
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 833040
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2910720
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 1233253
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1185035
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 90 | 1416960 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1190940 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 791900
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 831000 | Engine problem
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 49 | 922068
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 270 | 5181271 | On test.
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 12 | 89840 | On test.
| Dhaka area Total |  |  |  | 5199 | 3674 | 76697825
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 8 | 268740 | Low demand
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 25 | 411840 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 123 | 2597032 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 195 | 4763492 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 50 | 1538196 | FGMO
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 432000
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 75 | 408664
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 81 | 504427
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1381080 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 357168 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 242400
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 939840 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 819 | 13844879
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Under maint.
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2384695 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 671206 | Gas shortage
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 182 | 4655000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 302 | 6014000 | FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 301 | 7597750 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 42 | 948672
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 78 | 1890182 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 974267
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1185144
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 48 | 361773
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 152 | 3465982
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 437688
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228420
** | Tripura |  | Imported power | 0 | 160 | 172 | 3399360
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 709900
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 8 | 220867 | Low demand
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 443720
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 10 | 88320 | On test.
| Comilla Area Total |  |  |  | 2541 | 1621 | 35796946
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 69 | 1901120 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 461880
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 82 | 617932 | Engine problem
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12870
| United Mymensingh PPL |  | IPP | 200 | 0 | 205 | 4831200 | On test.
| Mymensingh Area Total |  |  |  | 322 | 376 | 7825002
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1241000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 61 | 1456360
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 100 | 3263072 | frequency control.
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 306 | 6049260 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1047000
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 874000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 246144
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 63 | 1457000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 89 | 1528320
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 50 | 1037160
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 55 | 224780
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 43 | 906800 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 554472
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 285 | 7620250 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 213120
| Sylhet Area Total |  |  |  | 1549 | 1251 | 27718738
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 49 | 259300
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 481 | 8573091
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 102 | 1329600
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 93 | 1594560 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 40 | 494400
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 160 | 3472320 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 74 | 915456
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 776625
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 53 | 205530
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 88 | 620160 | On test.
| Khulna Area Total |  |  |  | 1769 | 1180 | 18241042
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 96 | 1343040 | Low demand
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 34 | 626960
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 191 | 4631307
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2185595
| Barisal Area Total |  |  |  | 462 | 418 | 8786902
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 473033
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 37 | 199968
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1082170
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 998304 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 47 | 611600
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | FGMO
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 170 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 42 | 539651
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 498720
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 191448
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 211842 | Engine problem
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 756480 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 1827232
| Rajshahi Area Total |  |  |  | 1123 | 609 | 7390448
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 67 | 1625891
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 260 | 5062000
117 | Rangpur GT |  | PDB | 1*20 | 20 | 15 | 117000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 160000
| Rangpur Area Total |  |  |  | 484 | 359 | 6964891
| Total |  |  |  | 15010 | 10307 | 203266673
| Eastern Grid Total |  |  |  | 11172 | 7741 | 161883390
| Western Grid Total |  |  |  | 3838 | 2566 | 41383283
| National Grid Total |  |  |  | 15010 | 10307 | 203266673
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-11 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6730 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3281 | MW
i) Dhaka area |  |  | 3932 | MW | i) Khulna area |  |  | 1284 | MW
ii) Chittagong area |  |  | 730 | MW | ii) Rajshahi area |  |  | 1136 | MW
iii) Comilla area |  |  | 902 | MW | iii) Barisal area |  |  | 233 | MW
iv) Mymensingh area |  |  | 758 | MW | iv) Rangpur area |  |  | 628 | MW
v) Sylhet area |  |  | 408 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10011 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 134 | 1100 | Kishorganj | 94 | 2000 | Central s/s | 68 | 2000
Munsiganj | 124 | 2100 | Netrokona | 83 | 2100 | Noapara | 84 | 1900
Megnaghat | 49 | 2400 | Jamalpur | 103 | 2300 | Jessore | 138 | 2000
Shyampur | 166 | 1200 | Sherpur | 91 | 2000 | Jhenida | 95 | 1930
Bhulta | 176 | 2000 | Srimongal | 29 | 2100 | Bottail | 128 | 2100
Madanganj | 51 | 100 | Shahjibazar | 95 | 2100 | G.K Project | 57 | 2200
Shitalakhya | 112 | 1100 | Fenchuganj | 51 | 2100 | Faridpur | 144 | 2300
Rahim steel | 7 | 900 | Kulawara | 34 | 100 | Madaripur | 134 | 2100
Matuail | 90 | 1200 | Sylhet | 149 | 100 | Gopalganj | 77 | 2200
Ghorasal | 77 | 2300 | Chatak | 25 | 200 | Bagerhat | 76 | 2100
Narsingdi | 122 | 2100 | Sunamganj | 25 | 200 | Mongla | 36 | 1500
Haripur (SBU) | 99 | 2300 | Comilla (S) | 176 | 1930 | Satkhira | 77 | 2100
Ullon | 99 | 2300 | Comilla(N) | 93 | 1900 | Gallamari | 45 | 2200
Hasnabad | 210 | 2100 | Chandpur | 126 | 2200 | Magura | 46 | 2200
Magbazar | 133 | 1400 | Feni | 98 | 1900 | Chuadanga | 78 | 2000
Maniknagar | 94 | 1300 | Chowmuhani | 192 | 2100 | Barisal | 116 | 2100
Bangabhaban | 36 | 1200 | Ashuganj | 47 | 2300 | Patuakhali | 80 | 2200
Narinda | 80 | 1200 | Daudkandi | 90 | 1900 | Bhandaria | 32 | 2300
Dhanmondi | 117 | 1500 | B.Baria | 122 | 2100 | Ishurdi | 56 | 2100
Lalbag | 88 | 1300 | Madunaghat | 42 | 1830 | Ruppur Paromanobik | 2 | 1100
Madartek | 51 | 2100 | Hathazari | 62 | 2000 | Natore | 117 | 2100
Mirpur | 104 | 2200 | Khulshi | 178 | 1500 | Bogra | 236 | 2100
Kalyanpur | 123 | 2100 | Halishahar | 118 | 1600 | Noagaon | 112 | 1200
Gulshan | 140 | 1400 | Baraulia | 127 | 1100 | Rajshahi | 139 | 2000
Uttara | 86 | 2000 | Sikalbaha | 30 | 2100 | C.Nawabganj | 69 | 2000
Kamrangirchar | 74 | 2000 | Dohazari | 20 | 1830 | Amnura | 36 | 300
Savar | 155 | 2100 | Cox'sbazar | 69 | 2000 | Pabna | 115 | 2000
Bhasantec | 145 | 2100 | Chandraghona | 26 | 1900 | Shahjadpur | 88 | 2100
Agargaon | 43 | 2000 | Kaptai | 3.5 | 2000 | Serajganj | 96 | 2000
Satmosjid | 101 | 2000 | A. Khaer Stl. | 7 | 1100 | Niyamatpur | 52 | 2100
Tongi | 135 | 2100 | Bakulia | 98 | 1500 | Joypurhat | 46 | 2000
Kabirpur | 197 | 1600 | Julda | 20 | 2100 | Rangpur | 124 | 2000
Basundhara | 122 | 1400 | TK chemical | 1 | 2100 | Lalmonirhat | 84 | 1930
Manikganj | 110 | 2000 | Modern Steel | 15 | 700 | Saidpur | 102 | 1930
Joydevpur | 224 | 2100 | Shahmirpur | 12 | 2100 | Purbasadipur | 90 | 1930
New Tongi | 108 | 1100 | Abul Khair 230 | 7 | 1200 | Thakurgaon | 69 | 1930
Korda | 212 | 1400 | BSRM | 114 | 1300 | Palashbari | 105 | 2100
Tangail | 186 | 2000 | Khagrachhari | 11 | 2000 | Barapukuria | 52 | 2100
Mymensing | 232 | 1930 | Goalpara | 45 | 2000 | Panchagar | 42 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-11
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 388 | 24:00 | 381 | 21:00 | Kaliakoir | 367 | 13:00 | 357 | 20:00
Bheramara | 409 | 6:00 | 400 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 223 | 3:00 | 215 | 7:00
Ishurdi | 232 | 11:00 | 215 | 21:00 | Comilla (N) | 229 | 5:00 | 225 | 9:00
Ashuganj | 235 | 7:00 | 229 | 18:00 | Hathazari | 221 | 19:30 | 210 | 15:00
Serajganj | 220 | 5:00 | 215 | 20:00 | Megnaghat | 228 | 5:00 | 222 | 9:00
Baghabari | 225 | 15:00 | 212 | 21:00 | Fenchuganj | 233 | 5:00 | 229 | 19:00
Barapukuria | 234 | 6:00 | 225 | 19:30 | Siddhirganj | 224 | 6:00 | 220 | 9:00
Bogra | 221 | 7:00 | 206 | 21:00 | Maniknagar | 221 | 3:00 | 217 | 9:00
Khulna South | 241 | 16:00 | 226 | 21:00 | Old Airport | 222 | 3:00 | 216 | 9:00
Rampura | 221 | 2:00 | 219 | 9:00 | Barisal | 238 | 16:00 | 231 | 3:00
Haripur | 220 | 1:00 | 219 | 9:00 | AKSML | 222 | 2:00 | 212 | 3:00
Hasnabad | 223 | 2:00 | 220 | 1:00 | BSRM | 223 | 3:00 | 214 | 14:00
Aminbazar | 223 | 3:00 | 218 | 9:00 | Bibiyana | 232 | 20:00 | 227 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 1900 | 130 | 900 | Madanhat | 135 | 100 | 128 | 1400
Munsiganj | 135 | 400 | 130 | 800 | Hathazari | 133 | 2000 | 126 | 1500
Megnaghat | 132 | 1100 | 129 | 700 | Khulshi | 130 | 2000 | 123 | 1300
Shyampur | 131 | 1900 | 122 | 1000 | Halishahar | 132 | 2100 | 126 | 1300
Bhulta | 132 | 400 | 127 | 2100 | Baraulia | 130 | 100 | 125 | 1300
Madanganj | 134 | 1200 | 126 | 900 | Sikalbaha | 133 | 2000 | 126 | 1400
Shitalakhya | 136 | 1900 | 128 | 900 | Dohazari | 132 | 600 | 126 | 1400
Rahim steal | 133 | 200 | 130 | 800 | Cox'sbazar | 128 | 500 | 120 | 1800
Matuail | 134 | 1930 | 128 | 900 | Chandraghona | 133 | 200 | 128 | 1400
Ghorasal | 135 | 100 | 132 | 1400 | Kaptai | 132 | 1830 | 130 | 900
Narsinghdi | 128 | 300 | 125 | 1500 | A. Khaer Stl. | 131 | 2100 | 126 | 900
Haripur (SBU) | 134 | 800 | 130 | 100 | Bakulia | 130 | 1930 | 124 | 1400
Ullon | 136 | 600 | 131 | 1400 | Julda | 131 | 1930 | 125 | 1200
Hasnabad | 133 | 2000 | 131 | 1200 | TK Chemical | 134 | 2000 | 127 | 1300
Magbazar | 136 | 600 | 130 | 1400 | Modern Steel | 131 | 2000 | 125 | 1100
Maniknagar | 134 | 600 | 131 | 1400 | Shahmirpur | 131 | 1930 | 126 | 1200
Bangabhaban | 131 | 600 | 131 | 900 | Khagrachhari | 133 | 2100 | 128 | 1200
Narinda | 135 | 600 | 131 | 1200 | Goalpara | 137 | 1600 | 131 | 300
Dhanmondi | 136 | 600 | 131 | 1400 | Central s/s | 138 | 1600 | 132 | 400
Lalbag | 131 | 600 | 125 | 900 | Noapara | 135 | 1600 | 126 | 2100
Madartek | 135 | 600 | 131 | 1200 | Jessore | 130 | 1600 | 117 | 2100
Mirpur | 135 | 200 | 129 | 900 | Jhenida | 127 | 1600 | 111 | 2100
Kalyanpur | 135 | 300 | 130 | 800 | Bottail | 135 | 1500 | 120 | 2100
Gulshan | 135 | 300 | 130 | 1400 | G.K.Project | 137 | 600 | 125 | 2100
Uttara | 131 | 300 | 125 | 1700 | Faridpur | 132 | 1600 | 122 | 2100
Kamrangirchar | 133 | 100 | 127 | 900 | Madaripur | 133 | 300 | 123 | 2100
Savar | 132 | 200 | 127 | 1700 | Gopalganj | 135 | 1700 | 123 | 1400
Bhasantec | 131 | 300 | 126 | 1700 | Bagerhat | 135 | 1600 | 129 | 500
Agargaon | 131 | 100 | 127 | 1700 | Mongla | 132 | 1600 | 126 | 2100
Satmosjid | 131 | 200 | 127 | 900 | Satkhira | 136 | 1600 | 128 | 2100
Tongi | 134 | 300 | 129 | 1700 | Gallamari | 138 | 1600 | 131 | 500
Kabirpur | 134 | 1400 | 129 | 2100 | Magura | 127 | 1600 | 108 | 2100
Basundhara | 130 | 100 | 125 | 900 | Chuadanga | 123 | 1800 | 102 | 2100
Manikganj | 138 | 1800 | 133 | 2100 | Barisal | 138 | 1600 | 132 | 2100
Joydevpur | 138 | 1300 | 133 | 2100 | Patuakhali | 138 | 1600 | 132 | 2100
New Tongi | 133 | 200 | 127 | 2000 | Bhandaria | 135 | 1000 | 127 | 300
Kodda | 137 | 400 | 130 | 1300 | Ishurdi | 140 | 1600 | 125 | 2100
Tangail | 134 | 700 | 125 | 2100 | Ruppur Paromanobik | 137 | 1700 | 126 | 2100
Mymensing | 128 | 600 | 117 | 2100 | Natore | 137 | 1600 | 122 | 2100
Kishorganj | 129 | 1400 | 119 | 2200 | Bogra | 131 | 700 | 119 | 2100
Netrokona | 130 | 600 | 115 | 100 | Noagaon | 128 | 1800 | 115 | 2100
Jamalpur | 135 | 1400 | 124 | 2100 | Rajshahi | 135 | 1600 | 119 | 2100
Sherpur | 133 | 1500 | 122 | 2100 | C.Nawabganj | 132 | 600 | 125 | 300
Srimongal | 134 | 1900 | 130 | 900 | Amnura | 138 | 1830 | 124 | 2100
Shahjibazar | 135 | 400 | 130 | 800 | Pabna | 131 | 1600 | 120 | 2100
Fenchuganj | 132 | 1100 | 129 | 700 | Shahjadpur | 138 | 1800 | 130 | 2100
Khulawara | 131 | 1900 | 122 | 1000 | Serajganj | 131 | 600 | 121 | 2100
Sylhet | 132 | 400 | 127 | 2100 | Niyamatpur | 129 | 1830 | 112 | 2100
Chatak | 134 | 1200 | 126 | 900 | Joypurhat | 127 | 1800 | 110 | 2100
Sunamganj | 136 | 1900 | 128 | 900 | Rangpur | 125 | 700 | 107 | 2100
Comilla(s) | 128 | 400 | 121 | 1930 | Lalmonirhat | 125 | 700 | 98 | 1930
Comilla(n) | 135 | 800 | 130 | 1200 | Saidpur | 125 | 600 | 104 | 2000
Chandpur | 130 | 1200 | 127 | 1800 | Purbasadipur | 134 | 700 | 118 | 1930
Feni | 123 | 2000 | 120 | 2100 | Thakurgaon | 128 | 700 | 110 | 1930
Chowmuhani | 125 | 700 | 122 | 2100 | Palashbari | 125 | 700 | 110 | 1900
Ashuganj | 135 | 100 | 132 | 1900 | Barapukuria | 134 | 600 | 125 | 1930
Daudkandi | 135 | 1930 | 129 | 900 | Panchagar | 127 | 2000 | 104 | 1930
B.Baria | 136 | 1100 | 130 | 2000
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-06-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 700 | 7414 | 2652 | 10066 |  |  |  | QF-LDC-12
0:30 | 670 | 7140.5 | 2539 | 9679.5 | Date: | 2018-06-11
1:00 | 640 | 6867 | 2426 | 9293
1:30 | 650 | 6726.5 | 2353 | 9079.5
2:00 | 660 | 6586 | 2280 | 8866
2:30 | 700 | 6601 | 2280 | 8881 | [5 empty] | Gen. at Eve. Peak | 10480 | 10480 MW (21:00 )
3:00 | 740 | 6616 | 2280 | 8896 | [6 empty] | 21:00
3:30 | 740 | 6582 | 2224.5 | 8806.5 | [5 empty] | Gen. at Day Peak | 8523.6 | 8523.6 MW (12:00 )
4:00 | 740 | 6548 | 2169 | 8717 | [6 empty] | 12:00
4:30 | 390 | 6308 | 2031 | 8339 | [5 empty] | Highest Generation | 10480
5:00 | 40 | 6068 | 1893 | 7961 | [6 empty] | 21:00
5:30 | 320 | 5848.05 | 1851.5 | 7699.55
6:00 | 600 | 5628.1 | 1810 | 7438.1
6:30 | 560 | 5573.35 | 1767 | 7340.35
7:00 | 520 | 5518.6 | 1724 | 7242.6
7:30 | 510 | 5609.15 | 1729.5 | 7338.65
8:00 | 500 | 5699.7 | 1735 | 7434.7
8:30 | 490 | 5807.9 | 1768.5 | 7576.4
9:00 | 480 | 5916.1 | 1802 | 7718.1
9:30 | 480 | 6071.8 | 1816.5 | 7888.3
10:00 | 480 | 6227.5 | 1831 | 8058.5
10:30 | 620 | 6474.6 | 1683.5 | 8158.1
11:00 | 760 | 6721.7 | 1536 | 8257.7
11:30 | 790 | 6867.65 | 1523 | 8390.65
12:00 | 820 | 7013.6 | 1510 | 8523.6
12:30 | 860 | 7093.45 | 1564.5 | 8657.95
13:00 | 900 | 7173.3 | 1619 | 8792.3
13:30 | 900 | 7214.05 | 1672 | 8886.05
14:00 | 900 | 7254.8 | 1725 | 8979.8
14:30 | 920 | 7302.7 | 1767 | 9069.7
15:00 | 940 | 7350.6 | 1809 | 9159.6
15:30 | 830 | 7265.3 | 1894 | 9159.3
16:00 | 720 | 7180 | 1979 | 9159
16:30 | 705 | 6893.85 | 1909 | 8802.85
17:00 | 690 | 6607.7 | 1839 | 8446.7
17:30 | 595 | 6569.35 | 1986 | 8555.35
18:00 | 500 | 6531 | 2133 | 8664
18:30 | 570 | 6646 | 2289 | 8935
19:00 | 640 | 6761 | 2445 | 9206
19:30 | 720 | 7435 | 2722 | 10157
20:00 | 680 | 7369 | 2703 | 10072 |  |  |  | Executive Engineer
20:30 | 700 | 7555 | 2721 | 10276 |  |  |  | Network Operation Division
21:00 | 720 | 7741 | 2739 | 10480
21:30 | 700 | 7684 | 2747.5 | 10431.5
22:00 | 680 | 7627 | 2756 | 10383 |  |  |  |  | Page 6 of 7
22:30 | 660 | 7538 | 2743.5 | 10281.5
23:00 | 640 | 7449 | 2731 | 10180
23:30 | 670 | 7431.5 | 2691.5 | 10123
24:00 | 700 | 7414 | 2652 | 10066
10480 MW (21:00 )
8523.6 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-11 |  | Energy | 212428718
[10 empty] | 2018-06-11 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3496 | 479 | 1869 | 2318 | 327 | 122 | 1289 | 0 | 166
0:30 | 3431 | 478 | 1893.5 | 2129.5 | 289.5 | 111.5 | 1187.5 | 0 | 159 | Date: | 2018-06-11
1:00 | 3366 | 477 | 1918 | 1941 | 252 | 101 | 1086 | 0 | 152
1:30 | 3337.5 | 477 | 1838.5 | 1848 | 252.5 | 101.5 | 1076.5 | 0 | 148 | [7 empty] | Total Energy | 212.4287 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3309 | 477 | 1759 | 1755 | 253 | 102 | 1067 | 0 | 144 | [7 empty] | Energy not Served | 0
2:30 | 3315 | 470 | 1790 | 1732 | 253 | 103 | 1073 | 0 | 145 | [7 empty] | Energy Requirement | 212.4287
3:00 | 3321 | 463 | 1821 | 1709 | 253 | 104 | 1079 | 0 | 146
3:30 | 3339.5 | 462.5 | 1826 | 1620 | 253.5 | 104 | 1061 | 0 | 140 | [6 empty] | Shortage
4:00 | 3358 | 462 | 1831 | 1531 | 254 | 104 | 1043 | 0 | 134
4:30 | 3382 | 462 | 1751 | 1303.5 | 254 | 104.5 | 957 | 0 | 125
5:00 | 3406 | 462 | 1671 | 1076 | 254 | 105 | 871 | 0 | 116
5:30 | 3390.5 | 462 | 1542.5 | 1019 | 253.5 | 106.5 | 812.5 | 0 | 113
6:00 | 3375 | 462 | 1414 | 962 | 253 | 108 | 754 | 0 | 110
6:30 | 3374.5 | 462 | 1364.5 | 932 | 252.5 | 108 | 737.5 | 0 | 109 |  |  |  |  | Coal
7:00 | 3374 | 462 | 1315 | 902 | 252 | 108 | 721 | 0 | 108
7:30 | 3433 | 462.5 | 1350.5 | 900.5 | 253 | 108.5 | 722 | 0 | 108 |  |  |  | Oil |  |  |  | ,
8:00 | 3492 | 463 | 1386 | 899 | 254 | 109 | 723 | 0 | 108
8:30 | 3530.5 | 462.5 | 1479.5 | 903.5 | 259 | 110 | 725.5 | 0 | 105
9:00 | 3569 | 462 | 1573 | 908 | 264 | 111 | 728 | 0 | 102
9:30 | 3484.5 | 423 | 1675 | 1094.5 | 264 | 112 | 726.5 | 0 | 108
10:00 | 3400 | 384 | 1777 | 1281 | 264 | 113 | 725 | 0 | 114
10:30 | 3400 | 242 | 1793 | 1508.5 | 264 | 114 | 721 | 0 | 115
11:00 | 3400 | 100 | 1809 | 1736 | 264 | 115 | 717 | 0 | 116
11:30 | 3448.5 | 75 | 1816.5 | 1821 | 263.5 | 114 | 728.5 | 0 | 122
12:00 | 3497 | 50 | 1824 | 1906 | 263 | 113 | 740 | 0 | 128
12:30 | 3549 | 52 | 1823 | 1950.5 | 256.5 | 113 | 785.5 | 0 | 126
13:00 | 3601 | 54 | 1822 | 1995 | 250 | 113 | 831 | 0 | 124
13:30 | 3601 | 54 | 1822 | 1995 | 250 | 113 | 831 | 0 | 124
14:00 | 3601 | 54 | 1822 | 1995 | 250 | 113 | 831 | 0 | 124
14:30 | 3591 | 73.5 | 1830 | 2136 | 256 | 113.5 | 843.5 | 0 | 131
15:00 | 3581 | 93 | 1838 | 2277 | 262 | 114 | 856 | 0 | 138
15:30 | 3585.5 | 148.5 | 1808.5 | 2211 | 269 | 114 | 880.5 | 0 | 142
16:00 | 3590 | 204 | 1779 | 2145 | 276 | 114 | 905 | 0 | 146
16:30 | 3613.5 | 207 | 1615 | 1890 | 282 | 115 | 941 | 0 | 139
17:00 | 3637 | 210 | 1451 | 1635 | 288 | 116 | 977 | 0 | 132
17:30 | 3611.5 | 288 | 1523 | 1567 | 297 | 117.5 | 1008 | 0 | 143
18:00 | 3586 | 366 | 1595 | 1499 | 306 | 119 | 1039 | 0 | 154
18:30 | 3578.5 | 409.5 | 1606 | 1554.5 | 311.5 | 120.5 | 1193.5 | 0 | 161
19:00 | 3571 | 453 | 1617 | 1610 | 317 | 122 | 1348 | 0 | 168
19:30 | 3513 | 453 | 1801 | 2328 | 317 | 122 | 1447 | 0 | 176
20:00 | 3507 | 453 | 1713 | 2373 | 317 | 123 | 1420 | 0 | 166
20:30 | 3519.5 | 467 | 1765 | 2503.5 | 322 | 123 | 1407 | 0 | 169
21:00 | 3532 | 481 | 1817 | 2634 | 327 | 123 | 1394 | 0 | 172
21:30 | 3526 | 480 | 1844 | 2554 | 327 | 123 | 1404 | 0 | 173.5
22:00 | 3520 | 479 | 1871 | 2474 | 327 | 123 | 1414 | 0 | 175
22:30 | 3505.5 | 479.5 | 1835 | 2439.5 | 327.5 | 123 | 1399 | 0 | 172.5
23:00 | 3491 | 480 | 1799 | 2405 | 328 | 123 | 1384 | 0 | 170
23:30 | 3493.5 | 479.5 | 1834 | 2361.5 | 327.5 | 122.5 | 1336.5 | 0 | 168 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 3496 | 479 | 1869 | 2318 | 327 | 122 | 1289 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 75 | 75 | 76 | 76 | 77 | 80 | 79 | 80 | 81 | 83 | 84 | 83 | 83 | 83 | 84 | 84 | 85 | 87 |  | 90 | 90 | 91 | 91 | 91 | 91 | 91 | 1883632
2 | Kaptai Unit-4 & 5 | 26 | 27 | 28 | 28 | 28 | 28 | 29 | 29 | 30 | 30 | 31 | 30 | 30 | 30 | 30 | 30 | 31 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 713400
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 26 | 26 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 0 | 8 | 8 | 0 |  |  | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 268740
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 193 | 194 | 195 | 195 | 195 | 195 | 195 | 207 | 207 | 195 | 195 | 209 | 210 | 211 | 203 | 201 | 215 | 204 |  | 204 | 204 | 194 | 195 | 196 | 194 | 195 | 4763492
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 70 | 70 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 80 | 80 | 50 | 50 | 50 |  | 50 | 110 | 80 | 50 | 50 | 50 | 70 | 1538196
| Dohazari Peaking | 17 | 17 | 17 | 17 | 17 | 0 | [11 empty] | 0 |  | 82 | 81 | 81 | 81 | 81 | 77 | 50 | 504427
12 | Hathazari peaking | [17 empty] | 15 |  | 81 | 81 | 81 | 75 | 75 | 49 | 49 | 408664
| Daudkandi bangla trak | [14 empty] | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 0 |  | 88320
14 | Daudkandi Peaking 52MW | [15 empty] | 2 | 49 | 49 |  | 49 | 48 | 48 | 48 | 49 | 48 | 0 | 361773
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 208 | 208 | 208 | 200 | 199 | 200 | 200 | 190 | 190 | 190 | 190 | 195 | 205 | 210 | 203 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 195 | 190 | 190 | 4920750
18 | Summit Gazipur | 302 | 302 | 302 | 302 | 150 | 100 | 49 | 49 | 49 | 80 | 195 | 279 | 300 | 294 | 301 | 300 | 165 | 117 |  | 122 | 150 | 168 | 270 | 288 | 288 | 301 | 5181271
19 | Ashuganj 195MW Modular | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1890182
20 | Ghorasal ST: Unit-1,2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1364000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2754045
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2677500
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 335 |  | 335 | 365 | 340 | 340 | 340 | 340 | 340 | 8635218
26
28 | Ashuganj ST: Unit- 3 | [25 empty] | 0
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384695
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | [19 empty] | 671206
32 | Ashuganj Engines TSK | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 39 | 36 | 36 | 36 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 948672
33 | Ashuganj CCPP 225 MW | 194 | 186 | 193 | 182 | 187 | 182 | 183 | 205 | 205 | 185 | 193 | 205 | 197 | 202 | 195 | 181 | 204 | 194 |  | 195 | 182 | 180 | 182 | 181 | 181 | 181 | 4655000
34 | Ashuganj CCPP(South) | 292 | 290 | 301 | 290 | 309 | 301 | 320 | 334 | 334 | 301 | 316 | 338 | 320 | 331 | 320 | 301 | 334 | 320 |  | 320 | 301 | 301 | 301 | 301 | 301 | 301 | 7597750
| Ashuganj CCPP(North) | 15 | 15 | 20 | 84 | 104 | 120 | 188 | 255 | 305 | 308 | 315 | 340 | 320 | 330 | 323 | 300 | 336 | 317 |  | 323 | 300 | 300 | 302 | 300 | 300 | 300 | 6014000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 152 | 152 | 152 | 152 | 153 | 153 | 153 | 153 | 153 | 153 | 153 |  | 152 | 152 | 152 | 152 | 153 | 152 | 152 | 3465982
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 370 | 345 | 350 | 345 | 340 | 340 | 345 | 365 | 380 | 370 | 345 | 365 | 390 | 365 | 360 | 345 | 350 | 370 |  | 348 | 347 | 355 | 344 | 345 | 342 | 342 | 8574970
40 | Meghnaghat CCPP 450MW | 450 | 400 | 400 | 400 | 400 | 350 | 350 | 370 | 420 | 450 | 450 | 450 | 430 | 430 | 430 | 430 | 350 | 350 |  | 330 | 430 | 360 | 410 | 410 | 410 | 410 | 9218537
41 | Haripur Power CCPP 360MW | 301 | 302 | 331 | 341 | 350 | 352 | 301 | 332 | 330 | 308 | 300 | 286 | 272 | 267 | 257 | 257 | 250 | 250 |  | 260 | 271 | 262 | 261 | 251 | 181 | 251 | 6912000
42 | Mymensingh RPCL 210MW | 89 | 89 | 87 | 90 | 103 | 103 | 102 | 88 | 88 | 87 | 87 | 85 | 84 | 79 | 78 | 78 | 68 | 63 |  | 62 | 67 | 72 | 69 | 69 | 70 | 71 | 1901120
43 | Haripur NEPC 110MW | [8 empty] | 0 | 8 | 13 | 13 | 14 | 13 | 13 | 13 | 13 | 13 |  | 13 | 32 | 55 | 55 | 13 | 13 | 0 | 243900
44 | Fenchugonj CCPP-1 | 57 | 54 | 56 | 55 | 54 | 54 | 54 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 28 | 60 | 1241000
45 | Fenchugonj CCPP-2 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 60 | 61 | 61 | 61 |  | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 1456360
46 | Shajibazar 330 MW | 255 | 252 | 250 | 241 | 250 | 244 | 259 | 259 | 266 | 146 | 153 | 178 | 273 | 312 | 310 | 376 | 323 | 311 |  | 329 | 303 | 298 | 306 | 301 | 297 | 302 | 6049260
47 | Shahjibazar GT: Unit- 8, 9 | 64 | 63 | 62 | 61 | 62 | 64 | 63 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 58 | 62 | 62 |  | 62 | 63 | 54 | 63 | 63 | 62 | 51 | 1457000
48 | Shahjibazar 86MW | 84 | 84 | 84 | 84 | 10 | 10 | 10 | 10 | 10 | 70 | 81 | 84 | 84 | 84 | 84 | 84 | 20 | 20 |  | 20 | 20 | 89 | 89 | 89 | 89 | 89 | 1528320
49 | Shahjibazar (EPL) 50MW | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 10 | 10 | 48 | 48 | 49 | 50 | 50 | 49 | 49 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1037160
50 | Sylhet GT 150 MW | [21 empty] | 15 | 55 | 54 | 68 | 68 | 224780
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 42 | 42 | 42 | 42 | 42 | 11 | 11 | 11 | 38 | 37 | 42 | 42 | 42 | 42 | 42 | 40 | 41 | 42 |  | 42 | 43 | 43 | 43 | 43 | 43 | 43 | 906800
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 213120
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246144
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 45 | 45 | 45 | 45 | 45 | 49 | 50 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1047000
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 554472
57 | Summit Bibiana- 2 | 320 | 300 | 320 | 310 | 300 | 290 | 300 | 320 | 330 | 310 | 290 | 320 | 320 | 320 | 335 | 280 | 270 | 320 |  | 315 | 295 | 240 | 285 | 285 | 275 | 280 | 7620250
58 | Southern 55MW | 55 | 55 | 13 | 17 | 36 | 55 | 55 | 50 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1185035
59 | Sikalbaha (Energis) | 8 | [8 empty] | 0 | 20 | 12 | 24 | 24 | 38 | 0 | 6 | 8 |  | 8 | 24 | 41 | 51 | 51 | 51 | 51 | 432000
60 | Barabkunda (Regent) | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 0 |  |  |  | 357168
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 |  | 22 | 0 |  | 22 | 22 | 22 | 22 | 425376
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 461880
63 | Tripura | 152 | 144 | 146 | 134 | 116 | 110 | 108 | 108 | 102 | 114 | 116 | 128 | 124 | 134 | 138 | 146 | 132 | 154 |  | 168 | 176 | 166 | 172 | 175 | 170 | 166 | 3399360
64 | Malancha, Ctg. EPZ (United) | 26 | 0 | 16 | 26 | 16 | 15 | 5 | 6 | 3 | 3 | 5 | 1 | 3 | 5 | 2 | 2 | 3 | 3 |  | 13 | 13 | 18 | 23 | 23 | 27 | 27 | 242400
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 437688
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 8 | 0 | 228420
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 709900
68 | Summit Comilla 25MW | 22 | 22 | 22 | 22 | 19 | 19 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 443720
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22 | 22 | 22 | 22 | 22 | 25 | 25 | 31 |  | 17 | 17 | 32 | 28 | 28 | 28 | 28 | 590940
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791900
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 831000
73 | Ghorashal (Regent) | [17 empty] | 32 |  | 35 | 35 | 35 | 35 | 35 | 34 | 34 | 214841
76 | Siddhirganj (Desh) | [9 empty] | 0 | 10 | 17 | 10 | 17 | 17 | 17 | 17 | 17 |  | 17 | 20 | 30 | 50 | 17 | 17 | 0 | 312000
77 | Siddhirganj (Dutch Bangla) | 40 | 40 | 40 | 15 | 7 | 7 | 7 | 7 | 7 | 10 | 65 | 87 | 65 | 78 | 86 | 84 | 50 | 50 |  | 50 | 85 | 80 | 88 | 88 | 88 | 88 | 1366080
78 | Gazipur (RPCL) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 41 | 41 | 41 | 33 | 33 | 33 | 37 | 24 | 24 |  | 24 | 26 | 40 | 49 | 0 | 0 | 19 | 922068
79 | Kodda 150MW | 149 | 149 | 149 | 149 | 130 | 84 | 84 | 84 | 84 | 100 | 100 | 100 | 100 | 100 | 100 | 115 | 115 | 115 |  | 115 | 125 | 149 | 149 | 149 | 149 | 149 | 2910720
80 | Jamalpur 95MW | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 |  | 16 | 48 | 48 | 82 | 91 | 91 | 95 | 617932
81 | Lakdhanvi 52 MW | [9 empty] | 0 | 13 | 20 | 25 | 25 | 25 | 25 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 220867
82 | Madanganj 102MW | 81 | 81 | 81 | 70 | 15 | 15 | 15 | 16 | 16 | 25 | 45 | 48 | 38 | 48 | 50 | 70 | 56 | 32 |  | 32 | 55 | 45 | 65 | 65 | 64 | 64 | 1185144
83 | Pagla (DPA ) | 10 | 11 | 11 | 10 | 10 | 10 | 10 | 11 | 10 | 17 | 21 | 20 | 20 | 20 | 21 | 21 | 10 | 10 |  | 10 | 51 | 51 | 51 | 50 | 10 | 10 | 418610
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 10 | 10 | 10 | 11 | 42 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 22 | 22 |  | 22 | 50 | 85 | 85 | 85 | 85 | 86 | 1185144
85 | Keraniganj (Powerpac) 100MW | 30 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 50 | 50 | 90 | 50 | 10 | 10 |  | 10 | 50 | 50 | 50 | 20 | 20 | 20 | 782164
86 | Meghnaghat CCPP(Summit) | 250 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 240 | 240 | 240 | 240 | 200 | 200 | 200 |  | 200 | 250 | 200 | 200 | 200 | 200 | 200 | 5359418
87 | Meghnaghat (IEL) | 41 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 17 | 82 | 90 | 91 | 93 | 100 | 100 | 80 | 30 |  | 37 | 100 | 100 | 100 | 100 | 100 | 100 | 1373760
88 | Ghorashal 78MW (MAX) | [17 empty] | 10 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 221088
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 40 | 40 | 40 | 40 | 40 | 15 | 15 | 15 | 15 | 50 | 50 | 60 | 80 | 80 | 80 | 80 | 80 | 90 |  | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 1381080
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 874000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 5 | 5 | 5 | 5 | 12 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 974267
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 15 | 48 | 48 | 48 | 48 | 94 | 94 | 50 | 50 |  | 50 | 102 | 102 | 102 | 102 | 102 | 50 | 1143504
95 | Patenga 50MW | 6 | 6 | 4 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 13 | 19 | 24 | 24 | 26 | 31 | 26 | 30 |  | 36 | 28 | 31 | 25 | 26 | 27 | 21 | 411840
96 | Chittagong ECPV 108 MW | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 15 | 42 | 34 | 45 | 40 | 40 | 44 | 44 | 44 |  | 44 | 76 | 90 | 98 | 98 | 98 | 98 | 939840
97 | Katpotti 51 MW | 45 | 48 | 47 | 48 | 12 | 12 | 12 | 12 | 12 | 24 | 48 | 48 | 48 | 47 | 48 | 47 | 48 | 47 |  | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 972720
98 | Bosila 108MW | 90 | 90 | 90 | 90 | 16 | 8 | 8 | 8 | 8 | 77 | 90 | 90 | 85 | 90 | 90 | 28 | 8 | 8 |  | 8 | 28 | 86 | 90 | 90 | 90 | 90 | 1416960
99 | Madanganj-55 MW | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 23 | 48 | 42 | 55 | 55 | 55 | 55 | 40 | 30 |  | 38 | 55 | 55 | 55 | 55 | 55 | 55 | 1036173
100 | Northern 55 MW | 56 | 56 | 55 | 56 | 56 | 36 | 36 | 36 | 36 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 56 | 37 |  | 37 | 55 | 56 | 56 | 55 | 55 | 55 | 1233253
101 | Kushiara 163 MW CCPP GT | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 100 | 100 |  | 100 | 163 | 100 | 100 | 163 | 163 | 163 | 3263072
102 | Sarishabari (Solar) | [5 empty] | 0.1 | 0.6 | 0.7 | 1.1 | 0.5 | 0.7 | 2.6 | 2.3 | 1.8 | 0.6 | 0 | 0.7 | 0 |  | 0 | [6 empty] | 12870
103 | Banco Energy 54MW | 36 | 36 | 36 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 36 | 36 | 36 | 36 | 54 | 36 | 36 |  | 54 | 54 | 7 | 54 | 54 | 54 | 54 | 833040
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [14 empty] | 12 | 11 | 10 | 12 |  | 12 | 12 | 12 | 12 | 0 |  |  | 89840
106 | United Mymensingh PPL | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 |  | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 4831200
112
113
114
115
116
117
118 | Eastern Zone Total | 6867 | 6586 | 6616 | 6548 | 6068 | 5628.1 | 5518.6 | 5699.7 | 5916.1 | 6227.5 | 6721.7 | 7013.6 | 7173.3 | 7254.8 | 7350.6 | 7180 | 6607.7 | 6531 |  | 6761 | 7435 | 7369 | 7741 | 7627 | 7449 | 7414 | 161883390
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 108 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 27 | 27 | 27 | 51 | 51 | 105 | 107 | 33 | 33 |  | 51 | 107 | 107 | 102 | 101 | 101 | 101 | 1329600
124 | Khulna (KPCL-2) | 99 | 99 | 99 | 68 | 18 | 16 | 16 | 16 | 16 | 49 | 58 | 66 | 66 | 66 | 66 | 66 | 69 | 87 |  | 90 | 87 | 87 | 93 | 89 | 97 | 87 | 1594560
125
126 | Khulna (Aggreko) 55MW | [19 empty] | 12 | 48 | 48 | 53 | 53 | 23 | 13 | 205530
127 | Faridpur Peaking | 40 | 40 | 40 | 40 | 40 | 40 | 3 | [10 empty] | 27 |  | 47 | 46 | 46 | 40 | 40 | 40 | 40 | 494400
128 | Khulna CCPP 225MW | 160 | 160 | 160 | 160 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 140 | 140 | 160 | 190 | 210 | 210 | 3472320
129
130
131
132
133
| Summit Barisal 110 MW | 80 | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 64 | 64 | 64 | 64 | 64 |  | 64 | 96 | 96 | 96 | 96 | 80 | 64 | 1343040
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 96 | 97 | 95 | 96 | 96 | 95 | 50 | 50 | 95 | 95 | 94 | 96 | 95 | 95 | 95 | 95 | 48 | 98 |  | 97 | 96 | 96 | 97 | 98 | 98 | 98 | 2185595
137 | Bhola CCPP 194MW | 195 | 195 | 194 | 195 | 193 | 190 | 192 | 196 | 194 | 193 | 193 | 190 | 188 | 190 | 189 | 183 | 190 | 191 |  | 187 | 191 | 191 | 191 | 182 | 189 | 194 | 4631307
| Bhola (Venture) 33MW | 31 | 29 | 28 | 27 | 27 | 25 | 22 | 20 | 19 | 21 | 21 | 22 | 21 | 26 | 25 | 26 | 26 | 23 |  | 28 | 30 | 30 | 34 | 34 | 37 | 31 | 626960
140 | Bangla Trak Noapara | 22 | [12 empty] | 30 | 30 | 30 | 30 | 10 |  | 10 | 89 | 89 | 88 | 83 | 85 | 86 | 620160
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 40 | 32 | 32 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 776625
142 | Gopalganj Peaking | 50 | 46 | 50 | 50 | 40 | 35 | 35 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 31 | 32 | 52 |  | 84 | 73 | 73 | 74 | 71 | 71 | 71 | 915456
143 | Bheramara GT-1,2,3 | [19 empty] | 49 | 49 | 49 | 49 | 49 | 33 | 33 | 259300
144
145 |  | 477 | 477 | 463 | 462 | 462 | 462 | 462 | 463 | 462 | 384 | 100 | 50 | 54 | 113 | 93 | 204 | 210 | 366 |  | 453 | 453 | 453 | 481 | 479 | 480 | 479 | 8573091
146 | Bheramara 360 MW
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 67 | 68 | 68 | 69 | 69 | 68 | 67 | 69 | 69 | 69 | 69 | 68 | 55 | 54 | 67 | 67 | 66 | 66 |  | 67 | 67 | 67 | 67 | 67 | 68 | 67 | 1625891
151 | Barapukuria Unit-3 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 209 | 222 | 240 |  | 250 | 250 | 250 | 260 | 260 | 260 | 260 | 5062000
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | [12 empty] | 30 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 473033
| Sirajgonj Unit-1 225MW (Gas) | 194 | 179 | 186 | 182 | 178 | 175 | 179 | 195 | 196 | 195 | 188 | 194 | 198 | 191 | 191 | 179 | 181 | 193 |  | 185 | 191 | 183 | 173 | 182 | 175 | 175 | 4716918
157 | Sirajgonj Unit-1 225MW (Oil) | [12 empty] | 0
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 187 | 172 | 179 | 175 | 172 | 169 | 173 | 187 | 192 | 185 | 177 | 186 | 192 | 184 | 184 | 172 | 175 | 186 |  | 178 | 185 | 176 | 170 | 165 | 165 | 163 | 4445127
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | [15 empty] | 9 | 9 | 9 |  | 37 | 37 | 37 | 37 | 37 | 37 | 0 | 199968
161 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 18 | 18 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 498720
162 | Bogra (EPL) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 191448
163 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 0 | 10 | 11 | 11 | 211842
164 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1082170
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 998304
166 | Katakhali Peaking | 45 | 45 | 45 | 45 | 26 | 0 | 0 | [7 empty] | 27 | 42 | 43 | 43 |  | 47 | 47 | 47 | 47 | 43 | 43 | 43 | 611600
167 | Santahar Peaking | 41 | 41 | 41 | 41 | 0 | 0 | 0 | [8 empty] | 35 | 41 | 41 |  | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 539651
168 | Rajlanka 52 MW | 43 | 43 | 43 | 43 | 43 | 16 | 16 | 16 | 16 | 16 | 16 | 22 | 34 | 34 | 43 | 43 | 8 | 8 |  | 8 | 43 | 43 | 43 | 43 | 43 | 43 | 756480
169 | Chapainawabganj-100 MW | 101 | 101 | 101 | 101 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 85 | 85 | 85 | 85 | 85 | 85 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1827232
170
171
172 | Rangpur GT | 15 | 14 | 14 | 0 | [16 empty] | 17 | 15 | 15 | 15 | 13 | 13 | 117000
173 | Saidpur GT | 18 | 18 | 18 | 0 | [15 empty] | 18 | 17 | 17 | 17 | 17 | 18 | 17 | 160000
175
176
177
178 | Western Zone Total | 2426 | 2280 | 2280 | 2169 | 1893 | 1810 | 1724 | 1735 | 1802 | 1831 | 1536 | 1510 | 1619 | 1725 | 1809 | 1979 | 1839 | 2133 |  | 2445 | 2722 | 2703 | 2739 | 2756 | 2731 | 2652 | 50545328
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953