## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-14 | Thursday
|  | Date (day): | 2018-06-14 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11222 | MW |  |  | (b) At Evening Peak Hour : |  | 12363 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-13 | 2018-06-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 |  | 50 | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 260 | 260 | 260 | 350
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 77 | 40 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 25 | 106 | 102 | 102 | 6
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 20 | 20 | 20 | 20 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 380 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 84 | 84 |  | 26 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 342 | 331 | 350 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 380 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 55 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 200 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 48 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 50 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 199 | 120 | 120 | 120 | 90 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 40 | 84 | 88 |  | 12 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 210 | 210 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 10 | 10 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 50 | 94 | 102 |  | 0
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 24 | 48 | 49 | 49
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 25 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 100 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 54 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 100 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 56 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 30 | 26 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 50 | 51 | 51
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 105 | 298 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 0 | 0 | 100 |  |  | On test
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2515 | 3228 | 4115 | 4365 | 421 | 480
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 26 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 35 | 44 | 44 |  | 5 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 148 | 191 | 192 | 192 |  | 38
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 202 | 195 | 215 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 51 | 51 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 74 | 85 | 85
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 81 | 62 | 80
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 90 | 90 | 90 |  |  | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 42 | 15 | 40
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 18 | 98 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 530 | 902 | 896 | 949 | 360 | 93
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100 |  |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 130 | 100 | 100 | 100 |  |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint.
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 195 | 197 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 320 | 300 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 272 | 316 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 41 | 42 | 42
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 78 | 78 | 117 |  | Gas shortage
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 20 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 5 | 41 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 153 | 154 | 154 | 154
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 126 | 178 | 138 | 183
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 22 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200 |  |  | On test
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1518 | 1660 | 1780 | 2135 | 160 | 189
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 49 | 96 | 100 | 100 | 102 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 92 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.4 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 205 | 205 | 205 | 205
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 275.4 | 413 | 424 | 422 | 102 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 61 | 61
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 130 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 310 | 314 | 310 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 50 | 50
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 62 | 66 | 66
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 50 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 20 | 48 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 80 | 80 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 20 | 20 | 20
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 40 | 43 | 44 | 44
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 20 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1133 | 1273 | 1424 | 1464 | 0 | 0
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 48 | 0 | 49
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 477 | 474 | 487 | 487
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 102 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 34 | 41 | 46
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 226 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 9 | 60 | 50 | 74
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 360 | Under maint. |  | 27/06/2018
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 33 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 12 | 0 | 55
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 68 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 640 | 1172 | 1068 | 1301 | 0 | 360
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 112 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 37 | 35 | 35
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 172 | 186 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 20 | 98 | 96 | 98
| Barisal Area Total |  |  |  |  | 472 | 462 | 232 | 433 | 435 | 467 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 45 | 0 | 47
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 35 | 35 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 45 | 47
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 213 | 215 | 215 | 215
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 145 | 171 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 0 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 9 | 11 | 11 | 11
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 102 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 507 | 835 | 760 | 897 | 71 | 116
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 66 | 65 | 70 | 70
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 174 | 250 | 250 | 260
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 15
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 18 | 17 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 258 | 347 | 320 | 363 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 7608.4 | 10263 | 11222 | 12363 | 1114 | 1323
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7278.5025 | 9818 | 10735.4181 | 11826.9448
A. |  | 2018-06-13 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10276 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6865.4 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10263 | MW
3 | Day peak Generation : |  |  | 7608.4 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9818 | MW
4 | Evening peak Generation : |  |  | 10263 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 200.3069 | MKWHr | By Solar | 0.0106 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 119.2395 | MKWHr |  | By Oil: | 55.5219 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 7.1143 | MKWHr |  | By Hydro: | 3.7404 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1114 | MW | Dhaka | 3478 | 3478 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1323 | MW | Chittagong | 923 | 923 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2437 | MW | Khulna | 1272 | 1272 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1022.38 | MMCFD |  |  | Rajshahi | 1076 | 1076 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 88686685.928 | ii) Oil : | Taka | 457628055.55 | Comilla | 960 | 960 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 9381792 | Total | Taka | 555696533.478 | Mymensingh | 795 | 795 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 9.8655 | MKWHr. | Sylhet | 423 | 423 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -700 | MW at | 21:00 | hrs | Barisal | 249 | 249 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -730 | MW at | 19:30 | hrs | Rangpur | 642 | 642 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.5° C |  |  | Total | 9818 | 9818 |  | 0
B. |  | 2018-06-14 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 37.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12363 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 1863 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 204.6732 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7472.6 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.3825 | MKWHr. | ii) HVDC Flow at Peak Time |  | 474 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2976 | MKWHr. | iii) Maximum HVDC Flow : |  | 483 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.7 |  | (b) Today: | 91.7 |  | (c) Rule Curve: |  | 79.14
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-06-13
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 120 | 0 | 0 | 200 | 104 | 79 | 342 | 330 | 0 | 0 | 380 | 200 | 7 | 30 | 15 | 185 | 0 | 0 | 0 | 7 | 7 | 133 | 40 | 8 | 0 | 0 | 0 | 18 | 0 | 22 | 25 | 17 | 25 | 33 | 50 | 0 | 70 | 38 | 0 | 0 | 0 | 0 | 201 | 0 | 80 | 0 | 24 | 0 | 17 | 80 | 32 | 13 | 0 | 40 | 100 | 100 | 0 | 251 | 253 | 182 | 78 | 154 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 0 | 33 | 22 | 134 | 89 | 56 | 20 | 0 | 66 | 30 | 53 | 50 | 100 | 299 | 61 | 89 | 50 | 78 | 0 | 43 | 9 | 280 | 22 | 11 | 0 | 206 | 0 | 0 | 205 |  | 483 | 0 | 0 | 81 | 99 | 140 | 0 | 0 | 42 | 60 | 40 | 191 | 32 | 64 | 0 | 0 | 0 | 43 | 0 | 102 | 50 | 35 | 45 | 43 | 41 | 22 | 11 | 11 | 0 | 48 | 250 | 14 | 18 | 219 | 0 | 0 | 222 | 96 | 87 | 0 | 0 |  | 6298 | 2589 | 8887 | 3222 | 483 | 1987 | 1497 | 298 | 108 | 1158 | 134 | 0 | 0 | 90.7
2:00 | 0 | 120 | 0 | 0 | 200 | 104 | 80 | 342 | 346 | 0 | 0 | 380 | 200 | 7 | 30 | 15 | 185 | 0 | 0 | 0 | 7 | 7 | 133 | 10 | 8 | 0 | 0 | 0 | 18 | 17 | 0 | 25 | 17 | 25 | 33 | 50 | 0 | 70 | 63 | 0 | 0 | 0 | 0 | 201 | 0 | 60 | 0 | 24 | 0 | 17 | 80 | 32 | 17 | 16 | 42 | 100 | 100 | 0 | 251 | 257 | 182 | 78 | 154 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 0 | 33 | 22 | 136 | 89 | 8 | 20 | 0 | 66 | 30 | 53 | 50 | 100 | 299 | 63 | 89 | 50 | 77 | 0 | 43 | 9 | 290 | 21 | 11 | 0 | 205 | 0 | 0 | 205 |  | 482 | 0 | 0 | 10 | 99 | 120 | 0 | 0 | 42 | 60 | 40 | 187 | 33 | 64 | 0 | 0 | 0 | 43 | 0 | 102 | 50 | 35 | 45 | 8 | 41 | 22 | 11 | 11 | 0 | 49 | 250 | 14 | 18 | 218 | 0 | 0 | 223 | 97 | 50 | 0 | 0 |  | 6274 | 2424 | 8698 | 3215 | 482 | 2018 | 1296 | 299 | 133 | 1119 | 136 | 0 | 0 | 90.9
3:00 | 0 | 120 | 0 | 0 | 200 | 104 | 79 | 342 | 354 | 0 | 0 | 380 | 200 | 7 | 30 | 15 | 185 | 0 | 0 | 0 | 7 | 7 | 133 | 10 | 8 | 0 | 0 | 0 | 18 | 0 | 0 | 25 | 17 | 25 | 33 | 50 | 0 | 70 | 65 | 0 | 0 | 0 | 0 | 201 | 0 | 60 | 0 | 24 | 0 | 17 | 50 | 32 | 18 | 19 | 42 | 100 | 100 | 0 | 251 | 257 | 187 | 78 | 154 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 5 | 33 | 22 | 140 | 89 | 8 | 20 | 0 | 66 | 30 | 53 | 50 | 100 | 308 | 64 | 60 | 50 | 78 | 0 | 43 | 9 | 280 | 20 | 11 | 0 | 189 | 0 | 0 | 205 |  | 482 | 0 | 0 | 10 | 99 | 120 | 0 | 0 | 42 | 54 | 40 | 192 | 33 | 64 | 0 | 0 | 0 | 43 | 0 | 102 | 50 | 35 | 45 | 8 | 41 | 22 | 11 | 11 | 0 | 63 | 250 | 14 | 18 | 217 | 0 | 0 | 223 | 97 | 50 | 0 | 0 |  | 6209 | 2436 | 8645 | 3242 | 482 | 1986 | 1234 | 313 | 135 | 1113 | 140 | 0 | 0 | 91.1
4:00 | 0 | 120 | 0 | 0 | 200 | 104 | 79 | 342 | 354 | 0 | 0 | 360 | 200 | 7 | 30 | 15 | 185 | 0 | 0 | 0 | 7 | 7 | 133 | 10 | 8 | 0 | 0 | 0 | 18 | 17 | 0 | 25 | 17 | 25 | 33 | 25 | 0 | 72 | 64 | 0 | 0 | 0 | 0 | 195 | 0 | 60 | 0 | 8 | 0 | 17 | 30 | 18 | 18 | 19 | 42 | 100 | 100 | 0 | 251 | 253 | 183 | 78 | 154 | 42 | 0 | 5 | 40 | 85 | 0 | 0 | 19 | 5 | 8 | 22 | 130 | 103 | 8 | 20 | 0 | 66 | 30 | 53 | 50 | 100 | 302 | 52 | 30 | 50 | 78 | 0 | 7 | 9 | 280 | 20 | 11 | 0 | 189 | 0 | 0 | 205 |  | 482 | 0 | 0 | 10 | 99 | 120 | 0 | 0 | 42 | 48 | 40 | 191 | 30 | 64 | 0 | 0 | 0 | 43 | 0 | 102 | 50 | 35 | 45 | 8 | 41 | 22 | 10 | 11 | 0 | 66 | 250 | 0 | 18 | 217 | 0 | 0 | 223 | 96 | 0 | 0 | 0 |  | 6002 | 2363 | 8365 | 3204 | 482 | 1884 | 1126 | 316 | 136 | 1087 | 130 | 0 | 0 | 91.3
5:00 | 0 | 120 | 0 | 0 | 150 | 25 | 40 | 342 | 354 | 0 | 0 | 360 | 200 | 7 | 15 | 15 | 185 | 0 | 0 | 0 | 7 | 7 | 130 | 10 | 8 | 0 | 0 | 0 | 18 | 17 | 19 | 25 | 17 | 25 | 33 | 8 | 0 | 73 | 66 | 0 | 0 | 0 | 0 | 195 | 0 | 60 | 0 | 8 | 0 | 0 | 20 | 18 | 18 | 19 | 42 | 100 | 100 | 0 | 251 | 246 | 183 | 78 | 154 | 41 | 0 | 5 | 5 | 30 | 0 | 0 | 19 | 5 | 8 | 22 | 108 | 104 | 8 | 20 | 0 | 60 | 30 | 5 | 10 | 100 | 301 | 63 | 30 | 5 | 77 | 0 | 7 | 9 | 280 | 20 | 11 | 0 | 188 | 0 | 0 | 205 |  | 482 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 184 | 27 | 26 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 8 | 45 | 8 | 0 | 22 | 10 | 8 | 0 | 67 | 250 | 0 | 18 | 217 | 0 | 0 | 220 | 96 | 0 | 0 | 0 |  | 5544 | 1964 | 7508 | 3159 | 482 | 1540 | 865 | 317 | 139 | 898 | 108 | 0 | 0 | 91.5
6:00 | 0 | 120 | 0 | 0 | 100 | 25 | 40 | 280 | 321 | 0 | 0 | 330 | 200 | 7 | 15 | 15 | 185 | 0 | 0 | 0 | 7 | 7 | 115 | 10 | 8 | 0 | 0 | 0 | 18 | 17 | 0 | 25 | 17 | 25 | 33 | 8 | 0 | 73 | 68 | 0 | 0 | 0 | 0 | 195 | 0 | 60 | 0 | 8 | 0 | 0 | 20 | 18 | 6 | 19 | 34 | 100 | 100 | 0 | 251 | 246 | 184 | 78 | 154 | 10 | 0 | 5 | 5 | 6 | 0 | 0 | 0 | 5 | 8 | 22 | 116 | 104 | 8 | 0 | 0.2 | 60 | 30 | 5 | 10 | 100 | 309 | 62 | 5 | 5 | 78 | 0 | 7 | 9 | 280 | 20 | 11 | 0 | 188 | 0 | 0 | 205 |  | 482 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 192 | 25 | 17 | 0 | 0 | 0 | 0 | 0 | 102 | 12 | 8 | 0 | 8 | 0 | 22 | 10 | 8 | 0 | 67 | 250 | 0 | 0 | 217 | 0 | 0 | 171 | 41 | 0 | 0 | 0 |  | 5215.2 | 1794 | 7009.2 | 2975 | 482 | 1363 | 844 | 317 | 141 | 771 | 116 | 0.2 | 0 | 91.7
7:00 | 0 | 120 | 0 | 0 | 100 | 26 | 20 | 280 | 301 | 0 | 0 | 300 | 200 | 7 | 15 | 15 | 190 | 0 | 0 | 0 | 7 | 7 | 115 | 10 | 8 | 0 | 0 | 0 | 18 | 17 | 0 | 25 | 17 | 25 | 33 | 8 | 0 | 77 | 69 | 0 | 0 | 0 | 0 | 195 | 0 | 60 | 0 | 8 | 0 | 0 | 20 | 18 | 6 | 19 | 8 | 100 | 100 | 0 | 255 | 253 | 189 | 78 | 154 | 10 | 0 | 5 | 5 | 6 | 0 | 0 | 0 | 5 | 8 | 22 | 114 | 103 | 8 | 0 | 0.3 | 60 | 30 | 5 | 10 | 100 | 311 | 62 | 5 | 5 | 78 | 0 | 7 | 9 | 300 | 20 | 11 | 0 | 188 | 0 | 0 | 205 |  | 483 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 192 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 65 | 250 | 0 | 0 | 218 | 0 | 0 | 142 | 41 | 0 | 0 | 0 |  | 5165.3 | 1723 | 6888.3 | 2998 | 483 | 1288 | 878 | 315 | 146 | 666 | 114 | 0.3 | 0 | 91.9
8:00 | 0 | 120 | 0 | 0 | 100 | 26 | 20 | 280 | 302 | 0 | 0 | 300 | 200 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 16 | 7 | 115 | 10 | 8 | 0 | 0 | 12 | 18 | 17 | 0 | 25 | 28 | 25 | 33 | 11 | 0 | 78 | 70 | 0 | 0 | 0 | 0 | 202 | 0 | 60 | 0 | 8 | 0 | 0 | 20 | 18 | 6 | 19 | 6 | 100 | 100 | 0 | 280 | 279 | 204 | 78 | 154 | 10 | 0 | 5 | 5 | 5 | 0 | 0 | 0 | 5 | 8 | 22 | 100 | 103 | 8 | 0 | 0.4 | 60 | 30 | 5 | 29 | 100 | 321 | 62 | 5 | 5 | 78 | 0 | 43 | 9 | 320 | 20 | 11 | 0 | 185 | 0 | 0 | 205 |  | 476 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 192 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 16 | 0 | 43 | 0 | 22 | 10 | 8 | 0 | 68 | 250 | 0 | 0 | 217 | 0 | 0 | 145 | 41 | 0 | 0 | 0 |  | 5151.4 | 1714 | 6865.4 | 2894 | 476 | 1359 | 920 | 318 | 148 | 650 | 100 | 0.4 | 0 | 92.1
9:00 | 0 | 120 | 0 | 0 | 140 | 26 | 20 | 365 | 346 | 0 | 0 | 400 | 250 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 30 | 7 | 115 | 10 | 8 | 0 | 0 | 18 | 18 | 17 | 0 | 25 | 28 | 25 | 33 | 25 | 0 | 78 | 70 | 0 | 0 | 0 | 0 | 195 | 0 | 60 | 0 | 11 | 0 | 0 | 60 | 18 | 6 | 19 | 6 | 100 | 100 | 0 | 260 | 253 | 192 | 78 | 153 | 32 | 0 | 5 | 12 | 30 | 0 | 0 | 13 | 5 | 33 | 22 | 106 | 103 | 8 | 0 | 0.3 | 60 | 30 | 11 | 50 | 130 | 306 | 62 | 30 | 20 | 80 | 0 | 43 | 9 | 320 | 20 | 11 | 0 | 190 | 0 | 0 | 205 |  | 476 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 9 | 8 | 192 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 0 | 43 | 0 | 10 | 10 | 8 | 0 | 68 | 250 | 0 | 0 | 0 | 0 | 0 | 145 | 41 | 0 | 0 | 0 |  | 5668.3 | 1493 | 7161.3 | 2790 | 476 | 1619 | 1060 | 318 | 148 | 644 | 106 | 0.3 | 0 | 92.3
10:00 | 0 | 120 | 0 | 0 | 140 | 26 | 20 | 350 | 317 | 0 | 0 | 370 | 200 | 7 | 15 | 15 | 0 | 0 | 57 | 0 | 7 | 7 | 115 | 10 | 8 | 10 | 24 | 18 | 18 | 36 | 19 | 25 | 28 | 25 | 30 | 25 | 0 | 79 | 71 | 0 | 0 | 0 | 0 | 202 | 0 | 60 | 0 | 38 | 0 | 0 | 80 | 18 | 6 | 19 | 8 | 100 | 100 | 0 | 250 | 246 | 183 | 78 | 154 | 32 | 0 | 5 | 51 | 31 | 0 | 0 | 19 | 5 | 33 | 16 | 114 | 71 | 0 | 20 | 0.4 | 60 | 30 | 11 | 50 | 130 | 302 | 62 | 30 | 20 | 80 | 0 | 43 | 9 | 300 | 20 | 11 | 0 | 190 | 0 | 0 | 205 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 9 | 8 | 192 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 0 | 25 | 0 | 18 | 10 | 8 | 0 | 67 | 250 | 0 | 0 | 59 | 0 | 0 | 145 | 40 | 0 | 0 | 0 |  | 5684.4 | 1540 | 7224.4 | 2866 | 477 | 1588 | 1061 | 317 | 150 | 651 | 114 | 0.4 | 0 | 92.5
11:00 | 0 | 120 | 0 | 0 | 260 | 25 | 20 | 300 | 302 | 0 | 0 | 380 | 200 | 7 | 15 | 15 | 0 | 0 | 99 | 0 | 7 | 7 | 100 | 10 | 8 | 10 | 24 | 18 | 54 | 36 | 19 | 25 | 28 | 25 | 30 | 25 | 0 | 79 | 74 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 42 | 0 | 0 | 80 | 23 | 5 | 19 | 6 | 100 | 100 | 0 | 295 | 264 | 220 | 78 | 154 | 39 | 0 | 5 | 51 | 5 | 0 | 0 | 0 | 0 | 33 | 16 | 118 | 49 | 0 | 20 | 1 | 60 | 30 | 11 | 50 | 100 | 316 | 62 | 20 | 20 | 80 | 0 | 41 | 9 | 290 | 20 | 11 | 0 | 150 | 0 | 0 | 205 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 9 | 8 | 171 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 0 | 25 | 0 | 18 | 10 | 8 | 0 | 67 | 249 | 0 | 0 | 182 | 0 | 0 | 145 | 21 | 0 | 0 | 0 |  | 5722 | 1623 | 7345 | 3155 | 477 | 1484 | 1065 | 316 | 153 | 576 | 118 | 1 | 0 | 92.7
12:00 | 0 | 120 | 0 | 0 | 260 | 25 | 20 | 360 | 342 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 0 | 0 | 199 | 0 | 7 | 7 | 100 | 10 | 8 | 10 | 24 | 25 | 54 | 36 | 22 | 25 | 31 | 33 | 30 | 25 | 0 | 77 | 71 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 51 | 0 | 0 | 80 | 18 | 6 | 19 | 6 | 100 | 130 | 0 | 315 | 272 | 195 | 78 | 153 | 39 | 0 | 5 | 51 | 5 | 0 | 0 | 0 | 0 | 33 | 16 | 126 | 49 | 0 | 20 | 1.4 | 60 | 30 | 11 | 50 | 100 | 310 | 62 | 20 | 20 | 80 | 0 | 40 | 9 | 310 | 20 | 11 | 0 | 105 | 0 | 0 | 205 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 9 | 8 | 172 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 25 | 0 | 22 | 9 | 8 | 0 | 66 | 174 | 0 | 18 | 213 | 0 | 0 | 145 | 20 | 0 | 0 | 0 |  | 5971.4 | 1637 | 7608.4 | 3387 | 477 | 1567 | 1068 | 240 | 148 | 594 | 126 | 1.4 | 0 | 92.9
13:00 | 0 | 120 | 0 | 0 | 260 | 25 | 20 | 345 | 344 | 0 | 20 | 400 | 200 | 7 | 15 | 26 | 0 | 0 | 201 | 0 | 7 | 24 | 100 | 10 | 8 | 10 | 44 | 36 | 54 | 36 | 22 | 25 | 31 | 33 | 25 | 25 | 0 | 75 | 66 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 51 | 0 | 0 | 80 | 18 | 6 | 19 | 16 | 100 | 150 | 0 | 300 | 300 | 183 | 78 | 153 | 39 | 0 | 5 | 51 | 5 | 8 | 0 | 0 | 0 | 33 | 16 | 132 | 49 | 0 | 20 | 1.3 | 60 | 30 | 11 | 50 | 130 | 304 | 62 | 20 | 20 | 80 | 0 | 40 | 9 | 310 | 7 | 11 | 0 | 115 | 0 | 0 | 205 |  | 476 | 0 | 0 | 51 | 0 | 120 | 0 | 0 | 0 | 9 | 8 | 172 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 25 | 0 | 22 | 9 | 8 | 0 | 64 | 150 | 0 | 18 | 213 | 0 | 0 | 145 | 21 | 0 | 0 | 0 |  | 6093.3 | 1635 | 7728.3 | 3391 | 476 | 1609 | 1162 | 214 | 141 | 602 | 132 | 1.3 | 0 | 93.05
14:00 | 0 | 120 | 0 | 0 | 260 | 57 | 30 | 360 | 343 | 0 | 20 | 420 | 200 | 7 | 15 | 30 | 0 | 0 | 170 | 0 | 7 | 24 | 100 | 10 | 8 | 10 | 48 | 36 | 56 | 36 | 22 | 25 | 31 | 33 | 30 | 25 | 0 | 73 | 67 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 | 47 | 8 | 0 | 80 | 22 | 6 | 19 | 3 | 100 | 150 | 0 | 330 | 327 | 202 | 78 | 155 | 42 | 0 | 5 | 51 | 30 | 0 | 0 | 0 | 0 | 33 | 16 | 140 | 49 | 0 | 20 | 1 | 60 | 30 | 17 | 50 | 163 | 319 | 62 | 20 | 20 | 80 | 12 | 42 | 9 | 300 | 12 | 11 | 0 | 115 | 0 | 0 | 205 |  | 477 | 0 | 0 | 81 | 36 | 120 | 0 | 0 | 0 | 8 | 8 | 172 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 43 | 0 | 22 | 9 | 8 | 0 | 66 | 150 | 0 | 16 | 213 | 0 | 0 | 143 | 51 | 0 | 0 | 0 |  | 6330 | 1747 | 8077 | 3493 | 477 | 1743 | 1256 | 216 | 140 | 611 | 140 | 1 | 0 | 93.15
15:00 | 0 | 120 | 0 | 0 | 260 | 102 | 40 | 360 | 344 | 0 | 20 | 450 | 220 | 7 | 15 | 32 | 0 | 0 | 203 | 0 | 7 | 102 | 100 | 88 | 51 | 10 | 48 | 54 | 56 | 45 | 22 | 25 | 31 | 33 | 30 | 25 | 0 | 73 | 67 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 6 | 16 | 5 | 100 | 110 | 0 | 300 | 279 | 183 | 78 | 154 | 42 | 0 | 5 | 50 | 60 | 0 | 0 | 16 | 8 | 33 | 16 | 140 | 49 | 0 | 20 | 1.3 | 60 | 30 | 47 | 55 | 130 | 301 | 59 | 60 | 48 | 78 | 12 | 41 | 7 | 290 | 8 | 11 | 0 | 115 | 0 | 0 | 205 |  | 476 | 0 | 0 | 81 | 106 | 120 | 0 | 0 | 0 | 10 | 8 | 180 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 50 | 35 | 0 | 43 | 0 | 22 | 12 | 8 | 0 | 65 | 150 | 0 | 14 | 214 | 0 | 0 | 148 | 71 | 0 | 0 | 0 |  | 6568.3 | 1895 | 8463.3 | 3391 | 476 | 1943 | 1524 | 215 | 140 | 633 | 140 | 1.3 | 0 | 93.25
16:00 | 0 | 120 | 0 | 0 | 260 | 106 | 70 | 340 | 345 | 0 | 20 | 450 | 200 | 7 | 15 | 55 | 0 | 0 | 203 | 0 | 7 | 102 | 100 | 100 | 15 | 10 | 6 | 18 | 55 | 55 | 22 | 25 | 31 | 33 | 30 | 25 | 0 | 110 | 67 | 0 | 0 | 25 | 0 | 221 | 0 | 0 | 0 | 21 | 0 | 0 | 80 | 19 | 10 | 19 | 20 | 100 | 100 | 0 | 300 | 268 | 183 | 78 | 154 | 42 | 0 | 5 | 20 | 11 | 0 | 0 | 19 | 5 | 33 | 16 | 124 | 50 | 0 | 20 | 0.7 | 60 | 30 | 53 | 50 | 130 | 309 | 46 | 20 | 48 | 77 | 12 | 43 | 9 | 290 | 15 | 11 | 0 | 115 | 0 | 0 | 205 |  | 477 | 0 | 0 | 81 | 102 | 120 | 0 | 0 | 26 | 22 | 8 | 179 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 90 | 50 | 35 | 0 | 43 | 0 | 22 | 11 | 8 | 0 | 65 | 175 | 0 | 15 | 212 | 0 | 0 | 177 | 70 | 0 | 0 | 0 |  | 6468.7 | 2030 | 8498.7 | 3352 | 477 | 1877 | 1480 | 240 | 177 | 771 | 124 | 0.7 | 0 | 93.35
17:00 | 0 | 120 | 0 | 0 | 260 | 106 | 76 | 338 | 313 | 0 | 20 | 450 | 200 | 7 | 15 | 55 | 0 | 0 | 202 | 0 | 7 | 50 | 100 | 100 | 8 | 10 | 6 | 18 | 56 | 55 | 22 | 25 | 31 | 33 | 26 | 25 | 0 | 112 | 68 | 0 | 0 | 25 | 0 | 195 | 0 | 0 | 0 | 42 | 0 | 0 | 80 | 19 | 18 | 19 | 23 | 100 | 100 | 0 | 300 | 272 | 184 | 78 | 154 | 42 | 0 | 5 | 12 | 11 | 0 | 0 | 19 | 5 | 33 | 16 | 124 | 49 | 0 | 20 | 0.3 | 60 | 30 | 11 | 10 | 100 | 303 | 62 | 10 | 10 | 78 | 15 | 11 | 9 | 280 | 15 | 11 | 0 | 110 | 0 | 0 | 205 |  | 477 | 0 | 0 | 81 | 109 | 120 | 0 | 0 | 31 | 32 | 8 | 186 | 25 | 16 | 0 | 0 | 0 | 0 | 7 | 95 | 50 | 35 | 0 | 43 | 0 | 22 | 11 | 8 | 0 | 65 | 201 | 0 | 14 | 212 | 0 | 0 | 173 | 70 | 0 | 0 | 0 |  | 6189.3 | 2091 | 8280.3 | 3370 | 477 | 1643 | 1453 | 266 | 180 | 767 | 124 | 0.3 | 0 | 93.45
18:00 | 0 | 120 | 0 | 0 | 260 | 103 | 76 | 330 | 311 | 0 | 20 | 450 | 200 | 7 | 15 | 55 | 0 | 0 | 155 | 0 | 7 | 50 | 100 | 50 | 8 | 11 | 6 | 18 | 56 | 55 | 22 | 25 | 32 | 33 | 26 | 25 | 0 | 115 | 68 | 0 | 0 | 25 | 0 | 195 | 0 | 0 | 0 | 42 | 28 | 0 | 90 | 19 | 18 | 19 | 36 | 100 | 100 | 0 | 300 | 301 | 186 | 78 | 154 | 42 | 0 | 5 | 12 | 11 | 0 | 0 | 19 | 5 | 33 | 22 | 134 | 100 | 0 | 20 | 0.1 | 60 | 30 | 11 | 10 | 100 | 309 | 62 | 10 | 10 | 78 | 20 | 11 | 9 | 290 | 20 | 11 | 0 | 110 | 0 | 0 | 205 |  | 475 | 0 | 0 | 81 | 105 | 120 | 0 | 0 | 34 | 40 | 8 | 186 | 26 | 16 | 0 | 0 | 0 | 0 | 26 | 102 | 50 | 35 | 18 | 43 | 0 | 22 | 11 | 8 | 0 | 66 | 232 | 16 | 18 | 212 | 0 | 0 | 169 | 72 | 0 | 0 | 0 |  | 6259.1 | 2191 | 8450.1 | 3420 | 475 | 1664 | 1410 | 298 | 183 | 866 | 134 | 0.1 | 0 | 93.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 120 | 0 | 0 | 260 | 107 | 76 | 325 | 282 | 13 | 20 | 400 | 200 | 7 | 18 | 55 | 0 | 0 | 100 | 8 | 7 | 102 | 149 | 50 | 58 | 10 | 12 | 18 | 55 | 55 | 22 | 25 | 24 | 33 | 26 | 42 | 0 | 117 | 70 | 0 | 0 | 25 | 0 | 195 | 0 | 0 | 0 | 51 | 82 | 64 | 90 | 87 | 19 | 19 | 42 | 100 | 100 | 0 | 300 | 298 | 193 | 78 | 154 | 39 | 0 | 5 | 12 | 10 | 8 | 1 | 19 | 11 | 33 | 22 | 164 | 97 | 16 | 20 | 0 | 60 | 30 | 11 | 10 | 100 | 313 | 63 | 10 | 10 | 77 | 17 | 12 | 9 | 265 | 23 | 11 | 0 | 153 | 0 | 0 | 205 |  | 474 | 0 | 0 | 81 | 112 | 200 | 0 | 0 | 39 | 50 | 40 | 186 | 33 | 64 | 0 | 0 | 0 | 43 | 44 | 102 | 50 | 35 | 45 | 43 | 35 | 22 | 11 | 10 | 0 | 65 | 250 | 16 | 18 | 214 | 0 | 0 | 170 | 71 | 0 | 0 | 0 |  | 6599 | 2523 | 9122 | 3364 | 474 | 1576 | 1782 | 315 | 187 | 1260 | 164 | 0 | 0 | 93.65
19:30 | 0 | 120 | 0 | 0 | 260 | 107 | 76 | 344 | 326 | 13 | 20 | 400 | 200 | 25 | 50 | 55 | 0 | 0 | 150 | 15 | 16 | 102 | 149 | 86 | 100 | 10 | 12 | 55 | 55 | 55 | 22 | 25 | 32 | 33 | 26 | 49 | 0 | 117 | 70 | 0 | 0 | 25 | 0 | 195 | 0 | 0 | 0 | 51 | 82 | 77 | 90 | 97 | 30 | 19 | 41 | 100 | 100 | 0 | 300 | 300 | 184 | 78 | 154 | 39 | 0 | 5 | 12 | 41 | 8 | 25 | 19 | 11 | 33 | 22 | 168 | 102 | 50 | 20 | 0 | 60 | 30 | 34 | 25 | 163 | 302 | 50 | 50 | 48 | 79 | 17 | 44 | 7 | 290 | 23 | 11 | 0 | 260 | 0 | 0 | 205 |  | 475 | 0 | 0 | 102 | 110 | 223 | 0 | 48 | 15 | 55 | 40 | 180 | 36 | 74 | 0 | 0 | 0 | 43 | 44 | 102 | 50 | 35 | 45 | 43 | 42 | 22 | 11 | 10 | 0 | 66 | 250 | 16 | 18 | 214 | 0 | 0 | 175 | 96 | 56 | 0 | 0 |  | 7351 | 2696 | 10047 | 3411 | 475 | 1912 | 2289 | 316 | 187 | 1289 | 168 | 0 | 0 | 0
20:00 | 0 | 120 | 0 | 0 | 260 | 106 | 77 | 340 | 333 | 0 | 20 | 350 | 200 | 28 | 65 | 55 | 0 | 0 | 120 | 0 | 20 | 102 | 149 | 100 | 101 | 10 | 48 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 26 | 49 | 0 | 118 | 70 | 0 | 0 | 25 | 0 | 195 | 0 | 0 | 0 | 51 | 74 | 76 | 90 | 98 | 35 | 19 | 42 | 100 | 100 | 0 | 300 | 301 | 184 | 78 | 154 | 41 | 0 | 5 | 12 | 41 | 0 | 19 | 19 | 11 | 33 | 22 | 166 | 99 | 82 | 20 | 0 | 60 | 30 | 53 | 37 | 130 | 304 | 53 | 50 | 48 | 80 | 20 | 43 | 9 | 265 | 23 | 11 | 0 | 258 | 0 | 0 | 205 |  | 474 | 32 | 0 | 102 | 104 | 225 | 0 | 52 | 14 | 60 | 40 | 183 | 34 | 110 | 0 | 0 | 0 | 43 | 44 | 102 | 50 | 35 | 47 | 43 | 43 | 22 | 11 | 10 | 0 | 65 | 250 | 17 | 17 | 215 | 0 | 0 | 171 | 97 | 68 | 0 | 0 |  | 7315 | 2780 | 10095 | 3390 | 474 | 1843 | 2410 | 315 | 188 | 1309 | 166 | 0 | 0 | 93.8
21:00 | 0 | 120 | 0 | 0 | 260 | 106 | 77 | 380 | 331 | 0 | 20 | 380 | 200 | 55 | 48 | 55 | 0 | 0 | 120 | 0 | 40 | 50 | 149 | 50 | 100 | 10 | 48 | 54 | 56 | 55 | 0 | 25 | 32 | 33 | 26 | 50 | 0 | 119 | 72 | 0 | 0 | 26 | 0 | 195 | 0 | 0 | 0 | 51 | 74 | 81 | 90 | 98 | 35 | 19 | 42 | 100 | 100 | 0 | 320 | 316 | 197 | 78 | 154 | 41 | 0 | 5 | 20 | 41 | 0 | 25 | 19 | 11 | 33 | 22 | 178 | 96 | 92 | 20 | 0 | 60 | 30 | 53 | 50 | 130 | 314 | 62 | 50 | 48 | 80 | 20 | 43 | 9 | 290 | 23 | 11 | 0 | 298 | 0 | 0 | 205 |  | 474 | 48 | 0 | 102 | 115 | 226 | 0 | 12 | 34 | 60 | 33 | 186 | 37 | 112 | 0 | 0 | 0 | 43 | 45 | 102 | 50 | 35 | 45 | 43 | 43 | 22 | 11 | 10 | 0 | 65 | 250 | 15 | 17 | 215 | 0 | 0 | 171 | 98 | 68 | 0 | 0 |  | 7476 | 2787 | 10263 | 3475 | 474 | 1921 | 2361 | 315 | 191 | 1348 | 178 | 0 | 0 | 93.95
22:00 | 0 | 120 | 0 | 0 | 260 | 103 | 77 | 387 | 331 | 0 | 20 | 380 | 200 | 30 | 15 | 55 | 0 | 0 | 120 | 0 | 40 | 50 | 149 | 50 | 100 | 11 | 48 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 26 | 50 | 0 | 120 | 72 | 0 | 0 | 25 | 0 | 195 | 0 | 0 | 0 | 51 | 74 | 81 | 80 | 99 | 42 | 19 | 42 | 100 | 100 | 0 | 308 | 309 | 190 | 78 | 153 | 41 | 0 | 5 | 35 | 41 | 0 | 0 | 19 | 11 | 33 | 22 | 170 | 97 | 92 | 20 | 0 | 60 | 30 | 53 | 50 | 130 | 310 | 62 | 50 | 49 | 80 | 20 | 43 | 9 | 320 | 23 | 11 | 0 | 301 | 0 | 0 | 205 |  | 480 | 48 | 0 | 102 | 115 | 227 | 0 | 31 | 37 | 55 | 33 | 187 | 38 | 64 | 0 | 0 | 0 | 43 | 46 | 102 | 50 | 35 | 45 | 43 | 35 | 22 | 11 | 10 | 0 | 66 | 250 | 17 | 17 | 214 | 0 | 0 | 178 | 98 | 68 | 0 | 0 |  | 7429 | 2767 | 10196 | 3474 | 480 | 1965 | 2250 | 316 | 192 | 1349 | 170 | 0 | 0 | 94.1
23:00 | 0 | 120 | 0 | 0 | 260 | 103 | 77 | 382 | 342 | 0 | 20 | 400 | 200 | 15 | 15 | 55 | 0 | 0 | 120 | 0 | 40 | 50 | 149 | 50 | 100 | 10 | 48 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 28 | 50 | 0 | 120 | 72 | 0 | 0 | 25 | 0 | 201 | 0 | 0 | 0 | 51 | 74 | 81 | 80 | 99 | 43 | 19 | 42 | 100 | 100 | 0 | 328 | 327 | 201 | 78 | 154 | 41 | 0 | 5 | 51 | 41 | 0 | 0 | 19 | 11 | 33 | 22 | 170 | 95 | 92 | 20 | 0 | 60 | 30 | 53 | 50 | 130 | 316 | 62 | 50 | 49 | 78 | 20 | 43 | 9 | 320 | 23 | 11 | 0 | 302 | 0 | 0 | 205 |  | 475 | 48 | 0 | 101 | 115 | 228 | 0 | 31 | 39 | 55 | 33 | 189 | 37 | 64 | 0 | 0 | 0 | 43 | 46 | 99 | 50 | 35 | 44 | 43 | 35 | 22 | 11 | 10 | 0 | 64 | 250 | 14 | 17 | 214 | 0 | 0 | 181 | 98 | 68 | 0 | 0 |  | 7517 | 2759 | 10276 | 3525 | 475 | 2011 | 2235 | 314 | 192 | 1354 | 170 | 0 | 0 | 94.25
24:00 | 0 | 120 | 0 | 0 | 260 | 103 | 77 | 375 | 342 | 0 | 20 | 400 | 200 | 15 | 15 | 55 | 0 | 0 | 120 | 0 | 40 | 32 | 149 | 50 | 100 | 11 | 48 | 54 | 56 | 55 | 0 | 25 | 32 | 33 | 28 | 50 | 0 | 119 | 72 | 0 | 0 | 25 | 0 | 196 | 0 | 0 | 0 | 51 | 74 | 81 | 80 | 99 | 43 | 0 | 42 | 100 | 100 | 0 | 300 | 301 | 184 | 78 | 154 | 41 | 0 | 5 | 51 | 41 | 0 | 0 | 19 | 11 | 33 | 22 | 166 | 102 | 92 | 20 | 0 | 60 | 30 | 53 | 50 | 130 | 302 | 63 | 50 | 49 | 78 | 20 | 43 | 9 | 310 | 23 | 11 | 0 | 301 | 0 | 0 | 205 |  | 474 | 48 | 0 | 102 | 115 | 228 | 0 | 33 | 39 | 55 | 33 | 189 | 38 | 64 | 0 | 0 | 0 | 43 | 46 | 99 | 50 | 35 | 44 | 43 | 35 | 22 | 11 | 11 | 0 | 64 | 250 | 16 | 16 | 214 | 0 | 0 | 174 | 99 | 68 | 0 | 0 |  | 7354 | 2758 | 10112 | 3401 | 474 | 2003 | 2220 | 314 | 191 | 1343 | 166 | 0 | 0 | 94.4
KWH | 0 | 2882565 | 0 | 0 | 5060400 | 1732840 | 1386112 | 8340880 | 7911000 | 17500 | 226300 | 9105625 | 5196829 | 323520 | 636696 | 776627 | 0 | 0 | 2215000 | 23040 | 412800 | 877248 | 2960160 | 919773 | 730560 | 148420 | 505728 | 525600 | 940024 | 872638 | 307368 | 600000 | 614520 | 697700 | 763300 | 777672 | 0 | 2127898 | 1612500 | 0 | 0 | 205560 | 0 | 4731352 | 0 | 637155 | 0 | 800160 | 452016 | 501675 | 1601520 | 924480 | 401760 | 423216 | 637920 | 2412184 | 2562805 | 0 | 7204600 | 6790750 | 4613000 | 1906909 | 3622900 | 845784 | 0 | 120000 | 778462 | 636696 | 8096 | 53386 | 306756 | 125460 | 685300 | 501260 | 3297600 | 1903600 | 586096 | 392184 | 10600 | 1362000 | 709840 | 686400 | 926000 | 2965745 | 7006941 | 1438000 | 981120 | 750240 | 1927890 | 185000 | 795120 | 212040 | 7473100 | 457992 | 256992 | 0 | 2968253 | 0 | 0 | 4838400 |  | 11382546 | 217000 | 0 | 1191360 | 1620480 | 3576960 | 0 | 142340 | 440640 | 724864 | 468750 | 4529945 | 671568 | 951360 | 0 | 0 | 0 | 411728 | 270862 | 1539934 | 954710 | 673104 | 502562 | 794880 | 378710 | 486480 | 234936 | 219294 | 0 | 1545600 | 5568700 | 153000 | 296000 | 5020845 | 0 | 0 | 4303963 | 1628652 | 553920 | 0 | 0 |  | 148851158 | 51455693 | 200306851 | 77212571 | 11382546 | 42026965 | 33415194 | 7114300 | 3740398 | 22106677 | 3297600 | 10600 | 0
Fuel Cost | 0 | 2479005.9 | 0 | 0 | 4351944 | 1403600.4 | 1302945.28 | 5087936.8 | 4825710 | 168175 | 310031 | 6100768.75 | 78939832.51 | 2031705.6 | 4253129.28 | 4745190.97 | 0 | 0 | 2458650 | 358502.4 | 2580000 | 5781064.32 | 28624747.2 | 5858954.01 | 4376054.4 | 2373235.8 | 3373205.76 | 3747528 | 5875150 | 5471440.26 | 230526 | 450000 | 0 | 0 | 0 | 7356777.12 | 0 | 0 | 0 | 0 | 0 | 1946653.2 | 0 | 64582954.8 | 0 | 13960066.05 | 0 | 7033406.4 | 4868212.32 | 4881297.75 | 9913408.8 | 5972140.8 | 2627510.4 | 359733.6 | 0 | 2195087.44 | 2332152.55 | 0 | 6556186 | 4685617.5 | 3229100 | 1315767.21 | 3477984 | 566675.28 | 0 | 110400 | 638338.84 | 598494.24 | 87760.64 | 396124.12 | 236202.12 | 94095 | 527681 | 375945 | 22555584 | 1427700 | 5386222.24 | 301981.68 | 0 | 1416480 | 738233.6 | 658944 | 833400 | 3825811.05 | 4904858.7 | 1639320 | 1049798.4 | 825264 | 2197794.6 | 236800 | 739461.6 | 197197.2 | 4782784 | 343494 | 195313.92 | 0 | 0 | 0 | 0 | 0 |  | 58050984.6 | 6325550 | 0 | 7862976 | 10857216 | 57517516.8 | 0 | 2271746.4 | 4961606.4 | 8538897.92 | 2985937.5 | 4484645.55 | 664852.32 | 5879404.8 | 0 | 0 | 0 | 4714285.6 | 2903640.64 | 13797808.64 | 8258241.5 | 5990625.6 | 5352285.3 | 7885209.6 | 4078706.7 | 535128 | 220839.84 | 166005.558 | 0 | 9381792 | 0 | 3529710 | 6346240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 392741248.81 | 243561853.268 | 636303102.078 | 58057180.798 | 58050984.6 | 30629505.13 | 222556768.79 | 9381792 | 0 | 235071286.76 | 22555584 | 0 | 0
Yesterday Day Peak | 0 | 120 | 0 | 0 | 260 | 25 | 20 | 360 | 342 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 0 | 0 | 199 | 0 | 7 | 7 | 100 | 10 | 8 | 10 | 24 | 25 | 54 | 36 | 22 | 25 | 31 | 33 | 30 | 25 | 0 | 77 | 71 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 | 51 | 0 | 0 | 80 | 18 | 6 | 19 | 6 | 100 | 130 | 0 | 315 | 272 | 195 | 78 | 153 | 39 | 0 | 5 | 51 | 5 | 0 | 0 | 0 | 0 | 33 | 16 | 126 | 49 | 0 | 20 | 1.4 | 60 | 30 | 11 | 50 | 100 | 310 | 62 | 20 | 20 | 80 | 0 | 40 | 9 | 310 | 20 | 11 | 0 | 105 | 0 | 0 | 205 |  | 477 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 9 | 8 | 172 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 25 | 0 | 22 | 9 | 8 | 0 | 66 | 174 | 0 | 18 | 213 | 0 | 0 | 145 | 20 | 0 | 0 | 0 |  | 7608.4 | DayPeak
Yesterday Evening Peak | 0 | 120 | 0 | 0 | 260 | 106 | 77 | 380 | 331 | 0 | 20 | 380 | 200 | 55 | 48 | 55 | 0 | 0 | 120 | 0 | 40 | 50 | 149 | 50 | 100 | 10 | 48 | 54 | 56 | 55 | 0 | 25 | 32 | 33 | 26 | 50 | 0 | 119 | 72 | 0 | 0 | 26 | 0 | 195 | 0 | 0 | 0 | 51 | 74 | 81 | 90 | 98 | 35 | 19 | 42 | 100 | 100 | 0 | 320 | 316 | 197 | 78 | 154 | 41 | 0 | 5 | 20 | 41 | 0 | 25 | 19 | 11 | 33 | 22 | 178 | 96 | 92 | 20 | 0 | 60 | 30 | 53 | 50 | 130 | 314 | 62 | 50 | 48 | 80 | 20 | 43 | 9 | 290 | 23 | 11 | 0 | 298 | 0 | 0 | 205 |  | 474 | 48 | 0 | 102 | 115 | 226 | 0 | 12 | 34 | 60 | 33 | 186 | 37 | 112 | 0 | 0 | 0 | 43 | 45 | 102 | 50 | 35 | 45 | 43 | 43 | 22 | 11 | 10 | 0 | 65 | 250 | 15 | 17 | 215 | 0 | 0 | 171 | 98 | 68 | 0 | 0 |  | 10263 | EvPeak
Forecast for Evening | 0 | 120 | 0 | 0 | 350 | 102 | 78 | 412 | 360 | 84 | 20 | 450 | 305 | 100 | 100 | 55 | 210 | 0 | 120 | 100 | 88 | 102 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 120 | 72 | 0 | 0 | 25 | 0 | 225 | 0 | 0 | 0 | 51 | 85 | 80 | 90 | 98 | 44 | 19 | 40 | 100 | 100 | 0 | 360 | 360 | 225 | 78 | 154 | 42 | 0 | 10 | 51 | 85 | 50 | 52 | 19 | 11 | 33 | 22 | 183 | 100 | 95 | 22 | 0 | 60 | 61 | 50 | 50 | 163 | 330 | 66 | 86 | 50 | 100 | 20 | 44 | 9 | 341 | 23 | 11 | 200 | 300 | 0 | 100 | 205 |  | 487 | 49 | 0 | 110 | 115 | 225 | 0 | 55 | 46 | 74 | 40 | 194 | 35 | 110 | 30 | 0 | 0 | 43 | 47 | 102 | 50 | 43 | 47 | 43 | 43 | 22 | 11 | 11 | 0 | 70 | 260 | 15 | 18 | 215 | 0 | 0 | 220 | 98 | 100
Forecast for Day | 0 | 120 | 0 | 0 | 260 | 102 | 40 | 412 | 350 | 84 | 20 | 450 | 305 | 100 | 100 | 55 | 210 | 0 | 120 | 100 | 84 | 94 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 120 | 72 | 0 | 0 | 25 | 0 | 215 | 0 | 0 | 0 | 51 | 85 | 62 | 90 | 98 | 44 | 19 | 15 | 100 | 100 | 0 | 300 | 360 | 225 | 78 | 154 | 42 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 11 | 33 | 22 | 138 | 100 | 95 | 22 | 2 | 60 | 61 | 50 | 50 | 163 | 310 | 66 | 86 | 50 | 80 | 20 | 44 | 9 | 341 | 23 | 11 | 0 | 300 | 0 | 0 | 205 |  | 487 | 0 | 0 | 110 | 115 | 225 | 0 | 0 | 41 | 50 | 40 | 194 | 35 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 45 | 43 | 0 | 22 | 11 | 11 | 0 | 70 | 250 |  | 0 | 215 | 0 | 0 | 220 | 96
Generation at 08:00(Today) | 0 | 120 | 0 | 0 | 75 | 103 | 40 | 342 | 348 | 0 | 20 | 400 | 200 | 7 | 15 | 17 | 0 | 0 | 120 | 0 | 7 | 16 | 15 | 30 | 8 | 0 | 6 | 18 | 18 | 36 | 22 | 25 | 28 | 33 | 28 | 27 | 0 | 114 | 74 | 0 | 0 | 0 | 0 | 209 | 0 | 0 | 0 | 24 | 24 | 17 | 80 | 32 | 18 | 19 | 15 | 100 | 80 | 0 | 300 | 301 | 185 | 78 | 154 | 38 | 0 | 5 | 12 | 51 | 0 | 0 | 19 | 8 | 33 | 22 | 132 | 104 | 8 | 20 | 0.6 | 60 | 30 | 11 | 10 | 100 | 310 | 62 | 10 | 10 | 78 | 0 | 43 | 8 | 280 | 23 | 11 | 0 | 47 | 0 | 0 | 103 | 0 | 365 | 0 | 0 | 27 | 16 | 170 | 0 | 0 | 0 | 44 | 0 | 189 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 35 | 44 | 8 | 0 | 15 | 11 | 11 | 0 | 64 | 245 | 0 | 0 | 216 | 0 | 0 | 169 | 96 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6865.4 | 8:00
| Highest Generation |  | 10276 | 23:00
| Day Peak Generation |  | 7608.4 | 12:00
| Evening Peak Generation |  | 10263 | 21:00
| HVDC Max Flow |  | 483 | 1:00
| HVDC EvPeak Flow |  | 474 | 21:00
| Load factor L.F |  | 81.22%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-14
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7608.4 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7472.6 | MW
Evening Peak Generation : |  | 10263 | MW Hour : | 21:00 | Available Max Generation : |  | 12363 | MW
E.P. Demand (at gen end) : |  | 10263 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10500 | MW
Maximum Generation : |  | 10276 | MW Hour : | 23:00 | Reserve(Generation end) |  | 1863 | MW
Total Gen. (MKWH) : |  | 200.3069 | System Load Factor : | 81.22% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -730 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-14
Actual : | 91.7 | Ft.(MSL) , | Rule curve : | 79.14 | Ft.( MSL )
Gas Consumed : | Total = | 1022.38 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88686685.928
|  | Coal : | 9381792 | Oil : | 457628055.55 | Total : | 555696533.478
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3742.5641 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1271.1899 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1138.6787 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1028.7981 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 929.7619 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 750.2812 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 421.4364 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 193.2279 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 578.6449 |  |  | 0 | 0%
Total | 0 |  | 10054.5831 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Sylhet-150 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Haripur GT-1,2
|  |  |  | 3) Ghorasal Unit-4 |  | 11) Bheramara 360 MW
|  |  |  | 4) Baghabari 100 MW |  | 12) Ashuganj 55 MW
|  |  |  | 5) Tongi GT |  | 13) Ashuganj unit-5
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Sirajganj Unit-1 tripped at 08:13 due to problem at RMS and GT & ST were synchronized at 09:07 & 09:47 respectively.
b) After maintenance Ghorasal 230/132 kV AT2 was switched on at 09:50.
c) Savar 132/33 kV T2 transformer was under shut down from 11:10 to 17:30 for painting work.
d) Madanganj-Haripur 132 kV Ckt was under shut down from 12:00 to 13:53 for red hot maintenance at Madanganj end .
e) Tongi-Summit Gazipur 230 kV Ckt-1 was under shut down from 12:10 to 15:30 for C/M.
f) Saidpur-Barapukuria 132 kV Ckt-2 was under shut down from 09:40 to 14:15 for C/M.
g) Saidpur 132 bus-B was under shut down from 12:10 to 15:20 for C/M.
h) Bheramara HVDC-Bahrampur 400 kV Ckt-2 was under shut down from 12:50 to 15:12 for emergency maintenance
at Bahrampur end.
i) Sikalbaha 150 MW GT tripped at 10:09 due to auxiliary transformer problem.
j) Siddhirganj Peaking GT1 & GT2 were synchronized at 09:23 & 09:32 respectively.
k) Jhenidah 132/33 kV T1 transformer was under shut down from 09:21 11:12 for red hot maintenance.
l) Feni 132/33 kV T1 & T2 transformers were under shut down from 11:00 to 12:54 for red hot maintenance |  |  |  | About 65 MW Power interruption occurred under Feni S/S
at 33 kV sides. |  |  |  | area from 11:00 to 12:54.
m) Bottail 132/33 kV T1 transformer tripped at 12:54 showing O/C & E/F and was switched on at 12:57. |  |  |  | About 30 MW Power interruption occurred under Bottail S/S
area from 12:54 to 12:57.
n) Satkhira 132/33 kV T1 transformer was under shut down from 13:30 to 14:59 for 33 kV breaker replacement . |  |  |  | About 30 MW Power interruption occurred under Satkhira S/S
area from 13:30 to 14:59.
o) Saidpur-Purbasadipur 132 kV Ckt-1 was under shut down from 12:32 to 14:17 for C/M.
p) Saidpur-Purbasadipur 132 kV Ckt-2 was under shut down from 14:23 to 15:30 for C/M.
q) Hasnabad-Meghnaghat 230 kV Ckt-1 was under shut down from 15:10 to 16:50 for relay test.
r) After maintenance Sikalbaha 132 kV Ckt was switched on at 18:26.
s) Meghnaghat-APR keraniganj 230 kV Ckt was shut down at 07:14(14/06/2018) for C/M at Meghnaghat end..
t) Hasnabad 230 kV bus-1 was shut down at 07:02(14/06/2018) for C/M.
u) Noapara 132/33 kV T4 transformer tripped at 00:07(14/06/2018) from 33 kV side showing O/C and was |  |  |  | About 32 MW Power interruption occurred under Noapara S/S
switched on at 00:10. |  |  |  | area from 00:07 to 00:10(14/06/2018).
v) Bheramara 132 kV GTG bay was shut down at 07:20(14/06/2018) for C/M.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2882565 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 260 | 5060400
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 77 | 1386112
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 106 | 1732840
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 20 | 226300
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 380 | 8340880 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 17500 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 331 | 7911000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 380 | 9105625 | frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 55 | 323520 | Low demand
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 200 | 5196829 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 48 | 636696 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 776627
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 50 | 919773 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 307368 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 120 | 2215000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 23040 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 40 | 412800 | Low demand
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Under maint.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 10 | 148420 | Low demand
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 50 | 877248 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 505728
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 525600
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2960160
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 940024
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 872638
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 100 | 730560
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1214520 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 697700
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 26 | 763300
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 777672
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 298 | 2968253 | On test.
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5199 | 3228 | 61456698
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 26 | 205560
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 35 | 401760 | Low demand
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 191 | 3740398 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 195 | 4731352 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 637155 | Under maint.
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 800160
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 74 | 452016
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 81 | 501675
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1601520 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 423216
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 637920
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 924480 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 902 | 15057212
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2412184 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2562805 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 197 | 4613000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7204600 | FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 316 | 6790750 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 41 | 845784
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 78 | 1906909 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 20 | 778462 | Gas shortage
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 41 | 636696 | Low demand
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 8096 | Reserve
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 154 | 3622900
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 306756
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 125460
** | Tripura |  | Imported power | 0 | 160 | 178 | 3297600
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 685300
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 25 | 53386 | Low demand
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 501260
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | On test.
| Comilla Area Total |  |  |  | 2541 | 1660 | 36471948
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 96 | 1903600 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 392184
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 92 | 586096 | Low demand
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 10600
| United Mymensingh PPL |  | IPP | 200 | 0 | 205 | 4838400 | On test.
| Mymensingh Area Total |  |  |  | 322 | 413 | 7730880
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1362000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 30 | 709840 | # 4 under maint.
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 2965745 | frequency control.
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 314 | 7006941 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 686400
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 926000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 256992
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 62 | 1438000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 50 | 981120 | Low demand
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 48 | 750240
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 80 | 1927890 | frequency control.
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 20 | 185000
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 43 | 795120 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 457992
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 290 | 7473100 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 212040
| Sylhet Area Total |  |  |  | 1549 | 1273 | 28134420
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 48 | 217000
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 474 | 11382546
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 102 | 1191360
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1620480 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 34 | 440640 | Low demand
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 226 | 3576960
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 724864
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 33 | 468750
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 12 | 142340
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 68 | 553920 | On test.
| Khulna Area Total |  |  |  | 1769 | 1172 | 20318860
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 112 | 951360
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 37 | 671568
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 186 | 4529945
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 1628652
| Barisal Area Total |  |  |  | 462 | 433 | 7781525
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 411728
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 45 | 270862
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 954710
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 35 | 673104 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 502562
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | FGMO
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 171 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 43 | 378710
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 486480
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 234936
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 10 | 219294 | Engine problem
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 794880 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 1539934
| Rajshahi Area Total |  |  |  | 1123 | 620 | 6467200
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 65 | 1545600
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 250 | 5568700
117 | Rangpur GT |  | PDB | 1*20 | 20 | 15 | 153000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 296000
| Rangpur Area Total |  |  |  | 484 | 347 | 7563300
| Total |  |  |  | 15010 | 10048 | 190982043
| Eastern Grid Total |  |  |  | 11172 | 7476 | 148851158
| Western Grid Total |  |  |  | 3838 | 2572 | 42130885
| National Grid Total |  |  |  | 15010 | 10048 | 190982043
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-13 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6579 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3239 | MW
i) Dhaka area |  |  | 3478 | MW | i) Khulna area |  |  | 1272 | MW
ii) Chittagong area |  |  | 923 | MW | ii) Rajshahi area |  |  | 1076 | MW
iii) Comilla area |  |  | 960 | MW | iii) Barisal area |  |  | 249 | MW
iv) Mymensingh area |  |  | 795 | MW | iv) Rangpur area |  |  | 642 | MW
v) Sylhet area |  |  | 423 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9818 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 900 | Netrokona | 85 | 2000 | Central s/s | 68 | 2100
Munsiganj | 94 | 2000 | Jamalpur | 105 | 2100 | Noapara | 89 | 1930
Megnaghat | 43 | 200 | Sherpur | 88 | 2100 | Jessore | 144 | 2100
Shyampur | 148 | 1400 | Srimongal | 33 | 2100 | Jhenida | 90 | 1930
Bhulta | 144 | 2100 | Shahjibazar | 104 | 2200 | Bottail | 132 | 2100
Madanganj | 42 | 100 | Fenchuganj | 53 | 2100 | G.K Project | 58 | 2200
Shitalakhya | 108 | 1600 | Kulawara | 36 | 2100 | Faridpur | 144 | 2000
Rahim steel | 6 | 1000 | Sylhet | 128 | 2200 | Madaripur | 132 | 1900
Matuail | 84 | 1000 | Chatak | 25 | 1930 | Gopalganj | 85 | 2100
Ghorasal | 72 | 2100 | Sunamganj | 31 | 2100 | Bagerhat | 79 | 1930
Narsingdi | 114 | 2000 | Biani Bazar | 22 | 2000 | Mongla | 36 | 1000
Haripur (SBU) | 43 | 2100 | Comilla (S) | 178 | 2100 | Satkhira | 93 | 2100
Ullon | 93 | 2000 | Comilla(N) | 97 | 1900 | Gallamari | 48 | 1930
Hasnabad | 193 | 2000 | Chandpur | 128 | 1930 | Magura | 46 | 2100
Magbazar | 102 | 2000 | Feni | 112 | 2300 | Chuadanga | 79 | 2000
Maniknagar | 72 | 2000 | Chowmuhani | 186 | 2100 | Barisal | 116 | 2000
Bangabhaban | 14 | 2000 | Ashuganj | 51 | 2200 | Patuakhali | 89 | 2100
Narinda | 72 | 1500 | Daudkandi | 92 | 2100 | Bhandaria | 46 | 1930
Dhanmondi | 83 | 1900 | B.Baria | 125 | 2200 | Ishurdi | 54 | 100
Lalbag | 49 | 2000 | Ramganj | 0 | 0 | Ruppur Paromanobik | 1 | 100
Madartek | 96 | 1930 | Madunaghat | 62 | 2000 | Natore | 111 | 2000
Mirpur | 114 | 1930 | Hathazari | 64 | 2100 | Bogra | 219 | 100
Kalyanpur | 108 | 1930 | Khulshi | 153 | 1930 | Noagaon | 112 | 100
Gulshan | 81 | 1930 | Halishahar | 117 | 1930 | Rajshahi | 143 | 1900
Uttara | 64 | 1900 | Baraulia | 82 | 100 | C.Nawabganj | 67 | 100
Kamrangirchar | 137 | 2100 | Sikalbaha | 37 | 2100 | Amnura | 37 | 2000
Savar | 132 | 1930 | Dohazari | 78 | 2100 | Pabna | 114 | 2000
Bhasantec | 40 | 1900 | Cox'sbazar | 80 | 1900 | Shahjadpur | 90 | 1930
Agargaon | 93 | 2100 | Chandraghona | 34 | 2000 | Serajganj | 80 | 300
Satmosjid | 115 | 1900 | Kaptai | 4 | 2100 | Niyamatpur | 52 | 2000
Tongi | 175 | 1100 | A. Khaer Stl. | 6 | 1700 | Joypurhat | 46 | 2000
Kabirpur | 115 | 1930 | Bakulia | 92 | 2100 | Rangpur | 115 | 1900
Basundhara | 111 | 2000 | Julda | 16 | 2100 | Lalmonirhat | 87 | 1930
Manikganj | 204 | 2100 | TK chemical | 2 | 2000 | Saidpur | 109 | 1930
Joydevpur | 94 | 1000 | Modern Steel | 5 | 1200 | Purbasadipur | 101 | 120
New Tongi | 218 | 2100 | Shahmirpur | 18 | 1200 | Thakurgaon | 71 | 2000
Korda | 212 | 2100 | Abul Khair 230 | 166 | 2300 | Palashbari | 95 | 2000
Tangail | 195 | 2100 | BSRM | 105 | 300 | Barapukuria | 52 | 2000
Mymensing | 235 | 1930 | Khagrachhari | 9 | 2100 | Panchagar | 42 | 2000
Kishorganj | 92 | 1930 | Goalpara | 46 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-13
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 391 | 6:00 | 383 | 22:00 | Kaliakoir | 373 | 6:00 | 360 | 12:00
Bheramara | 411 | 6:00 | 389 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 1:00 | 224 | 16:00 | Tongi | 223 | 5:00 | 206 | 15:00
Ishurdi | 228 | 10:00 | 213 | 21:00 | Comilla (N) | 231 | 5:00 | 227 | 12:00
Ashuganj | 234 | 4:00 | 230 | 13:00 | Hathazari | 221 | 18:30 | 210 | 15:00
Serajganj | 222 | 18:30 | 212 | 1:00 | Megnaghat | 228 | 19:00 | 223 | 14:00
Baghabari | 222 | 18:00 | 210 | 24:00 | Fenchuganj | 236 | 9:00 | 232 | 21:00
Barapukuria | 236 | 10:00 | 225 | 1:00 | Siddhirganj | 225 | 18:30 | 219 | 11:00
Bogra | 222 | 10:00 | 205 | 21:00 | Maniknagar | 223 | 19:00 | 218 | 11:00
Khulna South | 236 | 18:30 | 222 | 21:00 | Old Airport | 223 | 6:00 | 216 | 12:00
Rampura | 222 | 7:00 | 219 | 15:00 | Barisal | 235 | 1:00 | 224 | 14:00
Haripur | 221 | 5:00 | 218 | 11:00 | AKSML | 222 | 20:00 | 204 | 14:00
Hasnabad | 224 | 5:00 | 218 | 12:00 | BSRM | 224 | 19:30 | 210 | 15:00
Aminbazar | 224 | 5:00 | 218 | 11:00 | Bibiyana | 232 | 1:00 | 230 | 5:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 2000 | 130 | 1100 | Ramganj | 0 | 0 | 0 | 0
Munsiganj | 136 | 1930 | 129 | 1200 | Madanhat | 133 | 1830 | 128 | 1400
Megnaghat | 132 | 1930 | 128 | 1500 | Hathazari | 132 | 1830 | 126 | 1400
Shyampur | 129 | 1830 | 126 | 900 | Khulshi | 130 | 1930 | 121 | 1500
Bhulta | 126 | 300 | 123 | 900 | Halishahar | 133 | 2000 | 123 | 1500
Madanganj | 137 | 1830 | 128 | 1200 | Baraulia | 130 | 1900 | 122 | 1500
Shitalakhya | 138 | 1900 | 128 | 1200 | Sikalbaha | 132 | 1930 | 124 | 1300
Rahim steal | 134 | 1900 | 131 | 100 | Dohazari | 132 | 2000 | 123 | 1500
Matuail | 133 | 1930 | 130 | 100 | Cox'sbazar | 127 | 2000 | 117 | 1500
Ghorasal | 135 | 100 | 133 | 1500 | Chandraghona | 133 | 1930 | 126 | 1500
Narsinghdi | 131 | 1930 | 125 | 200 | Kaptai | 133 | 1830 | 127 | 1500
Haripur (SBU) | 135 | 1900 | 130 | 1200 | A. Khaer Stl. | 131 | 1930 | 128 | 1500
Ullon | 136 | 500 | 132 | 1200 | Bakulia | 130 | 1900 | 121 | 1500
Hasnabad | 135 | 2000 | 130 | 1200 | Julda | 132 | 1930 | 122 | 1500
Magbazar | 136 | 500 | 132 | 1200 | TK Chemical | 135 | 2000 | 128 | 1500
Maniknagar | 135 | 500 | 131 | 1200 | Modern Steel | 131 | 1930 | 124 | 1500
Bangabhaban | 135 | 500 | 131 | 1200 | Shahmirpur | 132 | 2000 | 124 | 1500
Narinda | 135 | 500 | 131 | 1200 | Khagrachhari | 132 | 1830 | 129 | 1500
Dhanmondi | 136 | 500 | 132 | 1200 | Goalpara | 136 | 1830 | 129 | 1300
Lalbag | 131 | 500 | 125 | 1200 | Central s/s | 136 | 1830 | 128 | 1400
Madartek | 136 | 500 | 132 | 1200 | Noapara | 133 | 1830 | 123 | 1300
Mirpur | 134 | 100 | 130 | 1100 | Jessore | 128 | 900 | 116 | 2100
Kalyanpur | 134 | 600 | 131 | 1000 | Jhenida | 126 | 900 | 111 | 2100
Gulshan | 135 | 500 | 131 | 1200 | Bottail | 134 | 1830 | 119 | 2100
Uttara | 131 | 600 | 126 | 1200 | G.K.Project | 138 | 1830 | 125 | 2100
Kamrangirchar | 134 | 300 | 129 | 1100 | Faridpur | 130 | 900 | 116 | 2200
Savar | 132 | 600 | 128 | 1100 | Madaripur | 131 | 900 | 118 | 1900
Bhasantec | 132 | 500 | 127 | 1200 | Gopalganj | 132 | 900 | 116 | 1900
Agargaon | 133 | 600 | 127 | 1200 | Bagerhat | 131 | 1800 | 124 | 1900
Satmosjid | 132 | 500 | 128 | 1200 | Mongla | 130 | 1830 | 123 | 1400
Tongi | 134 | 500 | 124 | 1500 | Satkhira | 134 | 1700 | 124 | 2100
Kabirpur | 136 | 600 | 130 | 2100 | Gallamari | 136 | 1830 | 129 | 1200
Basundhara | 131 | 500 | 122 | 1400 | Magura | 125 | 600 | 107 | 2100
Manikganj | 140 | 600 | 135 | 2100 | Chuadanga | 121 | 700 | 103 | 2100
Joydevpur | 143 | 1830 | 129 | 1500 | Barisal | 136 | 700 | 129 | 1400
New Tongi | 134 | 500 | 123 | 1500 | Patuakhali | 134 | 900 | 123 | 2200
Kodda | 135 | 1900 | 128 | 1300 | Bhandaria | 134 | 1800 | 124 | 2200
Tangail | 135 | 500 | 125 | 2100 | Ishurdi | 137 | 1000 | 125 | 1900
Mymensing | 129 | 600 | 120 | 2100 | Ruppur Paromanobik | 135 | 700 | 125 | 100
Kishorganj | 131 | 700 | 116 | 2100 | Natore | 137 | 1830 | 119 | 200
Netrokona | 128 | 500 | 118 | 2100 | Bogra | 133 | 1000 | 119 | 100
Jamalpur | 132 | 900 | 125 | 1900 | Noagaon | 128 | 1900 | 115 | 2000
Sherpur | 134 | 1300 | 124 | 1900 | Rajshahi | 135 | 1800 | 118 | 2000
Srimongal | 136 | 900 | 131 | 2300 | C.Nawabganj | 137 | 1830 | 120 | 300
Shahjibazar | 135 | 100 | 130 | 2100 | Amnura | 140 | 1830 | 120 | 2000
Fenchuganj | 136 | 900 | 132 | 1800 | Pabna | 132 | 800 | 119 | 300
Khulawara | 135 | 500 | 132 | 1800 | Shahjadpur | 138 | 400 | 130 | 100
Sylhet | 136 | 900 | 132 | 1700 | Serajganj | 131 | 800 | 124 | 300
Chatak | 136 | 700 | 130 | 1900 | Niyamatpur | 129 | 1000 | 111 | 2000
Sunamganj | 136 | 1700 | 131 | 1800 | Joypurhat | 128 | 1000 | 111 | 2000
Biani Bazar | 135 | 1100 | 131 | 2100 | Rangpur | 125 | 800 | 106 | 2000
Comilla(s) | 128 | 700 | 120 | 2100 | Lalmonirhat | 122 | 1000 | 98 | 2000
Comilla(n) | 136 | 2100 | 133 | 2300 | Saidpur | 130 | 700 | 100 | 1930
Chandpur | 130 | 900 | 123 | 2300 | Purbasadipur | 132 | 1830 | 120 | 2000
Feni | 121 | 1000 | 115 | 2300 | Thakurgaon | 130 | 700 | 112 | 2000
Chowmuhani | 128 | 1000 | 120 | 2100 | Palashbari | 125 | 800 | 108 | 1900
Ashuganj | 135 | 600 | 131 | 2100 | Barapukuria | 136 | 1000 | 125 | 100
Daudkandi | 131 | 2000 | 128 | 1400 | Panchagar | 125 | 600 | 105 | 2000
B.Baria | 134 | 200 | 127 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-06-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 640 | 7354 | 2758 | 10112 |  |  |  | QF-LDC-12
0:30 | 660 | 6826 | 2673.5 | 9499.5 | Date: | 2018-06-13
1:00 | 680 | 6298 | 2589 | 8887
1:30 | 700 | 6286 | 2506.5 | 8792.5
2:00 | 720 | 6274 | 2424 | 8698
2:30 | 720 | 6241.5 | 2430 | 8671.5 | [5 empty] | Gen. at Eve. Peak | 10263 | 10263 MW (21:00 )
3:00 | 720 | 6209 | 2436 | 8645 | [6 empty] | 21:00
3:30 | 700 | 6105.5 | 2399.5 | 8505 | [5 empty] | Gen. at Day Peak | 7608.4 | 7608.4 MW (12:00 )
4:00 | 680 | 6002 | 2363 | 8365 | [6 empty] | 12:00
4:30 | 675 | 5773 | 2163.5 | 7936.5 | [5 empty] | Highest Generation | 10276
5:00 | 670 | 5544 | 1964 | 7508 | [6 empty] | 23:00
5:30 | 635 | 5379.6 | 1879 | 7258.6
6:00 | 600 | 5215.2 | 1794 | 7009.2
6:30 | 555 | 5190.25 | 1758.5 | 6948.75
7:00 | 510 | 5165.3 | 1723 | 6888.3
7:30 | 495 | 5158.35 | 1718.5 | 6876.85
8:00 | 480 | 5151.4 | 1714 | 6865.4
8:30 | 550 | 5409.85 | 1603.5 | 7013.35
9:00 | 620 | 5668.3 | 1493 | 7161.3
9:30 | 570 | 5676.35 | 1516.5 | 7192.85
10:00 | 520 | 5684.4 | 1540 | 7224.4
10:30 | 570 | 5703.2 | 1581.5 | 7284.7
11:00 | 620 | 5722 | 1623 | 7345
11:30 | 620 | 5846.7 | 1630 | 7476.7
12:00 | 620 | 5971.4 | 1637 | 7608.4
12:30 | 660 | 6032.35 | 1636 | 7668.35
13:00 | 700 | 6093.3 | 1635 | 7728.3
13:30 | 710 | 6211.65 | 1691 | 7902.65
14:00 | 720 | 6330 | 1747 | 8077
14:30 | 690 | 6449.15 | 1821 | 8270.15
15:00 | 660 | 6568.3 | 1895 | 8463.3
15:30 | 660 | 6518.5 | 1962.5 | 8481
16:00 | 660 | 6468.7 | 2030 | 8498.7
16:30 | 630 | 6329 | 2060.5 | 8389.5
17:00 | 600 | 6189.3 | 2091 | 8280.3
17:30 | 560 | 6224.2 | 2141 | 8365.2
18:00 | 520 | 6259.1 | 2191 | 8450.1
18:30 | 620 | 6429.05 | 2357 | 8786.05
19:00 | 720 | 6599 | 2523 | 9122
19:30 | 730 | 7351 | 2696 | 10047
20:00 | 700 | 7315 | 2780 | 10095 |  |  |  | Executive Engineer
20:30 | 700 | 7395.5 | 2783.5 | 10179 |  |  |  | Network Operation Division
21:00 | 700 | 7476 | 2787 | 10263
21:30 | 670 | 7452.5 | 2777 | 10229.5
22:00 | 640 | 7429 | 2767 | 10196 |  |  |  |  | Page 6 of 7
22:30 | 640 | 7473 | 2763 | 10236
23:00 | 640 | 7517 | 2759 | 10276
23:30 | 640 | 7435.5 | 2758.5 | 10194
24:00 | 640 | 7354 | 2758 | 10112
10263 MW (21:00 )
7608.4 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-13 |  | Energy | 200306851
[10 empty] | 2018-06-13 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3401 | 474 | 2003 | 2220 | 314 | 191 | 1343 | 0 | 166
0:30 | 3311.5 | 478.5 | 1995 | 1858.5 | 306 | 149.5 | 1250.5 | 0 | 150 | Date: | 2018-06-13
1:00 | 3222 | 483 | 1987 | 1497 | 298 | 108 | 1158 | 0 | 134
1:30 | 3218.5 | 482.5 | 2002.5 | 1396.5 | 298.5 | 120.5 | 1138.5 | 0 | 135 | [7 empty] | Total Energy | 200.3069 | Total Energy Gen 200.307 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 200.307 MKWHr
2:00 | 3215 | 482 | 2018 | 1296 | 299 | 133 | 1119 | 0 | 136 | [7 empty] | Energy not Served | 0
2:30 | 3228.5 | 482 | 2002 | 1265 | 306 | 134 | 1116 | 0 | 138 | [7 empty] | Energy Requirement | 200.3069
3:00 | 3242 | 482 | 1986 | 1234 | 313 | 135 | 1113 | 0 | 140
3:30 | 3223 | 482 | 1935 | 1180 | 314.5 | 135.5 | 1100 | 0 | 135 | [6 empty] | Shortage
4:00 | 3204 | 482 | 1884 | 1126 | 316 | 136 | 1087 | 0 | 130
4:30 | 3181.5 | 482 | 1712 | 995.5 | 316.5 | 137.5 | 992.5 | 0 | 119
5:00 | 3159 | 482 | 1540 | 865 | 317 | 139 | 898 | 0 | 108
5:30 | 3067 | 482 | 1451.5 | 854.5 | 317 | 140 | 834.5 | 0 | 112
6:00 | 2975 | 482 | 1363 | 844 | 317 | 141 | 771 | 0 | 116
6:30 | 2986.5 | 482.5 | 1325.5 | 861 | 316 | 143.5 | 718.5 | 0 | 115 |  |  |  |  | Coal
7:00 | 2998 | 483 | 1288 | 878 | 315 | 146 | 666 | 0 | 114
7:30 | 2946 | 479.5 | 1323.5 | 899 | 316.5 | 147 | 658 | 0 | 107 |  |  |  | Oil |  |  |  | ,
8:00 | 2894 | 476 | 1359 | 920 | 318 | 148 | 650 | 0 | 100
8:30 | 2842 | 476 | 1489 | 990 | 318 | 148 | 647 | 0 | 103
9:00 | 2790 | 476 | 1619 | 1060 | 318 | 148 | 644 | 0 | 106
9:30 | 2828 | 476.5 | 1603.5 | 1060.5 | 317.5 | 149 | 647.5 | 0 | 110
10:00 | 2866 | 477 | 1588 | 1061 | 317 | 150 | 651 | 0 | 114
10:30 | 3010.5 | 477 | 1536 | 1063 | 316.5 | 151.5 | 613.5 | 0 | 116
11:00 | 3155 | 477 | 1484 | 1065 | 316 | 153 | 576 | 0 | 118
11:30 | 3271 | 477 | 1525.5 | 1066.5 | 278 | 150.5 | 585 | 0 | 122
12:00 | 3387 | 477 | 1567 | 1068 | 240 | 148 | 594 | 0 | 126
12:30 | 3389 | 476.5 | 1588 | 1115 | 227 | 144.5 | 598 | 0 | 129
13:00 | 3391 | 476 | 1609 | 1162 | 214 | 141 | 602 | 0 | 132
13:30 | 3391 | 476 | 1609 | 1162 | 214 | 141 | 602 | 0 | 132
14:00 | 3391 | 476 | 1609 | 1162 | 214 | 141 | 602 | 0 | 132
14:30 | 3391 | 476 | 1776 | 1343 | 214.5 | 140.5 | 617.5 | 0 | 136
15:00 | 3391 | 476 | 1943 | 1524 | 215 | 140 | 633 | 0 | 140
15:30 | 3371.5 | 476.5 | 1910 | 1502 | 227.5 | 158.5 | 702 | 0 | 132
16:00 | 3352 | 477 | 1877 | 1480 | 240 | 177 | 771 | 0 | 124
16:30 | 3361 | 477 | 1760 | 1466.5 | 253 | 178.5 | 769 | 0 | 124
17:00 | 3370 | 477 | 1643 | 1453 | 266 | 180 | 767 | 0 | 124
17:30 | 3395 | 476 | 1653.5 | 1431.5 | 282 | 181.5 | 816.5 | 0 | 129
18:00 | 3420 | 475 | 1664 | 1410 | 298 | 183 | 866 | 0 | 134
18:30 | 3392 | 474.5 | 1620 | 1596 | 306.5 | 185 | 1063 | 0 | 149
19:00 | 3364 | 474 | 1576 | 1782 | 315 | 187 | 1260 | 0 | 164
19:30 | 3411 | 475 | 1912 | 2289 | 316 | 187 | 1289 | 0 | 168
20:00 | 3390 | 474 | 1843 | 2410 | 315 | 188 | 1309 | 0 | 166
20:30 | 3432.5 | 474 | 1882 | 2385.5 | 315 | 189.5 | 1328.5 | 0 | 172
21:00 | 3475 | 474 | 1921 | 2361 | 315 | 191 | 1348 | 0 | 178
21:30 | 3474.5 | 477 | 1943 | 2305.5 | 315.5 | 191.5 | 1348.5 | 0 | 174
22:00 | 3474 | 480 | 1965 | 2250 | 316 | 192 | 1349 | 0 | 170
22:30 | 3499.5 | 477.5 | 1988 | 2242.5 | 315 | 192 | 1351.5 | 0 | 170
23:00 | 3525 | 475 | 2011 | 2235 | 314 | 192 | 1354 | 0 | 170
23:30 | 3463 | 474.5 | 2007 | 2227.5 | 314 | 191.5 | 1348.5 | 0 | 168 | Max Temp. in Dhaka |  | 31.5° C
24:00 | 3401 | 474 | 2003 | 2220 | 314 | 191 | 1343 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 200.307 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 200.307 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 70 | 70 | 70 | 72 | 73 | 73 | 77 | 78 | 78 | 79 | 79 | 77 | 75 | 73 | 73 | 110 | 112 | 115 |  | 117 | 117 | 118 | 119 | 120 | 120 | 119 | 2127898
2 | Kaptai Unit-4 & 5 | 38 | 63 | 65 | 64 | 66 | 68 | 69 | 70 | 70 | 71 | 74 | 71 | 66 | 67 | 67 | 67 | 68 | 68 |  | 70 | 70 | 70 | 72 | 72 | 72 | 72 | 1612500
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | [15 empty] | 25 | 25 | 25 |  | 25 | 25 | 25 | 26 | 25 | 25 | 25 | 205560
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 201 | 201 | 201 | 195 | 195 | 195 | 195 | 202 | 195 | 202 | 202 | 202 | 202 | 216 | 201 | 221 | 195 | 195 |  | 195 | 195 | 195 | 195 | 195 | 201 | 196 | 4731352
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 0 | [15 empty] | 637155
| Dohazari Peaking | 17 | 17 | 17 | 17 | 0 | [14 empty] | 64 | 77 | 76 | 81 | 81 | 81 | 81 | 501675
12 | Hathazari peaking | [13 empty] | 8 | 0 |  |  | 28 |  | 82 | 82 | 74 | 74 | 74 | 74 | 74 | 452016
Daudkandi bangla trak
14 | Daudkandi Peaking 52MW | [12 empty] | 8 | 0 | [5 empty] | 8 | 8 | 0 |  |  |  |  | 8096
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | [8 empty] | 0 | 57 | 99 | 199 | 201 | 170 | 203 | 203 | 202 | 155 |  | 100 | 150 | 120 | 120 | 120 | 120 | 120 | 2215000
17 | Siddhirganj CCPP-335 MW | 185 | 185 | 185 | 185 | 185 | 185 | 190 | 0 | 0
18 | Summit Gazipur | 206 | 205 | 189 | 189 | 188 | 188 | 188 | 185 | 190 | 190 | 150 | 105 | 115 | 115 | 115 | 115 | 110 | 110 |  | 153 | 260 | 258 | 298 | 301 | 302 | 301 | 2968253
19 | Ashuganj 195MW Modular | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1906909
20 | Ghorasal ST: Unit-1,2
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2882565
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 200 | 200 | 200 | 200 | 150 | 100 | 100 | 100 | 140 | 140 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5060400
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2412184
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 150 | 150 | 110 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2562805
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 42 | 42 | 42 | 42 | 41 | 10 | 10 | 10 | 32 | 32 | 39 | 39 | 39 | 42 | 42 | 42 | 42 | 42 |  | 39 | 39 | 41 | 41 | 41 | 41 | 41 | 845784
33 | Ashuganj CCPP 225 MW | 182 | 182 | 187 | 183 | 183 | 184 | 189 | 204 | 192 | 183 | 220 | 195 | 183 | 202 | 183 | 183 | 184 | 186 |  | 193 | 184 | 184 | 197 | 190 | 201 | 184 | 4613000
34 | Ashuganj CCPP(South) | 253 | 257 | 257 | 253 | 246 | 246 | 253 | 279 | 253 | 246 | 264 | 272 | 300 | 327 | 279 | 268 | 272 | 301 |  | 298 | 300 | 301 | 316 | 309 | 327 | 301 | 6790750
| Ashuganj CCPP(North) | 251 | 251 | 251 | 251 | 251 | 251 | 255 | 280 | 260 | 250 | 295 | 315 | 300 | 330 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 320 | 308 | 328 | 300 | 7204600
35 | Ashuganj (Precision) 55MW | [7 empty] | 0
36 | Chandpur CCPP | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 153 | 154 | 154 | 153 | 153 | 155 | 154 | 154 | 154 | 154 |  | 154 | 154 | 154 | 154 | 153 | 154 | 154 | 3622900
37 | Tongi GT
38 | Haripur GT: Unit-1, 2 | [12 empty] | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 226300
39 | Haripur 412 MW CCPP | 342 | 342 | 342 | 342 | 342 | 280 | 280 | 280 | 365 | 350 | 300 | 360 | 345 | 360 | 360 | 340 | 338 | 330 |  | 325 | 344 | 340 | 380 | 387 | 382 | 375 | 8340880
40 | Meghnaghat CCPP 450MW | 380 | 380 | 380 | 360 | 360 | 330 | 300 | 300 | 400 | 370 | 380 | 400 | 400 | 420 | 450 | 450 | 450 | 450 |  | 400 | 400 | 350 | 380 | 380 | 400 | 400 | 9105625
41 | Haripur Power CCPP 360MW | 330 | 346 | 354 | 354 | 354 | 321 | 301 | 302 | 346 | 317 | 302 | 342 | 344 | 343 | 344 | 345 | 313 | 311 |  | 282 | 326 | 333 | 331 | 331 | 342 | 342 | 7911000
42 | Mymensingh RPCL 210MW | 89 | 89 | 89 | 103 | 104 | 104 | 103 | 103 | 103 | 71 | 49 | 49 | 49 | 49 | 49 | 50 | 49 | 100 |  | 97 | 102 | 99 | 96 | 97 | 95 | 102 | 1903600
43 | Haripur NEPC 110MW | [19 empty] | 13 | 13 | 0 |  |  |  |  | 17500
44 | Fenchugonj CCPP-1 | 66 | 66 | 66 | 66 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1362000
45 | Fenchugonj CCPP-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 709840
46 | Shajibazar 330 MW | 299 | 299 | 308 | 302 | 301 | 309 | 311 | 321 | 306 | 302 | 316 | 310 | 304 | 319 | 301 | 309 | 303 | 309 |  | 313 | 302 | 304 | 314 | 310 | 316 | 302 | 7006941
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 63 | 64 | 52 | 63 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 59 | 46 | 62 | 62 |  | 63 | 50 | 53 | 62 | 62 | 62 | 63 | 1438000
48 | Shahjibazar 86MW | 89 | 89 | 60 | 30 | 30 | 5 | 5 | 5 | 30 | 30 | 20 | 20 | 20 | 20 | 60 | 20 | 10 | 10 |  | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 981120
49 | Shahjibazar (EPL) 50MW | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 20 | 20 | 20 | 20 | 20 | 20 | 48 | 48 | 10 | 10 |  | 10 | 48 | 48 | 48 | 49 | 49 | 49 | 750240
50 | Sylhet GT 150 MW | 78 | 77 | 78 | 78 | 77 | 78 | 78 | 78 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 77 | 78 | 78 |  | 77 | 79 | 80 | 80 | 80 | 78 | 78 | 1927890
51 | Sylhet GT 20 MW | [13 empty] | 12 | 12 | 12 | 15 | 20 |  | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 185000
52 | Sylhet (EPL) 50MW | 43 | 43 | 43 | 7 | 7 | 7 | 7 | 43 | 43 | 43 | 41 | 40 | 40 | 42 | 41 | 43 | 11 | 11 |  | 12 | 44 | 43 | 43 | 43 | 43 | 43 | 795120
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 |  | 9 | 7 | 9 | 9 | 9 | 9 | 9 | 212040
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256992
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 17 | 47 | 53 | 11 | 11 |  | 11 | 34 | 53 | 53 | 53 | 53 | 53 | 686400
56 | Shahjahanulla 25 MW | 22 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 7 | 12 | 8 | 15 | 15 | 20 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 457992
57 | Summit Bibiana- 2 | 280 | 290 | 280 | 280 | 280 | 280 | 300 | 320 | 320 | 300 | 290 | 310 | 310 | 300 | 290 | 290 | 280 | 290 |  | 265 | 290 | 265 | 290 | 320 | 320 | 310 | 7473100
58 | Southern 55MW | 0 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 45 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 872638
59 | Sikalbaha (Energis) | 24 | 24 | 24 | 8 | 8 | 8 | 8 | 8 | 11 | 38 | 42 | 51 | 51 | 47 | 0 | 21 | 42 | 42 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 800160
60 | Barabkunda (Regent) | 0 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 423216
61 | Narshingdi (Doreen) | 22 | 0 |  | 0 | 19 | 0 |  |  |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 0 | 22 | 22 | 0 | 307368
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 0 |  |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 392184
63 | Tripura | 134 | 136 | 140 | 130 | 108 | 116 | 114 | 100 | 106 | 114 | 118 | 126 | 132 | 140 | 140 | 124 | 124 | 134 |  | 164 | 168 | 166 | 178 | 170 | 170 | 166 | 3297600
64 | Malancha, Ctg. EPZ (United) | 40 | 42 | 42 | 42 | 42 | 34 | 8 | 6 | 6 | 8 | 6 | 6 | 16 | 3 | 5 | 20 | 23 | 36 |  | 42 | 41 | 42 | 42 | 42 | 42 | 42 | 637920
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 0 |  |  | 13 | 19 | 0 | 0 |  |  | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 306756
66 | Feni, Mohipal (Doreen) | 0 | 0 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 |  | 0 | 8 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 125460
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 685300
68 | Summit Comilla 25MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 501260
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 28 | 28 | 28 | 31 | 31 | 31 | 31 | 31 | 31 | 32 |  | 24 | 32 | 32 | 32 | 32 | 32 | 32 | 614520
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 697700
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 30 | 25 | 30 | 30 | 30 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 28 | 28 | 763300
73 | Ghorashal (Regent) | 104 | 104 | 104 | 104 | 25 | 25 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 57 | 102 | 106 | 106 | 103 |  | 107 | 107 | 106 | 106 | 103 | 103 | 103 | 1732840
76 | Siddhirganj (Desh) | [19 empty] | 8 | 15 | 0 |  |  |  |  | 23040
77 | Siddhirganj (Dutch Bangla) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 30 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 16 | 20 | 40 | 40 | 40 | 40 | 412800
78 | Gazipur (RPCL) | 50 | 50 | 50 | 25 | 8 | 8 | 8 | 11 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 42 | 49 | 49 | 50 | 50 | 50 | 50 | 777672
79 | Kodda 150MW | 133 | 133 | 133 | 133 | 130 | 115 | 115 | 115 | 115 | 115 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2960160
80 | Jamalpur 95MW | 56 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [9 empty] | 16 | 50 | 82 | 92 | 92 | 92 | 92 | 586096
81 | Lakdhanvi 52 MW | [19 empty] | 1 | 25 | 19 | 25 | 0 |  |  | 53386
82 | Madanganj 102MW | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 18 | 50 | 65 | 48 | 15 | 15 | 15 | 636696
83 | Pagla (DPA ) | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 |  | 10 | 10 | 10 | 10 | 11 | 10 | 11 | 148420
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 30 | 6 | 6 | 5 | 30 | 31 | 5 | 5 | 5 | 30 | 60 | 11 | 11 | 11 |  | 10 | 41 | 41 | 41 | 41 | 41 | 41 | 636696
85 | Keraniganj (Powerpac) 100MW | 40 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 88 | 100 | 100 | 50 |  | 50 | 86 | 100 | 50 | 50 | 50 | 50 | 919773
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 200 | 200 | 200 | 200 | 200 | 220 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 5196829
87 | Meghnaghat (IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 25 | 28 | 55 | 30 | 15 | 15 | 323520
88 | Ghorashal 78MW (MAX) | 79 | 80 | 79 | 79 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 40 | 70 | 76 | 76 |  | 76 | 76 | 77 | 77 | 77 | 77 | 77 | 1386112
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 80 | 80 | 50 | 30 | 20 | 20 | 20 | 20 | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 |  | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 1601520
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 29 | 50 | 50 | 50 | 50 | 50 | 50 | 55 | 50 | 10 | 10 |  | 10 | 25 | 37 | 50 | 50 | 50 | 50 | 926000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 40 | 5 | 5 | 5 | 5 | 12 | 51 | 51 | 51 | 51 | 51 | 50 | 20 | 12 | 12 |  | 12 | 12 | 12 | 20 | 35 | 51 | 51 | 778462
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 | 24 | 102 | 102 | 50 | 50 |  | 102 | 102 | 102 | 50 | 50 | 50 | 32 | 877248
95 | Patenga 50MW | 13 | 17 | 18 | 18 | 18 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 10 | 18 | 18 |  | 19 | 30 | 35 | 35 | 42 | 43 | 43 | 401760
96 | Chittagong ECPV 108 MW | 32 | 32 | 32 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 23 | 18 | 18 | 22 | 19 | 19 | 19 | 19 |  | 87 | 97 | 98 | 98 | 99 | 99 | 99 | 924480
97 | Katpotti 51 MW | 0 | [7 empty] | 0 | 24 | 24 | 24 | 44 | 48 | 48 | 6 | 6 | 6 |  | 12 | 12 | 48 | 48 | 48 | 48 | 48 | 505728
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 51 | 15 | 8 | 8 |  | 58 | 100 | 101 | 100 | 100 | 100 | 100 | 730560
99 | Madanganj-55 MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 26 | 30 | 32 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 776627
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 | 54 | 54 | 56 | 56 | 55 | 56 | 56 |  | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 940024
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 130 | 100 | 100 | 130 | 163 | 130 | 130 | 100 | 100 |  | 100 | 163 | 130 | 130 | 130 | 130 | 130 | 2965745
102 | Sarishabari (Solar) | [5 empty] | 0.2 | 0.3 | 0.4 | 0.3 | 0.4 | 1 | 1.4 | 1.3 | 1 | 1.3 | 0.7 | 0.3 | 0.1 |  | 0 | [6 empty] | 10600
103 | Banco Energy 54MW | [7 empty] | 12 | 18 | 18 | 18 | 25 | 36 | 36 | 54 | 18 | 18 | 18 |  | 18 | 55 | 54 | 54 | 54 | 54 | 54 | 525600
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 |  | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 4838400
112
113
114
115
116
117
118 | Eastern Zone Total | 6298 | 6274 | 6209 | 6002 | 5544 | 5215.2 | 5165.3 | 5151.4 | 5668.3 | 5684.4 | 5722 | 5971.4 | 6093.3 | 6330 | 6568.3 | 6468.7 | 6189.3 | 6259.1 | 0 | 6599 | 7351 | 7315 | 7476 | 7429 | 7517 | 7354 | 148851158
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 81 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 51 | 81 | 81 | 81 | 81 | 81 |  | 81 | 102 | 102 | 102 | 102 | 101 | 102 | 1191360
124 | Khulna (KPCL-2) | 99 | 99 | 99 | 99 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 36 | 106 | 102 | 109 | 105 |  | 112 | 110 | 104 | 115 | 115 | 115 | 115 | 1620480
125
126 | Khulna (Aggreko) 55MW | [20 empty] | 48 | 52 | 12 | 31 | 31 | 33 | 142340
127 | Faridpur Peaking | 42 | 42 | 42 | 42 | 0 | [10 empty] | 26 | 31 | 34 |  | 39 | 15 | 14 | 34 | 37 | 39 | 39 | 440640
128 | Khulna CCPP 225MW | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 200 | 223 | 225 | 226 | 227 | 228 | 228 | 3576960
129
130
131
132
133
| Summit Barisal 110 MW | 64 | 64 | 64 | 64 | 26 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 64 | 74 | 110 | 112 | 64 | 64 | 64 | 951360
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 96 | 97 | 97 | 96 | 96 | 41 | 41 | 41 | 41 | 40 | 21 | 20 | 21 | 51 | 71 | 70 | 70 | 72 |  | 71 | 96 | 97 | 98 | 98 | 98 | 99 | 1628652
137 | Bhola CCPP 194MW | 191 | 187 | 192 | 191 | 184 | 192 | 192 | 192 | 192 | 192 | 171 | 172 | 172 | 172 | 180 | 179 | 186 | 186 |  | 186 | 180 | 183 | 186 | 187 | 189 | 189 | 4529945
| Bhola (Venture) 33MW | 32 | 33 | 33 | 30 | 27 | 25 | 25 | 23 | 22 | 21 | 22 | 24 | 23 | 23 | 26 | 26 | 25 | 26 |  | 33 | 36 | 34 | 37 | 38 | 37 | 38 | 671568
140 | Bangla Trak Noapara | 87 | 50 | 50 | 0 | [16 empty] | 56 | 68 | 68 | 68 | 68 | 68 | 553920
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 33 | 33 | 33 | 33 | 468750
142 | Gopalganj Peaking | 60 | 60 | 54 | 48 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 8 | 10 | 22 | 32 | 40 |  | 50 | 55 | 60 | 60 | 55 | 55 | 55 | 724864
143 | Bheramara GT-1,2,3 | [21 empty] | 32 | 48 | 48 | 48 | 48 | 217000
144
145 | Bheramara HVDC | 483 | 482 | 482 | 482 | 482 | 482 | 483 | 476 | 476 | 477 | 477 | 477 | 476 | 477 | 476 | 477 | 477 | 475 |  | 474 | 475 | 474 | 474 | 480 | 475 | 474 | 11382546
146 | Bheramara 360 MW
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 48 | 49 | 63 | 66 | 67 | 67 | 65 | 68 | 68 | 67 | 67 | 66 | 64 | 66 | 65 | 65 | 65 | 66 |  | 65 | 66 | 65 | 65 | 66 | 64 | 64 | 1545600
151 | Barapukuria Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 249 | 174 | 150 | 150 | 150 | 175 | 201 | 232 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 5568700
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | 43 | 43 | 43 | 43 | 0 | [12 empty] | 0 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 411728
| Sirajgonj Unit-1 225MW (Gas) | 219 | 218 | 217 | 217 | 217 | 217 | 218 | 217 |  | 59 | 182 | 213 | 213 | 213 | 214 | 212 | 212 | 212 |  | 214 | 214 | 215 | 215 | 214 | 214 | 214 | 5020845
157 | Sirajgonj Unit-1 225MW (Oil)
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 222 | 223 | 223 | 223 | 220 | 171 | 142 | 145 | 145 | 145 | 145 | 145 | 145 | 143 | 148 | 177 | 173 | 169 |  | 170 | 175 | 171 | 171 | 178 | 181 | 174 | 4303963
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | [16 empty] | 7 | 26 |  | 44 | 44 | 44 | 45 | 46 | 46 | 46 | 270862
161 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 486480
162 | Bogra (EPL) | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 12 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234936
163 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 219294
164 | Amnura 50MW | 50 | 50 | 50 | 50 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 954710
165 | Katakhali (Northern) | 35 | 35 | 35 | 35 | 8 | 8 | 8 | 16 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 673104
166 | Katakhali Peaking | 45 | 45 | 45 | 45 | 45 | 0 | [11 empty] | 18 |  | 45 | 45 | 47 | 45 | 45 | 44 | 44 | 502562
167 | Santahar Peaking | 41 | 41 | 41 | 41 | 0 | [14 empty] | 35 | 42 | 43 | 43 | 35 | 35 | 35 | 378710
168 | Rajlanka 52 MW | 43 | 8 | 8 | 8 | 8 | 8 | 43 | 43 | 43 | 25 | 25 | 25 | 25 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 794880
169 | Chapainawabganj-100 MW | 102 | 102 | 102 | 102 | 102 | 102 | 26 | [6 empty] | 0 | 40 | 90 | 95 | 102 |  | 102 | 102 | 102 | 102 | 102 | 99 | 99 | 1539934
170
171
172 | Rangpur GT | 14 | 14 | 14 | 0 | [13 empty] | 16 |  | 16 | 16 | 17 | 15 | 17 | 14 | 16 | 153000
173 | Saidpur GT | 18 | 18 | 18 | 18 | 18 | 0 | [5 empty] | 18 | 18 | 16 | 14 | 15 | 14 | 18 |  | 18 | 18 | 17 | 17 | 17 | 17 | 16 | 296000
175
176
177
178 | Western Zone Total | 2589 | 2424 | 2436 | 2363 | 1964 | 1794 | 1723 | 1714 | 1493 | 1540 | 1623 | 1637 | 1635 | 1747 | 1895 | 2030 | 2091 | 2191 |  | 2523 | 2696 | 2780 | 2787 | 2767 | 2759 | 2758 | 51455693
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953