## Daily Gen
Hourly Generation & Demand
Date | 2014-08-13
Time | Generation | Demand | Shortage | Remarks
Hour | MW | MW | MW
1:00 | 6568 | 6568 | 0
2:00 | 6406 | 6406 | 0
3:00 | 6183 | 6183 | 0
4:00 | 6064 | 6064 | 0
5:00 | 5982 | 5982 | 0
6:00 | 5430 | 5430 | 0
7:00 | 5437 | 5437 | 0
8:00 | 5470 | 5470 | 0
9:00 | 5683 | 5683 | 0
10:00 | 5693 | 5693 | 0 | Day peak
11:00 | 5635 | 5790 | 139.5
12:00 | 5679 | 5840 | 144.9
13:00 | 5683 | 5683 | 0
14:00 | 5499 | 5720 | 198.9
15:00 | 5577 | 5700 | 110.7
16:00 | 5622 | 5622 | 0
17:00 | 5621 | 5621 | 0
18:00 | 5858 | 5858 | 0
18:30 | 6114 | 6114 | 0
19:00 | 6363 | 6363 | 0
19:30 | 6488 | 6488 | 0
20:00 | 6647 | 6647 | 0 | Evening Peak
21:00 | 6633 | 6633 | 0
22:00 | 6536 | 6536 | 0
23:00 | 6320 | 6320 | 0
24:00 | 6060 | 6060 | 0

## forecast
[7 empty] | POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-07
SUMMARY OF DAILY ELECTRICITY GENERATION
|  | Month : |  | 2014-08-14 |  |  | Day : | Thursday |  |  |  | Date : | 2014-08-14
| Probable Maximum Generation : |  |  |  | (a) At Day Peak Hour : |  | 5546 | MW |  | (b) At Evening Peak Hour : |  |  | 6716 | MW
| Water Level of Kaptai Lake at 06:00 AM (ft) |  |  |  | (a) Yesterday : |  | 85.81 |  |  | (b) Today: | 86.57 | (c) Rule Curve: |  | 93.16
Sl. | Name of the Power Station |  | Fuel | Producer | Instslled Capacity |  | Derated/ | Actual Generation |  | Available Geneneration |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[7 empty] | Present | On | 2014-08-13 | On | 2014-08-14 | for Fuel | for Plants S/D | Shut down (Date) / |  | Start up
[7 empty] | Capacity | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | or M/C prob. | Remarks |  | Date
[6 empty] | MW | MW | MW | MW | MW | MW | MW | MW
1a | Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2X55 | 110 | 85 | 88 | 88 | 88 | 88
1b | Ghorasal ST: Unit-3 |  | Gas | PDB | 1x210 | 210 | 170 | 100 | 100 | 100 | 100 |  | 70
1c | Ghorasal ST: Unit-4 |  | Gas | PDB | 1x210 | 210 | 180 | 180 | 180 | 180 | 180
1d | Ghorasal ST: Unit-5 |  | Gas | PDB | 1x210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | 2014-12-08 |  | 15/08/2014
1e | Ghorasal ST: Unit-6 |  | Gas | PDB | 1x210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6 (18/07/2010) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128X0.85 | 100 | 100 | 91 | 94 | 92 | 94
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58X0.85 | 45 | 45 | 42 | 42 | 42 | 42
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4x21.5 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract date expired 26/05/2014
5 | Ghorashal (Regent) |  | Gas | IPP | 34x3.35 | 108 | 108 | 99 | 102 | 101 | 104
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3x32 | 96 | 60 | 0 | 0 | 0 | 0 | 40 | 20 | #1&#2(22/10/13),#3(18/6/09) |  | #3 long term maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1x273+1x139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | 2014-03-08 |  | 21/08/2014
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8x15 | 110 | 110 | 70 | 83 | 70 | 83 |  | 27
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 346 | 354 | 346 | 14
10 | Meghnaghat CCPP |  | Gas | IPP | 2X150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | 21/04/2014 |  | Long term maint.
11 | Meghnaghat (IEL) |  | HFO | RPP | 12x8.9 | 100 | 100 | 81 | 89 | 90 | 89 |  | 11 | 1 Engine problem
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2x110+1x110 | 203 | 203 | 208 | 205 | 101 | 203
13 | Madanganj (Summit) |  | HFO | QRPP | 6x17 | 102 | 100 | 92 | 92 | 77 | 92
14 | Keraniganj (Powerpac) |  | HFO | RPP | 8x13.45 | 100 | 100 | 89 | 101 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8X2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Synchronized at 33KV, 1 Engine problem
16a | Siddhirgonj ST |  | Gas | PDB | 1x210 | 210 | 150 | 110 | 110 | 110 | 110 | 40
16b | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2x105 | 210 | 210 | 76 | 61 | 60 | 61 | 149
17 | Siddhirganj (Desh) |  | HSD | QRPP | 96x1.2 | 96 | 98 | 67 | 84 | 72 | 84 |  | 14 | 11 Engine problem
18 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12x8.9 | 100 | 100 | 67 | 67 | 67 | 67 |  | 33 | 3 Engine problem
19 | Pagla (DPA ) |  | HSD | QRPP | 100X0.5 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract date expired
20 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
21 | Summit Power, Dhaka |  | Gas | SIPP,REB | 6*3.67+2*6.97+14*8.73 | 146 | 146 | 105 | 96 | 108 | 96 |  |  | Synchronized at 33KV
22 | Gazipur (RPCL) |  | HFO | IPP | 6x8.9 | 52 | 52 | 34 | 34 | 34 | 34 |  | 18 | 2 Engine problem
23 | Tongi GT |  | Gas | PDB | 1X 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105
| Dhaka Area Total |  |  |  |  | 4307 | 4076 | 2061 | 2093 | 1965 | 2092 | 348 | 1028
24a | Chittagong ST: Unit-1 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 13/08/2014 |  | 15/08/2014
24b | Chittagong ST: Unit-2 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 80 | 100 | 80 | 100
25 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3x8.9 | 25 | 25 | 26 | 26 | 26 | 26
26 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8x6.89 | 50 | 50 | 6 | 40 | 0 | 45
27 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2X40, 3X50 | 230 | 230 | 78 | 181 | 44 | 181
28a | Sikalbaha ST |  | Gas | PDB | 1X60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | 2014-03-07 |  | Unknown
28b | Sikalbaha Peaking GT |  | Gas | PDB | 1x150 | 150 | 150 | 128 | 148 | 113 | 148
29 | Sikalbaha (Energis) |  | HFO | RPP |  | 26 | 26 | 17 | 25 | 25 | 25
30 | Hathazari peaking |  | HFO | PDB | 11x8.9 | 98 | 98 | 0 | 96 | 0 | 98
31 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6x17 | 102 | 102 | 0 | 102 | 0 | 102
32 | Juldah (Acorn) |  | HFO | QRPP | 8x13.45 | 100 | 100 | 92 | 92 | 80 | 92 |  | 8
33 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | Synchronized at 33KV
34 | Malancha, Ctg. EPZ (United) |  | Gas |  |  |  |  | 3 | 26 | 5 | 26
| Chittagong area Total |  |  |  |  | 1283 | 1203 | 372 | 838 | 415 | 845 | 100 | 228
35a | Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2x64 | 128 | 97 | 90 | 90 | 90 | 90
35b | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1x150 | 150 | 135 | 130 | 130 | 130 | 130
35c | Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1x150 | 150 | 129 | 140 | 140 | 140 | 140
35d | Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1x150 | 150 | 134 | 130 | 130 | 130 | 130
35e | Ashuganj CCPP: GT-2 |  | Gas | APSCL | 1x56 | 56 | 40 | 40 | 40 | 40 | 40
35f | Ashuganj Engines |  | Gas | APSCL | 14x3.968 | 53 | 45 | 36 | 38 | 39 | 38 |  | 7 | 2 Machine problem
36 | Ashuganj (Precision) |  | Gas | RPP | 15x4 | 55 | 55 | 49 | 53 | 49 | 55
37 | Ashuganj (Aggrekko) |  | Gas | QRPP | 82x1.1 | 80 | 80 | 79 | 81 | 79 | 80
38 | Ashuganj (United) |  | Gas | QRPP | 14x4 | 53 | 53 | 53 | 49 | 49 | 49
39 | Ashuganj (Midland) |  | Gas | IPP | 6x9.34 | 51 | 51 | 41 | 42 | 42 | 42 |  | 9 | 1 Machine problem
40 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 72x1.10 | 70 | 70 | 85 | 85 | 83 | 85
41 | Titas (Daudkandi) Peaking |  | HFO | PDB | 6x8.92 | 52 | 52 | 0 | 34 | 0 | 42 |  | 18 | 2 Engine problem
42 | Chandpur CCPP |  | Gas | PDB | 1x106+1x57 | 163 | 163 | 162 | 162 | 160 | 163
43 | Feni (Doreen) |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 13 | 15 | 14 | 15 |  | 7 | 2 Machine problem
44 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 0 | 8 | 0 | 8 |  | 3 | Synchronized at 33KV , 1 Machine problem
45 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4X8.73 | 33 | 33 | 18 | 34 | 0 | 33 |  |  | Synchronized at 33KV
46 | Summit Power, Comilla |  | Gas | SIPP,REB | 3x3.67+2x6.97 | 25 | 25 | 14 | 15 | 12 | 15 |  | 10 | Synchronized at 33KV, 3 Engine problem
| Comilla Area Total |  |  |  |  | 1302 | 1195 | 1080 | 1146 | 1057 | 1155 | 0 | 54
47 | RPCL CCPP |  | Gas | IPP | 4X35+1x70 | 210 | 202 | 149 | 135 | 150 | 135 | 67
48 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8X2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Synchronized at 33KV, 1 Machine problem
| Mymensingh Area Total |  |  |  |  | 232 | 224 | 166 | 152 | 167 | 152 | 67 | 0
49a | Fenchugonj CCPP-1 |  | Gas | PDB | 2x32+1x33 | 97 | 80 | 52 | 52 | 33 | 52 |  | 28
49b | Fenchugonj CCPP-2 |  | Gas | PDB | 2x35+1x35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | #3(28/07/14) |  | 15/08/2014
50 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19X2.90 | 51 | 51 | 43 | 50 | 50 | 51
51 | Fenchuganj (Energyprima) |  | Gas | RPP | 12x3.3+5x2 | 44 | 44 | 47 | 45 | 42 | 44
52 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4X2.90 | 11 | 11 | 4 | 10 | 11 | 10 |  |  | Synchronized at 33KV
53 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2X35 | 70 | 66 | 52 | 64 | 68 | 64
54 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32X2.90 | 86 | 86 | 81 | 84 | 84 | 84
55 | Shahjibazar (Energyprima) |  | Gas | RPP | 27X2.0 | 50 | 50 | 46 | 48 | 47 | 48
56 | Sylhet 150 MW GT |  | Gas | PDB | 1X142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | 28/07/2014 |  | 18/8/2014
57 | Sylhet 20 MW GT |  | Gas | PDB | 1X20 | 20 | 20 | 20 | 19 | 20 | 19
58 | Sylhet (Energyprima) |  | Gas | RPP | 27X2 | 50 | 50 | 46 | 46 | 45 | 46 |  | 4 | 2 Machine problem
59 | Shahjahanulla 25 MW |  | Gas | CIPP, REB | 3x9.34 | 25 | 25 | 18 | 24 | 18 | 25
60 | Sylhet (Desh) |  | Gas | RPP | 6X1.95 | 10 | 10 | 9 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 760 | 725 | 461 | 494 | 470 | 495 | 0 | 221
61 | Bheramara GT: Unit- 1, 2 ,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 44 | 0 | 46
62 | Bheramara (Quantum) |  | HSD | RPP | 12X8.5+2X6+2X13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | 16 Engine problem |  | Long term maint.
63 | Bheramara HVDC Interconnector |  |  | India |  | 500 | 500 | 401 | 349 | 400 | 353
64a | Khulna ST 110MW |  | HFO | PDB | 1X110 | 110 | 55 | 56 | 0 | 0 | 0 |  | 55 | 20/7/14 |  | Unknown
64b | Khulna ST 60 MW |  | HFO | PDB | 1X60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
65 | Khulna (KPCL-1) |  | HFO | IPP | 19x6.5 | 110 | 110 | 101 | 107 | 23 | 110
66 | Khulna (KPCL-2) |  | HFO | QRPP | 7x17 | 115 | 115 | 83 | 100 | 99 | 100 |  | 15 | 1 Engine problem
67 | Faridpur Peaking |  | HFO | PDB | 8x6.89 | 54 | 54 | 0 | 36 | 0 | 36 |  | 18 | 2 Engine problem
68 | Khulna 150MW GT |  | HSD | NWZPGCL | 1x150 | 158 | 158 | 0 | 130 | 155 | 158
69 | Gopalganj Peaking |  | HFO | PDB | 16x6.98 | 109 | 109 | 25 | 60 | 0 | 60 |  | 49 | 7 Engine problem
70 | Noapara (Quantam) |  | HFO | RPP | 5x9.9+6x9.5+2x9.2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | Long term maint.
71 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5x8.5 | 40 | 40 | 32 | 32 | 32 | 32 |  | 8 | 1 Engine problem
0
72 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71X0.85 | 55 | 55 | 43 | 31 | 37 | 37 |  |  | Contract date expired
| Khulna Area Total |  |  |  |  | 1517 | 1448 | 741 | 889 | 746 | 932 | 0 | 351
73 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2X20 | 40 | 30 | 0 | 31 | 0 | 30
74 | Bhola (Venture) |  | Gas | RPP | 1X34.50 | 33 | 33 | 22 | 38 | 16 | 33
| Barisal Area Total |  |  |  |  | 73 | 63 | 22 | 69 | 16 | 63 | 0 | 0
75a | Baghabari GT |  | Gas | PDB | 1X71 | 71 | 71 | 69 | 69 | 70 | 69
75b | Baghabari GT |  | Gas | PDB | 1X100 | 100 | 100 | 80 | 98 | 98 | 98
76 | Baghabari Peaking |  | HFO | PDB | 6x8.9 | 52 | 52 | 32 | 40 | 0 | 40 |  | 12 | 1 Engine problem
77 | Westmont GT, Baghabari |  | Gas | IPP |  |  |  | 0 | 0 | 0 | 0 |  |  | Plant Retired in FY 2013-2014
78 | Bera Peaking |  | HFO | PDB | 9x8.29 | 71 | 71 | 45 | 64 | 0 | 64 |  |  | Low demand.
79 | Amnura |  | HFO | QRPP | 7x7.79 | 50 | 50 | 28 | 28 | 9 | 44 |  | 22 | 1 Engine problem
80 | Katakhali (Northern) |  | HFO | QRPP | 6x8.92 | 50 | 50 | 50 | 50 | 42 | 50
81 | Katakhali Peaking |  | HFO | PDB | 6x8.7 | 50 | 50 | 0 | 45 | 0 | 45
82 | Sirajganj CCPP |  | Gas | NWPGCL | 1x150+1x75 | 210 | 210 | 210 | 210 | 213 | 210
83 | Santahar Peaking |  | HFO | PDB | 6x8.7 | 50 | 50 | 0 | 46 | 0 | 46
84 | Bogra (GBB) |  | Gas | RPP | 6X4 | 20 | 22 | 18 | 18 | 18 | 18 |  | 4 | 1 Machine problem
85 | Bogra (Energyprima) |  | Gas | RPP | 5x3.3+5x2 | 20 | 20 | 13 | 17 | 17 | 17 |  | 4 | 1 Machine problem
86 | Ullapara (Summit) |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 10 | 10 | 10 | 10 |  |  | Synchronized at 33KV
87 | Rajlanka 52 MW |  | HFO | IPP | 6X8.92 | 52 | 52 | 52 | 43 | 43 | 43
| Rajshahi Area Total |  |  |  |  | 807 | 809 | 607 | 738 | 520 | 754 | 0 | 42
88a | Barapukuria ST: Unit-1 |  | Coal | PDB | 1x125 | 125 | 100 | 74 | 76 | 70 | 76 |  | 24
88b | Barapukuria ST: Unit-2 |  | Coal | PDB | 1x125 | 125 | 100 | 88 | 89 | 90 | 89 |  | 11
89 | Rangpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 15 | 0 | 15 |  | 5
90 | Syedpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 17 | 0 | 17
91 | Thakurgaon (RZ) |  | HSD | RPP | 20X1.5+21X1.1 | 47 | 40 | 21 | 31 | 30 | 31 |  | 9 | 10 Engine problem
| Rangpur Area Total |  |  |  |  | 337 | 280 | 183 | 228 | 190 | 228 | 0 | 49
| Total |  |  |  |  | 10618 | 10023 | 5693 | 6647 | 5546 | 6716 | 515 | 1973
| Useable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5118.6915 | 6132 | 4986.5208 | 6038
A. |  | 2014-08-13 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 6647 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs. |  | EWIC
2 | Minimum Generation : |  |  | 5430 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6647 | MW |  | 160
3 | Day peak Generation : |  |  | 5693 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6132 | MW |  | 60
4 | Evening peak Generation : |  |  | 6647 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW |  | -10
5 | Total Energy Generation : |  |  | 141.6899 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during |  |  | -30
| By Gas: | 86.8935 | MKWHr |  | By Oil: | 39.6873 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours : |  |  | -20
| By Coal: | 3.8439 | MKWHr |  | By Hydro: | 1.8884 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed | -60
6 | Generation Shortfall : |  | For Gas: | 515 | For Oil: | 0 | MW | Dhaka | 2513 | 2513 | 0 |  |  | Hour |  | MW | Loadshed
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 653 | 653 | 0 |  |  | 18:00 |  | 0 | 0%
|  |  | For Plants S/D or M/C prob: |  |  | 1973 | MW | Khulna | 650 | 650 | 0 |  |  | 18:30 |  | 0 | 0%
7 | Total Gas Supplied : |  | 855.68 | MMCFD |  |  |  | Rajshahi | 669 | 669 | 0 |  |  | 19:00 |  | 0 | 0%
8 | Fuel Cost : | i) Gas : | Taka | 81719385.27 | ii) Oil : Taka |  | 503442012.069 | Comilla | 462 | 462 | 0 |  |  | 19:30 |  | 0 | 0%
|  | iii) Coal : | Taka | 14960563.884 | Total | Taka | 600121961.223 | Mymensingh | 388 | 388 | 0 |  |  | 20:00 |  | 0 | 0%
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 306 | 306 | 0 |  |  | 21:00 |  | 0 | 0%
| ii) During Peak Demand : |  |  | -20 | MW at | 20:00 | hrs | Barisal | 161 | 161 | 0 |  |  | 22:00 |  | 0 | 0%
| iii) Maximum : |  |  | 180 | MW at | 13:00 | hrs | Rangpur | 330 | 330 | 0 |  |  | 23:00 |  | 0 | 0%
10 | Maximum Temperature in Dhaka was |  |  |  | 29.7° C |  |  | Total | 6132 | 6132 | 0 | [5 empty] | 0%
B. |  | 2014-08-14 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.7° C
Forecast
1 | Maximum Demand (Generation end) |  |  |  | 6700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 6716 | MW |  | 7 Area wise Load Shed forecast (Substation end) : | [8 empty] | L/S
3 | Shortage (Generation end) |  |  |  | -16 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
4 | Total Energy Generation |  |  |  | 142 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
5 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4818 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 9.3767 | MKWHr.
ii) During peak Demand : |  |  | 401 | MW at | 20:00 | hrs
iii) Maximum : |  |  | 407 | MW at | 8:00 | hrs
Cost for HVDC energy is not usaually included in the total fuel cost.

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2014-08-14
Till now the maximum generation is : - |  |  | 7418 MW | 21:00 | Hrs on | 2014-07-18
The Summary of Yesterday's ( |  | 2014-08-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 5693 | MW Hour : | 10:00 | Min. Gen. at | 7:00 | 4818 | MW
Evening Peak Generation : |  | 6647 | MW Hour : | 20:00 | Max Generation : |  | 6716 | MW
E.P. Demand (at gen end) : |  | 6647 | MW Hour : | 20:00 | Max Demand : |  | 6700 | MW
Maximum Generation : |  | 6647 | MW Hour : | 20:00 | Shortage : |  | -16 | MW
Total Gen. (MKWH) : |  | 141.6899 | System L/ Factor : | 78.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 180 | MW at | 13:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2014-08-14
Actual : | 87.64 | Ft.(MSL) , | Rule curve : | 93.16 | Ft.( MSL )
Gas Consumed : | Total | 855.68 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : Gas : |  |  | 81719385.27
|  | Coal : | 14960563.884 | Oil : | 503442012.069 | Total : | 600121961.223
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand(s/s end) |  | Estimated Shedding (s/s end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | - | 0:00 | 2422 |  |  | - | -
Chittagong Area | - | 0:00 | 622 |  |  | - | -
Khulna Area | - | 0:00 | 681 |  |  | - | -
Rajshahi Area | - | 0:00 | 660 |  |  | - | -
Comilla Area | - | 0:00 | 454 |  |  | - | -
Mymensingh Area | - | 0:00 | 375 |  |  | - | -
Sylhet Area | - | 0:00 | 305 |  |  | - | -
Barisal Area | - | 0:00 | 136 |  |  | - | -
Rangpur Area | - | 0:00 | 383 |  |  | - | -
-
Total | 0 |  | 6038 |  |  | 0
Information of the Generating machines under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
| 1) Haripur GT: Unit-3 (18/06/2009) |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010)
2) Megnaghat CCPP (21/04/2014)
3) Ghorasal ST: Unit-5(12/08/2014)
4) Sikalbaha ST (03/07/2014)
5) Sylhet 150 MW (28/07/14)
6) Chittagong ST: Unit-1(14/08/2014)
7) Haripur 412 MW CCPP(03/08/2014)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Forced load shaded / Interrupted Areas
a) Ishurdi 132/33 kV T2 transformer was shut down at 09:50 due to red hot maintenance and was switched on at 10:43.
b) After maintenance Chandpur GT & ST were synchronized at 15:07 & 16:28 respectively.
c) Jhenidah-Chandpur 132 kV Ckt tripped at 15:59 showing dist.Z1 and was switched on at 16:10.
d) Feni-Hathazari 132 kV Ckt-2 tripped at 19:05 showing dist. Z1 & E/F relays and was switched on at 19:19.
e) Halishahar 33 kV upper bus was shut down from 07:15 to 08:35(14/08/2014) due to red hot maintenance. |  |  |  | About 20 MW power interruption occurred under Halishar S/S areas
f) Ishurdi-HVDC 230 kV Ckt-1 tripped at 07:40(14/8/14) showing CB auto trip relay and was switched on at 10:01. |  |  |  | from 07:15 to 08:35(14/08/2014).

## P2
POWER GRID COMPANY OF BANGLADESH LTD.
Description of the generation of various Power Stations
| Date : | 2014-08-13 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1 | Ghorasal ST: Unit-1, 2 |  | 2x55 | PDB | 85 | 50 | 2060000
38
2 | Ghorasal ST: Unit-3 |  | 1x210 | PDB | 170 | 100 | 2171610 | Machine problem
3 | Ghorasal ST: Unit-4 |  | 1x210 | PDB | 180 | 180 | 4000185
4 | Ghorasal ST: Unit-5 |  | 1x210 | PDB | 190 | 0 | 0 | Machine problem
5 | Ghorasal ST: Unit-6 |  | 1x210 | PDB | 190 | 0 | 0 | Long term maint.
6 | Ghorashal 100MW(Agreko) |  | 128x0.85 | QRPP | 100 | 94 | 2247170
7 | Ghorashal 45MW(Agreko) |  | 58x0.85 | QRPP | 45 | 42 | 1013230
8 | Ghorashal 78.5 MW (MAX) |  | 4x21.5 | QRPP | 78 | 0 | 0 | Contract Date Expired
9 | Ghorashal (Regent) |  | 34x3.35 | IPP | 108 | 102 | 2406637 | On test
|  |  | 1x32 | PDB | 20 | 0 | 0 | Gas pressure low
10 | Haripur GT: Unit-1, 2, 3 |  | 1x32 | PDB | 20 | 0 | 0 | Gas pressure low
|  |  | 1x32 | PDB | 20 | 0 | 0 | Under maint. since 18/06/09
11 | Haripur EGCB 412 MW CCPP |  | 1x273+1x139 | EGCB | 412 | 0 | 0 | Machine problem
12 | Haripur NEPC(HFO) |  | 8x15 | IPP | 110 | 83 | 1959400 | 2 Engine problem
13 | Haripur Power CCPP |  | 1x235+1x125 | IPP | 360 | 346 | 8280000 | Gas pressure low
14 | Meghnaghat CCPP |  | 2x150+1x150 | IPP | 450 | 0 | 0 | Long term maint.
15 | Meghnaghat (IEL) |  | 12x8.9 | RPP | 100 | 89 | 2024640 | Engine problem
16 | Meghnaghat CCPP(Summit) |  | 2x110+1x110 | IPP | 203 | 205 | 4455476
17 | Madanganj (Summit) |  | 6x17 | QRPP | 100 | 92 | 2014464 | Engine problem
18 | Keraniganj (Powerpac) |  | 8x13.45 | RPP | 100 | 101 | 2313941
19 | Narsingdi (Doreen) |  | 8 x 2.9 | SIPP, REB | 22 | 17 | 362304 | Synchronized at 33KV, 1 Machine problem
20 | Siddhirgonj ST |  | 1x210 | PDB | 150 | 110 | 2545200 | Gas pressure low
21 | Siddhirgonj GT : Unit-1 & 2 |  | 2x105 | EGCB | 210 | 61 | 2387000 | Gas pressure low
22 | Siddhirgonj (Desh) |  | 96x1.2 | QRPP | 98 | 84 | 1423680 | Engine problem
23 | Siddhirgonj (Dutch Bangla) |  | 12x8.9 | RPP | 100 | 67 | 1565760 | Engine problem
24 | Pagla (DPA) |  | 100x0.5 | QRPP | 50 | 0 | 0 | Contract expired
25 | Gagnagar (Orion) |  | 12x8.924 | IPP | 102 | 102 | 2277216
26 | Summit Power,Dhaka |  | 6*3.67+2*6.97+14*8.73 | SIPP, REB | 146 | 96 | 2471703 | Synchronized at 33KV, Machine problem
27 | Gazipur (RPCL) |  | 6x8.9 | IPP | 52 | 34 | 739200 | Engine problem
28 | Tongi GT |  | 1x105 | PDB | 105 | 0 | 301558 | Gas pressure low
| Dhaka Area Total |  |  |  | 4076 | 2093 | 49020374
29 | Chitagong ST:Unit-1 |  | 1x210 | PDB | 180 | 0 | 700000 | Gas pressure low
30 | Chitagong ST:Unit-2 |  | 1x210 | PDB | 180 | 80 | 500000 | Gas pressure low
31 | Raozan 25 MW (RPCL) |  | 3x8.9 | IPP | 25 | 26 | 621180
32 | Patenga 50 MW(Barakatulla) |  | 8x6.89 | IPP | 50 | 40 | 225120
|  |  | 1x40 | PDB | 40 | 39 | 1537040 | Water level low
|  |  | 1x40 | PDB | 40 | 38 | 0
33 | Karnafuli Hydro Power Station |  | 1x50 | PDB | 50 | 24 | 0 | Water level low
|  |  | 1x50 | PDB | 50 | 40 | 351400
|  |  | 1x50 | PDB | 50 | 40 | 0
34 | Shikalbaha ST |  | 1x60 | PDB | 40 | 0 | 0 | Under maint.
35 | Shikalbaha peaking GT |  | 1x150 | PDB | 150 | 148 | 2721109
36 | Hathazari peaking |  | 11x8.9 | PDB | 98 | 96 | 952608
37 | Dohazari-Kalaish peaking |  | 6x17 | PDB | 102 | 102 | 642694
38 | Juldah (Acorn) |  | 8x13.45 | QRPP | 100 | 92 | 2096160 | Engine problem
39 | Shikalbaha (Energis) |  |  | RPP | 26 | 25 | 517440 | Contract expired date (06/05/2013)
40 | Barabkunda (regent) |  | 8x2.90 | SIPP, PDB | 22 | 22 | 453120 | Synchronized at 33KV,
41 | Malancha, Ctg EPZ(United) |  |  |  |  | 26 | 497760 | Synchronized at 33KV
| Chittagong Area Total |  |  |  | 1203 | 838 | 11815631
42 | Ashuganj ST: Unit- 1 & 2 |  | 1x64 | APSCL | 97 | 40 | 2163711
|  |  | 1x64 | APSCL |  | 50 | 0
43 | Ashuganj ST: Unit- 3 |  | 1x150 | APSCL | 135 | 130 | 3133862
44 | Ashuganj ST: Unit- 4 |  | 1x150 | APSCL | 129 | 140 | 3344510
45 | Ashuganj ST: Unit- 5 |  | 1x150 | APSCL | 134 | 130 | 3115598
46 | Ashuganj CCPP: GT-2 |  | 1x56 | APSCL | 40 | 40 | 968300
47 | Ashuganj-Engines |  | 14x3.968 | APSCL | 45 | 38 | 838872
48 | Ashugonj (Precision) |  | 15x4 | RPP | 55 | 53 | 1233120
49 | Ashuganj (Aggrekko) |  | 82x1.1 | RPP | 80 | 81 | 1913150
50 | Ashuganj (United) |  | 14x4 | RPP | 53 | 49 | 1240000
51 | Ashuganj (Midland) |  | 6x9.34 | IPP | 51 | 42 | 1000490 | Machine problem
52 | Brahmanbaria (Aggreko) |  | 72x1.1 | QRPP | 70 | 85 | 2039000
53 | Titas (Daudkandi) Peaking |  | 6 x 8.92 | PDB | 52 | 34 | 460400 | Engine problem
54 | Chandpur CCPP |  | 1x106+1x57 | PDB | 163 | 162 | 3147720
55 | Feni(Doreen) |  | 8 X 2.94 | SIPP, PDB | 22 | 15 | 349668 | 2 Machine problem
56 | Feni Mohipal (Doreen) |  | 4x2.9 | SIPP, REB | 11 | 8 | 150480 | Synchronized at 33 KV, 1 Machine problem
57 | Jangalia (Summit) |  | 4x8.73 | SIPP, PDB | 33 | 34 | 760200
58 | Summit Power,Comilla |  | 3x3.67+2x6.9 | SIPP, REB | 25 | 15 | 383680 | 3 Machine problem
| Comilla Area Total |  |  |  | 1195 | 1146 | 26242761
59 | RPCL CCPP |  | 4x35+1x70 | IPP | 202 | 135 | 3340000 | gas prerssure low.
60 | Tangail (Doreen) |  | 8 x 2.9 | SIPP,PDB | 22 | 17 | 403596 | Synchronized at 33KV, 2 Engine problem
| Mymensingh Area Total |  |  |  | 224 | 152 | 3743596
61 | Fenchugonj CCPP-1 |  | 2x32+1x33 | PDB | 80 | 52 | 1181000 | Machine problem
62 | Fenchugonj CCPP-2 |  | 2x35+1x35 | PDB | 90 | 43 | 1034600 | Machine problem
63 | Fenchugonj RPP (51 MW) |  | 2.9X19 | RPP | 51 | 50 | 1185600
64 | Fenchuganj (Energyprima) |  | 12x3.3+5x2 | RPP | 44 | 45 | 1070000
65 | Hobiganj (Confidence-EP) |  | 4x2.9 | SIPP, REB | 11 | 10 | 192192 | Synchronized at 33 KV
66 |  |  |  |  | 0 | 0 | 0
67 | Shahjibazar GT: Unit-8,9 |  | 32x2.9 | PDB | 66 | 64 | 1465000
68 | Shahjibazar (Shahjibazar) |  | 32X2.9 | RPP | 86 | 84 | 1986240
69 | Shahjibazar (Energyprima) |  | 27x2.0 | RPP | 50 | 48 | 1053360
70 | Sylhet 150 MW GT |  | 1x142 | PDB | 142 | 0 | 0 | Under maint.
71 | Sylhet 20 MW GT |  | 1x20 | PDB | 20 | 19 | 462000
72 | Sylhet (Energyprima) |  | 27 x 2.0 | RPP | 50 | 46 | 1101700
73 | Shahjahanulla 25MW |  | 3 x 9.34 | CIPP,REB | 25 | 24 | 507744
74 | Sylhet (Desh) |  | 6x1.95 | RPP | 10 | 9 | 212040 | Synchronized at 33KV
| Sylhet Area Total |  |  |  | 725 | 494 | 11451476
|  |  | 1x20 | PDB | 16 | 14 | 0
75 | Bheramara GT: Unit-1,2,3 |  | 1x20 | PDB | 14 | 14 | 314600
|  |  | 1x20 | PDB | 16 | 16 | 0
76 | Bheramara (Quantum) |  | 12x8.5+2x6+2x13 | RPP | 105 | 0 | 0 | All Engine problem
77 | Bheramara HVDC Interconnector |  |  | India | 500 | 349 | 9376727
78 | Khulna ST 110 MW |  | 1x110 | PDB | 55 | 0 | 752440 | Under maint.
79 | Khulna ST 60 MW |  | 1x60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
80 | Khulna (KPCL-1) |  | 19x6.5 | IPP | 110 | 107 | 2286700
81 | Khulna (KPCL-2) |  | 7x17 | QRPP | 115 | 100 | 2116800 | Engine problem
82 | Faridpur Peaking |  | 8x6.89 | PDB | 54 | 36 | 484320 | 3 Engine problem
83 | Khulna 150 MW GT |  | 1x150 | NWZPGCL | 158 | 130 | 591360 | Low demand
84 | Gopalganj Peaking |  | 16x6.98 | PDB | 109 | 60 | 1106752 | 7 Engine problem
85 | Noapara (Quantam) |  | 9.9x5+9.5x6+9.2x2 | RPP | 101 | 0 | 0 | All Engine problem
86 | Noapara (Khanjahan Ali) |  | 5x8.5 | QRPP | 40 | 32 | 732000 | Synchronized at 33KV, 1 Engine problem
87 | Khulna (Aggreko) 55MW |  | 71X0.85 | QRPP | 55 | 31 | 631340 | Contract Date expired
| Khulna Area Total |  |  |  | 1448 | 889 | 18393039
88 | Barisal GT: Unit-1,2 |  | 1x20 | PDB | 16 | 16 | 0
89 |  |  | 1x20 | PDB | 14 | 15 | 303896
90 | Bhola (Venture) |  | 1x34.5 | RPP | 33 | 38 | 651020 | Synchronized at 33KV
| Barisal Area Total |  |  |  | 63 | 69 | 954916
91 | Baghabari GT |  | 1x71 | PDB | 71 | 69 | 1615000
92 | Baghabari GT |  | 1x100 | PDB | 100 | 98 | 2265000
93 | Baghabari Peaking |  | 6x8.9 | PDB | 52 | 40 | 824332 | Engine problem
94 | Westmont GT, Baghabari |  |  | IPP |  | 0 | 0 | Plant Retired in FY 2013-2014
95 | Bera Peaking |  | 9x8.29 | PDB | 71 | 64 | 1381617 | Engine problem
96 | Amnura |  | 7x7.79 | QRPP | 50 | 28 | 407280 | Engine problem
97 | Katakhali (Northern) |  | 6x8.92 | QRPP | 50 | 50 | 763020
98 | Katakhali Peaking |  | 6x8.7 | PDB | 50 | 45 | 308245
99 | Sirajganj CCPP |  | 1x50+1x75 | NWPGCL | 210 | 210 | 5234645
100 | Santahar Peaking |  | 6x8.7 | PDB | 50 | 46 | 752251 | Engine problem
101 | Bogra (GBB) |  | 6x4 | RPP | 22 | 18 | 421040 | Machine problem
102 | Bogra (Energyprima) |  | 5x3.3+5x2 | RPP | 20 | 17 | 392040 | Engine problem
103 | Ullapara (Summit) |  | 4 X 2.90 | SIPP, REB | 11 | 10 | 218740 | Synchronized at 33KV
104 | Rajlanka 52 MW |  | 6x8.92 | IPP | 52 | 43 | 971040 | Engine problem
| Rajshahi Area Total |  |  |  | 809 | 738 | 15554250
105 | Barapukuria ST: Unit-1 |  | 1x125 | PDB | 100 | 76 | 1746327 | Machine problem
106 | Barapukuria ST: Unit-2 |  | 1x125 | PDB | 100 | 89 | 2097600 | Engine problem
107 | Rangpur GT |  | 1x20 | PDB | 20 | 15 | 68500
108 | Saidpur GT |  | 1x20 | PDB | 20 | 17 | 163000
109 | Thakurgaon (RZ) |  | 20x1.5+21x1.1 | RPP | 40 | 31 | 438460 | Contract date expired
| Rangpur Area Total |  |  |  | 280 | 228 | 4513887
| Eastern Grid Total |  |  |  | 7423 | 4723 | 102273838
| Western Grid Total |  |  |  | 2600 | 1924 | 39416092
| National Grid Total |  |  |  | 10023 | 6647 | 141689930
* Data collected from respective power station over telephone.

## P3
| POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-09
NATIONAL LOAD DESPATCH CENTER
PEAK HOUR DEMAND (AT S/S END) OF DIFFERENT AREAS
Date: | 2014-08-13
(a) ENTIRE EASTERN GRID : |  |  | 4322 | MW | (b) ENTIRE WESTERN GRID : |  |  | 1810 | MW
i) Dhaka area |  |  | 2513 | MW | i) Khulna area |  |  | 650 | MW
ii) Chittagong area |  |  | 653 | MW | ii) Rajshahi area |  |  | 669 | MW
iii) Comilla area |  |  | 462 | MW | iii) Barisal area |  |  | 161 | MW
iv) Mymensingh area |  |  | 388 | MW | iv) Rangpur area |  |  | 330 | MW
v) Sylhet area |  |  | 306 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6132 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUBSTATIONS
Sub-Station | Load (MW) | Hour | Sub-Station | Load (MW) | Hour | Sub-Station | Load (MW) | Hour
Siddhirganj | 114 | 1200 | Kishoreganj | 48 | 2100 | Jessore | 86 | 2100
Munsiganj | 77 | 1930 | Netrokona | 43 | 1930 | Jhenida | 50 | 100
Megnaghat | 18 | 1930 | Jamalpur | 88 | 100 | Bottail | 64 | 100
Shyampur | 110 | 2400 | Srimongal | 34 | 2100 | G.K Project | 34 | 1900
Bhulta | 108 | 2200 | Shahjibazar | 35 | 1800 | Faridpur | 82 | 400
Madanganj | 32 | 100 | Fenchuganj | 31 | 1930 | Madaripur | 81 | 2000
Shitalakhya | 82 | 1000 | Sylhet | 124 | 1830 | Gopalganj | 34.4 | 2100
Rahim steel | 1 | 1000 | Chatak | 36 | 2000 | Bagerhat | 50 | 2000
Matuail | 52 | 800 | B.Baria | 66 | 100 | Mongla | 20 | 900
Ghorasal | 73 | 2000 | Comilla(S) | 136 | 2200 | Satkhira | 48.6 | 2100
Narsingdi | 61 | 1800 | Comilla(N) | 40 | 2000 | Gallamari | 35.6 | 100
Haripur (SBU) | 45 | 900 | Chandpur | 65 | 2100 | Magura | 22 | 100
Ullon | 84 | 1830 | Feni | 69 | 2200 | Chuadanga | 38 | 100
Hasnabad | 131 | 1900 | Chowmuhani | 115 | 2200 | Barisal | 76 | 1930
Magbazar | 123 | 1200 | Ashuganj | 40 | 1900 | Patuakhali | 61 | 2100
Maniknagar | 96 | 1930 | Daudkandi | 42 | 2400 | Bhandaria | 28 | 1930
Bangabhaban | 44 | 1100 | Madanhat | 32.5 | 1930 | Ishurdi | 38 | 100
Narinda | 72 | 1100 | Hathazari | 75 | 2200 | Natore | 68 | 1930
Dhanmondi | 157 | 1300 | Khulshi | 132 | 1600 | Bogra | 161 | 2000
Agargaon | 16 | 1100 | Halishahar | 119 | 2000 | Noagaon | 77 | 2100
Mirpur | 93.5 | 1930 | Baraulia | 70 | 2100 | Rajshahi | 99 | 2000
Kalyanpur | 150 | 1100 | Sikalbaha | 24 | 1900 | C.Nawabganj | 52 | 1930
Gulshan | 113.4 | 1100 | Dohazari | 62 | 2100 | Pabna | 62 | 200
Uttara | 83 | 1500 | Cox'sbazar | 48 | 100 | Shahjadpur | 41 | 1800
Kamrangirchar | 94 | 1930 | Chandraghona | 23.2 | 1830 | Serajganj | 50 | 900
Savar | 76 | 1200 | Kaptai | 3.6 | 1930 | Niyamatpur | 39 | 1930
Bhasantec | 70 | 1930 | A. Khaer Stl. | 4.1 | 2100 | Joypurhat | 23 | 1930
Tongi | 67 | 1930 | Bakulia | 92 | 2000 | Rangpur | 72 | 1930
Kabirpur | 165 | 900 | Julda | 16 | 500 | Lalmonirhat | 53 | 2100
Basundhara | 109 | 1100 | TK chemical | 13.2 | 1300 | Saidpur | 61 | 1900
Manikganj | 54 | 2100 | Modern Steel | 11 | 1600 | Purbasadipur | 55 | 2100
Joydevpur | 188 | 2100 | Shahmirpur | 14.2 | 2000 | Thakurgaon | 53 | 2100
New Tongi | 93 | 1000 | Goalpara | 38 | 1900 | Palashbari | 40 | 100
Tangail | 104 | 200 | Central S/S | 66 | 2000 | Barapukuria | 26 | 1930
Mymensingh | 120 | 2000 | Noapara | 47 | 1930 | Panchagar | 18 | 1200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## L.curve
Date | 2014-08-13 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -510 | 4650 | 1858 | 6508 | -510 | 6508 | 0:00 | DAILY LOAD CURVE | 2014-08-13
0:30 | -320 | 4681 | 1857 | 6538 | -130 | 6538 | 1:00
1:00 | -130 | 4712 | 1856 | 6568 | -150 | 6568 | 2:00
1:30 | -140 | 4653.5 | 1833.5 | 6487 | -160 | 6487 | 3:00
2:00 | -150 | 4595 | 1811 | 6406 | -200 | 6406 | 4:00
2:30 | -155 | 4551 | 1743.5 | 6294.5 | -230 | 6294.5 | 5:00
3:00 | -160 | 4507 | 1676 | 6183 | -230 | 6183 | 6:00
3:30 | -180 | 4485.5 | 1638 | 6123.5 | -220 | 6123.5 | 7:00
4:00 | -200 | 4464 | 1600 | 6064 | -200 | 6064 | 8:00
4:30 | -215 | 4423 | 1600 | 6023 | 20 | 6023 | 9:00
5:00 | -230 | 4382 | 1600 | 5982 | 100 | 5982 | 10:00
5:30 | -230 | 4234 | 1472 | 5706 | 160 | 5706 | 11:00
6:00 | -230 | 4086 | 1344 | 5430 | 116 | 5430 | 12:00
6:30 | -225 | 4098.5 | 1335 | 5433.5 | 180 | 5433.5 | 13:00
7:00 | -220 | 4111 | 1326 | 5437 | 136 | 5437 | 14:00
7:30 | -210 | 4089 | 1364.5 | 5453.5 | 140 | 5453.5 | 15:00
8:00 | -200 | 4067 | 1403 | 5470 | 160 | 5470 | 16:00
8:30 | -90 | 4106.5 | 1470 | 5576.5 | 110 | 5576.5 | 17:00
9:00 | 20 | 4146 | 1537 | 5683 | 160 | 5683 | 18:00
9:30 | 60 | 4143 | 1545 | 5688 | 60 | 5688 | 18:30
10:00 | 100 | 4140 | 1553 | 5693 | -10 | 5693 | 19:00
10:30 | 130 | 4080.5 | 1583.5 | 5664 | -30 | 5741.5 | 19:30
11:00 | 160 | 4021 | 1614 | 5635 | -20 | 5790 | 20:00
11:30 | 138 | 4029.5 | 1627.5 | 5657 | -60 | 5815 | 21:00
12:00 | 116 | 4038 | 1641 | 5679 | -50 | 5840 | 22:00
12:30 | 148 | 4040 | 1641 | 5681 | -100 | 5761.5 | 23:00
13:00 | 180 | 4042 | 1641 | 5683 | -120 | 5683 | 24:00
13:30 | 158 | 3999.5 | 1591.5 | 5591 |  | 5701.5
14:00 | 136 | 3957 | 1542 | 5499 | 128.92 | 5720
14:30 | 138 | 3965 | 1573 | 5538 | 86.5 | 5710
15:00 | 140 | 3973 | 1604 | 5577 |  | 5700
15:30 | 150 | 4015 | 1584.5 | 5599.5 | 7867500 | 5661
16:00 | 160 | 4057 | 1565 | 5622 |  | 5622
16:30 | 135 | 4081 | 1540.5 | 5621.5 |  | 5621.5
17:00 | 110 | 4105 | 1516 | 5621 | 700 | 5621
17:30 | 110 | 4105 | 1580.5 | 5685.5 | 1800 | 5685.5
18:00 | 110 | 4105 | 1645 | 5750 | 100 | 5750
18:30 | 60 | 4446 | 1668 | 6114 | 1400 | 6114
19:00 | -10 | 4576 | 1787 | 6363 | 100 | 6363
19:30 | -30 | 4629 | 1859 | 6488 | 1800 | 6488
20:00 | -20 | 4723 | 1924 | 6647 | 1800 | 6647
20:30 | -40 | 4707.5 | 1932.5 | 6640 | 1800 | 6640
21:00 | -60 | 4692 | 1941 | 6633 | 2100 | 6633
21:30 | -55 | 4641 | 1943.5 | 6584.5 | 1900 | 6584.5
22:00 | -50 | 4590 | 1946 | 6536 | 1900 | 6536
22:30 | -75 | 4600.5 | 1827.5 | 6428 |  | 6428
23:00 | -100 | 4611 | 1709 | 6320 |  | 6320
23:30 | -110 | 4526 | 1664 | 6190 |  | 6190
24:00 | -120 | 4441 | 1619 | 6060 |  | 6060
*MAX.GEN.(E.P.) |  | 6647 |  | 0.83333
*MAX.GEN.(D.P.) |  | 5693 |  | 0.41667
|  |  |  | min | max
|  | 3063.9 | 3349 | 0.33333 | 0.041667
|  | 2664.1 | 3286.1 | 0.54167 | 0.45833
|  | 2910.2 | 3139.4 | 0.77083 | 24:00
|  | 2664.1 | 3349 | 0.54167 | 0.041667
|  | 282 |  | 0.16667
|  | 276 |  | 0.75
|  | 348 |  | 0.875
|  | 348 |  | 0.875
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
6647 MW (20:00)
5693 MW (10:00)

## En.Curve
QF-LDC-12
Date | 2014-08-13 |  | Energy | 141689930
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE |  | DAILY ENERGY CURVE |  | 2014-08-13
0:00 | 1184 | 346 | 2456 | 1415 | 163 | 188 | 664 | 0
0:30 | 1221 | 374 | 2520 | 1410 | 162 | 177.5 | 631 | 0
1:00 | 1258 | 402 | 2584 | 1405 | 161 | 167 | 598 | 0
1:30 | 1277 | 402 | 2624 | 1398 | 161.5 | 122.5 | 506.5 | 0 | [5 empty] | 141.6899
2:00 | 1296 | 402 | 2664 | 1391 | 162 | 78 | 415 | 0 | [5 empty] | 8.3983
2:30 | 1300.5 | 402 | 2662 | 1311 | 161 | 74 | 393 | 0 | [5 empty] | 150.0882
3:00 | 1305 | 402 | 2660 | 1231 | 160 | 70 | 371 | 0
3:30 | 1312 | 402 | 2651.5 | 1194 | 160 | 70 | 335 | 0
4:00 | 1319 | 402 | 2643 | 1157 | 160 | 70 | 299 | 0
4:30 | 1321.5 | 402 | 2646 | 1130.5 | 162 | 70 | 279 | 0
5:00 | 1324 | 402 | 2649 | 1104 | 164 | 70 | 259 | 0
5:30 | 1313 | 402 | 2629 | 897 | 164 | 70 | 236 | 0
6:00 | 1302 | 402 | 2609 | 690 | 164 | 70 | 213 | 0
6:30 | 1310.5 | 402 | 2615 | 687.5 | 164 | 73 | 204.5 | 0
7:00 | 1319 | 402 | 2621 | 685 | 164 | 76 | 196 | 0
7:30 | 1229 | 404.5 | 2524.5 | 868 | 164.5 | 73 | 201.5 | 0
8:00 | 1139 | 407 | 2428 | 1051 | 165 | 70 | 207 | 0
8:30 | 1144.5 | 404 | 2409 | 1180.5 | 165.5 | 70 | 224 | 0
9:00 | 1150 | 401 | 2390 | 1310 | 166 | 70 | 241 | 0
9:30 | 1152 | 401 | 2383 | 1327 | 164 | 74 | 237 | 0
10:00 | 1154 | 401 | 2376 | 1344 | 162 | 78 | 233 | 0
10:30 | 1125.5 | 400.5 | 2362 | 1347 | 163.5 | 62 | 248 | 77.5
11:00 | 1097 | 400 | 2348 | 1350 | 165 | 46 | 263 | 155
11:30 | 1105 | 399 | 2341 | 1350 | 164 | 46 | 131.5 | 158
12:00 | 1113 | 398 | 2334 | 1350 | 163 | 46 | 0 | 161
12:30 | 1104 | 397 | 2328 | 1351 | 164.5 | 46 | 157.5 | 80.5
13:00 | 1095 | 396 | 2322 | 1352 | 166 | 46 | 315 | 0
13:30 | 1032 | 396.5 | 2328 | 1340.5 | 166 | 43 | 283 | 110.5
14:00 | 969 | 397 | 2334 | 1329 | 166 | 40 | 251 | 221
14:30 | 993 | 397 | 2339.5 | 1335.5 | 165 | 40 | 270 | 172
15:00 | 1017 | 397 | 2345 | 1342 | 164 | 40 | 289 | 123
15:30 | 1045 | 397 | 2340.5 | 1346.5 | 164 | 40 | 294.5 | 61.5 | Max Temp. in Dhaka |  | 29.7° C
16:00 | 1073 | 397 | 2336 | 1351 | 164 | 40 | 300 | 0
16:30 | 1099.5 | 396.5 | 2337.5 | 1290 | 165 | 40 | 312.5 | 0
17:00 | 1126 | 396 | 2339 | 1229 | 166 | 40 | 325 | 0
17:30 | 1133 | 396 | 2366.5 | 1258 | 166 | 40 | 384.5 | 0
18:00 | 1140 | 396 | 2394 | 1287 | 166 | 40 | 444 | 0
18:30 | 1198 | 348 | 2429 | 1318 | 162 | 112 | 496 | 0
19:00 | 1218 | 350 | 2436 | 1378 | 165 | 162 | 595 | 0
19:30 | 1236 | 350 | 2457 | 1483 | 165 | 160 | 599 | 0
20:00 | 1301 | 349 | 2475 | 1567 | 165 | 181 | 582 | 0
20:30 | 1295 | 349.5 | 2490.5 | 1553.5 | 165 | 181 | 584 | 0
21:00 | 1289 | 350 | 2506 | 1540 | 165 | 181 | 586 | 0
21:30 | 1288.5 | 349.5 | 2510 | 1547.5 | 164.5 | 132.5 | 580 | 0
22:00 | 1288 | 349 | 2514 | 1555 | 164 | 84 | 574 | 0
22:30 | 1300.5 | 348.5 | 2524.5 | 1493 | 165 | 63 | 557.5 | 0
23:00 | 1313 | 348 | 2535 | 1431 | 166 | 42 | 541 | 0
23:30 | 1315.5 | 348.5 | 2546 | 1435.5 | 164.5 | 42 | 377 | 0
24:00 | 1318 | 349 | 2557 | 1440 | 163 | 42 | 213 | 0
|  | 1490 |  |  |  |  | 2380 | 1320
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER

## volt
NATIONAL LOAD DESPATCH CENTER
The Maximum & Minimum Voltages of different Sub-Stations.
Date : | 2014-08-13
| Maxm |  | Minm |  |  | Maxm |  | Minm
Sub-Station | Voltage | Hour | Voltage | Hour | Sub-Station | Voltage | Hour | Voltage | Hour
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Hathazari | 217 | 1930 | 201 | 1400 | Megnaghat | 216 | 700 | 208 | 1300
Comilla(N) | 226 | 600 | 215 | 1400 | Haripur | 216 | 400 | 210 | 1300
Ashuganj | 230 | 2200 | 225 | 1100 | Ishurdi | 234 | 1930 | 223 | 900
Ghorasal | 225 | 900 | 220 | 1830 | Baghabari | 229 | 1500 | 222 | 1200
Rampura | 215 | 200 | 208 | 1400 | Serajganj | 226 | 1600 | 223 | 700
Tongi | 212 | 2400 | 205 | 1000 | Bogra | 232 | 1500 | 225 | 700
Aminbazar | 213 | 2400 | 205 | 1200 | Barapukuria | 229 | 1600 | 225 | 100
Hasnabad | 235 | 2400 | 223 | 1800 | Khulna South | 234 | 1600 | 221 | 700
Fenchuganj | 229 | 200 | 221 | 1600 | Siddhirganj | 224 | 300 | 208 | 1600
Maniknagar | 221 | 500 | 206 | 1200
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 137 | 200 | 128 | 1200 | Khulshi | 132 | 1900 | 122 | 1400
Munsiganj | 135 | 200 | 128 | 1200 | Halishahar | 130 | 1900 | 119 | 1400
Megnaghat | 135 | 900 | 129 | 1300 | Baraulia | 129 | 1900 | 119 | 1600
Shyampur | 133 | 500 | 124 | 1200 | Sikalbaha | 129 | 1900 | 118 | 1400
Bhulta | 128 | 100 | 120 | 1200 | Dohazari | 127 | 1930 | 117 | 1600
Madanganj | 131 | 800 | 127 | 1200 | Cox'sbazar | 128 | 1900 | 115 | 1400
Shitalakhya | 137 | 200 | 130 | 1100 | Chandraghona | 132 | 1930 | 120 | 1400
Rahim steal | 134 | 100 | 129 | 1000 | Kaptai | 130 | 1900 | 122 | 2000
Matuail | 134 | 100 | 127 | 1200 | A. Khaer Stl. | 130 | 2200 | 122 | 1700
Ghorasal | 133 | 800 | 132 | 100 | Bakulia | 127 | 1830 | 117 | 1400
Narsinghdi | 135 | 1930 | 130 | 1200 | Julda | 128 | 1900 | 118 | 1700
Haripur (SBU) | 135 | 400 | 127 | 1200 | TK Chemical | 131 | 1830 | 122 | 1200
Ullon | 134 | 2300 | 126 | 1400 | Modern Steel | 128 | 1900 | 118 | 1300
Hasnabad | 135 | 2000 | 128 | 1100 | Shahmirpur | 128 | 1900 | 118 | 1400
Magbazar | 132 | 600 | 122 | 1200 | Goalpara | 139 | 1600 | 130 | 600
Maniknagar | 133 | 500 | 127 | 1200 | Central s/s | 139 | 1600 | 131 | 600
Bangabhaban | 133 | 500 | 127 | 1200 | Noapara | 136 | 900 | 127 | 700
Narinda | 133 | 500 | 127 | 1200 | Jessore | 132 | 1830 | 122 | 600
Dhanmondi | 134 | 2300 | 126 | 1400 | Jhenida | 135 | 1600 | 120 | 500
Agargaon | 133 | 300 | 124 | 1200 | Bottail | 139 | 1900 | 135 | 300
Mirpur | 131 | 800 | 122 | 1200 | G.K.Project | 140 | 1500 | 134 | 400
Kalyanpur | 134 | 300 | 127 | 1200 | Faridpur | 133 | 1900 | 124 | 900
Gulshan | 134 | 200 | 122 | 1200 | Madaripur | 131 | 1300 | 120 | 2000
Uttara | 131 | 400 | 123 | 1100 | Gopalganj | 136 | 1300 | 126 | 1830
Kamrangirchar | 131 | 300 | 123 | 1600 | Bagerhat | 132 | 900 | 123 | 2000
Savar | 133 | 200 | 124 | 1200 | Mongla | 134 | 900 | 125 | 1900
Bhasantec | 131 | 400 | 124 | 1100 | Satkhira | 137 | 900 | 129 | 700
Tongi | 134 | 2300 | 127 | 12 | Gallamari | 139 | 1600 | 131 | 600
Kabirpur | 129 | 2300 | 123 | 1300 | Magura | 135 | 1830 | 120 | 100
Basundhara | 129 | 500 | 119 | 1300 | Chuadanga | 133 | 1830 | 117 | 600
Manikganj | 128 | 2400 | 120 | 1000 | Barisal | 130 | 1100 | 120 | 2000
Joydevpur | 135 | 1900 | 129 | 1000 | Patuakhali | 130 | 900 | 114 | 2000
New Tongi | 132 | 2400 | 124 | 1200 | Bhandaria | 132 | 900 | 120 | 1900
Tangail | 130 | 2300 | 120 | 1200 | Ishurdi | 140 | 900 | 134 | 600
Mymensing | 132 | 1500 | 122 | 2200 | Natore | 136 | 1800 | 129 | 600
Kishorganj | 132 | 600 | 127 | 100 | Bogra | 137 | 1500 | 130 | 500
Netrokona | 132 | 1500 | 123 | 200 | Noagaon | 134 | 1500 | 127 | 200
Jamalpur | 126 | 1600 | 116 | 200 | Rajshahi | 136 | 1300 | 128 | 500
Srimongal | 142 | 700 | 140 | 100 | C.Nawabganj | 133 | 100 | 125 | 400
Shahjibazar | 144 | 100 | 142 | 1000 | Pabna | 135 | 1700 | 130 | 100
Fenchuganj | 139 | 700 | 135 | 1400 | Shahjadpur | 139 | 300 | 137 | 1400
Sylhet | 136 | 500 | 133 | 200 | Serajganj | 135 | 1400 | 131 | 300
Chatak | 136 | 600 | 132 | 1830 | Niyamatpur | 134 | 1500 | 127 | 200
B.Baria | 138 | 700 | 136 | 100 | Joypurhat | 136 | 1500 | 126 | 500
Comilla(S) | 135 | 800 | 126 | 1400 | Rangpur | 129 | 1300 | 122 | 400
Comilla(N) | 137 | 800 | 130 | 1200 | Lalmonirhat | 128 | 900 | 122 | 100
Chandpur | 134 | 700 | 120 | 1500 | Saidpur | 128 | 1000 | 124 | 100
Feni | 125 | 700 | 117 | 1400 | Purbasadipur | 130 | 1000 | 125 | 100
Chowmuhani | 127 | 700 | 1119 | 1600 | Thakurgaon | 128 | 1000 | 120 | 1900
Ashuganj | 145 | 400 | 142 | 1300 | Palashbari | 130 | 1400 | 125 | 100
Daudkandi | 133 | 1930 | 126 | 1400 | Barapukuria | 129 | 1300 | 125 | 100
Madanhat | 132 | 1830 | 124 | 1100 | Panchagar | 125 | 900 | 118 | 400
Hathazari | 131 | 200 | 121 | 1400