## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-07-29 | Monday
|  | Date (day): | 2019-07-29 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12889 | MW |  |  | (b) At Evening Peak Hour : |  | 14718 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-07-28 | 2019-07-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 35 | 35 | 35 | 35 |  | 50 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 199 | 249 | 230 | 230
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 219 | 220 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 73 | 73 | 40 | 40
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 93 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 342 | 370 | 370 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 312 | 351 | 340 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 360 | 400 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 28 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 250 | 280 | 280 | 280 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 48 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 24 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 10 | 9 | 10 | 10 |  |  | Test
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 24 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 13 | 47 | 47 | 47
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 98 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 56 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 72 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 41 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 14 | 0 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 48 | 115 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 102 | 102 | 100 | 100
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2414 | 2969 | 3678 | 4300 | 355 | 789
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 95 | 95 | 85
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13.3 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 183 | 184 | 220 | 220
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 206 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maintenance.
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 42 | 0 | 85
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 32 | 15 | 30
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 10 | 97 | 90 | 96
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4.6 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 195 | 214 | 230 | 260
| Jodiac Power |  | HFO | IPP | 54.36 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 1008.9 | 1214 | 1356.4 | 1518 | 145 | 150
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 135 | 100 | 100
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 186 | 220 | 220 |  |  | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 360 | 360
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 310 | 340 | 360 |  |  | FGMO
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 37 | 37 | 37 |  | 8 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 48 | 50 | 50
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 68 | 68 | 68 | 68 | 127 |  | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 30 | 43 | 45 | 45 |  | 5 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 10 | 50 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 42
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 0 | 90
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 180 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 172 | 140 | 184
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1458 | 1764 | 1848 | 2244 | 390 | 18
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 145 | 145 | 145 |  | 57 | GT-1 Under maint.
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 95 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.4 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 160 | 100 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 297.4 | 537 | 478.6 | 577 | 0 | 57
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 53 | 52 | 53 | 53
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 58 | 58 | 58 | 58
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 262 | 264 | 260 | 267
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 63 | 64 | 66 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 75 | 75 | 75
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 40 | 43 | 42 | 42 |  | 8 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 110 | 115 | 120 | 125
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17 |  | 3 | Engine problem
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 45 | 45 | 45
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 7 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 300 | 315 | 320 |  |  | FGMO
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 200 | 250 | 300 | 300
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1424 | 1593 | 1652 | 1671 | 0 | 11
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 841 | 845 | 937 | 937
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 35 | 0 | 35
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 150 | 150 |  | 80 | ST Under maint
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 52 | 0 | 70
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 52 | 86 | 84 | 85 |  | 20 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 934 | 1410 | 1431 | 1669 | 0 | 510
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 11 | 28 | 33 | 33
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 172 | 173 | 175 | 175
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 72 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 255 | 331 | 373 | 443 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 6 | 6 | 12 | 12 |  | 38 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 42 | 42 | 42 |  | 8 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 45 | 45
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 181 | 181 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 184 | 200 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 206 | 183 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 300 | 300 | 400 | 400
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 0 | 36
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 15 | 15 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 80 | 100
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 30 | 113 | 110 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 1020 | 1423 | 1719 | 1828 | 0 | 146
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 70 | 71 | 100 | 100
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 249 | 249 | 250 | 250
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 18
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 47 | 0 | 0 | 100
| Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 0 | 0 | 3 | 0 | 3 | 0
| Rangpur Area Total |  |  |  |  | 564 | 484 | 369 | 337 | 353 | 468 | 0 | 105
| Total |  |  |  |  | 18961 | 18438 | 9180.3 | 11578 | 12889 | 14718 | 890 | 1786
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8756.8866 | 11044 | 12294.5341 | 14039.1771
A. |  | 2019-07-28 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11578 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8059.3 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11578 | MW
3 | Minimum Generation : |  |  | 9180.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11044 | MW
4 | Minimum Generation : |  |  | 11578 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Minimum Generation : |  | 234.4773 | MKWHr | By Solar | 0.16753 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| Minimum Generation : | 151.877 | MKWHr |  | By Oil: | 46.8878 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| Minimum Generation : | 7.7337 | MKWHr |  | By Hydro: | 4.2348 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Minimum Generation : |  | For Fuel Limitation = |  |  | 890 | MW | Dhaka | 3982 | 3982 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1786 | MW | Chittagong | 1095 | 1095 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2676 | MW | Khulna | 1370 | 1370 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1373.96 | MMCFD |  |  | Rajshahi | 1188 | 1188 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 147966615.796 | ii) Oil : | Taka | 408147839.29 | Comilla | 1019 | 1019 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 35429542.32 | Total | Taka | 591543997.406 | Mymensingh | 901 | 901 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 2.292 | MKWHr. | Sylhet | 504 | 504 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -235 | MW (E to W) at | 21:00 | hrs | Barisal | 296 | 296 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -502 | MW at | 1:00 | hrs | Rangpur | 689 | 689 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.2° C |  |  | Total | 11044 | 11044 |  | 0
B. |  | 2019-07-29 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14718 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 2718 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 243.0236 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8382.81 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.1484 | MKWHr. | ii) HVDC Flow at Peak Time |  | 845 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4282 | MKWHr. | iii) Maximum HVDC Flow : |  | 860 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.27 |  | (b) Today: | 106.14 |  | (c) Rule Curve: |  | 88.49
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-07-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 35 | 230 | 220 | 0 | 0 | 71 | 0 | 339 | 320 |  | 0 | 370 | 265 | 0 | 15 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 72 | 0 | 13 | 53 | 37 | 55 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 93 | 90 | 95 | 120 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 96 | 50 | 22 | 40 | 135 | 0 | 0 | 310 | 305 | 182 | 68 | 90 | 33 | 48 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 152 | 146 | 95 | 22 | 0 | 52 | 58 | 50 | 50 | 130 | 263 | 54 | 75 | 43 | 73 | 18 | 45 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 139 | 0 | 100 | 180 | 100 | 299 | 115 | 102 | 0 | 0 | 234 | 0 |  | 849 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 33 | 67 | 40 | 173 | 30 | 48 | 0 | 0 | 60 | 50 | 0 | 50 | 6 | 42 | 8 | 52 | 36 | 22 | 15 | 8 | 69 | 0 | 249 | 0 | 0 | 176 | 0 | 176 | 0 | 98 | 30 | 186 | 0 | 0 | 105 | 0 | 113 | 86 | 0 | 0 | 0 |  | 7667 | 2976 | 10643 | 4356 | 849 | 1821 | 2571 | 318 | 183 | 393 | 152 | 0 | 0 | 106.28
2:00 | 35 | 230 | 220 | 0 | 0 | 85 | 0 | 339 | 300 |  | 0 | 370 | 275 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 72 | 0 | 13 | 53 | 37 | 35 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 94 | 90 | 95 | 120 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 96 | 50 | 22 | 40 | 135 | 0 | 0 | 310 | 305 | 188 | 68 | 90 | 33 | 48 | 0 | 51 | 0 | 0 | 52 | 19 | 11 | 30 | 20 | 148 | 145 | 95 | 22 | 0 | 53 | 58 | 50 | 50 | 130 | 263 | 52 | 75 | 43 | 73 | 18 | 45 | 10 | 290 | 24 | 3 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 180 | 100 | 297 | 115 | 102 | 0 | 0 | 234 | 0 |  | 849 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 28 | 18 | 40 | 173 | 29 | 32 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 42 | 0 | 8 | 36 | 22 | 12 | 8 | 69 | 0 | 249 | 0 | 0 | 155 | 0 | 146 | 0 | 95 | 0 | 163 | 0 | 0 | 105 | 0 | 113 | 86 | 0 | 0 | 0 |  | 7369 | 2667 | 10036 | 4273 | 849 | 1813 | 2297 | 318 | 184 | 154 | 148 | 0 | 0 | 106.28
3:00 | 35 | 230 | 220 | 0 | 0 | 93 | 0 | 344 | 300 |  | 0 | 370 | 275 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 13 | 53 | 17 | 35 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 94 | 90 | 95 | 120 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 96 | 41 | 22 | 40 | 135 | 0 | 0 | 310 | 320 | 194 | 68 | 90 | 33 | 47 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 14 | 130 | 145 | 95 | 22 | 0 | 52 | 58 | 50 | 50 | 130 | 260 | 63 | 75 | 43 | 75 | 18 | 45 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 155 | 10 | 251 | 115 | 102 | 0 | 0 | 234 | 0 |  | 850 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 16 | 0 | 8 | 173 | 29 | 16 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 42 | 0 | 8 | 0 | 22 | 12 | 8 | 69 | 0 | 249 | 0 | 0 | 160 | 0 | 151 | 0 | 97 | 0 | 163 | 0 | 90 | 105 | 0 | 113 | 85 | 0 | 0 | 0 |  | 7022 | 2655 | 9677 | 4277 | 850 | 1917 | 1961 | 318 | 184 | 40 | 130 | 0 | 0 | 106.28
4:00 | 35 | 230 | 220 | 0 | 0 | 94 | 0 | 340 | 300 |  | 0 | 370 | 271 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 13 | 53 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 94 | 90 | 95 | 120 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 50 | 22 | 40 | 135 | 0 | 0 | 310 | 305 | 182 | 68 | 90 | 33 | 45 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 14 | 128 | 145 | 95 | 22 | 0 | 53 | 58 | 50 | 50 | 130 | 260 | 64 | 75 | 43 | 70 | 18 | 45 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 120 | 10 | 250 | 115 | 102 | 0 | 0 | 232 | 0 |  | 849 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 2 | 0 | 8 | 173 | 29 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 16 | 0 | 8 | 0 | 22 | 12 | 8 | 70 | 0 | 249 | 0 | 0 | 158 | 0 | 149 | 0 | 96 | 0 | 160 | 0 | 170 | 105 | 0 | 113 | 85 | 0 | 0 | 0 |  | 6831 | 2671 | 9502 | 4236 | 849 | 2000 | 1760 | 319 | 184 | 26 | 128 | 0 | 0 | 106.27
5:00 | 35 | 230 | 220 | 0 | 0 | 94 | 0 | 340 | 300 |  | 0 | 370 | 270 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 13 | 35 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 94 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 12 | 27 | 22 | 40 | 135 | 0 | 0 | 310 | 305 | 182 | 68 | 90 | 33 | 45 | 0 | 51 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 116 | 146 | 24 | 22 | 0 | 53 | 58 | 50 | 50 | 130 | 262 | 64 | 75 | 43 | 69 | 18 | 45 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 60 | 58 | 10 | 250 | 115 | 102 | 0 | 0 | 162 | 0 |  | 850 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 28 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 6 | 16 | 0 | 8 | 0 | 22 | 12 | 8 | 70 | 0 | 249 | 0 | 0 | 158 | 0 | 149 | 0 | 96 | 0 | 166 | 0 | 230 | 27 | 0 | 113 | 85 | 0 | 0 | 0 |  | 6532 | 2586 | 9118 | 4247 | 850 | 2069 | 1309 | 319 | 184 | 24 | 116 | 0 | 0 | 106.27
6:00 | 35 | 230 | 220 | 0 | 0 | 94 | 0 | 338 | 277 |  | 0 | 330 | 285 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 35 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 8 | 0 | 93 | 90 | 95 | 120 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 8 | 22 | 41 | 135 | 0 | 0 | 310 | 305 | 182 | 68 | 90 | 33 | 45 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 14 | 116 | 148 | 8 | 22 | 0.1 | 53 | 58 | 50 | 50 | 100 | 264 | 40 | 75 | 43 | 69 | 18 | 13 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 1 | 30 | 17 | 10 | 200 | 68 | 50 | 0 | 0.144 | 107 | 0 |  | 850 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 26 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 12 | 8 | 70 | 0 | 249 | 0 | 0 | 154 | 0 | 145 | 0 | 73 | 0 | 167 | 0 | 250 | 17 | 0 | 17 | 16 | 0 | 0 | 0.1 |  | 5977.244 | 2355.1 | 8332.344 | 4162 | 850 | 1889 | 812 | 319 | 183 | 0 | 116 | 1.344 | 0 | 106.27
7:00 | 35 | 230 | 220 | 0 | 0 | 91 | 0 | 340 | 270 |  | 0 | 330 | 280 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 8 | 0 | 93 | 90 | 95 | 120 | 0 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 6 | 22 | 31 | 135 | 0 | 0 | 310 | 315 | 186 | 68 | 90 | 33 | 48 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 0 | 100 | 145 | 8 | 22 | 0.4 | 53 | 58 | 5 | 5 | 100 | 264 | 40 | 40 | 43 | 78 | 17 | 10 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 2 | 30 | 17 | 10 | 200 | 40 | 50 | 0 | 1.38 | 106 | 0 |  | 822 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 12 | 5 | 71 | 0 | 250 | 0 | 0 | 162 | 0 | 153 | 0 | 54 | 0 | 175 | 0 | 250 | 17 | 0 | 17 | 16 | 0 | 0 | 2.2 |  | 5784.78 | 2327.2 | 8111.98 | 4192 | 822 | 1730 | 758 | 321 | 183 | 0 | 100 | 5.98 | 0 | 106.26
8:00 | 35 | 230 | 220 | 0 | 0 | 90 | 0 | 340 | 250 |  | 0 | 300 | 285 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 17 | 19 | 25 | 31 | 33 | 33 | 8 | 0 | 93 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 6 | 22 | 14 | 135 | 0 | 0 | 320 | 320 | 195 | 68 | 90 | 33 | 45 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 10 | 102 | 145 | 8 | 22 | 1.5 | 53 | 58 | 5 | 5 | 100 | 266 | 40 | 40 | 43 | 77 | 17 | 10 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 2 | 30 | 17 | 10 | 201 | 40 | 50 | 0 | 2.2 | 106 | 0 |  | 821 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 12 | 5 | 71 | 0 | 249 | 0 | 0 | 163 | 0 | 154 | 0 | 53 | 0 | 164 | 0 | 250 | 16 | 0 | 17 | 16 | 0 | 0 | 3.6 |  | 5744.7 | 2314.6 | 8059.3 | 4216 | 821 | 1646 | 762 | 320 | 183 | 0 | 102 | 9.3 | 0 | 106.26
9:00 | 35 | 230 | 220 | 0 | 0 | 90 | 0 | 357 | 282 |  | 0 | 330 | 280 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 17 | 19 | 25 | 30 | 33 | 33 | 40 | 0 | 93 | 90 | 95 | 120 | 0 | 231 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 7 | 19 | 3 | 135 | 0 | 0 | 310 | 315 | 191 | 68 | 90 | 33 | 49 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 118 | 143 | 8 | 22 | 2.2 | 53 | 58 | 5 | 5 | 100 | 262 | 40 | 40 | 43 | 70 | 17 | 10 | 10 | 320 | 16 | 11 | 0 | 3 | 0 | 0 | 7 | 0 | 32 | 4.1 | 30 | 17 | 10 | 200 | 40 | 102 | 0 | 4.4 | 120 | 0 |  | 825 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 12 | 5 | 71 | 0 | 250 | 0 | 0 | 172 | 0 | 178 | 0 | 53 | 0 | 184 | 0 | 250 | 17 | 0 | 17 | 16 | 10 | 0 | 2.9 |  | 5978.7 | 2380.9 | 8359.6 | 4278 | 825 | 1719 | 902 | 321 | 183 | 0 | 118 | 13.6 | 0 | 106.25
10:00 | 35 | 199 | 220 | 0 | 0 | 94 | 0 | 345 | 311 |  | 0 | 330 | 277 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 8 | 0 | 13 | 17 | 17 | 17 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 93 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 36 | 22 | 3 | 135 | 0 | 0 | 310 | 305 | 184 | 68 | 90 | 33 | 48 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 134 | 143 | 8 | 22 | 0.7 | 53 | 58 | 17 | 12 | 130 | 261 | 40 | 40 | 42 | 70 | 17 | 46 | 10 | 310 | 16 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 45 | 1.2 | 30 | 17 | 10 | 230 | 40 | 102 | 0 | 5.8 | 195 | 0 |  | 825 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 12 | 5 | 71 | 0 | 250 | 0 | 0 | 204 | 0 | 183 | 0 | 52 | 0 | 209 | 0 | 320 | 17 | 0 | 17 | 16 | 20 | 0 | 5.1 |  | 6171.7 | 2522.1 | 8693.8 | 4285 | 825 | 1892 | 1041 | 321 | 183 | 0 | 134 | 12.8 | 0 | 106.25
11:00 | 35 | 199 | 220 | 0 | 0 | 97 | 71 | 340 | 312 |  | 0 | 330 | 283 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 14 | 0 | 13 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 93 | 90 | 95 | 120 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 2 | 135 | 0 | 0 | 310 | 305 | 183 | 68 | 85 | 33 | 48 | 0 | 20 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 132 | 144 | 8 | 22 | 1 | 53 | 58 | 50 | 50 | 130 | 261 | 40 | 50 | 42 | 70 | 17 | 42 | 10 | 300 | 0 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 45 | 6.8 | 50 | 17 | 10 | 230 | 68 | 102 | 0 | 6.5 | 196 | 0 |  | 836 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 16 | 0 | 10 | 0 | 55 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 12 | 5 | 70 | 0 | 250 | 0 | 0 | 186 | 0 | 190 | 0 | 60 | 0 | 204 | 0 | 320 | 17 | 0 | 17 | 21 | 34 | 0 | 8.3 |  | 6396.3 | 2552.3 | 8948.6 | 4244 | 836 | 2052 | 1149 | 320 | 183 | 10 | 132 | 22.6 | 0 | 106.25
12:00 | 35 | 199 | 219 | 0 | 0 | 97 | 73 | 340 | 312 |  | 0 | 360 | 250 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 72 | 0 | 13 | 17 | 17 | 17 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 93 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 2 | 135 | 0 | 0 | 310 | 305 | 182 | 68 | 90 | 33 | 47 | 0 | 30 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 140 | 144 | 8 | 22 | 1.4 | 53 | 58 | 50 | 50 | 130 | 262 | 40 | 73 | 40 | 110 | 17 | 43 | 0 | 280 | 7 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 48 | 13.3 | 100 | 17 | 10 | 200 | 115 | 102 | 0 | 4.6 | 195 | 0 |  | 841 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 11 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 70 | 0 | 249 | 0 | 0 | 181 | 0 | 185 | 0 | 72 | 0 | 206 | 0 | 300 | 17 | 0 | 30 | 52 | 47 | 0 | 3 |  | 6602.3 | 2578 | 9180.3 | 4255 | 841 | 2074 | 1346 | 319 | 183 | 0 | 140 | 22.3 | 0 | 106.25
13:00 | 35 | 199 | 209 | 0 | 0 | 97 | 72 | 340 | 312 |  | 0 | 360 | 232 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 72 | 0 | 13 | 17 | 17 | 17 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 93 | 90 | 95 | 120 | 0 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 45 | 22 | 10 | 135 | 0 | 0 | 310 | 305 | 183 | 68 | 90 | 37 | 46 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 138 | 144 | 8 | 22 | 0.6 | 53 | 58 | 53 | 50 | 130 | 254 | 40 | 73 | 41 | 75 | 17 | 43 | 10 | 280 | 7 | 11 | 0 | 14 | 0 | 0 | 7 | 11 | 45 | 17.8 | 100 | 17 | 10 | 201 | 115 | 102 | 0 | 3.2 | 196 | 0 |  | 842 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 173 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 15 | 5 | 70 | 0 | 249 | 0 | 0 | 182 | 0 | 185 | 0 | 53 | 0 | 197 | 0 | 300 | 17 | 0 | 72 | 34 | 48 | 0 | 4.3 |  | 6572.6 | 2583.3 | 9155.9 | 4199 | 842 | 2092 | 1357 | 319 | 183 | 0 | 138 | 25.9 | 0 | 106.24
14:00 | 35 | 199 | 220 | 0 | 0 | 97 | 50 | 340 | 282 |  | 0 | 330 | 285 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 72 | 0 | 13 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 24 | 22 | 4 | 135 | 0 | 0 | 320 | 320 | 203 | 68 | 90 | 33 | 40 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 142 | 141 | 8 | 22 | 1.2 | 53 | 58 | 22 | 20 | 100 | 265 | 40 | 50 | 41 | 87 | 17 | 23 | 10 | 260 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 103 | 30 | 4 | 100 | 17 | 10 | 200 | 115 | 102 | 0 | 5.08 | 198 | 0 |  | 841 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 9 | 8 | 172 | 15 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 70 | 0 | 249 | 0 | 0 | 197 | 0 | 156 | 0 | 52 | 0 | 183 | 0 | 270 | 17 | 0 | 73 | 34 | 64 | 0 | 2.5 |  | 6516.28 | 2546.5 | 9062.78 | 4258 | 841 | 1813 | 1485 | 319 | 183 | 9 | 142 | 12.78 | 0 | 106.24
15:00 | 35 | 199 | 220 | 0 | 0 | 96 | 50 | 362 | 301 |  | 0 | 360 | 288 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 72 | 0 | 13 | 35 | 35 | 17 | 22 | 25 | 27 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 0 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 25 | 22 | 4 | 135 | 0 | 0 | 320 | 320 | 195 | 68 | 90 | 37 | 46 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 158 | 140 | 8 | 22 | 1.7 | 52 | 58 | 50 | 44 | 130 | 263 | 59 | 72 | 41 | 105 | 17 | 42 | 10 | 325 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 104 | 17 | 5 | 100 | 17 | 10 | 250 | 115 | 102 | 0 | 4.9 | 198 | 0 |  | 842 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 9 | 8 | 173 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 6 | 16 | 0 | 8 | 0 | 22 | 14 | 5 | 70 | 0 | 249 | 0 | 0 | 198 | 0 | 180 | 0 | 52 | 0 | 180 | 0 | 350 | 17 | 0 | 74 | 34 | 0 | 0 | 3.5 |  | 6904.6 | 2595.5 | 9500.1 | 4382 | 842 | 2134 | 1458 | 319 | 183 | 9 | 158 | 15.1 | 0 | 106.24
16:00 | 35 | 199 | 223 | 0 | 0 | 96 | 50 | 339 | 302 |  | 0 | 360 | 272 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 72 | 0 | 13 | 35 | 35 | 17 | 22 | 25 | 30 | 33 | 33 | 41 | 0 | 92 | 90 | 95 | 120 | 8 | 203 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 33 | 22 | 6 | 135 | 0 | 0 | 310 | 310 | 183 | 68 | 88 | 37 | 45 | 0 | 43 | 0 | 0 | 8 | 19 | 5 | 33 | 20 | 150 | 143 | 37 | 22 | 1.4 | 52 | 58 | 50 | 49 | 163 | 264 | 61 | 73 | 40 | 93 | 17 | 41 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 104 | 65 | 0 | 60 | 17 | 10 | 250 | 115 | 102 | 17 | 2.6 | 143 | 6 |  | 851 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 9 | 8 | 172 | 9 | 0 | 12 | 0 | 55 | 0 | 0 | 0 | 6 | 24 | 0 | 8 | 0 | 22 | 12 | 5 | 70 | 0 | 249 | 0 | 0 | 188 | 0 | 191 | 0 | 53 | 0 | 193 | 0 | 350 | 35 | 0 | 74 | 34 | 0 | 0 | 3.6 |  | 6872 | 2649.6 | 9521.6 | 4328 | 851 | 2142 | 1489 | 319 | 182 | 53 | 150 | 7.6 | 0 | 106.23
17:00 | 35 | 199 | 220 | 0 | 0 | 96 | 50 | 305 | 302 |  | 0 | 360 | 255 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 72 | 0 | 13 | 35 | 56 | 17 | 22 | 25 | 30 | 33 | 33 | 41 | 0 | 87 | 90 | 95 | 120 | 8 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 47 | 22 | 12 | 135 | 0 | 0 | 260 | 270 | 161 | 68 | 90 | 37 | 47 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 140 | 142 | 40 | 22 | 0.2 | 53 | 58 | 46 | 49 | 163 | 266 | 63 | 40 | 5 | 73 | 17 | 42 | 10 | 300 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 104 | 63 | 2 | 60 | 17 | 10 | 250 | 115 | 102 | 17 | 1.44 | 106 | 8 |  | 851 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 15 | 11 | 8 | 173 | 9 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 6 | 24 | 0 | 8 | 0 | 22 | 13 | 5 | 71 | 0 | 249 | 0 | 0 | 180 | 0 | 181 | 0 | 53 | 0 | 184 | 0 | 350 | 35 | 0 | 55 | 34 | 20 | 0 | 2.8 |  | 6622.64 | 2630.8 | 9253.44 | 4147 | 851 | 2080 | 1474 | 320 | 177 | 58 | 140 | 6.44 | 0 | 106.23
18:00 | 35 | 199 | 220 | 0 | 0 | 53 | 50 | 305 | 252 |  | 0 | 300 | 258 | 7 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 32 | 0 | 72 | 0 | 13 | 35 | 56 | 17 | 22 | 25 | 30 | 33 | 33 | 41 | 0 | 87 | 90 | 95 | 120 | 8 | 205 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 2 | 135 | 0 | 0 | 260 | 265 | 161 | 68 | 87 | 37 | 46 | 0 | 10 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 124 | 144 | 40 | 22 | 0.1 | 53 | 58 | 5 | 5 | 100 | 266 | 61 | 10 | 5 | 73 | 17 | 11 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 104 | 60 | 0 | 60 | 17 | 10 | 200 | 115 | 102 | 17 | 0.26 | 106 | 6 |  | 852 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 36 | 26 | 8 | 172 | 7 | 16 | 12 | 0 | 55 | 0 | 0 | 0 | 6 | 24 | 0 | 8 | 0 | 22 | 13 | 5 | 70 | 0 | 249 | 0 | 0 | 167 | 0 | 152 | 0 | 52 | 0 | 156 | 0 | 250 | 35 | 0 | 55 | 34 | 47 | 0 | 1.1 |  | 6137.36 | 2546.1 | 8683.46 | 4018 | 852 | 1561 | 1525 | 319 | 177 | 106 | 124 | 1.46 | 0 | 106.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 35 | 199 | 220 | 0 | 0 | 93 | 50 | 294 | 265 |  | 0 | 350 | 306 | 7 | 23 | 15 | 10 | 0 | 0 | 0 | 15 | 64 | 115 | 10 | 72 | 0 | 13 | 35 | 56 | 55 | 22 | 25 | 22 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 25 | 228 | 0 | 0 | 0 |  | 0 | 0 | 44 | 10 | 76 | 50 | 22 | 19 | 135 | 0 | 0 | 335 | 310 | 182 | 68 | 90 | 37 | 47 | 0 | 10 | 0 | 8 | 8 | 19 | 11 | 33 | 0 | 164 | 141 | 75 | 22 | 0 | 53 | 58 | 5 | 7 | 100 | 266 | 59 | 10 | 5 | 88 | 17 | 42 | 10 | 265 | 21 | 11 | 0 | 60 | 0 | 0 | 7 | 104 | 88 | 0 | 60 | 17 | 10 | 140 | 115 | 102 | 17 | 0 | 163 | 0 |  | 852 | 16 | 0 | 0 | 49 | 0 | 0 | 0 | 29 | 47 | 40 | 173 | 25 | 40 | 12 | 0 | 55 | 42 | 10 | 81 | 6 | 42 | 31 | 8 | 38 | 22 | 14 | 5 | 71 | 0 | 249 | 0 | 17 | 168 | 0 | 154 | 0 | 32 | 7 | 159 | 0 | 232 | 43 | 0 | 55 | 59 | 33 | 0 | 0 |  | 6945 | 2916 | 9861 | 4100 | 852 | 1671 | 2081 | 320 | 183 | 490 | 164 | 0 | 0 | 106.22
19:30 | 35 | 234 | 220 | 0 | 0 | 93 | 73 | 340 | 302 |  | 0 | 350 | 240 | 22 | 48 | 55 | 10 | 0 | 0 | 0 | 50 | 102 | 149 | 10 | 72 | 0 | 20 | 53 | 56 | 55 | 22 | 25 | 22 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 25 | 204 | 0 | 0 | 0 |  | 0 | 0 | 82 | 10 | 96 | 50 | 22 | 21 | 135 | 0 | 0 | 310 | 310 | 182 | 68 | 90 | 37 | 47 | 0 | 16 | 0 | 8 | 40 | 19 | 11 | 33 | 0 | 172 | 141 | 95 | 22 | 0 | 53 | 58 | 50 | 46 | 100 | 262 | 59 | 75 | 38 | 73 | 17 | 45 | 10 | 280 | 21 | 11 | 0 | 64 | 0 | 0 | 36 | 103 | 99 | 0 | 90 | 80 | 45 | 200 | 115 | 102 | 17 | 0 | 210 | 0 |  | 852 | 16 | 0 | 0 | 95 | 0 | 0 | 0 | 31 | 52 | 40 | 172 | 20 | 48 | 12 | 0 | 55 | 50 | 10 | 95 | 6 | 42 | 45 | 40 | 38 | 22 | 14 | 5 | 69 | 0 | 249 | 0 | 17 | 173 | 0 | 159 | 0 | 97 | 85 | 158 | 0 | 300 | 105 | 0 | 105 | 87 | 0 | 0 | 0 |  | 7768 | 3364 | 11132 | 4181 | 852 | 2067 | 2754 | 318 | 183 | 605 | 172 | 0 | 0 | 0
20:00 | 35 | 260 | 221 | 0 | 0 | 90 | 73 | 342 | 300 |  | 0 | 350 | 237 | 48 | 52 | 30 | 9 | 0 | 0 | 0 | 40 | 50 | 149 | 10 | 72 | 0 | 28 | 53 | 56 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 88 | 90 | 95 | 120 | 25 | 205 | 0 | 0 | 0 |  | 0 | 0 | 85 | 10 | 97 | 50 | 22 | 26 | 135 | 0 | 0 | 310 | 310 | 182 | 66 | 90 | 37 | 47 | 0 | 30 | 0 | 8 | 43 | 19 | 11 | 33 | 14 | 174 | 147 | 95 | 22 | 0 | 53 | 58 | 50 | 50 | 100 | 266 | 57 | 75 | 43 | 74 | 17 | 45 | 10 | 280 | 24 | 11 | 0 | 45 | 0 | 0 | 113 | 102 | 149 | 0 | 100 | 135 | 50 | 200 | 115 | 102 | 17 | 0 | 214 | 0 |  | 846 | 32 | 0 | 0 | 105 | 0 | 0 | 0 | 33 | 60 | 40 | 172 | 20 | 48 | 0 | 0 | 55 | 50 | 26 | 95 | 6 | 42 | 47 | 52 | 38 | 22 | 14 | 11 | 70 | 0 | 249 | 0 | 17 | 167 | 0 | 156 | 0 | 97 | 85 | 159 | 0 | 300 | 105 | 0 | 112 | 86 | 0 | 0 | 0 |  | 7986 | 3417 | 11403 | 4243 | 846 | 2088 | 2915 | 319 | 178 | 640 | 174 | 0 | 0 | 106.21
21:00 | 35 | 249 | 220 | 0 | 0 | 93 | 73 | 342 | 351 |  | 0 | 400 | 280 | 28 | 48 | 0 | 9 | 0 | 0 | 0 | 24 | 24 | 98 | 10 | 72 | 0 | 47 | 53 | 56 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 94 | 90 | 95 | 120 | 25 | 206 | 0 | 0 | 0 |  | 0 | 0 | 42 | 10 | 97 | 50 | 22 | 32 | 135 | 0 | 0 | 310 | 310 | 186 | 68 | 90 | 37 | 48 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 172 | 145 | 95 | 22 | 0 | 52 | 58 | 53 | 50 | 163 | 264 | 63 | 75 | 43 | 115 | 17 | 45 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 100 | 180 | 50 | 250 | 115 | 102 | 17 | 0 | 214 | 0 |  | 845 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 52 | 40 | 173 | 28 | 32 | 0 | 0 | 55 | 50 | 31 | 95 | 6 | 42 | 45 | 52 | 38 | 22 | 15 | 11 | 71 | 0 | 249 | 0 | 17 | 181 | 0 | 184 | 0 | 98 | 100 | 183 | 0 | 300 | 105 | 0 | 113 | 86 | 0 | 0 | 0 |  | 8077 | 3501 | 11578 | 4401 | 845 | 2310 | 2811 | 320 | 184 | 535 | 172 | 0 | 0 | 106.21
22:00 | 35 | 249 | 220 | 0 | 0 | 91 | 74 | 340 | 352 |  | 0 | 400 | 260 | 24 | 48 | 0 | 9 | 0 | 0 | 0 | 24 | 24 | 98 | 10 | 72 | 0 | 47 | 53 | 56 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 25 | 205 | 0 | 0 | 0 |  | 0 | 0 | 34 | 10 | 97 | 50 | 22 | 38 | 135 | 0 | 0 | 310 | 310 | 182 | 73 | 90 | 37 | 48 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 168 | 145 | 95 | 22 | 0 | 53 | 58 | 53 | 50 | 163 | 265 | 62 | 75 | 43 | 110 | 17 | 45 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 90 | 0 | 100 | 182 | 50 | 250 | 117 | 102 | 17 | 0 | 214 | 0 |  | 845 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 34 | 52 | 40 | 173 | 31 | 32 | 0 | 0 | 55 | 50 | 31 | 95 | 6 | 42 | 45 | 52 | 38 | 22 | 15 | 11 | 71 | 0 | 249 | 0 | 0 | 184 | 0 | 188 | 0 | 98 | 100 | 190 | 0 | 300 | 105 | 0 | 113 | 87 | 0 | 0 | 0 |  | 8019 | 3485 | 11504 | 4404 | 845 | 2324 | 2767 | 320 | 183 | 493 | 168 | 0 | 0 | 106.2
23:00 | 35 | 219 | 218 | 0 | 0 | 96 | 74 | 341 | 354 |  | 0 | 400 | 280 | 10 | 48 | 0 | 9 | 0 | 0 | 0 | 8 | 24 | 98 | 0 | 72 | 0 | 33 | 53 | 56 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 25 | 206 | 0 | 0 | 0 |  | 0 | 0 | 34 | 10 | 97 | 50 | 22 | 39 | 135 | 0 | 0 | 310 | 310 | 188 | 73 | 90 | 37 | 47 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 168 | 145 | 95 | 22 | 0 | 53 | 58 | 53 | 50 | 163 | 265 | 63 | 75 | 43 | 115 | 17 | 45 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 90 | 0 | 100 | 182 | 50 | 254 | 117 | 102 | 17 | 0 | 216 | 0 |  | 860 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 30 | 52 | 40 | 173 | 31 | 32 | 0 | 0 | 55 | 50 | 26 | 95 | 6 | 42 | 45 | 52 | 37 | 22 | 15 | 11 | 70 | 0 | 250 | 0 | 17 | 186 | 0 | 190 | 0 | 96 | 100 | 192 | 0 | 300 | 105 | 0 | 113 | 87 | 0 | 0 | 0 |  | 7950 | 3495 | 11445 | 4396 | 860 | 2329 | 2705 | 320 | 183 | 484 | 168 | 0 | 0 | 106.2
24:00 | 35 | 219 | 220 | 0 | 0 | 96 | 74 | 341 | 354 |  | 0 | 400 | 280 | 0 | 15 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 80 | 0 | 72 | 0 | 13 | 53 | 56 | 35 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 93 | 90 | 95 | 120 | 25 | 206 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 97 | 50 | 22 | 40 | 135 | 0 | 0 | 315 | 310 | 192 | 73 | 90 | 37 | 49 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 166 | 145 | 95 | 22 | 0 | 53 | 58 | 53 | 50 | 163 | 264 | 63 | 75 | 43 | 116 | 16 | 45 | 10 | 305 | 24 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 67 | 0 | 100 | 183 | 50 | 254 | 117 | 102 | 17 | 0 | 215 | 0 |  | 859 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 29 | 52 | 40 | 173 | 27 | 32 | 0 | 0 | 55 | 25 | 26 | 95 | 6 | 42 | 45 | 52 | 37 | 22 | 16 | 11 | 70 | 0 | 250 | 0 | 18 | 186 | 0 | 190 | 0 | 96 | 40 | 192 | 0 | 300 | 105 | 0 | 113 | 86 | 0 | 0 | 0 |  | 7803 | 3405 | 11208 | 4408 | 859 | 2334 | 2514 | 320 | 183 | 424 | 166 | 0 | 0 | 106.2
KWH | 820000 | 5536400 | 5291000 | 0 | 0 | 2044909 | 900032 | 8263680 | 7286000 |  | 0 | 8510375 | 6589207 | 134400 | 279672 | 93489 | 231510 | 0 | 0 | 0 | 127680 | 509328 | 957600 | 73121 | 1323840 | 0 | 420000 | 871560 | 788389 | 726873 | 481572 | 600000 | 716940 | 807400 | 792100 | 838800 | 0 | 2074756 | 2160000 | 2200000 | 2900000 | 255924 | 4888468 | 0 | 0 | 0 |  | 0 | 0 | 305106 | 258720 | 1079040 | 912480 | 508128 | 498240 | 3301924 | 0 | 0 | 7755700 | 7489000 | 4489000 | 1672727 | 2226590 | 799560 | 1124160 | 0 | 889140 | 0 | 15312 | 520890 | 440172 | 242820 | 813900 | 435190 | 3428160 | 3392280 | 1225920 | 524988 | 11550 | 1249000 | 1463077 | 913800 | 932544 | 3366196 | 5964000 | 1282272 | 1481280 | 902880 | 2161770 | 431330 | 860500 | 227340 | 7336500 | 505104 | 253968 | 0 | 326181 | 0 | 0 | 1120800 | 1035608 | 1264320 | 74385 | 1812480 | 1843200 | 727636 | 5541000 | 2376000 | 2264100 | 159744 | 39000 | 4375854 | 48500 |  | 20148364 | 90100 | 0 | 0 | 1218240 | 0 | 0 | 0 | 299520 | 564640 | 441750 | 4187000 | 489464 | 323520 | 42107 | 0 | 1365000 | 314184 | 126424 | 661072 | 157640 | 601453 | 260010 | 471840 | 280690 | 513360 | 311436 | 167328 | 1666036 | 0 | 6067700 | 0 | 95000 | 4489427 | 0 | 4282291 | 0 | 1780126 | 561600 | 4542091 | 0 | 6003000 | 1330560 | 0 | 1766592 | 1285920 | 333120 | 0 | 42600 |  | 167196091 | 67281205 | 234477296 | 103832980 | 20148364 | 48044009 | 42875991 | 7733736 | 4234756 | 4011765 | 3428160 | 167535 | 0
Fuel Cost | 918400 | 5979312 | 5661370 | 0 | 0 | 1983561.73 | 1314046.72 | 5949849.6 | 5537360 |  | 0 | 6808300 | 5930286.3 | 1370880 | 3028847.76 | 959197.14 | 287072.4 | 0 | 0 | 0 | 1417248 | 5174772.48 | 9489816 | 766308.08 | 12046944 | 0 | 3931200 | 8358260.4 | 7521231.06 | 7239655.08 | 361179 | 450000 | 0 | 0 | 0 | 8035704 | 0 | 539436.56 | 561600 | 3366000 | 4437000 | 2459429.64 | 5132891.4 | 0 | 0 | 0 |  | 0 | 0 | 3200561.94 | 2662228.8 | 10261670.4 | 8540812.8 | 467477.76 | 1385107.2 | 3467020.2 | 0 | 0 | 5739218 | 6290760 | 4129880 | 1639272.46 | 2961364.7 | 655639.2 | 1157884.8 | 0 | 1271470.2 | 0 | 179456.64 | 4896366 | 448975.44 | 182115 | 1538271 | 326392.5 | 23654304 | 2781669.6 | 11658499.2 | 535487.76 | 189420 | 1698640 | 1989784.72 | 1242768 | 1165680 | 4174083.04 | 5486880 | 1910585.28 | 2607052.8 | 1002196.8 | 3285890.4 | 685814.7 | 1006785 | 534249 | 5208915 | 378828 | 193015.68 | 0 | 3415115.07 | 0 | 0 | 10782096 | 17294653.6 | 12756988.8 | 858402.9 | 16892313.6 | 17289216 | 6817949.32 | 5208540 | 20837520 | 20173131 | 1509580.8 | 0 | 40345373.88 | 0 |  | 54400582.8 | 2635425 | 0 | 0 | 11743833.6 | 0 | 0 | 0 | 3474432 | 7396784 | 4368907.5 | 3349600 | 758669.2 | 3474604.8 | 1395847.05 | 0 | 2566200 | 3500009.76 | 1548694 | 6544612.8 | 1634726.8 | 7043014.63 | 3133120.5 | 4699526.4 | 2764796.5 | 564696 | 513869.4 | 126667.296 | 10612649.32 | 0 | 24816893 | 0 | 2681850 | 3950695.76 | 0 | 3982530.63 | 0 | 2830400.34 | 9491040 | 3997040.08 | 0 | 4382190 | 12587097.6 | 0 | 16217314.56 | 11457547.2 | 3111340.8 | 0 | 0 |  | 433990534.34 | 237757209.326 | 671747743.666 | 100878058.106 | 54400582.8 | 47088557.69 | 360202433.1 | 35429542.32 | 1101036.56 | 47945406.19 | 23654304 | 1047822.9 | 0
Yesterday Day Peak | 35 | 199 | 219 | 0 | 0 | 97 | 73 | 340 | 312 |  | 0 | 360 | 250 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 72 | 0 | 13 | 17 | 17 | 17 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 93 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 50 | 22 | 2 | 135 | 0 | 0 | 310 | 305 | 182 | 68 | 90 | 33 | 47 | 0 | 30 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 140 | 144 | 8 | 22 | 1.4 | 53 | 58 | 50 | 50 | 130 | 262 | 40 | 73 | 40 | 110 | 17 | 43 | 0 | 280 | 7 | 11 | 0 | 14 | 0 | 0 | 7 | 0 | 48 | 13.3 | 100 | 17 | 10 | 200 | 115 | 102 | 0 | 4.6 | 195 | 0 |  | 841 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 11 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 6 | 8 | 0 | 8 | 0 | 22 | 14 | 5 | 70 | 0 | 249 | 0 | 0 | 181 | 0 | 185 | 0 | 72 | 0 | 206 | 0 | 300 | 17 | 0 | 30 | 52 | 47 | 0 | 3 |  | 9180.3 | DayPeak
Yesterday Evening Peak | 35 | 249 | 220 | 0 | 0 | 93 | 73 | 342 | 351 | 0 | 0 | 400 | 280 | 28 | 48 | 0 | 9 | 0 | 0 | 0 | 24 | 24 | 98 | 10 | 72 | 0 | 47 | 53 | 56 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 94 | 90 | 95 | 120 | 25 | 206 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 10 | 97 | 50 | 22 | 32 | 135 | 0 | 0 | 310 | 310 | 186 | 68 | 90 | 37 | 48 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 172 | 145 | 95 | 22 | 0 | 52 | 58 | 53 | 50 | 163 | 264 | 63 | 75 | 43 | 115 | 17 | 45 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 115 | 0 | 100 | 180 | 50 | 250 | 115 | 102 | 17 | 0 | 214 | 0 |  | 845 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 35 | 52 | 40 | 173 | 28 | 32 | 0 | 0 | 55 | 50 | 31 | 95 | 6 | 42 | 45 | 52 | 38 | 22 | 15 | 11 | 71 | 0 | 249 | 0 | 17 | 181 | 0 | 184 | 0 | 98 | 100 | 183 | 0 | 300 | 105 | 0 | 113 | 86 | 0 | 0 | 0 |  | 11578 | EvPeak
Forecast for Evening | 35 | 230 | 200 | 0 | 0 | 100 | 40 | 370 | 360 | 0 | 0 | 450 | 280 | 100 | 100 | 55 | 10 | 0 | 0 | 0 | 100 | 102 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 130 | 90 | 95 | 120 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 100 | 96 | 50 | 22 | 30 | 100 | 0 | 0 | 360 | 360 | 220 | 68 | 90 | 37 | 50 | 0 | 45 | 0 | 42 | 52 | 22 | 11 | 33 | 20 | 184 | 145 | 95 | 22 | 0 | 53 | 58 | 51 | 44 | 163 | 267 | 66 | 75 | 42 | 125 | 17 | 45 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 300 | 115 | 100 | 100 | 0 | 260 |  |  | 937 | 32 | 0 | 0 | 115 | 150 | 0 | 0 | 35 | 70 | 40 | 175 | 33 | 110 | 30 | 0 | 60 | 50 | 30 | 100 | 12 | 42 | 45 | 52 | 36 | 22 | 15 | 11 | 100 | 0 | 250 | 0 | 18 | 215 | 0 | 210 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 0 | 113 | 85 | 100 | 0
Forecast for Day | 35 | 230 | 200 | 0 | 0 | 100 | 40 | 370 | 340 | 0 | 0 | 450 | 280 | 100 | 100 | 55 | 10 | 0 | 0 | 0 | 100 | 100 | 149 | 100 | 72 | 0 | 47 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 130 | 90 | 95 | 120 | 25 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 90 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 340 | 220 | 68 | 0 | 37 | 50 | 0 | 45 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 140 | 145 | 95 | 22 | 1.6 | 53 | 58 | 51 | 44 | 163 | 260 | 64 | 75 | 42 | 120 | 17 | 45 | 10 | 315 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 149 | 20 | 100 | 200 | 150 | 300 | 115 | 100 | 50 | 4.4 | 230 |  |  | 937 | 0 | 0 | 0 | 115 | 150 | 0 | 0 | 0 | 0 | 40 | 175 | 33 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 12 | 42 | 45 | 52 | 0 | 22 | 15 | 11 | 100 | 0 | 250 | 0 | 0 | 215 | 0 | 200 | 0 | 95 | 0 | 205 | 0 | 400 | 105 | 0 | 110 | 84 | 0 | 0 | 3
Generation at 08:00(Today) | 35 | 219 | 220 | 0 | 0 | 97 | 40 | 340 | 324 | 0 | 0 | 370 | 282 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 13 | 35 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 4 | 0 | 92 | 90 | 95 | 120 | 0 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 48 | 22 | 12 | 100 | 0 | 0 | 320 | 295 | 194 | 68 | 90 | 37 | 50 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 0 | 116 | 145 | 8 | 22 | 1 | 53 | 58 | 11 | 10 | 100 | 265 | 52 | 10 | 10 | 117 | 16 | 13 | 10 | 310 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 4 | 10 | 17 | 10 | 201 | 115 | 102 | 0 | 2.81 | 71 | 0 | 0 | 927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 6 | 8 | 0 | 0 | 0 | 22 | 16 | 8 | 71 | 0 | 249 | 0 | 0 | 160 | 0 | 157 | 0 | 12 | 0 | 161 | 0 | 250 | 17 | 0 | 17 | 51 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8059.3 | 8:00
| Highest Generation |  | 11578 | 21:00
| Day Peak Generation |  | 9180.3 | 12:00
| Evening Peak Generation |  | 11578 | 21:00
| HVDC Max Flow |  | 860 | 23:00
| HVDC EvPeak Flow |  | 845 | 21:00
| Load factor L.F |  | 84.38%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-07-29
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-07-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9180.3 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8382.81 | MW
Evening Peak Generation : |  | 11578 | MW Hour : | 21:00 | Available Max Generation : |  | 14718 | MW
E.P. Demand (at gen end) : |  | 11578 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11578 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2718 | MW
Total Gen. (MKWH) : |  | 234.4773 | System Load Factor : | 84.38% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -502 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-07-29
Actual : | 106.14 | Ft.(MSL) , | Rule curve : | 88.49 | Ft.( MSL )
Gas Consumed : | Total = | 1373.96 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 147966615.796
|  | Coal : | 35429542.32 | Oil : | 408147839.29 | Total : | 591543997.406
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4257.8438 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1450.1494 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1299.6861 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1174.5182 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1061.3167 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 856.4507 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 475.9938 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 220.4365 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 660.5511 |  |  | 0 | 0%
Total | 0 |  | 11456.9462 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal Unit-2
|  |  |  | 4) Bheramara 410 MW. | 11) Sikalbaha 150 MW GT
|  |  |  | 5) Siddhirganj ST | 12) Ghorasal Unit-5
6) Ashuganj #4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Barishal(N) 132/33 kV T-5 transformer was under shut down from 09:14 to 14:36 for C/M.
b) Faridpur-Madaripur 132 kV Ckt-1 was under shutdown from 09:57 to 12:20 for C/M.
c) Madanganj 132/33 kV T-2 transformer tripped at 11:15 showing buchhollz relay and was switched on at 12:53.
d) Faridpur-Madaripur 132 kV Ckt-2 was under shutdown from 12:47 to 15:33 for C/M.
e) Barishal(N) 132/33 kV T-4 transformer was under shut down from 15:19 to 17:45 for C/M.
f) Pabna 132/33 kV T-2 transformer was under shut down from 15:26 to 17:03 for energy meter replacement work.
g) Saidpur 132/33 kV T-4 transformer was under shut down from 20:14 to 20:45 for R/H mainttenance at 33 kV |  |  |  |  | About 10 MW power interruption occurred under Saidpur S/S area
incoming CB at Y-phase. |  |  |  |  | from 20:14 to 20:45.
h) Kishorganj 132/33 kV T-3 transformer was under shut down from 23:20 to 23:45 for C/M by PDB.
i) Halisahar-Juldah 132 kV Ckt was under shut down from 06:16(29/7/2019) to 08:33 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-07-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 35 | 820000 | #2 Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 249 | 5536400
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 220 | 5291000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 73 | 900032
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 93 | 2044909
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8263680 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 7286000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 400 | 8510375 | Frequency control
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 28 | 134400 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6589207 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 48 | 279672 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 93489 | High Voltage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 10 | 73121 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 481572
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 24 | 127680 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 9 | 231510 | Testing
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 509328 | High Voltage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 47 | 420000 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 871560
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 957600 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 56 | 788389
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 726873
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 1323840 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1316940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 807400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 792100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 41 | 838800 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 326181 | Reserve
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 1035608 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 115 | 1264320 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 102 | 2264100
| Dhaka area Total |  |  |  | 5693 | 2969 | 60906086
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2200000
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 255924
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 74385
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 912480
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 184 | 4234756
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 206 | 4888468 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 159744 | Transformer O/L
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 42 | 305106 | Low demand
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 258720 | Line O/L
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1812480
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 508128
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 32 | 498240
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1079040
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 39000
53 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 214 | 4375854 | Transformer over load
| Jodiac Power |  | IPP | 54.36 | 0 | 0 | 48500
| Chattogram area Total |  |  |  | 2053 | 1214 | 24550825
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 3301924 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 186 | 4489000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7755700 | FGMO
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7489000 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 37 | 799560 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 48 | 1124160 | Engine problem
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1672727 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 889140 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 727636 | Transformer over load
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 15312 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2226590 | Gas shortage
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 1843200 | Engine problem
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440172
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242820
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 172 | 3428160
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 813900
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 520890
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 435190 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1764 | 38215081
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 145 | 3392280 | GT-1 under maint.
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 524988
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1225920
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11550
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 160 | 1120800 | Engine problem
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2376000
| Mymensingh Area Total |  |  |  | 637 | 537 | 8651538
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 52 | 1249000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 58 | 1463077
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3366196
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 264 | 5964000 | FGMO
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 913800
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 50 | 932544
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 253968
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1282272
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1481280 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 43 | 902880 | Engine problem
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 115 | 2161770 | FGMO
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 431330
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 45 | 860500 | Engine problem
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 505104
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7336500 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 250 | 5541000 | Frequency control
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 227340
| Sylhet Area Total |  |  |  | 1834 | 1593 | 34872561
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 32 | 90100
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 845 | 20148364
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1218240
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 35 | 299520
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 52 | 564640
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 441750
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 561600
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1330560
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 86 | 1285920 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1410 | 25940694
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 323520 | Line over load
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 42107 | Reserve
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 489464
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 173 | 4187000 | Machine problem
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 98 | 1780126
| Barisal Area Total |  |  |  | 462 | 331 | 6822217
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1365000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 314184
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 126424
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 6 | 157640 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 601453 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 45 | 260010
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 181 | 4489427 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4282291 | FGMO
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4542091 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 300 | 6003000 | Frequency control
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 280690
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 513360
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 15 | 311436
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 167328
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 471840
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 661072
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1766592
| Rajshahi Area Total |  |  |  | 2070 | 1423 | 26313838
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 71 | 1666036
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 249 | 6067700
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 95000
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 0 | 333120 | On test
| Sympa Solar Power 8MW |  | IPP | 8 MW | 0 | 0 | 42600
| Rangpur Area Total |  |  |  | 484 | 337 | 8204456
| Total |  |  |  | 18438 | 11578 | 234477296
| Eastern Grid Total |  |  |  | 13108 | 8077 | 167196091
| Western Grid Total |  |  |  | 5330 | 3501 | 67281205
| National Grid Total |  |  |  | 18438 | 11578 | 234477296
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2019-07-28
(a) ENTIRE EASTERN GRID : |  | 7501 | MW | (b) ENTIRE WESTERN GRID : |  | 3543 | MW
i) Dhaka area |  | 3982 | MW | i) Khulna area |  | 1370 | MW
ii) Chittagong area |  | 1095 | MW | ii) Rajshahi area |  | 1188 | MW
iii) Comilla area |  | 1019 | MW | iii) Barisal area |  | 296 | MW
iv) Mymensingh area |  | 901 | MW | iv) Rangpur area |  | 689 | MW
v) Sylhet area |  | 504 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11044 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 1500 | Jamalpur | 110 | 2100 | Jessore | 104 | 1930
Munsiganj | 124 | 2100 | Sherpur | 102 | 2000 | Benapol | 40 | 2000
Sonargaon | 74 | 1930 | Srimongal | 39 | 1900 | Jhenida | 103 | 2000
Shyampur | 184 | 900 | Shahjibazar | 120 | 2200 | Bottail | 124 | 2000
Bhulta | 188 | 2000 | Fenchuganj | 51 | 1930 | G.K Project | 58 | 2100
Madanganj | 41 | 100 | Kulawara | 48 | 2000 | Faridpur | 170 | 2000
Shitalakhya | 103 | 1300 | Sylhet | 151 | 1900 | Madaripur | 107 | 2200
Rahim steel | 7 | 1000 | Chatak | 30 | 2200 | Sariatpur | 32 | 2300
Matuail | 100 | 1000 | Sunamganj | 34 | 2100 | Gopalganj | 85 | 2100
Ghorasal | 76 | 2100 | Biani Bazar | 47 | 2100 | Bagerhat | 73 | 2000
Narsingdi | 141 | 2100 | Comilla (S) | 174 | 2000 | Mongla | 36 | 400
Haripur (SBU) | 99 | 1200 | Comilla(N) | 113 | 2000 | Satkhira | 93 | 2200
Ullon | 83 | 2000 | Chandpur | 96 | 2200 | Gallamari | 48 | 1300
Hasnabad | 195 | 2000 | Feni | 129 | 2000 | Magura | 50 | 1930
Magbazar | 135 | 1600 | Chowmuhani | 156 | 2100 | Chuadanga | 86 | 2100
Maniknagar | 118 | 1300 | Ashuganj | 54 | 2300 | Barisal(N) | 39 | 2100
Bangabhaban | 38 | 1300 | Daudkandi | 128 | 2400 | Barisal (S) | 90 | 2100
Narinda | 90 | 1700 | B.Baria | 140 | 2000 | Patuakhali | 92 | 2300
Dhanmondi | 158 | 1300 | Ramganj | 76 | 1930 | Bhandaria | 52 | 2200
Lalbag | 80 | 1300 | Madunaghat | 55 | 1930 | Borhan Uddin | 33 | 100
Madartek | 52 | 2100 | Hathazari | 94 | 1930 | Ishurdi | 61 | 2100
Mirpur | 104 | 1900 | Khulshi | 160 | 1400 | Ruppur Paromanobik | 1 | 100
Kalyanpur | 114 | 2000 | Halishahar | 132 | 1000 | Natore | 120 | 2100
Gulshan | 156 | 1500 | Baraulia | 185 | 1400 | Bogra | 223 | 2000
Uttara | 80 | 1600 | Sikalbaha | 34 | 1930 | Noagaon | 117 | 2100
Uttara New | 18 | 1600 | Dohazari | 78 | 2100 | Rajshahi | 145 | 2000
Kamrangirchar | 73 | 1900 | Cox'sbazar | 83 | 2100 | C.Nawabganj | 66 | 2000
Savar | 136 | 1200 | Chandraghona | 24 | 1930 | Amnura | 34 | 2100
Bhasantec | 85 | 1300 | Kaptai | 4 | 2000 | Pabna | 107 | 2100
Agargaon | 57 | 1300 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 92 | 2100
Satmosjid | 97 | 1400 | Bakulia | 103 | 2000 | Serajganj | 104 | 2100
Tongi | 147 | 2100 | Julda | 16 | 100 | Niyamatpur | 56 | 2100
Kabirpur | 208 | 1500 | TK chemical | 3 | 2000 | Joypurhat | 52 | 2100
Basundhara | 130 | 1400 | Modern Steel | 12 | 1000 | Mohastangor | 16 | 2000
Manikganj | 90 | 2100 | Shahmirpur | 28 | 100 | Rangpur | 143 | 1930
Joydevpur | 224 | 2100 | Khagrachhari | 20 | 1900 | Lalmonirhat | 91 | 2100
New Tongi | 100 | 1500 | Matarbari | 25 | 2100 | Saidpur | 93 | 2000
Korda | 249 | 1500 | Baroiar Hat | 24 | 1900 | Purbasadipur | 100 | 2000
Dhamrai | 58 | 2000 | Rangamati | 12 | 1900 | Thakurgaon | 75 | 2100
Valuka | 92 | 1930 | Abul Khair 230 | 126 | 300 | Palashbari | 109 | 2100
Tangail | 184 | 2200 | BSRM | 153 | 700 | Barapukuria | 50 | 2100
Mymensing | 241 | 2200 | Goalpara | 29 | 1930 | Panchagar | 42 | 2000
Kishorganj | 123 | 1930 | Central (S) | 90 | 2100 | Joldhaka | 23 | 1900
Netrokona | 104 | 2000 | Noapara | 98 | 2200
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-07-28
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 390 | 5:00 | 381 | 12:00 | Kaliakoir | 367 | 6:00 | 356
Bheramara | 401 | 7:00 | 393 | 22:00 | Bhulta | 384 | 20:00 | 370
Ashuganj(N) | 386 | 6:00 | 375 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 12:00
Ghorasal | 230 | 1:00 | 222 | 14:00 | Hathazari | 222 | 2:00 | 215
Ishurdi | 236 | 8:00 | 224 | 5:00 | Megnaghat | 223 | 6:00 | 217
Ashuganj | 235 | 1:00 | 231 | 15:00 | Fenchuganj | 237 | 6:00 | 233
Serajganj | 234 | 18:30 | 225 | 2:00 | Siddhirganj | 222 | 6:00 | 213
Baghabari | 235 | 10:00 | 230 | 2:00 | Maniknagar | 219 | 1:00 | 211
Barapukuria | 235 | 14:00 | 223 | 22:00 | Old Airport | 219 | 1:00 | 209
Bogra | 229 | 18:30 | 214 | 22:00 | Barisal | 233 | 13:00 | 219
Khulna South | 226 | 18:30 | 207 | 5:00 | AKSML | 219 | 1:00 | 213
Rampura | 222 | 6:00 | 213 | 11:00 | BSRM | 221 | 1:00 | 215
Haripur | 220 | 1:00 | 213 | 11:00 | Bibiyana | 233 | 1:00 | 228
Hasnabad | 221 | 7:00 | 212 | 15:00 | Bhulta | 222 | 1:00 | 213
Aminbazar | 221 | 3:00 | 211 | 11:00 | Ashuganj (S) | 234 | 6:00 | 228
Tongi | 221 | 1:00 | 212 | 11:00 | Kaliakoir | 222 | 1:00 | 215
Comilla (N) | 230 | 20:00 | 224 | 11:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 1930 | 125 | 1500 | Hathazari | 132 | 100 | 129
Munsiganj | 133 | 1930 | 124 | 1100 | Khulshi | 130 | 2000 | 126
Megnaghat | 130 | 2000 | 126 | 900 | Halishahar | 134 | 100 | 129
Shyampur | 132 | 1930 | 124 | 1200 | Baraulia | 130 | 1830 | 126
Bhulta | 125 | 100 | 120 | 1200 | Sikalbaha | 134 | 300 | 129
Madanganj | 134 | 1900 | 122 | 1000 | Dohazari | 132 | 100 | 127
Shitalakhya | 137 | 1930 | 123 | 1000 | Cox'sbazar | 126 | 400 | 120
Rahim steal | 131 | 400 | 125 | 1100 | Chandraghona | 133 | 100 | 130
Matuail | 130 | 600 | 124 | 1500 | Kaptai | 133 | 100 | 130
Ghorasal | 128 | 1800 | 132 | 1400 | A. Khaer Stl. | 130 | 1800 | 126
Narsinghdi | 126 | 400 | 119 | 1200 | Bakulia | 132 | 200 | 128
Haripur (SBU) | 132 | 700 | 125 | 1100 | Julda | 132 | 100 | 128
Ullon | 135 | 600 | 127 | 1200 | TK Chemical | 134 | 100 | 130
Hasnabad | 134 | 1830 | 124 | 1200 | Modern Steel | 133 | 1930 | 129
Magbazar | 136 | 300 | 126 | 1200 | Shahmirpur | 134 | 2000 | 128
Maniknagar | 135 | 600 | 128 | 1100 | Khagrachhari | 132 | 2000 | 129
Bangabhaban | 135 | 600 | 128 | 1100 | Matarbari | 128 | 1200 | 123
Narinda | 135 | 600 | 128 | 1100 | Baroiar Hat | 130 | 1830 | 127
Dhanmondi | 135 | 600 | 127 | 1200 | Rangamati | 133 | 100 | 129
Lalbag | 135 | 600 | 121 | 1200 | Goalpara | 138 | 100 | 125
Madartek | 135 | 700 | 127 | 1200 | Central s/s | 136 | 1830 | 126
Mirpur | 135 | 400 | 128 | 1600 | Noapara | 134 | 1830 | 123
Kalyanpur | 137 | 300 | 129 | 1100 | Jessore | 130 | 1830 | 117
Gulshan | 134 | 200 | 126 | 1200 | Benapol | 134 | 1830 | 116
Uttara | 133 | 100 | 124 | 1100 | Jhenida | 131 | 1830 | 117
Uttara New | 131 | 100 | 124 | 1600 | Bottail | 135 | 1830 | 124
Kamrangirchar | 130 | 100 | 121 | 1100 | G.K Project | 141 | 1830 | 133
Savar | 133 | 100 | 125 | 1100 | Faridpur | 133 | 1830 | 122
Bhasantec | 135 | 500 | 126 | 1100 | Madaripur | 134 | 1830 | 123
Agargaon | 136 | 600 | 128 | 1100 | Sariatpur | 133 | 800 | 123
Satmosjid | 136 | 500 | 127 | 1100 | Gopalganj | 140 | 1930 | 128
Tongi | 134 | 1800 | 127 | 1500 | Bagerhat | 135 | 1830 | 125
Kabirpur | 133 | 400 | 126 | 1500 | Mongla | 132 | 1800 | 121
Basundhara | 130 | 1830 | 122 | 1500 | Satkhira | 135 | 1800 | 121
Manikganj | 139 | 100 | 127 | 1500 | Gallamari | 138 | 1830 | 124
Joydevpur | 137 | 100 | 129 | 1100 | Magura | 130 | 1830 | 114
New Tongi | 133 | 2000 | 125 | 1500 | Chuadanga | 127 | 1830 | 108
Kodda | 136 | 100 | 122 | 800 | Barisal(N) | 138 | 1300 | 132
Dhamrai | 132 | 600 | 126 | 2100 | Barisal (S) | 136 | 900 | 130
Valuka | 128 | 1830 | 117 | 2100 | Patuakhali | 137 | 1300 | 125
Tangail | 134 | 1830 | 124 | 2200 | Bhandaria | 135 | 1300 | 124
Mymensing | 130 | 1830 | 119 | 1500 | Ishurdi | 138 | 1800 | 131
Kishorganj | 130 | 1000 | 123 | 2300 | Ruppur Paromanobik | 137 | 1800 | 132
Netrokona | 130 | 1830 | 117 | 1900 | Natore | 137 | 1830 | 128
Jamalpur | 139 | 1930 | 126 | 1000 | Bogra | 137 | 1830 | 126
Sherpur | 134 | 1830 | 123 | 600 | Noagaon | 131 | 1830 | 120
Srimongal | 137 | 600 | 132 | 2200 | Rajshahi | 135 | 1800 | 122
Shahjibazar | 134 | 500 | 130 | 1900 | C.Nawabganj | 130 | 1830 | 120
Fenchuganj | 136 | 600 | 133 | 1200 | Amnura | 136 | 1830 | 120
Khulawara | 134 | 400 | 131 | 1900 | Pabna | 136 | 800 | 129
Sylhet | 134 | 400 | 132 | 1600 | Shahjadpur | 140 | 700 | 135
Chatak | 134 | 600 | 130 | 1900 | Serajganj | 136 | 800 | 127
Sunamganj | 133 | 600 | 129 | 2100 | Niyamatpur | 131 | 1830 | 115
Biani Bazar | 134 | 600 | 129 | 1900 | Joypurhat | 134 | 1830 | 117
Comilla(s) | 127 | 700 | 120 | 2000 | Mohastangor | 135 | 1800 | 123
Comilla(n) | 134 | 700 | 132 | 2400 | Rangpur | 132 | 1800 | 115
Chandpur | 135 | 2200 | 132 | 700 | Lalmonirhat | 127 | 1800 | 108
Feni | 128 | 700 | 125 | 1600 | Saidpur | 130 | 1800 | 115
Chowmuhani | 128 | 1400 | 122 | 1600 | Purbasadipur | 130 | 1800 | 112
Ashuganj | 135 | 700 | 132 | 2200 | Thakurgaon | 124 | 1800 | 106
Daudkandi | 130 | 700 | 124 | 2400 | Palashbari | 131 | 1830 | 116
B.Baria | 132 | 500 | 126 | 2100 | Barapukuria | 135 | 1700 | 124

## L-Curve
Date | 2019-07-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 170 | 7803 | 3405 | 11208 |  |  |  | QF-LDC-12
0:30 | 336 | 7735 | 3190.5 | 10925.5 | Date: | 2019-07-28
1:00 | 502 | 7667 | 2976 | 10643
1:30 | 502 | 7518 | 2821.5 | 10339.5
2:00 | 502 | 7369 | 2667 | 10036
2:30 | 441 | 7195.5 | 2661 | 9856.5 | [5 empty] | Gen. at Eve. Peak | 11578 | 9880 MW (21:00 )
3:00 | 380 | 7022 | 2655 | 9677 | [6 empty] | 21:00
3:30 | 340 | 6926.5 | 2663 | 9589.5 | [5 empty] | Gen. at Day Peak | 9180.3 | 7665.7 MW (12:00 )
4:00 | 300 | 6831 | 2671 | 9502 | [6 empty] | 12:00
4:30 | 250 | 6681.5 | 2628.5 | 9310 | [5 empty] | Highest Generation | 11578
5:00 | 200 | 6532 | 2586 | 9118 | [6 empty] | 21:00
5:30 | 190 | 6254.622 | 2470.55 | 8725.172
6:00 | 180 | 5977.244 | 2355.1 | 8332.344
6:30 | 107.5 | 5881.012 | 2341.15 | 8222.162
7:00 | 35 | 5784.78 | 2327.2 | 8111.98
7:30 | 77.5 | 5764.74 | 2320.9 | 8085.64
8:00 | 120 | 5744.7 | 2314.6 | 8059.3
8:30 | 190 | 5861.7 | 2347.75 | 8209.45
9:00 | 260 | 5978.7 | 2380.9 | 8359.6
9:30 | 295 | 6075.2 | 2451.5 | 8526.7
10:00 | 330 | 6171.7 | 2522.1 | 8693.8
10:30 | 320 | 6284 | 2537.2 | 8821.2
11:00 | 310 | 6396.3 | 2552.3 | 8948.6
11:30 | 290 | 6499.3 | 2565.15 | 9064.45
12:00 | 270 | 6602.3 | 2578 | 9180.3
12:30 | 270 | 6587.45 | 2580.65 | 9168.1
13:00 | 270 | 6572.6 | 2583.3 | 9155.9
13:30 | 260 | 6544.44 | 2564.9 | 9109.34
14:00 | 250 | 6516.28 | 2546.5 | 9062.78
14:30 | 225 | 6710.44 | 2571 | 9281.44
15:00 | 200 | 6904.6 | 2595.5 | 9500.1
15:30 | 230 | 6888.3 | 2622.55 | 9510.85
16:00 | 260 | 6872 | 2649.6 | 9521.6
16:30 | 245 | 6747.32 | 2640.2 | 9387.52
17:00 | 230 | 6622.64 | 2630.8 | 9253.44
17:30 | 262.5 | 6380 | 2588.45 | 8968.45
18:00 | 295 | 6137.36 | 2546.1 | 8683.46
18:30 | 175 | 6541.18 | 2731.05 | 9272.23
19:00 | 55 | 6945 | 2916 | 9861
19:30 | 260 | 7768 | 3364 | 11132
20:00 | 280 | 7986 | 3417 | 11403 |  |  |  | Executive Engineer
20:30 | 257.5 | 8031.5 | 3459 | 11490.5 |  |  |  | Network Operation Division
21:00 | 235 | 8077 | 3501 | 11578
21:30 | 247.5 | 8048 | 3493 | 11541
22:00 | 260 | 8019 | 3485 | 11504 |  |  |  |  | Page 6 of 7
22:30 | 225 | 7984.5 | 3490 | 11474.5
23:00 | 190 | 7950 | 3495 | 11445
23:30 | 180 | 7876.5 | 3450 | 11326.5
24:00 | 170 | 7803 | 3405 | 11208
9880 MW (21:00 )
7665.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-07-28 |  | Energy | 234477296
[10 empty] | 2019-07-28 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4408 | 859 | 2334 | 2514 | 320 | 183 | 424 | 0 | 166
0:30 | 4382 | 854 | 2077.5 | 2542.5 | 319 | 183 | 408.5 | 0 | 159 | Date: | 2019-07-28
1:00 | 4356 | 849 | 1821 | 2571 | 318 | 183 | 393 | 0 | 152
1:30 | 4314.5 | 849 | 1817 | 2434 | 318 | 183.5 | 273.5 | 0 | 150 | [7 empty] | Total Energy | 234.4773 | Total Energy Gen 197.480 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 197.480 MKWHr
2:00 | 4273 | 849 | 1813 | 2297 | 318 | 184 | 154 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 4275 | 849.5 | 1865 | 2129 | 318 | 184 | 97 | 0 | 139 | [7 empty] | Energy Requirement | 234.4773
3:00 | 4277 | 850 | 1917 | 1961 | 318 | 184 | 40 | 0 | 130
3:30 | 4256.5 | 849.5 | 1958.5 | 1860.5 | 318.5 | 184 | 33 | 0 | 129 | [6 empty] | Shortage
4:00 | 4236 | 849 | 2000 | 1760 | 319 | 184 | 26 | 0 | 128
4:30 | 4241.5 | 849.5 | 2034.5 | 1534.5 | 319 | 184 | 25 | 0 | 122
5:00 | 4247 | 850 | 2069 | 1309 | 319 | 184 | 24 | 0 | 116
5:30 | 4204.5 | 850 | 1979 | 1060.5 | 319 | 183.5 | 12 | 0 | 116
6:00 | 4162 | 850 | 1889 | 812 | 319 | 183 | 0 | 0 | 116
6:30 | 4177 | 836 | 1809.5 | 785 | 320 | 183 | 0 | 0 | 108 |  |  |  |  | Coal
7:00 | 4192 | 822 | 1730 | 758 | 321 | 183 | 0 | 0 | 100
7:30 | 4204 | 821.5 | 1688 | 760 | 320.5 | 183 | 0 | 0 | 101 |  |  |  | Oil |  |  |  | ,
8:00 | 4216 | 821 | 1646 | 762 | 320 | 183 | 0 | 0 | 102
8:30 | 4247 | 823 | 1682.5 | 832 | 320.5 | 183 | 0 | 0 | 110
9:00 | 4278 | 825 | 1719 | 902 | 321 | 183 | 0 | 0 | 118
9:30 | 4281.5 | 825 | 1805.5 | 971.5 | 321 | 183 | 0 | 0 | 126
10:00 | 4285 | 825 | 1892 | 1041 | 321 | 183 | 0 | 0 | 134
10:30 | 4264.5 | 830.5 | 1972 | 1095 | 320.5 | 183 | 5 | 0 | 133
11:00 | 4244 | 836 | 2052 | 1149 | 320 | 183 | 10 | 0 | 132
11:30 | 4249.5 | 838.5 | 2063 | 1247.5 | 319.5 | 183 | 5 | 0 | 136
12:00 | 4255 | 841 | 2074 | 1346 | 319 | 183 | 0 | 0 | 140
12:30 | 4227 | 841.5 | 2083 | 1351.5 | 319 | 183 | 0 | 0 | 139
13:00 | 4199 | 842 | 2092 | 1357 | 319 | 183 | 0 | 0 | 138
13:30 | 4199 | 842 | 2092 | 1357 | 319 | 183 | 0 | 0 | 138
14:00 | 4199 | 842 | 2092 | 1357 | 319 | 183 | 0 | 0 | 138
14:30 | 4290.5 | 842 | 2113 | 1407.5 | 319 | 183 | 4.5 | 0 | 148
15:00 | 4382 | 842 | 2134 | 1458 | 319 | 183 | 9 | 0 | 158
15:30 | 4355 | 846.5 | 2138 | 1473.5 | 319 | 182.5 | 31 | 0 | 154
16:00 | 4328 | 851 | 2142 | 1489 | 319 | 182 | 53 | 0 | 150
16:30 | 4237.5 | 851 | 2111 | 1481.5 | 319.5 | 179.5 | 55.5 | 0 | 145
17:00 | 4147 | 851 | 2080 | 1474 | 320 | 177 | 58 | 0 | 140
17:30 | 4082.5 | 851.5 | 1820.5 | 1499.5 | 319.5 | 177 | 82 | 0 | 132
18:00 | 4018 | 852 | 1561 | 1525 | 319 | 177 | 106 | 0 | 124
18:30 | 4059 | 852 | 1616 | 1803 | 319.5 | 180 | 298 | 0 | 144
19:00 | 4100 | 852 | 1671 | 2081 | 320 | 183 | 490 | 0 | 164
19:30 | 4181 | 852 | 2067 | 2754 | 318 | 183 | 605 | 0 | 172
20:00 | 4243 | 846 | 2088 | 2915 | 319 | 178 | 640 | 0 | 174
20:30 | 4322 | 845.5 | 2199 | 2863 | 319.5 | 181 | 587.5 | 0 | 173
21:00 | 4401 | 845 | 2310 | 2811 | 320 | 184 | 535 | 0 | 172
21:30 | 4402.5 | 845 | 2317 | 2789 | 320 | 183.5 | 514 | 0 | 170
22:00 | 4404 | 845 | 2324 | 2767 | 320 | 183 | 493 | 0 | 168
22:30 | 4400 | 852.5 | 2326.5 | 2736 | 320 | 183 | 488.5 | 0 | 168
23:00 | 4396 | 860 | 2329 | 2705 | 320 | 183 | 484 | 0 | 168
23:30 | 4402 | 859.5 | 2331.5 | 2609.5 | 320 | 183 | 454 | 0 | 167 | Max Temp. in Dhaka |  | 32.2° C
24:00 | 4408 | 859 | 2334 | 2514 | 320 | 183 | 424 | 0 | 166
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 197.480 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 197.480 MKWHr
Note on W13: Author:

## Generation
2019-07-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 93 | 94 | 94 | 94 | 94 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 87 | 87 |  | 93 | 93 | 88 | 94 | 93 | 93 | 93 | 2074756
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2160000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2200000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | 25 | 25 | 25 | [12 empty] | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 255924
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 2 | 4.1 | 1.2 | 6.8 | 13.3 | 17.8 | 4 | 5 |  | 2 | 0 | [8 empty] | 74385
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 204 | 204 | 205 | 204 | 205 | 205 | 204 | 231 | 204 | 207 | 204 | 203 | 204 | 207 | 203 | 205 | 205 |  | 228 | 204 | 205 | 206 | 205 | 206 | 206 | 4888468
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 0 | [17 empty] | 44 | 82 | 85 | 42 | 34 | 34 | 17 | 305106
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [15 empty] | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 159744
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [19 empty] | 8 | 8 | 8 | 0 | 0 |  |  | 15312
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 9 | 9 | 9 | 9 | 11 | 231510
18 | Kodda 300 MW PP Unit-2 (Summit) | 0 | [7 empty] | 3 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 |  | 60 | 64 | 45 | 0 | 0 |  |  | 326181
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 66 | 68 | 73 | 73 | 73 | 1672727
20 | Ghorasal TPP (Unit-1&2) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 820000
21 | Ghorasal Repowered CCPP Unit-3 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 234 | 260 | 249 | 249 | 219 | 219 | 5536400
22 | Ghorasal Repowered CCPP Unit-4 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 219 | 209 | 220 | 220 | 223 | 220 | 220 |  | 220 | 220 | 221 | 220 | 220 | 218 | 220 | 5291000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3301924
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 37 | 33 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 799560
33 | Ashuganj 225 MW CCPP | 182 | 188 | 194 | 182 | 182 | 182 | 186 | 195 | 191 | 184 | 183 | 182 | 183 | 203 | 195 | 183 | 161 | 161 |  | 182 | 182 | 182 | 186 | 182 | 188 | 192 | 4489000
34 | Ashuganj 450 MW CCPP(South) | 305 | 305 | 320 | 305 | 305 | 305 | 315 | 320 | 315 | 305 | 305 | 305 | 305 | 320 | 320 | 310 | 270 | 265 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7489000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 320 | 310 | 310 | 310 | 310 | 310 | 320 | 320 | 310 | 260 | 260 |  | 335 | 310 | 310 | 310 | 310 | 310 | 315 | 7755700
35 | Ashuganj 55 MW PP (Precision) | 48 | 48 | 47 | 45 | 45 | 45 | 48 | 45 | 49 | 48 | 48 | 47 | 46 | 40 | 46 | 45 | 47 | 46 |  | 47 | 47 | 47 | 48 | 48 | 47 | 49 | 1124160
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 85 | 90 | 90 | 90 | 90 | 88 | 90 | 87 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2226590
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 339 | 344 | 340 | 340 | 338 | 340 | 340 | 357 | 345 | 340 | 340 | 340 | 340 | 362 | 339 | 305 | 305 |  | 294 | 340 | 342 | 342 | 340 | 341 | 341 | 8263680
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 370 | 370 | 370 | 370 | 330 | 330 | 300 | 330 | 330 | 330 | 360 | 360 | 330 | 360 | 360 | 360 | 300 |  | 350 | 350 | 350 | 400 | 400 | 400 | 400 | 8510375
41 | Haripur 360MW CCPP(HPL) | 320 | 300 | 300 | 300 | 300 | 277 | 270 | 250 | 282 | 311 | 312 | 312 | 312 | 282 | 301 | 302 | 302 | 252 |  | 265 | 302 | 300 | 351 | 352 | 354 | 354 | 7286000
42 | RPCL 210MW CCPP | 146 | 145 | 145 | 145 | 146 | 148 | 145 | 145 | 143 | 143 | 144 | 144 | 144 | 141 | 140 | 143 | 142 | 144 |  | 141 | 141 | 147 | 145 | 145 | 145 | 145 | 3392280
43
44 | Fenchugonj CCPP Phase-1 | 52 | 53 | 52 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 52 | 53 | 53 |  | 53 | 53 | 53 | 52 | 53 | 53 | 53 | 1249000
45 | Fenchugonj CCPP Phase-2 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1463077
46 | Shajibazar 330 MW CCPP | 263 | 263 | 260 | 260 | 262 | 264 | 264 | 266 | 262 | 261 | 261 | 262 | 254 | 265 | 263 | 264 | 266 | 266 |  | 266 | 262 | 266 | 264 | 265 | 265 | 264 | 5964000
47 | Shahjibazar GTPP Unit- 8 & 9 | 54 | 52 | 63 | 64 | 64 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 59 | 61 | 63 | 61 |  | 59 | 59 | 57 | 63 | 62 | 63 | 63 | 1282272
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 40 | 40 | 40 | 40 | 50 | 73 | 73 | 50 | 72 | 73 | 40 | 10 |  | 10 | 75 | 75 | 75 | 75 | 75 | 75 | 1481280
49 | Shahjibazar 50MW PP (EPL) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 40 | 41 | 41 | 41 | 40 | 5 | 5 |  | 5 | 38 | 43 | 43 | 43 | 43 | 43 | 902880
50 | Sylhet 150 MW CCPP | 73 | 73 | 75 | 70 | 69 | 69 | 78 | 77 | 70 | 70 | 70 | 110 | 75 | 87 | 105 | 93 | 73 | 73 |  | 88 | 73 | 74 | 115 | 110 | 115 | 116 | 2161770
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 431330
52 | Sylhet 50MW PP (EPL) | 45 | 45 | 45 | 45 | 45 | 13 | 10 | 10 | 10 | 46 | 42 | 43 | 43 | 23 | 42 | 41 | 42 | 11 |  | 42 | 45 | 45 | 45 | 45 | 45 | 45 | 860500
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 227340
54 | Hobiganj 11MW PP Cofidence-E | 11 | 3 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253968
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 17 | 50 | 50 | 53 | 22 | 50 | 50 | 46 | 5 |  | 5 | 50 | 50 | 53 | 53 | 53 | 53 | 913800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 |  | 7 | 7 | 24 | 24 | 24 | 24 | 24 |  | 21 | 21 | 24 | 24 | 24 | 24 | 24 | 505104
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 295 | 300 | 310 | 300 | 310 | 300 | 320 | 310 | 300 | 280 | 280 | 260 | 325 | 300 | 300 | 290 |  | 265 | 280 | 280 | 300 | 300 | 300 | 305 | 7336500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 726873
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508128
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 481572
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524988
63 | Impoprt (Tripura) | 152 | 148 | 130 | 128 | 116 | 116 | 100 | 102 | 118 | 134 | 132 | 140 | 138 | 142 | 158 | 150 | 140 | 124 |  | 164 | 172 | 174 | 172 | 168 | 168 | 166 | 3428160
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 41 | 31 | 14 | 3 | 3 | 2 | 2 | 10 | 4 | 4 | 6 | 12 | 2 |  | 19 | 21 | 26 | 32 | 38 | 39 | 40 | 498240
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 440172
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242820
67 | Jangalia 33MW PP (Summit) | 33 | 30 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 813900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 14 | 14 | 18 | 14 | 0 | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 0 |  | 14 | 20 | 20 | 20 | 20 | 435190
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 32 | 31 | 30 | 27 | 30 | 30 | 30 |  | 22 | 22 | 31 | 31 | 31 | 31 | 31 | 716940
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792100
73 | Ghorashal 108MW PP (Regent) | 71 | 85 | 93 | 94 | 94 | 94 | 91 | 90 | 90 | 94 | 97 | 97 | 97 | 97 | 96 | 96 | 96 | 53 |  | 93 | 93 | 90 | 93 | 91 | 96 | 96 | 2044909
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 15 | 50 | 40 | 24 | 24 | 8 | 0 | 127680
78 | Gazipur 52 MW PP | 42 | 42 | 16 | 16 | 16 | 8 | 8 | 8 | 40 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 838800
79 | Kodda 150MW PP | 132 | 48 | [13 empty] | 32 | 32 | 32 |  | 115 | 149 | 149 | 98 | 98 | 98 | 80 | 957600
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 37 | 40 | 40 |  | 75 | 95 | 95 | 95 | 95 | 95 | 95 | 1225920
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 40 | 43 | 52 | 52 | 52 | 52 | 520890
| Gazipur 100 MW PP | 102 | 102 | 102 | 102 | 102 | 50 | 50 | 50 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2264100
| Kaptai 7 MW Solar PP | [5 empty] | 0.144 | 1.38 | 2.2 | 4.4 | 5.8 | 6.5 | 4.6 | 3.2 | 5.08 | 4.9 | 2.6 | 1.44 | 0.26 | [8 empty] | 39000
| Jodiac Power | [14 empty] | 0 | 6 | 8 | 6 |  | 0 | [6 empty] | 48500
82 | Madanganj 102 PP(Summit) | 15 | 0 | [15 empty] | 0 |  | 23 | 48 | 52 | 48 | 48 | 48 | 15 | 279672
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 10 | 10 | 10 | 10 | 10 |  | 0 | 73121
86 | Meghnaghat CCPP(Summit) | 265 | 275 | 275 | 271 | 270 | 285 | 280 | 285 | 280 | 277 | 283 | 250 | 232 | 285 | 288 | 272 | 255 | 258 |  | 306 | 240 | 237 | 280 | 260 | 280 | 280 | 6589207
87 | Meghnaghat 100 MW(IEL) | [17 empty] | 7 |  | 7 | 22 | 48 | 28 | 24 | 10 | 0 | 134400
88 | Ghorashal 78.5 MW PP(MAX) | [10 empty] | 71 | 73 | 72 | 50 | 50 | 50 | 50 | 50 |  | 50 | 73 | 73 | 73 | 74 | 74 | 74 | 900032
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 258720
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 12 | 50 | 50 | 50 | 20 | 44 | 49 | 49 | 5 |  | 7 | 46 | 50 | 50 | 50 | 50 | 50 | 932544
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 20 | 30 | 43 | 43 | 43 | 43 | 43 | 10 |  | 10 | 16 | 30 | 43 | 43 | 43 | 43 | 889140
94 | Gagnagar 102 MW PP (Digital Power) | 0 | [8 empty] | 2 | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 64 | 102 | 50 | 24 | 24 | 24 | 8 | 509328
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 41 | 50 | 27 | 8 | 6 | 6 | 7 | 36 | 50 | 50 | 45 | 24 | 25 | 33 | 47 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 912480
96 | Chattogram 108 MW PP (ECPV) | 96 | 96 | 96 | 12 | 12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 76 | 96 | 97 | 97 | 97 | 97 | 97 | 1079040
97 | Katpotti 52 MW PP (Sinha) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 20 | 28 | 47 | 47 | 33 | 13 | 420000
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 55 | 8 | 8 | 8 | 8 | 8 | 14 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1323840
99 | Madanganj-55 MW PP(Summit) | 0 | [18 empty] | 15 | 55 | 30 | 0 | 0 |  |  | 93489
100 | Manikganj 55 MW PP (Northern) | 37 | 37 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 788389
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 100 | 130 | 163 | 163 | 100 |  | 100 | 100 | 100 | 163 | 163 | 163 | 163 | 3366196
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0.1 | 0.4 | 1.5 | 2.2 | 0.7 | 1 | 1.4 | 0.6 | 1.2 | 1.7 | 1.4 | 0.2 | 0.1 | [8 empty] | 11550
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 35 | 53 | 53 | 53 | 53 | 53 | 53 | 871560
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 80 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 36 | 113 | 160 | 160 | 130 | 130 | 1120800
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 11 | 103 | 104 | 104 | 104 | 104 |  | 104 | 103 | 102 |  |  |  | 0 | 1035608
114 | Kodda 149 MW PP Unit-1 (Summit) | 139 | 0 | [5 empty] | 0 | 32 | 45 | 45 | 48 | 45 | 30 | 17 | 65 | 63 | 60 |  | 88 | 99 | 149 | 115 | 90 | 90 | 67 | 1264320
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 60 | 30 | 30 | 30 | 30 | 30 | 50 | 100 | 100 | 100 | 100 | 60 | 60 | 60 |  | 60 | 90 | 100 | 100 | 100 | 100 | 100 | 1812480
116 | Chandpur 200MW (Desh energy) | 180 | 180 | 155 | 120 | 58 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 80 | 135 | 180 | 182 | 182 | 183 | 1843200
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 45 | 50 | 50 | 50 | 50 | 50 | 727636
118 | Bibiyana-III 400 MW CCPP | 299 | 297 | 251 | 250 | 250 | 200 | 200 | 201 | 200 | 230 | 230 | 200 | 201 | 200 | 250 | 250 | 250 | 200 |  | 140 | 200 | 200 | 250 | 250 | 254 | 254 | 5541000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 68 | 40 | 40 | 40 | 40 | 68 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 117 | 117 | 117 | 2376000
| Anwara 300 MW PP (United) | 234 | 234 | 234 | 232 | 162 | 107 | 106 | 106 | 120 | 195 | 196 | 195 | 196 | 198 | 198 | 143 | 106 | 106 |  | 163 | 210 | 214 | 214 | 214 | 216 | 215 | 4375854
120 | Eastern Zone Total | 7667 | 7369 | 7022 | 6831 | 6532 | 5977.244 | 5784.78 | 5744.7 | 5978.7 | 6171.7 | 6396.3 | 6602.3 | 6572.6 | 6516.28 | 6904.6 | 6872 | 6622.64 | 6050.36 |  | 6782 | 7558 | 7772 | 7863 | 7805 | 7734 | 7588 | 162820237
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 28 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 49 | 95 | 105 | 115 | 115 | 115 | 115 | 1218240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 28 | 16 | 2 | 0 | [11 empty] | 15 | 36 |  | 29 | 31 | 33 | 35 | 34 | 30 | 29 | 299520
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 27 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 43 | 105 | 105 | 105 | 105 | 105 | 105 | 1330560
130
131
132
133
| Barisal 110 MW PP (Summit ) | 48 | 32 | 16 | 0 | [13 empty] | 16 |  | 40 | 48 | 48 | 32 | 32 | 32 | 32 | 323520
136 | Barisal GT PP Unit-1& 2 | [10 empty] | 10 | 0 |  |  |  | 12 | 0 | 12 |  | 12 | 12 | 0 |  |  |  |  | 42107
137 | Bhola 95 MW PP (Aggreko) | 98 | 95 | 97 | 96 | 96 | 73 | 54 | 53 | 53 | 52 | 60 | 72 | 53 | 52 | 52 | 53 | 53 | 52 |  | 32 | 97 | 97 | 98 | 98 | 96 | 96 | 1780126
| Bhola 225 MW CCPP | 173 | 173 | 173 | 173 | 173 | 173 | 172 | 173 | 173 | 173 | 173 | 172 | 173 | 172 | 173 | 172 | 173 | 172 |  | 173 | 172 | 172 | 173 | 173 | 173 | 173 | 4187000
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 29 | 29 | 28 | 26 | 21 | 19 | 17 | 15 | 16 | 11 | 14 | 15 | 14 | 9 | 9 | 7 |  | 25 | 20 | 20 | 28 | 31 | 31 | 27 | 489464
141 | Noapara 100 MW PP (Bangla Trac) | 30 | 0 | [17 empty] | 7 | 85 | 85 | 100 | 100 | 100 | 40 | 561600
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 441750
143 | Gopalganj 100 MW Peaking PP | 67 | 18 | 0 | [10 empty] | 9 | 9 | 9 | 11 | 26 |  | 47 | 52 | 60 | 52 | 52 | 52 | 52 | 564640
144 | Bheramara GTPP Unit-1,2 & 3 | [19 empty] | 16 | 16 | 32 | 32 | 16 | 0 |  | 90100
145 | Madhumati 100 MW PP | 86 | 86 | 85 | 85 | 85 | 16 | 16 | 16 | 16 | 16 | 21 | 52 | 34 | 34 | 34 | 34 | 34 | 34 |  | 59 | 87 | 86 | 86 | 87 | 87 | 86 | 1285920
146 | Bheramara HVDC | 849 | 849 | 850 | 849 | 850 | 850 | 822 | 821 | 825 | 825 | 836 | 841 | 842 | 841 | 842 | 851 | 851 | 852 |  | 852 | 852 | 846 | 845 | 845 | 860 | 859 | 20148364
147 | Bheramara 360 MW CCPP
148
149
150 | Barapukuria TPP Unit-1 | 69 | 69 | 69 | 70 | 70 | 70 | 71 | 71 | 71 | 71 | 70 | 70 | 70 | 70 | 70 | 70 | 71 | 70 |  | 71 | 69 | 70 | 71 | 71 | 70 | 70 | 1666036
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 249 | 249 | 249 | 249 | 249 | 249 | 250 | 249 | 250 | 250 | 250 | 249 | 249 | 249 | 249 | 249 | 249 | 249 |  | 249 | 249 | 249 | 249 | 249 | 250 | 250 | 6067700
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1365000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 0 | [17 empty] | 42 | 50 | 50 | 50 | 50 | 50 | 25 | 314184
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 176 | 155 | 160 | 158 | 158 | 154 | 162 | 163 | 172 | 204 | 186 | 181 | 182 | 197 | 198 | 188 | 180 | 167 |  | 168 | 173 | 167 | 181 | 184 | 186 | 186 | 4489427
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 176 | 146 | 151 | 149 | 149 | 145 | 153 | 154 | 178 | 183 | 190 | 185 | 185 | 156 | 180 | 191 | 181 | 152 |  | 154 | 159 | 156 | 184 | 188 | 190 | 190 | 4282291
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 163 | 163 | 160 | 166 | 167 | 175 | 164 | 184 | 209 | 204 | 206 | 197 | 183 | 180 | 193 | 184 | 156 |  | 159 | 158 | 159 | 183 | 190 | 192 | 192 | 4542091
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 |  | 0 | 90 | 170 | 230 | 250 | 250 | 250 | 250 | 320 | 320 | 300 | 300 | 270 | 350 | 350 | 350 | 250 |  | 232 | 300 | 300 | 300 | 300 | 300 | 300 | 6003000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [19 empty] | 10 | 10 | 26 | 31 | 31 | 26 | 26 | 126424
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 513360
163 | Bogura 20 MW PP (Energyprima) | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 14 | 15 | 14 | 14 | 12 | 13 | 13 |  | 14 | 14 | 14 | 15 | 15 | 15 | 16 | 311436
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 167328
165 | Amnura 50 MW PP(Sinha) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 157640
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 24 | 24 | 24 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 601453
167 | Katakhali 50 MW Peaking PP | 8 | 0 | [17 empty] | 31 | 45 | 47 | 45 | 45 | 45 | 45 | 260010
168 | Santahar 50 MW Peaking PP | 36 | 36 | 0 | [16 empty] | 38 | 38 | 38 | 38 | 38 | 37 | 37 | 280690
169 | Natore 52 MW PP (Rajlanka) | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 40 | 52 | 52 | 52 | 52 | 52 | 471840
170 | Chapainawabganj 100 MW Peaking PP | 50 | 24 | 24 | 24 | 24 | 0 | [13 empty] | 81 | 95 | 95 | 95 | 95 | 95 | 95 | 661072
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 72 | 73 | 74 | 74 | 55 | 55 |  | 55 | 105 | 112 | 113 | 113 | 113 | 113 | 1766592
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | [18 empty] | 17 | 17 | 17 | 17 | 0 | 17 | 18 | 95000
176 | Rangpur 113 MW PP (Confidence) | [8 empty] | 10 | 20 | 34 | 47 | 48 | 64 | 0 |  | 20 | 47 |  | 33 | 0 | [5 empty] | 333120
177 | Sympa Solar Power 8MW | [5 empty] | 0.1 | 2.2 | 3.6 | 2.9 | 5.1 | 8.3 | 3 | 4.3 | 2.5 | 3.5 | 3.6 | 2.8 | 1.1 |  | 0 | [6 empty] | 42600
178
178