## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:February 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-02-01 |  | 2022-01-01 |  | 2021-02-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 10737 | 2022-02-28 | 10021 | 2022-01-25 | 10603 | 28-02.2021 | 13792 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 20:00
2 | Minimum Generation (MW) | 4663 | 2022-02-05 | 5475 | 2022-01-08 | 5490 | 06/02/21 | - | -
|  |  | 6:00 |  | 6:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 10737 | 2022-02-28 | 10021 | 2022-01-25 | 10603 | 28-02.2021 | 13792 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 19:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 9529 | 2022-02-28 | 8945 | 2022-01-30 | 9477 | 28-02.2021 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 10737 | 2022-02-28 | 10021 | 2022-01-25 | 10603 | 28-02.2021 | 14097 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 19:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 9618.2857 |  | 9483.1935 |  | 9322.5714 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak |  |  | 8138.6774 |  | 8098.1429 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 746 | 2022-02-13 | 768 | 2022-01-31 | 914 | 07/02/2021 | 956 | 27/3/2019
|  |  | 23:00 |  | 200:00 |  | 22:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 136 | 2022-02-26 | 136 | 2022-01-26 | 146 | 27/02/2021 | 194 | 12/06/19
|  |  | 18:30 |  | 18:30 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1150.9855 |  | 1181.174 |  | 1022.6216 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 63.5251 |  | 67.0345 |  | 74.8015
22 | Net Generation of BPDB (MKWH) | 1087.4604 |  | 1114.1395 |  | 947.8201
23 | Net Generation of IPP (MKWH) | 3220.9387 |  | 3576.4276 |  | 3226.3213
24 | Net Generation of REB (MKWH) | 126.4229 |  | 117.4558 |  | 123.6043
24 | Net Generation of Rental Power Plant (MKWH) | 320.0645 |  | 409.5082 |  | 326.6792
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4754.8865 |  | 5217.5311 |  | 4624.4249 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 2892.5467 |  | 2951.4743 |  | 3020.1887 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 131.3412 |  | 221.4774 |  | 280.0725 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1350.3741 |  | 1606.076 |  | 918.8193 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 33.9959 |  | 70.6636 |  | 44.929 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 33.0046 |  | 27.2583 |  | 15.6531 |  | 33 | February-22
31 | Energy Generation by Coal (MKWH) | 377.1491 |  | 407.6161 |  | 419.5638 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 529.8419 |  | 535.5104 |  | 510.4868 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 74.1352 |  | 78.0725 |  | 73.1166 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:February 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 10737 | 2022-02-28 | 19:00
Generation Period
| Dhaka | MW | 3947
| Chattogram | MW | 1096
| Cumilla | MW | 853
| Mymensingh | MW | 893
| Sylhet | MW | 359
a) | Total supply in East zone | MW | 7148
| Khulna | MW | 1173
| Barisal | MW | 260
| Rajshahi | MW | 1074
| Rangpur | MW | 682
b) | Total supply in West zone | MW | 3189
c) | Total supply in both zone ( a+b) | MW | 10337
Ref: | 27.21.0000.603.16.087.20.488 | Date: 20/03/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:February 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 750 | 2022-02-02 | 7:00
| b) Ishurdi end | MW | 416 | 2022-02-04 | 14:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1400 | 2022-02-04 | 14:00 |  |  | 1.7815
| b) Ishurdi end | MW | 342 | 2022-02-11 | 8:00
19 | Daily Maximum Energy Export through EWI/NO-1 | [6 empty] | 0 | Ghorashal
| a) Ghorashal end | MKWH | - | - |  |  |  | 0
| b) Ishurdi end | MKWH | - | - |  |  |  | 0
20 | Daily Maximum Energy Import through EWI/ NO-1 | [6 empty] | 0
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 13.4 |  |  |  |  | #REF! | Imp | Exp
| b) Ishurdi end | MKWH | 46.95 |  |  |  |  | #REF! | #REF! | 0
22 | Total Energy Import through EWI/ NO-1 | [6 empty] | #REF! | #REF! | 0
| a) Ghorashal end | MKWH | - |  |  |  |  | 0
| b) Ishurdi end | MKWH | - |  |  |  |  | 0
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  |  |  | 0 |  |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 | [6 empty] | 0 |  |  |  | 2.955
| a) Ashuganj end | MW | 460 | 2022-02-11 | 8:00 |  |  | 0
| b)Serajganj end | MW | 305 | 2022-02-04 | 14:00 |  |  |  | #REF! | 0
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2022-02-04 | 14:00
| b)Sirajganj end | MW | 470 | 2022-02-11 | 8:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.182 | 2022-02-22 |  |  | 2366 | 4.732
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH |  |  |  |  | 2370 | 4.74
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 40.43
| b)Sirajganj end | MKWH | 21.7
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 21.17
| b)Sirajganj end | MKWH | 41.06 |  |  |  |  | 132.822 | 132822000 | 0.01099 | 1.099
30 | Transmission loss of EWI /NO-2 | % | 0.09 |  |  |  |  | 134.298 | 134298000
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken | [7 empty] | 1.099 | 1476000 | 0.01099 | 1.099
from the calculation of GMD, PGCB, Ishwardi. | [8 empty] | 1.099
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken | [10 empty] | 420
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65 | 0.83636
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74 | 0.81127
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
| 2nd East-West Interconnector Loss: |  |  |  |  | 99387644.47
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578 |  | 96795991.85
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062 |  | 2308363.67
| Difference (-) : | 3516000 |  |  |  | 2239112.76
| Loss : | 1.432%

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai | 132/33 kV transformer T-1 | 2022-02-02 12:15 | 2022-02-02 14:42 | 2:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2022-02-16 18:33 | 2022-02-16 19:18 | 0:45 | T | Due to red-hot maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-02-26 12:15 | 2022-02-26 12:50 | 0:35 | T | Tripped showing O/C relay at 33 kV side | 32 | 18.6667 | Power interruption
|  |  | Total : | 3:47 |  | Unserved Energy: |  | 18.6667
Dhaka (South) Grid Circle :
Bhulta | 400/230 kV transformer T01 | 2022-02-04 17:46 | 2022-02-04 18:54 | 1:08 | T | Due to 400 kV Bus dead | 0 | 0 | No interruption
| 400/230 kV transformer T02 | 2022-02-04 17:46 | 2022-02-04 18:55 | 1:08 | T |  | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-02-05 18:45 | 2022-02-05 19:35 | 1:09 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-02-05 20:00 | 2022-02-05 21:55 | 0:50 | T |  | 0 | 0 | No interruption
| 400/230 kV transformer ATR01 | 2022-02-07 05:30 | 2022-02-07 06:51 | 1:55 | T | Due to over excitation at 230 kV side | 0 | 0 | No interruption
| 400/230 kV transformer ATR02 | 2022-02-07 05:23 | 2022-02-07 13:25 | 1:21 | T |  | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 | 2022-02-07 10:57 | 2022-02-07 11:41 | 8:02 | T | Due to red-hot maintby PBS | 0 | 0 | No interruption
Ghorashal | 132/33 kV transformers T-1 & T2 | 2022-02-16 16:27 | 2022-02-16 16:37 | 0:10 | T | Tripped showing O/C & E/F relay | 55 | 9.1667 | Power interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-02-20 19:04 | 2022-02-20 19:30 | 0:10 | T | Due to red-hot maint at 33 kV side | 5 | 0.83333 | Power interruption
Siddhirganj | 132/33 kV transformer T-2 | 2022-02-25 08:41 | 2022-02-25 12:37 | 0:26 | T | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 16:19 |  | Unserved Energy: |  | 10
Chattogram Grid Circle :
Hathazari | 132/33 kV transformer T1 | 2022-02-05 06:14 | 2022-02-05 07:12 | 0:58 | T | Due to 33 kV feeder fault | 22 | 21.2667 | Power interruption
Bakulia | 132/33 kV transformer T3 | 2022-02-05 15:00 | 2022-02-05 19:00 | 4:00 | E/O | Due to oil lakage at 33 kV side | 10 | 40 | No interruption
Hathazari | 132/33 kV transformer T2 | 2022-02-11 14:46 | 2022-02-11 18:30 | 3:44 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T3 | 2022-02-13 23:56 | 2022-02-14 00:10 | 0:14 | T | Tripped showing O/C relay | 29 | 6.7667 | Power interruption
Hathazari | 230/132 kV transformer T01 | 2022-02-18 14:44 | 2022-02-18 18:02 | 3:18 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Halishahar | 132/33 kV transformers T1 & T2 | 2022-02-19 19:18 | 2022-02-19 19:41 | 0:23 | T | Tripped showing O/C relay 33 kV side | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-02-20 09:12 | 2022-02-20 09:56 | 0:44 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T3 | 2022-02-25 10:02 | 2022-02-25 10:40 | 0:38 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 13:59 |  | Unserved Energy: |  | 68.0333
Cumilla Grid Circle :
Ashuganj | 400/230 kV transformer ICT01 | 2022-02-04 17:05 | 2022-02-04 21:10 | 4:05 | T | Due to elecrical fault | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T4 | 2022-02-09 17:50 | 2022-02-09 18:05 | 0:15 | T | Tripped showing internal fault | 13 | 3.25 | Power interruption
Ashuganj(N) | 400/230 kV transformer T01 | 2022-02-11 12:25 | 2022-02-12 11:03 | 22:38 | T | Due to voltage fluctuation | 0 | 0 | No interruption
| 400/230 kV transformer T01 | 2022-02-12 18:12 | 2022-02-12 23:50 | 5:38 | T | Tripped showing internal fault | 0 | 0 | No interruption
| 400/230 kV transformer T01 | 2022-02-12 23:58 | 2022-02-12 23:58 | 0:00 | T | Tripped showing over flux. | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T1 | 2022-02-12 22:22 | 2022-02-12 23:19 | 0:57 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Ashuganj(N) | 400/230 kV transformer T01 | 2022-02-14 05:54 | 2022-02-14 10:50 | 4:56 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV transformer T3 | 2022-02-21 03:21 | 2022-02-21 11:05 | 7:44 | T | Tripped showing Diff.relay | 0 | 0 | No interruption
Ashuganj(N) | 400/230 kV transformer T02 | 2022-02-22 16:06 | 2022-02-22 16:45 | 0:39 | E/O | Due to Oil temperature high | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T1 | 2022-02-23 09:17 | 2022-02-23 10:30 | 1:13 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 48:05 |  |  |  | 3.25
Page: 2/2
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: February2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Madaripur | 132/33 kV transformers T1 | 2022-02-04 15:33 | 2022-02-04 15:47 | 0:14 | T | Tripped showing O/V relay | 4 | 0.93333 | Power interruption 15:33 to 15:47
| 132/33 kV transformers T2 | 2022-02-04 15:33 | 2022-02-04 15:48 | 0:15 | T | Due to trail of sadar feeder fault of WZPDCO
| 132/33 kV transformers T3 | 2022-02-04 15:33 | 2022-02-04 15:49 | 0:16 | T
Rajbari | 132/33 kV transformer T1 | 2022-02-04 15:39 | 2022-02-04 16:02 | 0:23 | E/O | Due to over voltage over fluxing | 0 | 0 | No interruption
Barisal | 132/33 kV transformer T2 | 2022-02-10 06:33 | 2022-02-10 08:02 | 1:29 | E/O | Due to red-hot maint | 48 | 71.2 | Power interruption
Satkhira | 132/33 kV transformersT1 & T2 | 2022-02-14 01:10 | 2022-02-14 01:42 | 0:32 | T | Tripped showing O/C & E/F relay | 43 | 22.9333 | Power interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-02-19 08:27 | 2022-02-19 09:38 | 1:11 | E/O | Due to REB feeder fault | 8 | 9.4667 | Power interruption
Madaripur | 132/33 kV transformers T1 T2 & T3 | 2022-02-27 18:05 | 2022-02-27 18:15 | 0:10 | T | Due to bad weather | 20 | 3.3333 | Power interruption
|  |  | Total : | 4:30 |  | Unserved Energy: |  | 106.9333
HVDC Grid Circle :
Bottail | 132/33 kV transformer T1 | 2022-02-04 19:32 | 2022-02-04 20:20 | 0:48 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-04 20:53 | 2022-02-04 21:28 | 0:35 | E/O | Due to red-hot maint at 33 kV side | 16 | 9.3333 | Power interruption 22:51 to23:16
| 132/33 kV transformers T1 | 2022-02-04 21:58 | 2022-02-04 22:44 | 0:46 | T | Tripped showing Over voltage | 0 | 0 | No interruption
| 132/33 kV transformers T2 | 2022-02-04 21:58 | 2022-02-04 22:40 | 0:42 | T |  | 0 | 0 | No interruption
HVDC | Auxiliary transformer T2 | 2022-02-07 00:21 | 2022-02-07 00:21 | 0:00 | T |  | 0 | 0 | No interruption
|  |  | Total : | 2:51 |  |  |  | 9.3333
Bogura Grid Circle:
Rajshahi | 132/33 kV transformers T2 | 2022-02-04 21:15 | 2022-02-04 23:53 | 2:38 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-02-04 21:15 | 2022-02-05 00:50 | 3:35 | T |  | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T3 | 2022-02-05 08:45 | 2022-02-05 10:40 | 1:55 | E/O | Due to gas filling | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T1 | 2022-02-09 00:20 | 2022-02-11 14:22 | 62:02 | E/O | Due to bursting of CT | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T4 | 2022-02-21 08:07 | 2022-02-21 09:58 | 1:51 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 72:01 |  |  |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 161:32 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kaliakoir 132 kV Ckt-1 | 2022-02-04 16:08 | 2022-02-04 16:53 | 0:45 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Uttara 3rd | Uttara 3rd-Matro Rail 132 kV U/G line | 2022-02-07 13:17 | 2022-02-07 13:32 | 0:15 | T |  | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV Ckt-1 | 2022-02-17 08:49 | 2022-02-17 09:04 | 0:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Tongi (N) 132 kV Ckt-2 | 2022-02-18 17:53 | 2022-02-18 18:15 | 0:22 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:37 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Bhulta | Bhulta-Ashuganj 400 kV Ckt-1 | 2022-02-04 17:46 | 2022-02-04 19:43 | 3:24 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
| Bhulta-Ashuganj 400 kV Ckt-2 | 2022-02-04 17:46 | 2022-02-04 19:18 | 2:22 | E/O | Due to 400 kV Bus dead | 0 | 0 | No interruption
| Bhulta-Ashuganj 400 kV Ckt-1 | 2022-02-05 06:49 | 2022-02-05 06:49 | 4:33 | E/O | Due to over fluxing relay | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur (O) 132 kV Ckt-2 | 2022-02-06 23:02 | 2022-02-07 00:35 | 1:33 | E/O | Due to red-hot maint | 60 | 93 | Power interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2022-02-20 11:55 | 2022-02-20 13:20 | 1:25 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur (N) 132 kV Ckt-2 | 2022-02-23 09:46 | 2022-02-23 12:22 | 2:36 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Shyampur(O)-Shyampur (N) 132 kV Ckt-2 | 2022-02-23 09:46 | 2022-02-23 10:08 | 5:49 | T | Tripped showing Dist. Z1 relay | 168 | 977.2 | Power interruption
Ghorashal AIS | Ghorashal AIS-GIS 230 kV Ckt-2 | 2022-02-28 09:39 | 2022-02-28 10:44 | 1:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-2 | 2022-02-28 09:39 | 2022-02-28 15:35 | 5:56 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 28:43 |  | Unserved Energy: |  | 1070.2
Chattogram Grid Circle :
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-02-04 14:57 | 2022-02-04 15:12 | 0:15 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Baraulia | Baraulia-BSRM 132 kV Ckt | 2022-02-05 00:20 | 2022-02-05 00:36 | 0:16 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-02-05 03:09 | 2022-02-05 06:56 | 3:47 | T | Tripped showing Dist.Z1 relay | 15 | 56.75 | Power interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-2 | 2022-02-12 10:35 | 2022-02-12 17:57 | 7:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Hathazari | Hathazari-Baroerhat 132 kV Ckt-1 | 2022-02-25 21:15 | 2022-02-25 21:26 | 0:11 | T | Tripped showing O/C. relay | 398 | 72.9667 | Power interruption 21:15 to 21:26
| Hathazari-Baroerhat 132 kV Ckt-2 | 2022-02-25 21:15 | 2022-02-25 21:36 | 0:21 | T
| Hathazari-Baroerhat 132 kV Ckt-2 | 2022-02-27 22:42 | 2022-02-27 23:03 | 0:21 | T | Tripped showing Dist. relay. | 0 | 0
|  |  | Total : | 12:33 |  | Unserved Energy: |  | 129.7167
Cumilla Grid Circle :
Feni | Feni-Chowmuhani 132 kV Ckt-1 | 2021-02-01 12:26 | 2021-02-01 14:10 | 1:44 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-1 | 2021-02-01 15:24 | 2021-02-01 16:53 | 1:29 | T |  | 0 | 0 | No interruption
BSRM | BSRM-Cumilla(N) 230 kV Ckt-1 | 2021-02-03 11:27 | 2021-02-03 11:54 | 0:27 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV Ckt-1 | 2021-02-08 12:55 | 2021-02-08 15:54 | 2:59 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV Ckt-1 | 2021-02-09 09:55 | 2021-02-09 10:46 | 0:51 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj(N)-Bhulta 400 kV Ckt-1 & 2 | 2021-02-11 02:25 | 2021-02-11 02:46 | 0:21 | T | Due to high voltage | 0 | 0 | No interruption
Tripura | Tripura-Cumilla(S) 132 kV Ckt-1 & 2 | 2021-02-13 06:26 | 2021-02-13 13:04 | 6:38 | T | Tripped showing Dist.86A,86B relay. | 72 | 477.6 | Power interruption
Sylhet | Sylhet-Fenchuganj-Beanibazar 132 kV Ckt | 2022-02-19 21:50 | 2022-02-19 22:02 | 0:12 | T | Tripped showing Dist. relay.
Ashuganj | Ashuganj-Ashuganj(S) 230 kV Ckt-2 | 2022-02-22 18:11 | 2022-02-22 18:11 | 0:00 | E/O | Due to R-phase flashing | 0 | 0
Cumilla (N) | Cumilla (N)-Kachua 132 kV Ckt | 2022-02-25 21:15 | 2022-02-25 21:43 | 0:28 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Cumilla (N)-Cumilla(S) 132 kV Ckt | 2022-02-25 21:15 | 2022-02-25 21:49 | 0:34 | T |  | 0 | 0 | No interruption
|  |  | Total : | 15:43 |  | Unserved Energy: |  | 477.6
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: February2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Rajbari | Rajbari-Bharamara 132 kV Ckt-1 | 2022-02-01 12:26 | 2022-02-01 13:47 | 1:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Satkhira | Satkhira-Khulna(S) 132 kV Ckt-1 | 2022-02-04 01:08 | 2022-02-04 09:42 | 8:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Madaripur 132 kV Ckt-1 | 2022-02-04 22:20 | 2022-02-04 23:35 | 1:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (new) 132 kV Ckt-1 | 2022-02-11 15:07 | 2022-02-11 16:26 | 1:19 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| Faridpur-Gopalganj 132 kV Ckt-1 | 2022-02-12 11:05 | 2022-02-12 12:13 | 1:08 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Barisal | Barisal-Bhandaria 132 kV Ckt | 2022-02-14 07:06 | 2022-02-14 08:05 | 0:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Faridpur | Faridpur -Rajbarai 132 kV both Ckt | 2022-02-24 21:58 | 2022-02-24 22:40 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Khulna GT | Khulna GT-Goalpara 132 kV Ckt | 2022-02-27 17:50 | 2022-02-27 17:50 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
|  |  | Total : | 15:18 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jashore | Jashore-Jhenadah 132 kV Ckt-1 | 2022-02-20 16:29 | 2022-02-20 16:48 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Rajbari 132 kV both Ckt | 2022-02-24 21:58 | 2022-02-24 22:37 | 0:39 | T | Tripped showing Dist. relay | 0 | 0
|  |  | Total : | 0:58 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura | Bogura -Sirajganj 230 kV Ckt-1 & 2 | 2022-02-27 09:27 | 2022-02-27 09:40 | 0:13 | T | Tripped showing Dist. relay | 24 | 5.2 | Power interruption
|  |  | Total : | 0:13 |  | Unserved Energy: |  | 5.2
Others :
Ullon | Ullon-Siddhirganj 132 kV Ckt-1 | 2022-02-14 22:33 | 2022-02-15 00:13 | 1:40 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 1:40 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 74:52 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Cantonment | 132/33 kV transformer T-1 | 2022-02-01 09:04 | 2022-02-01 17:25 | 8:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-02-01 09:38 | 2022-02-01 11:10 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-02-02 10:04 | 2022-02-02 12:25 | 2:21 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-02-02 12:28 | 2022-02-02 14:39 | 2:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-1 | 2022-02-03 09:44 | 2022-02-03 17:02 | 7:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi Milegate | 132/33 kV transformer T-2 | 2022-02-03 10:17 | 2022-02-03 15:35 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2022-02-03 01:32 | 2022-02-03 17:30 | 15:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3(A) | 2022-02-04 10:32 | 2022-02-04 12:32 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-02-05 10:36 | 2022-02-05 15:57 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-02-05 13:59 | 2022-02-05 14:35 | 0:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-1 | 2022-02-06 10:36 | 2022-02-06 10:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 230/132 kV transformer T-02 | 2022-02-07 08:13 | 2022-02-07 16:57 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2022-02-07 09:20 | 2022-02-07 19:22 | 10:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2022-02-07 10:15 | 2022-02-07 17:22 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-02-08 11:48 | 2022-02-08 15:55 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2022-02-08 10:14 | 2022-02-08 17:34 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2022-02-08 10:30 | 2022-02-08 17:33 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2022-02-09 09:23 | 2022-02-09 16:14 | 6:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2022-02-10 09:44 | 2022-02-10 15:57 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | all 33 kV feeder | 2022-02-11 08:55 | 2022-02-11 17:56 | 9:01 | S/O | Due to C/M work | 102 | 919.7 | Power interruption
Jamalpur | 132/33 kV transformers T-1 & T4 | 2022-02-11 08:42 | 2022-02-11 11:40 | 2:58 | S/O | Due to C/M work | 20 | 59.3333 | Power interruption
Kaliakoir | 400 kV Bus-1 | 2022-02-12 09:54 | 2022-02-12 16:23 | 6:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh RPCL | 132 kV Bus-1 | 2022-02-12 10:54 | 2022-02-12 17:01 | 6:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | 400 kV Bus-2 | 2022-02-13 08:50 | 2022-02-13 16:05 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2022-02-13 09:56 | 2022-02-13 16:48 | 6:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-5 | 2022-02-13 09:06 | 2022-02-13 10:55 | 1:49 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-02-13 11:15 | 2022-02-13 12:50 | 1:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-02-13 12:57 | 2022-02-13 13:57 | 1:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-1 | 2022-02-14 07:02 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 | 2022-02-14 10:02 | 2022-02-14 12:08 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-2 | 2022-02-14 10:02 | 2022-02-14 14:40 | 4:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-3 | 2022-02-14 09:13 | 2022-02-14 12:16 | 3:03 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-02-14 12:22 | 2022-02-14 14:13 | 1:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-02-14 14:15 | 2022-02-14 15:49 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-02-15 08:55 | 2022-02-15 17:56 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2022-02-15 10:19 | 2022-02-15 17:55 | 7:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-4 | 2022-02-15 10:28 | 2022-02-15 14:04 | 3:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-4 |  | 2022-02-15 14:22 |  | S/O | After.maint work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 |  | 2022-02-15 14:18 |  | S/O |  | 0 | 0 | No interruption
Page: 2/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV transformer T-2 | 2022-02-16 11:33 | 2022-02-16 13:43 | 2:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-2 | 2022-02-16 14:26 | 2022-02-16 16:30 | 2:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer T-2 | 2022-02-17 10:54 | 2022-02-17 17:35 | 6:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV transformer T-4 |  | 2022-02-17 11:36 |  | S/O | After.maint work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-1 | 2022-02-19 10:15 | 2022-02-19 10:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2022-02-20 09:28 | 2022-02-20 19:44 | 10:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-2 | 2022-02-20 09:25 | 2022-02-20 15:56 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2022-02-20 12:57 | 2022-02-20 13:02 | 0:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-02-20 16:52 | 2022-02-20 18:11 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-01 | 2022-02-22 09:34 | 2022-02-22 17:30 | 7:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-3 | 2022-02-23 06:40 | 2022-02-23 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-02-23 08:25 | 2022-02-23 08:25 | 0:00 | S/O | Due to Oil centrifuging work | 0 | 0 | No interruption
Agargaon | 132/33 kV transformer T-1 | 2022-02-23 08:28 | 2022-02-23 12:57 | 4:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-02-23 09:16 | 2022-02-23 14:38 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Camtonment | 132/33 kV transformer T-1 | 2022-02-23 09:46 | 2022-02-23 13:40 | 3:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformers T-1 & T3 | 2022-02-24 06:32 | 2022-02-24 07:33 | 1:01 | S/O | Due to C/M work | 30 | 30.5 | Power interruption
Kallyanpur | 132/33 kV transformers T-1 & T3 | 2022-02-24 09:47 | 2022-02-24 16:32 | 6:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-1 | 2022-02-24 09:06 | 2022-02-24 16:06 | 7:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-1 | 2022-02-24 17:39 | 2022-02-24 17:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-2 | 2022-02-25 08:45 | 2022-02-25 14:55 | 6:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-02-26 08:50 | 2022-02-26 08:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-02 | 2022-02-26 09:25 | 2022-02-26 18:27 | 9:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T-3 | 2022-02-27 08:24 | 2022-02-27 17:01 | 8:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-02-28 07:12 | 2022-02-28 07:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2022-02-28 07:28 | 2022-02-28 17:32 | 10:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhluka | 132/33 kV transformer T-1 with 33 kv Bus | 2022-02-28 07:26 | 2022-02-28 11:33 | 4:07 | S/O | Due to D/W work | 40 | 164.6667 | Power interruption
Mirpur | 132/33 kV transformer T-3 | 2022-02-28 09:08 | 2022-02-28 18:01 | 8:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2022-02-28 09:22 | 2022-02-28 12:03 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2022-02-28 12:15 | 2022-02-28 18:05 | 5:50 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 305:51 |  | Unserved Energy: |  | 1174.2
Dhaka (South) Grid Circle :
Munshiganj | 132/33 kV transformer T-1 | 2022-02-01 09:24 | 2022-02-01 15:40 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Madartek | 132/33 kV transformer T-1 | 2022-02-02 08:55 | 2022-02-02 15:30 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV transformer T-3 | 2022-02-02 09:50 | 2022-02-02 14:11 | 4:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/132 kV transformer T-2 | 2022-02-02 07:32 | 2022-02-02 18:11 | 10:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 | 2022-02-03 09:55 | 2022-02-03 17:26 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(N) | 400/132 kV transformer T-1 | 2022-02-03 10:38 | 2022-02-03 14:39 | 4:01 | S/O | Due to maint. work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer T01 | 2022-02-03 10:50 | 2022-02-03 16:08 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-02-04 09:21 | 2022-02-04 18:24 | 9:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 | 2022-02-04 10:21 | 2022-02-04 17:05 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-02-05 09:10 | 2022-02-05 13:07 | 3:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 3/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Keraniganj | 132/33 kV transformer T-2 | 2022-02-05 11:58 | 2022-02-05 16:31 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | 400/132 kV transformer T-2 |  | 2022-02-05 14:39 |  | S/O | After.maint work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-1 |  | 2022-02-05 16:58 |  | S/O | After.maint work | 0 | 0 | No interruption
Narsingdi | 132 kV Bus & Bus coupler | 2022-02-06 08:24 | 2022-02-06 16:38 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T-2 | 2022-02-06 09:57 | 2022-02-06 16:34 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakyha | 132/33 kV transformer GT-1 | 2022-02-06 10:00 | 2022-02-06 16:50 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132 kV main Bus | 2022-02-07 09:48 | 2022-02-07 15:01 | 5:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | 132 kV Bus-2 | 2022-02-07 09:58 | 2022-02-07 16:24 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 33 kV reserve Bus | 2022-02-08 10:15 | 2022-02-08 17:40 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer ATR-2 | 2022-02-08 10:34 | 2022-02-08 15:18 | 4:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | 132 kV main Bus | 2022-02-09 09:47 | 2022-02-09 17:04 | 7:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Aftabnagar | 132/33 kV transformer T-2 | 2022-02-09 09:32 | 2022-02-09 12:57 | 3:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer ATR-3 | 2022-02-10 09:54 | 2022-02-10 16:28 | 6:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T-1 | 2022-02-11 10:28 | 2022-02-11 12:30 | 2:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghangaht | 230 kV Bus-2 | 2022-02-12 10:22 | 2022-02-12 17:00 | 6:38 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2022-02-13 10:02 | 2022-02-13 16:52 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 132/33 kV transformer T-1 | 2022-02-13 09:50 | 2022-02-13 16:56 | 7:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-1 | 2022-02-13 08:56 | 2022-02-13 13:26 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 |  | 2022-02-14 12:48 |  | S/O | After.maint work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-2 | 2022-02-15 08:25 | 2022-02-15 16:36 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Sitalakyha | 132/33 kV transformer GT-2 | 2022-02-15 09:54 | 2022-02-15 18:32 | 8:38 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghangaht | 230 kV Bus-2 | 2022-02-15 11:28 | 2022-02-15 16:27 | 4:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Gulshan | 132/33 kV transformer T-1 | 2022-02-15 11:50 | 2022-02-15 14:53 | 3:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-02-15 14:58 | 2022-02-15 17:43 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 400/132 kV transformer T-1 | 2022-02-16 10:56 | 2022-02-16 17:04 | 6:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghangaht | 230 kV Bus-2 | 2022-02-16 11:19 | 2022-02-16 11:42 | 0:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(O) | 132/33 kV transformer T-3 | 2022-02-18 09:18 | 2022-02-18 14:50 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T1 | 2022-02-19 08:30 | 2022-02-19 16:24 | 7:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-02-19 08:31 | 2022-02-19 16:15 | 7:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T1 | 2022-02-24 09:25 | 2022-02-24 16:56 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | 132/33 kV transformer T2 | 2022-02-25 08:48 | 2022-02-25 18:30 | 9:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T1 | 2022-02-27 09:44 | 2022-02-27 17:08 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-02-28 09:45 | 2022-02-28 17:53 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 246:51 |  | Unserved Energy: |  | 0
Page: 4/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Hathazari | 132 kV bus-1 | 2022-02-01 06:29 | 2022-02-01 08:08 | 1:39 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV main Bus-2 | 2022-02-04 08:30 | 2022-02-04 11:26 | 2:56 | S/O | Due to A/M work | 20 | 12.3333 | 07:28 to 08:05 Power interruption
Rangamati | 132 kV main Bus-1 | 2022-02-06 09:41 | 2022-02-06 13:40 | 3:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-02-06 13:43 | 2022-02-06 16:22 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV transformer T1 | 2022-02-07 08:30 | 2022-02-07 14:45 | 6:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsharai | 230/132 kV transformer T01 | 2022-02-07 11:32 | 2022-02-07 14:00 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-02-07 12:37 | 2022-02-07 14:00 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | 230/132 kV transformer T01 | 2022-02-06 11:10 | 2022-02-06 18:07 | 6:57 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-02-06 11:11 | 2022-02-06 18:07 | 6:56 | S/O |  | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-02-07 12:42 | 2022-02-07 13:30 | 0:48 | S/O | Due to SCADA maint.work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T1 |  | 2022-02-08 11:59 |  |  | After.maint work | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T1 | 2022-02-09 09:29 | 2022-02-09 16:38 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-10 09:18 | 2022-02-10 18:25 | 9:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T1 | 2022-02-11 08:02 | 2022-02-11 10:53 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | GIS bay-1 & 2 from Sikalbaha(N) | 2022-02-11 09:52 | 2022-02-11 21:44 | 11:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T3 | 2022-02-11 09:52 | 2022-02-11 16:48 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
T.K chemical | 132 kV main Bus | 2022-02-12 09:05 | 2022-02-12 12:12 | 3:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T1 |  | 2022-02-12 10:53 |  |  | After.maint work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T2 | 2022-02-13 09:30 | 2022-02-13 17:29 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV transformer T04 | 2022-02-14 09:51 | 2022-02-14 17:50 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T03 | 2022-02-15 09:20 | 2022-02-15 17:29 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-02-16 09:30 | 2022-02-16 16:58 | 7:28 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-02-17 09:15 | 2022-02-17 09:15 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-B | 2022-02-17 08:23 | 2022-02-17 12:33 | 4:10 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | 132 kV main Bus | 2022-02-19 06:57 | 2022-02-19 10:22 | 3:25 | S/O | Due to D/W work | 119 | 406.5833 | Power interruption
Kulshi | 132/33 kV transformer T1 & 33 kV Bus | 2022-02-19 08:29 | 2022-02-19 14:27 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer T1 | 2022-02-19 08:51 | 2022-02-19 17:31 | 8:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulshi | 132/33 kV transformer T2 | 2022-02-20 14:37 | 2022-02-20 15:54 | 1:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV transformer MT-1 |  | 2022-02-20 14:40 |  | S/O | After.maint work | 0 | 0 | No interruption
Khagrachari | 132/33 kV transformer T2 | 2022-02-20 09:12 | 2022-02-20 17:55 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | 132/33 kV transformer T1 | 2022-02-22 09:43 | 2022-02-22 16:13 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-23 08:17 | 2022-02-23 16:42 | 8:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | 132 kV Bus-1 | 2022-02-23 09:48 | 2022-02-23 19:38 | 9:50 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 165:35 |  | Unserved Energy : |  | 418.9167
Page: 5/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Sreemongal | 132/33 kV transformer T-1 | 2022-02-01 09:04 | 2022-02-01 14:41 | 5:37 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T3 | 2022-02-01 09:27 | 2022-02-01 09:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T-1 | 2022-02-01 08:55 | 2022-02-01 08:55 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformers T-2 & T3 | 2022-02-02 09:45 | 2022-02-02 17:44 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(N) | 400/230 kV transformer ICT-1 | 2022-02-03 18:26 | 2022-02-04 09:16 | 14:50 | S/O | Due to extention work | 0 | 0 | No interruption
| 400/230 kV transformer IBT-1 |  | 2022-02-05 11:38 |  | S/O | After maint.work | 0 | 0 | No interruption
Baroirhat | 132/33 kV transformer T-1 |  | 2022-02-05 14:40 |  | S/O |  | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T-1 |  | 2022-02-05 16:44 |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-02-05 16:48 | 2022-02-05 16:48 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | 230/132 kV transformer T02 | 2022-02-06 08:57 | 2022-02-06 17:20 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-3 | 2022-02-06 09:15 | 2022-02-06 17:10 | 7:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132 kV Bus-1 | 2022-02-09 07:35 | 2022-02-09 17:33 | 9:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla (S) | 132 kV Bus-1 | 2022-02-09 09:37 | 2022-02-09 17:06 | 7:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T-3 | 2022-02-10 09:24 | 2022-02-10 09:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj(N) | 400/230 kV transformer ICT-1 | 2022-02-11 02:23 | 2022-02-13 10:41 | 56:18 | S/O | Due to maint.work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T-1 with 33 kV Bus | 2022-02-11 08:20 | 2022-02-11 09:51 | 1:31 | S/O | Due to C/M work | 8 | 12.1333 | Power interruption
Sylhet | 132/33 kV transformer T-1 & 33 kV Bus | 2022-02-12 07:21 | 2022-02-12 17:52 | 10:31 | S/O | Due to maint.work | 30 | 2.3333 | Power interruption 07:21 to 7:25
Kulauara | 132 kV Bus-2 | 2022-02-12 10:15 | 2022-02-12 13:30 | 3:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | 400/132 kV transformer T-01 |  | 2022-02-12 11:03 |  | S/O | After maint.work | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T-4 |  | 2022-02-13 13:44 |  | S/O |  | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-1 | 2022-02-14 09:44 | 2022-02-14 17:15 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230/132 kV transformer OAT-12 | 2022-02-14 10:16 | 2022-02-14 12:37 | 2:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 | 2022-02-15 10:29 | 2022-02-15 16:30 | 6:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-1 | 2022-02-16 08:12 | 2022-02-16 11:54 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-02-17 07:52 | 2022-02-17 15:39 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV transformer T-3 | 2022-02-17 10:06 | 2022-02-17 11:28 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T-3 |  | 2022-02-19 08:58 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-02-19 09:00 | 2022-02-19 16:24 | 7:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 | 2022-02-19 09:53 | 2022-02-19 17:20 | 7:27 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-02-20 09:39 | 2022-02-20 17:29 | 7:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-1 | 2022-02-22 07:33 | 2022-02-22 07:33 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla (N) | 132/33 kV transformer T-3 | 2022-02-22 09:16 | 2022-02-22 09:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T1 | 2022-02-22 09:21 | 2022-02-22 17:24 | 8:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-1 | 2022-02-22 07:33 | 2022-02-22 17:58 | 10:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformersT1 & T2 | 2022-02-23 07:45 | 2022-02-23 09:19 | 1:34 | S/O | Due to D/W work | 20 | 31.3333 | Power interruption
Ashuganj | 230 kV Bus-2 | 2022-02-23 09:35 | 2022-02-23 17:17 | 7:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T-1 | 2022-02-24 09:42 | 2022-02-24 14:19 | 4:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj | 230/132 kV transformer OAT-12 | 2022-02-24 10:29 | 2022-02-24 11:12 | 0:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T-4 | 2022-02-26 10:17 | 2022-02-26 14:48 | 4:31 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-02-27 10:02 | 2022-02-27 12:56 | 2:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T-2 | 2022-02-28 08:30 | 2022-02-28 12:48 | 4:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-02-28 12:58 | 2022-02-28 16:20 | 3:22 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 233:20 |  | Unserved Energy : |  | 45.8
Khulna Grid Circle :
Madaripur | 132/33 kV transformer T2 | 2022-02-01 09:44 | 2022-02-01 10:49 | 1:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T-2 | 2022-02-02 10:19 | 2022-02-02 11:00 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132 kV full Bus | 2022-02-04 08:26 | 2022-02-04 17:10 | 8:44 | S/O | Due to C/M work | 35 | 102.6667 | Power interruption 08:30 to 11:26
Faridpur | 132/33 kV transformer T-3 | 2022-02-08 09:10 | 2022-02-08 17:08 | 7:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | 132 kV Bus-B | 2022-02-08 11:15 | 2022-02-08 11:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T-1 | 2022-02-09 07:48 | 2022-02-09 07:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(O) | 132/33 kV transformer T2 | 2022-02-09 15:52 | 2022-02-09 17:15 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-02-09 17:22 | 2022-02-09 17:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Patuakhali | 33 kV Bus | 2022-02-12 08:18 | 2022-02-12 11:49 | 3:31 | S/O | Due to C/M work | 40 | 140.6667 | Power interruption
Naril | 132/33 kV transformer T-1 | 2022-02-12 08:32 | 2022-02-12 09:36 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T-1 | 2022-02-14 13:24 | 2022-02-14 19:05 | 5:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-1 | 2022-02-14 12:06 | 2022-02-14 14:42 | 2:36 | S/O | Due to isolator maint.work | 0 | 0 | No interruption
Goalpara | 33 kV Bus | 2022-02-15 07:49 | 2022-02-15 09:33 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Mongla | 132/33 kV transformer T2 | 2022-02-16 11:37 | 2022-02-16 14:07 | 2:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | 230/132 kV transformer T-02 | 2022-02-19 09:46 | 2022-02-19 11:47 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T1 | 2022-02-19 08:12 | 2022-02-19 10:35 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Gollamari | 132/33 kV transformer T2 | 2022-02-22 09:04 | 2022-02-22 15:04 | 6:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV transformer T4 | 2022-02-22 10:24 | 2022-02-22 14:04 | 3:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra | 132 kV Bus-2 | 2022-02-22 09:33 | 2022-02-22 18:21 | 8:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132 kV Bus-B |  | 2022-02-23 11:50 |  |  | After maint.work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T2 | 2022-02-24 07:45 | 2022-02-24 11:15 | 3:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | 400/132 kV transformer T1 | 2022-02-24 21:25 | 2022-02-24 21:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-1 | 2022-02-25 09:39 | 2022-02-25 16:40 | 7:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2022-02-26 09:32 | 2022-02-26 13:52 | 4:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T-1 & 33 kV Bus | 2022-02-27 07:16 | 2022-02-27 08:52 | 1:36 | S/O | Due to C/M work | 10 | 16 | Power interruption
|  |  | Total : | 76:16 |  | Unserved Energy : |  | 259.3333
Page: 7/7 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle
Jhenaidah(N) | 230/132 kV transformer T-02 | 2022-02-03 09:27 | 2022-02-03 18:32 | 9:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T-02 | 2022-02-04 09:53 | 2022-02-04 14:47 | 4:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T1 | 2022-02-06 09:23 | 2022-02-06 09:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC pole-1 | 2022-02-11 07:19 | 2022-02-11 15:26 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| HVDC pole-2 | 2022-02-11 07:26 | 2022-02-11 16:08 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T2 | 2022-02-11 08:58 | 2022-02-11 17:20 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jashore | 132 kV Bus-A & B | 2022-02-12 08:58 | 2022-02-12 15:06 | 6:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T1 | 2022-02-17 08:02 | 2022-02-17 23:23 | 15:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara Block-2 | 2022-02-18 07:28 | 2022-02-18 10:09 | 2:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara Block-2 | 2022-02-18 08:38 | 2022-02-18 10:56 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T1 | 2022-02-19 08:09 | 2022-02-19 11:05 | 2:56 | S/O | Due to C/M work | 40 | 117.3333 | Power interruption
| 132/33 kV transformer T2 | 2022-02-19 08:16 | 2022-02-19 18:10 | 9:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-20 10:10 | 2022-02-20 16:30 | 6:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(N) | 230/132 kV transformer T-02 | 2022-02-22 10:09 | 2022-02-22 18:33 | 8:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus | 2022-02-22 10:32 | 2022-02-22 10:32 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
HVDC | HVDC10CO4C Bus reactor-2 | 2022-02-22 11:27 | 2022-02-22 16:13 | 4:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara GK | 132/33 kV transformer T3 | 2022-02-22 16:40 | 2022-02-22 17:57 | 1:17 | S/O | Due to C/M work | 5 | 6.4167 | Power interruption
Jhenaidah(N) | 230/132 kV transformer T-02 | 2022-02-24 08:50 | 2022-02-24 10:50 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2022-02-24 11:15 | 2022-02-24 17:27 | 6:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2022-02-25 07:51 | 2022-02-25 18:06 | 10:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T-02 | 2022-02-25 07:56 | 2022-02-25 18:10 | 10:14 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 127:56 |  | Unserved Energy : |  | 123.75
Bogura Grid Circle:
Rajshahi(O) | 132 kV main Bus | 2022-02-04 07:30 | 2022-02-04 09:40 | 2:10 | S/O | Due to C/M work | 50 | 108.3333 | Power interruption
Niyamatpur | 132/33 kV transformer T2 | 2022-02-05 12:34 | 2022-02-05 16:56 | 4:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T1 | 2022-02-06 13:08 | 2022-02-06 14:10 | 1:02 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-06 14:35 | 2022-02-06 15:50 | 1:15 | S/O | Due to C/M work by NESCO | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 & 33 kV Bus | 2022-02-10 09:15 | 2022-02-10 14:10 | 4:55 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T1 | 2022-02-12 09:25 | 2022-02-12 13:36 | 4:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-13 09:30 | 2022-02-13 12:12 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 |  | 2022-02-14 12:02 |  |  | After maint.work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T3 | 2022-02-14 17:05 | 2022-02-14 17:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T3 | 2022-02-16 15:00 | 2022-02-16 16:16 | 1:16 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
Mohasthangarh | 132/33 kV transformer T2 with 33 kV Bus | 2022-02-17 09:20 | 2022-02-17 12:29 | 3:09 | S/O | Due to C/M work | 15 | 47.25 | Power interruption
Rajshahi | 132 kV main Bus | 2022-02-18 06:58 | 2022-02-18 11:10 | 4:12 | S/O | Due to C/M work | 60 | 252 | Power interruption
Niyamatpur | 132 kV Bus-2 | 2022-02-18 20:15 | 2022-02-18 20:55 | 0:40 | S/O | Due to C/M work | 20 | 13.3333 | Power interruption
Purbasadipur | 132 kV Bus | 2022-02-19 06:30 | 2022-02-19 08:13 | 1:43 | S/O | Due to C/M work | 130 | 223.1667 | Power interruption
Bogura(O) | 132/33 kV transformer T2 & 33 kV Bus | 2022-02-19 07:55 | 2022-02-19 11:09 | 3:14 | S/O | Due to A/M work | 0 | 0 | No interruption
C.nawabganj | 132/33 kV transformer T1 | 2022-02-20 09:20 | 2022-02-20 15:03 | 5:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T2 | 2022-02-20 11:11 | 2022-02-20 14:25 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-02-24 06:39 | 2022-02-24 08:41 | 2:02 | S/O | Due to C/M work | 10 | 20.3333 | Power interruption
Niyamatpur | 132/33 kV transformer T1 | 2022-02-24 16:05 | 2022-02-24 17:07 | 1:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T5 | 2022-02-25 07:30 | 2022-02-25 09:18 | 1:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T2 | 2022-02-25 07:31 | 2022-02-25 07:31 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-02-28 09:20 | 2022-02-28 10:20 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 49:40 |  | Unserved Energy : |  | 664.4167
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1205:29 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Kishoreganj 230 kV Ckt-2 | 2022-02-01 10:05 | 2022-02-01 17:32 | 7:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-02-01 09:23 | 2022-02-01 16:11 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-2 | 2022-02-01 11:30 | 2022-02-01 16:04 | 4:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Netrakona 132 kV Ckt-1 | 2022-02-01 10:59 | 2022-02-01 18:03 | 7:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-2 | 2022-02-02 09:22 | 2022-02-02 17:03 | 7:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-02-02 09:39 | 2022-02-02 17:53 | 8:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-2 | 2022-02-03 09:22 | 2022-02-03 16:51 | 7:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Mymensingh RPCL 132 kV Ckt-1 | 2022-02-03 10:00 | 2022-02-03 17:26 | 7:26 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Bhaluka 132 kV Ckt-2 | 2022-02-03 10:08 | 2022-02-03 18:59 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Kishoreganj 132 kV Ckt-1 | 2022-02-04 12:40 | 2022-02-04 18:59 | 6:19 | S/O | Due to removing kite | 0 | 0 | No interruption
| Mymensingh -Bhaluka 132 kV Ckt-1 | 2022-02-05 10:22 | 2022-02-05 16:19 | 5:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Jamalpur 132 kV Ckt-1 | 2022-02-05 10:28 | 2022-02-05 18:05 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
| Mymensingh -Kishoreganj 132 kV Ckt-1 | 2022-02-05 10:17 | 2022-02-05 17:48 | 7:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2022-02-06 09:13 | 2022-02-06 17:17 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-1 | 2022-02-06 09:40 | 2022-02-06 17:15 | 7:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-1 | 2022-02-06 09:11 | 2022-02-06 17:01 | 7:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-02-06 10:56 | 2022-02-06 17:24 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-2 | 2022-02-07 08:40 | 2022-02-07 15:40 | 7:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2022-02-07 08:58 | 2022-02-07 17:09 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-1 | 2022-02-07 09:59 | 2022-02-07 16:51 | 6:52 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV Ckt-1 | 2022-02-07 10:18 | 2022-02-07 13:22 | 3:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2022-02-08 09:05 | 2022-02-08 15:35 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-1 | 2022-02-08 10:01 | 2022-02-08 17:26 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-1 | 2022-02-08 10:39 | 2022-02-08 12:22 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sherpur-UMPL 132 kV Ckt-2 | 2022-02-08 12:28 | 2022-02-08 12:59 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2022-02-09 11:19 | 2022-02-09 16:28 | 5:09 | S/O | Due to tree trimming | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-02-09 13:18 | 2022-02-09 15:37 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2022-02-10 08:23 | 2022-02-10 14:48 | 6:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-1 | 2022-02-10 09:51 | 2022-02-10 16:15 | 6:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-02-12 08:21 | 2022-02-12 15:19 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-2 | 2022-02-12 09:34 | 2022-02-12 17:43 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-2 | 2022-02-12 09:41 | 2022-02-12 17:56 | 8:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV CKt-2 | 2022-02-12 09:15 | 2022-02-12 13:40 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-1 | 2022-02-13 08:29 | 2022-02-13 15:15 | 6:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-2 | 2022-02-13 09:25 | 2022-02-13 13:07 | 3:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2022-02-13 09:28 | 2022-02-13 21:00 | 11:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Mymensingh RPCL 132 kV Ckt-1 & 2 | 2022-02-13 10:18 | 2022-02-13 16:34 | 6:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-1 | 2022-02-14 08:18 | 2022-02-14 15:25 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-1 | 2022-02-14 09:38 | 2022-02-14 18:37 | 8:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt-2 | 2022-02-14 10:00 | 2022-02-14 17:45 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2022-02-14 10:38 | 2022-02-14 17:25 | 6:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 2/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-02-15 09:34 | 2022-02-15 16:22 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Agargaon 230 kV Ckt-1 | 2022-02-16 07:41 | 2022-02-16 16:28 | 8:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P 132 kV Ckt | 2022-02-16 09:33 | 2022-02-16 14:54 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV Ckt-2 | 2022-02-16 09:09 | 2022-02-16 14:47 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-1 | 2022-02-17 06:59 | 2022-02-17 06:59 | 0:00 | S/O | Due to replacement work | 0 | 0 | No interruption
| Kabirpur-Manikganj 132 kV Ckt-1 | 2022-02-17 06:55 | 2022-02-17 06:55 | 0:00 | S/O |  | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV Ckt-2 | 2022-02-17 07:36 |  |  | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV Ckt-1 | 2022-02-17 09:46 | 2022-02-17 15:08 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 230 kV Ckt | 2022-02-17 11:24 | 2022-02-17 17:31 | 6:07 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV CKt-2 | 2022-02-19 09:34 | 2022-02-19 20:04 | 10:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Tongi P/P 132 kV Ckt-2 | 2022-02-19 09:25 | 2022-02-19 18:00 | 8:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Tongi P/S 132 kV Ckt | 2022-02-20 09:58 | 2022-02-20 17:10 | 7:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-02-22 07:40 | 2022-02-22 15:55 | 8:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-02-23 06:46 | 2022-02-23 06:46 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Kallyanpur 230 kV Ckt-2 | 2022-02-23 07:43 | 2022-02-23 09:20 | 1:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminabazar 230 kV Ckt-2 | 2022-02-24 07:31 | 2022-02-24 15:20 | 7:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Kodda MW P/S 132 kV Ckt | 2022-02-24 08:42 | 2022-02-24 15:30 | 6:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Tongi P/S 132 kV Ckt | 2022-02-24 09:55 | 2022-02-24 09:55 |  | S/O | Due to A/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Bhaluka 132 kV Ckt-1 | 2022-02-24 10:58 | 2022-02-24 13:33 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Mymensingh -Kishoreganj 132 kV Ckt-1 | 2022-02-24 15:40 | 2022-02-24 16:29 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi P/S-Tongi S/S 132 kV Ckt | 2022-02-25 09:28 | 2022-02-25 09:28 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Aminbazar 230 kV Ckt-1 | 2022-02-26 07:31 | 2022-02-26 15:42 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi S/S | Tongi S/S-Tongi P/S 230 kV Ckt | 2022-02-26 10:02 | 2022-02-26 15:20 | 5:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-02-27 09:24 | 2022-02-27 14:38 | 5:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 132 kV Ckt | 2022-02-27 09:22 | 2022-02-27 17:18 | 7:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-1 | 2022-02-28 07:40 | 2022-02-28 07:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-02-28 08:24 | 2022-02-28 17:39 | 9:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2022-02-28 09:27 | 2022-02-28 20:26 | 10:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 410:15 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Haripur 230 kV Ckt-2 | 2022-02-02 10:53 | 2022-02-02 16:23 | 5:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-lalbagh 132 kV Ckt | 2022-02-03 09:22 | 2022-02-03 19:56 | 10:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsinghdi | Narsinghdi-Bhulta 132 kV Ckt | 2022-02-05 08:48 | 2022-02-05 15:16 | 6:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-lalbagh 132 kV Ckt-1 | 2022-02-05 09:30 | 2022-02-05 15:31 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Ashuganj 400 kV Ckt-1 |  | 2022-02-05 14:52 |  | S/O | After maint.work | 0 | 0 | No interruption
| Bhulta-Ashuganj 400 kV Ckt-2 |  | 2022-02-05 14:39 |  | S/O |  | 0 | 0 | No interruption
Keraniganj | Keraniganj-Kamrangirchar 132 kV Ckt | 2022-02-06 10:00 | 2022-02-06 20:06 | 10:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Keraniganj-Kamrangirchar 132 kV Ckt | 2022-02-07 09:25 | 2022-02-07 17:11 | 7:46 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-2 | 2022-02-09 07:36 | 2022-02-09 14:04 | 6:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Kamrangirchar | Kamrangirchar-lalbagh 132 kV Ckt-1 | 2022-02-09 09:38 | 2022-02-09 17:50 | 8:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Fatulla 132 kV Ckt-1 | 2022-02-11 08:39 | 2022-02-11 16:12 | 7:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Katpotti 132 kV Ckt | 2022-02-12 08:14 | 2022-02-12 16:06 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 | 2022-02-13 08:28 | 2022-02-13 16:27 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-02-13 10:31 | 2022-02-13 17:21 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj 230 kV Ckt-1 | 2022-02-13 11:28 | 2022-02-13 18:05 | 6:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 | 2022-02-14 08:45 | 2022-02-14 15:24 | 6:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV Ckt-1 | 2022-02-14 08:50 | 2022-02-14 15:13 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-02-14 09:54 | 2022-02-14 17:20 | 7:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-2 | 2022-02-15 09:06 | 2022-02-15 15:48 | 6:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-02-15 09:46 | 2022-02-15 17:30 | 7:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-02-16 08:49 | 2022-02-16 16:46 | 7:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV Ckt-2 | 2022-02-16 08:35 | 2022-02-16 16:05 | 7:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Tongi 230 kV Ckt-2 | 2022-02-18 08:39 | 2022-02-19 00:23 | 15:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 132 kV Ckt | 2022-02-18 08:48 | 2022-02-18 19:36 | 10:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 230 kV Ckt-1 | 2022-02-18 09:30 | 2022-02-18 19:10 | 9:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Shyampur | Shyampur-Fatulla 132 kV Ckt-2 | 2022-02-18 08:58 | 2022-02-18 15:35 | 6:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj 230 kV S/S-Siddhirganj P.S 132 kV Ckt-1 | 2022-02-19 08:41 | 2022-02-19 12:50 | 4:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 | 2022-02-19 08:58 | 2022-02-19 12:22 | 3:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Keraniganj-Sreenagar 132 kV Ckt-2 | 2022-02-19 12:36 | 2022-02-19 14:58 | 2:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV Ckt-2 | 2022-02-19 08:16 | 2022-02-19 12:49 | 4:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj EGCB 230 kV Ckt | 2022-02-19 09:02 | 2022-02-19 15:32 | 6:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Purbachal 132 kV Ckt | 2022-02-20 12:51 | 2022-02-20 14:07 | 1:16 | S/O | Due to maint.work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV Ckt-1 | 2022-02-20 13:05 | 2022-02-20 16:17 | 3:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Aurahati | Aurahati-Keraniganj 132 kV Ckt | 2022-02-20 13:57 | 2022-02-20 19:46 | 5:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | Nawabganj-Keraniganj 132 kV Ckt-1 | 2022-02-22 11:18 | 2022-02-22 17:17 | 5:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV Ckt | 2022-02-22 10:49 | 2022-02-22 10:49 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132 kV Ckt | 2022-02-22 09:12 | 2022-02-22 16:27 | 7:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | Nawabganj-Keraniganj 132 kV Ckt-1 | 2022-02-23 10:30 | 2022-02-23 17:45 | 7:15 | S/O | Due to D/W work by DPDC | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV Ckt-1 | 2022-02-24 09:18 | 2022-02-24 15:33 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | Nawabganj-Keraniganj 132 kV Ckt-2 | 2022-02-24 09:56 | 2022-02-24 17:36 | 7:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Kazla 132 kV Ckt-1 | 2022-02-25 11:21 | 2022-02-25 14:31 | 3:10 | S/O | Due to mant. work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV Ckt-1 | 2022-02-26 08:24 | 2022-02-26 15:08 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV Ckt-1 | 2022-02-26 08:24 | 2022-02-26 17:45 | 9:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV Ckt-2 | 2022-02-27 08:20 | 2022-02-27 13:20 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj S/S | Madanganj S/S-Madanganj P/S 132 kV Ckt | 2022-02-27 09:26 | 2022-02-27 09:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Matuail S/S | Matuail -Maniknagar 132 kV Ckt | 2022-02-27 10:48 | 2022-02-27 13:38 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-02-27 12:40 | 2022-02-27 17:44 | 5:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2022-02-27 13:33 | 2022-02-27 17:09 | 3:36 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-02-28 08:22 | 2022-02-28 18:05 | 9:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonaragon | Sonaragon-Daudkandi 132 kV Ckt-1 | 2022-02-28 10:45 | 2022-02-28 11:40 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Sddhirganj | Sddhirganj-Dauthbangla 132 kV Ckt | 2022-02-28 09:08 | 2022-02-28 13:53 | 4:45 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 307:53 |  | Unserved Energy: |  | 0
Page: 4/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Kaptai | Kaptai-Chandraghona 132 kV Ckt-2 | 2022-02-01 08:36 | 2022-02-01 17:10 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Khagrachari 132 kV Ckt-1 | 2022-02-01 08:47 | 2022-02-01 16:11 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV Ckt-1 |  | 2022-02-01 11:19 |  | S/O | After maint.work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-1 | 2022-02-01 08:41 | 2022-02-01 15:31 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV Ckt-1 | 2022-02-01 10:21 | 2022-02-01 15:29 | 5:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2022-02-02 08:20 | 2022-02-02 19:42 | 11:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-1 | 2022-02-02 08:57 | 2022-02-02 16:06 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Khagrachari 132 kV Ckt-2 | 2022-02-02 09:07 | 2022-02-02 16:32 | 7:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV Ckt-2 | 2022-02-02 12:59 | 2022-02-02 13:57 | 0:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-2 | 2022-02-03 08:19 | 2022-02-03 16:03 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-1 | 2022-02-03 08:40 | 2022-02-03 15:24 | 6:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-BSRM 132 kV Ckt | 2022-02-05 00:20 | 2022-02-05 00:20 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV Ckt-2 | 2022-02-05 08:41 | 2022-02-05 13:58 | 5:17 | S/O | Due to A/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-2 | 2022-02-05 09:07 | 2022-02-05 16:29 | 7:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV Ckt | 2022-02-06 08:28 | 2022-02-06 16:36 | 8:08 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madunaghat-Hathazari 132 kV Ckt-1 | 2022-02-06 09:25 | 2022-02-06 18:08 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Rampur-Halishahar 132 kV Ckt-1 | 2022-02-07 09:54 | 2022-02-07 14:47 | 4:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Rampur | Rampur-Agrabad 132 kV Ckt-1 | 2022-02-08 10:06 | 2022-02-08 13:54 | 3:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Baraulia | Baraulia-ASRM 132 kV Ckt | 2022-02-08 09:35 | 2022-02-08 14:34 | 4:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-AKSML 132 kV Ckt | 2022-02-08 09:38 | 2022-02-08 14:33 | 4:55 | S/O | Due to A/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur 132 kV Ckt-2 | 2022-02-08 10:35 | 2022-02-08 18:00 | 7:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV Ckt | 2022-02-08 12:14 | 2022-02-08 13:44 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Abulkhair | Abulkhair steel-Baraulia 132 kV Ckt | 2022-02-09 08:49 | 2022-02-09 16:09 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV Ckt-2 | 2022-02-10 08:30 | 2022-02-10 14:28 | 5:58 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-Madunaghat 132 kV Ckt-1 | 2022-02-10 09:16 | 2022-02-10 09:16 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha(O) | Sikalbaha(O)-Bakulia 132 kV Ckt-2 | 2022-02-11 09:02 | 2022-02-11 21:40 | 12:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Bibiyana 230 kV Ckt-2 | 2022-02-12 08:35 | 2022-02-12 16:05 | 7:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-T.K chemical 132 kV Ckt | 2022-02-12 08:34 | 2022-02-12 12:12 | 3:38 | S/O | Due to A/M work | 0 | 0 | No interruption
T.K chemical | T.K chemical-Sikalbaha 132 kV Ckt | 2022-02-12 08:53 | 2022-02-12 12:11 | 3:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-2 | 2022-02-13 07:47 | 2022-02-13 12:42 | 4:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Abulkhair 132 kV Ckt | 2022-02-13 08:49 | 2022-02-13 13:18 | 4:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-02-14 08:09 | 2022-02-14 12:58 | 4:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Ramganj -Khulshi 132 kV Ckt-1 | 2022-02-14 08:48 | 2022-02-14 14:54 | 6:06 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-02-14 11:49 | 2022-02-14 13:27 | 1:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Materbari -Cox;sbazar 132 kV Ckt-1 | 2022-02-15 06:21 | 2022-02-15 09:31 | 3:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Ramganj -Khulshi 132 kV Ckt-2 | 2022-02-15 08:08 | 2022-02-15 13:40 | 5:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-1 | 2022-02-15 08:46 | 2022-02-15 16:03 | 7:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Hlishahar-Khulshi 132 kV Ckt-3 | 2022-02-16 08:25 | 2022-02-16 17:20 | 8:55 | S/O | Due to A/M work | 0 | 0 | No interruption
| Halishahar-Juldah 132 kV Ckt | 2022-02-17 08:33 | 2022-02-17 13:41 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 | 2022-02-17 08:19 | 2022-02-17 20:29 | 12:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha(N) | Sikalbaha(N)-Bakulia 132 kV Ckt-1 | 2022-02-19 08:47 |  | 7:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 |  | 2022-02-19 16:06 |  | S/O | After maint.work | 0 | 0 | No interruption
Bakulia | Bakulia-Khulshi 132 kV Ckt-1 | 2022-02-22 08:48 | 2022-02-22 15:14 | 6:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Halishahar 132 kV Ckt | 2022-02-24 07:30 | 2022-02-24 13:31 | 6:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Anuwara P/S 230 kV Ckt-1 | 2022-02-25 03:22 | 2022-02-25 15:15 | 11:53 | S/O | Due to maint.work | 0 | 0 | No interruption
| Sikalbaha-Juldah 132 kV Ckt | 2022-02-26 08:41 | 2022-02-26 12:30 | 3:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Juldah | Juldah-Shahmirpur 132 kV Ckt-1 | 2022-02-27 08:17 | 2022-02-27 14:32 | 6:15 | S/O | Due to A/M work | 0 | 0 | No interruption
| Juldah-Shahmirpur 132 kV Ckt-2 | 2022-02-28 07:37 | 2022-02-28 12:45 | 5:08 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 277:40 |  | Unserved Energy: |  | 0
Page: 5/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-1 | 2022-02-01 17:06 | 2022-02-01 17:06 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Fenchuganj P/S 132 kV Ckt-3 | 2022-02-01 09:24 | 2022-02-01 15:43 | 6:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-02-01 09:35 | 2022-02-01 17:03 | 7:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV Ckt-1 | 2021-02-01 07:32 | 2021-02-01 16:53 | 9:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-02-02 07:32 | 2021-02-02 18:11 | 10:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-1 | 2021-02-02 09:09 | 2021-02-02 17:31 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-2 | 2021-02-02 09:57 | 2021-02-02 17:53 | 7:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-1 | 2021-02-03 08:28 | 2021-02-03 16:26 | 7:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Chaddagram 132 kV Ckt-1 |  | 2021-02-04 10:07 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-02-03 08:53 | 2021-02-03 17:19 | 8:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV Ckt-1 | 2021-02-05 09:14 | 2021-02-05 16:48 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-02-06 08:47 | 2021-02-06 17:33 | 8:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-1 | 2021-02-06 08:50 | 2021-02-06 16:13 | 7:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV Ckt-1 | 2021-02-06 09:17 | 2021-02-06 17:21 | 8:04 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-1 | 2021-02-07 08:53 | 2021-02-07 16:38 | 7:45 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-02-07 09:02 | 2021-02-07 17:19 | 8:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur Desh 132 kV Ckt-1 | 2021-02-08 08:23 | 2021-02-08 08:41 | 0:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV Ckt | 2021-02-08 08:23 | 2021-02-08 08:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-02-08 08:40 | 2021-02-08 16:14 | 7:34 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-02-08 08:55 | 2021-02-08 17:31 | 8:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-2 | 2021-02-08 09:01 | 2021-02-08 17:08 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bibiyana-Kaliakoir 400 kV Ckt-2 | 2021-02-08 10:09 | 2021-02-08 12:48 | 2:39 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-02-09 08:29 | 2021-02-09 18:14 | 9:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-2 | 2021-02-09 08:37 | 2021-02-09 17:34 | 8:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-1 | 2021-02-09 09:03 | 2021-02-09 17:25 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 230 kV Ckt-1 | 2021-02-09 15:24 | 2021-02-09 17:36 | 2:12 | S/O | Due to tree trimming | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-2 | 2021-02-10 08:34 | 2021-02-10 16:18 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(Net) | Ashuganj(Net)-Ashuganj(S) 230 kV Ckt-1 | 2021-02-10 08:46 | 2021-02-10 12:22 | 3:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2021-02-10 09:00 | 2021-02-10 16:47 | 7:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj(Net) | Ashuganj(Net)-Ashuganj(S) 230 kV Ckt-2 | 2021-02-12 09:21 | 2021-02-12 18:06 | 8:45 | S/O | Due to protection test | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV Ckt-2 |  | 2021-02-13 10:06 |  |  | After maint.work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-2 | 2021-02-13 08:45 | 2021-02-13 19:04 | 10:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj#5 230 kV Ckt | 2021-02-13 10:40 | 2021-02-13 10:50 | 0:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2021-02-13 10:23 | 2021-02-13 13:47 | 3:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Chowmuhani-Ramganj 132 kV Ckt-2 | 2021-02-13 13:59 | 2021-02-13 15:56 | 1:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur Desh 200 MW P/P 132 kV Ckt-2 | 2021-02-14 08:26 | 2021-02-14 16:18 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-1 | 2021-02-14 08:34 | 2021-02-14 16:54 | 8:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Cumilla(N)-Lakdhanvi-Chowddogram 132 kV Ckt-2 | 2021-02-14 10:11 | 2021-02-14 12:19 | 2:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-02-14 16:19 | 2021-02-14 16:31 | 0:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-02-14 16:21 | 2021-02-14 17:15 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-1 | 2021-02-15 08:25 | 2021-02-15 17:17 | 8:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh-Ramganj 132 kV Ckt-2 | 2021-02-15 09:40 | 2021-02-15 16:20 | 6:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV Ckt-1 | 2021-02-16 08:20 | 2021-02-16 12:28 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2021-02-16 09:27 | 2021-02-16 16:29 | 7:02 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-2 | 2021-02-16 08:31 | 2021-02-16 18:03 | 9:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirsorai | Mirsorai-BSRM 230 kV Ckt-2 |  | 2021-02-16 17:30 |  |  | After maint.work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-1 | 2021-02-17 09:01 | 2021-02-17 18:45 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV Ckt-1 | 2021-02-17 08:47 | 2021-02-17 14:14 | 5:27 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 6/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt | 2021-02-17 11:50 | 2021-02-17 12:46 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-2 | 2021-02-19 08:42 | 2021-02-19 16:06 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-2 | 2021-02-19 08:53 | 2021-02-19 18:42 | 9:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-2 | 2021-02-19 08:59 | 2021-02-19 16:06 | 7:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV Ckt-2 | 2021-02-22 09:10 | 2021-02-22 16:22 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-02-22 09:32 | 2021-02-22 10:13 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2021-02-22 10:19 | 2021-02-22 12:39 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV Ckt-2 | 2021-02-23 09:20 | 2021-02-23 16:24 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-02-23 09:57 | 2021-02-23 11:22 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-02-23 11:23 | 2021-02-23 15:42 | 4:19 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Ashuganj(S) 230 kV Ckt-2 | 2021-02-24 07:24 | 2021-02-24 16:38 | 9:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2021-02-24 07:53 | 2021-02-24 08:28 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulauara 132 kV Ckt-1 | 2021-02-24 16:31 | 2021-02-24 17:11 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana S/S | Bibiyana S/S-Bibiyana P/S 400 kV Ckt-1 | 2021-02-24 16:25 | 2021-02-24 16:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh-Chandpur S/S 132 kV Ckt-1 | 2021-02-26 08:17 | 2021-02-26 08:36 | 0:19 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Midland 150 MW 230 kV Ckt | 2021-02-26 08:30 | 2021-02-26 20:31 | 12:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur Desh 132 kV Ckt-2 | 2021-02-27 08:32 | 2021-02-27 17:15 | 8:43 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-1 | 2021-02-27 08:48 | 2021-02-27 17:56 | 9:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV Ckt-2 | 2021-02-27 08:21 | 2021-02-27 15:31 | 7:10 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-1 | 2021-02-28 08:29 | 2021-02-28 20:20 | 11:51 | S/O | Due to A/M work | 0 | 0 | No interruption
|  |  | Total : | 393:19 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Rajbari | Rajbari-Bharamara 132 kV Ckt-1 | 2022-01-01 07:48 | 2022-01-01 07:48 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Madaripur | Madaripur-Barisal(N) 132 kV Ckt-2 | 2022-02-01 08:17 | 2022-02-01 16:47 | 8:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Madaripur-Barisal(N) 132 kV Ckt-2 | 2022-02-02 08:29 | 2022-02-02 17:03 | 8:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madhumati P.P 132 kV Ckt | 2022-02-02 09:26 | 2022-02-02 16:24 | 6:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Jhenaidah 230 kV Ckt-2 | 2022-02-03 09:08 | 2022-02-03 18:33 | 9:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 Ckt-1 | 2022-02-03 10:51 | 2022-02-03 14:17 | 3:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-1 & 2 | 2022-02-04 08:26 | 2022-02-04 17:08 | 8:42 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Khulna(S) 230 kV Ckt-2 | 2022-02-04 09:43 | 2022-02-04 14:44 | 5:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | Satkhira-Khulna(S) 132 kV Ckt-1 | 2022-02-07 07:45 | 2022-02-07 07:45 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-2 | 2022-02-07 09:23 | 2022-02-07 15:36 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Satkhira 132 kV Ckt-1 | 2022-02-08 07:18 | 2022-02-08 13:53 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Faridpur 132 kV Ckt-2 | 2022-02-08 08:54 | 2022-02-08 14:55 | 6:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-2 | 2022-02-09 09:08 | 2022-02-09 16:11 | 7:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Satkhira 132 kV Ckt-1 | 2022-02-12 09:08 | 2022-02-12 13:07 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-2 | 2022-02-13 08:30 | 2022-02-13 12:53 | 4:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Faridpur-Rajbari 132 kV Ckt-1 | 2022-02-13 12:59 | 2022-02-13 15:10 | 2:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Barisal 132 kV Ckt |  | 2022-02-14 17:04 |  | S/O | After maint.work | 0 | 0 | No interruption
Barishal | Barishal(S)-Patuakhali 132 kV Ckt | 2022-02-16 14:49 | 2022-02-16 14:49 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt- |  | 2022-02-16 15:03 |  |  | After maint.work | 0 | 0 | No interruption
Barisal(S) | Barisal(S)-Patuakhali 132 kV Ckt | 2022-02-17 07:03 | 2022-02-17 19:30 | 12:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Barisal(S)-Patuakhali 132 kV Ckt | 2022-02-18 07:08 | 2022-02-18 19:34 | 12:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Page: 7/7 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: February2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Barisal(S) | Barisal(S)-Patuakhali 132 kV Ckt | 2022-02-19 07:09 | 2022-02-19 07:09 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 kV Ckt-2 | 2022-02-22 09:18 | 2022-02-22 18:23 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Payra P/S | Payra P/S-Payra S/S 400 kV Ckt-3 | 2022-02-24 21:40 | 2022-02-24 21:40 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Patuakhali | Patuakhali-Payra 132 both Ckt |  | 2022-02-24 21:50 |  | S/O | After maint.work | 0 | 0 | No interruption
Payra P/S | Payra P/S-Gopalganj (N) 400 kV Ckt-2 | 2022-02-25 07:12 | 2022-02-25 07:12 | 0:00 | S/O | Due to maint. work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Jhenaidah 230 kV Ckt-1 | 2022-02-26 08:55 | 2022-02-26 14:53 | 5:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Goaplaganj(O) | Goaplaganj(O)-Payra 400 kV Ckt-1 |  | 2022-02-26 15:07 |  |  | new connection
|  |  | Total : | 126:57 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
HVDC | HVDC-Jhenaidah 230 kV Ckt-2 | 2022-02-03 09:20 | 2022-02-03 18:37 | 9:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara | Bheramara-Rajbari 132 kV Ckt-1 | 2022-02-06 08:07 | 2022-02-06 17:10 | 9:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari P.P 132 kV Ckt | 2022-02-12 08:40 | 2022-02-12 19:07 | 10:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | Jashore-Banapole 132 kV Ckt-2 | 2022-02-14 10:01 | 2022-02-14 13:39 | 3:38 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jashore-Noapara 132 kV Ckt-2 | 2022-02-15 09:03 | 2022-02-17 13:45 | 52:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Jashore 132 kV Ckt-1 | 2022-02-22 09:41 | 2022-02-22 17:52 | 8:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-1 | 2022-02-22 09:29 | 2022-02-22 18:30 | 9:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-1 | 2022-02-24 08:39 | 2022-02-24 10:59 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-2 | 2022-02-24 11:02 | 2022-02-24 17:16 | 6:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah-Jashore 132 kV Ckt-1 | 2022-02-24 08:43 | 2022-02-24 11:01 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah-Jashore 132 kV Ckt-2 | 2022-02-24 11:05 | 2022-02-24 17:13 | 6:08 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC-Jhenaidah 230 kV Ckt-1 & 2 | 2022-02-25 08:14 | 2022-02-25 18:02 | 9:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Khulna 230 kV Ckt-1 & 2 | 2022-02-25 08:15 | 2022-02-25 18:03 | 9:48 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 138:55 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-2 |  | 2022-02-06 14:10 |  | S/O | After maint.work | 0 | 0 | No interruption
Bogura | Bogura -Natore 132 kV Ckt-1 | 2022-02-06 08:55 | 2022-02-06 16:15 | 7:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-1 | 2022-02-16 08:25 | 2022-02-16 15:41 | 7:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-1 | 2022-02-19 07:49 | 2022-02-19 13:15 | 5:26 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barapukuria-Saidpur 132 kV Ckt-2 | 2022-02-19 13:19 | 2022-02-19 16:30 | 3:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura-B.Pukuria 230 kV Ckt-1 | 2022-02-20 10:48 | 2022-02-20 10:48 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 23:13 |  | Unserved Energy: |  | 0
Others :
Ullon | Ullon-Dhanmondi 132 kV cable line-1 | 2022-02-22 17:08 | 2022-02-23 00:25 | 7:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ullon-Dhanmondi 132 kV cable line-3 | 2022-02-23 00:05 | 2022-02-23 00:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ullon-Siddirganj 132 kV Ckt-1 | 2022-02-23 08:36 | 2022-02-23 13:36 | 5:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ullon-Siddirganj 132 kV Ckt-1 | 2022-02-24 09:33 | 2022-02-24 12:00 | 2:27 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ullon-Dhanmondi 132 kV cable line-3 | 2022-02-24 16:25 | 2022-02-24 16:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 14:44 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1692:56 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:February 2022
| Area | Previous Month (January' 2022) |  |  |  | Current Month (February '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 7 | 5 | 248 | 260 | 7 | 1 | 135 | 143
2 | Dhaka (South) Grid Circle. | 9 | 4 | 110 | 123 | 15 | 4 | 95 | 114
3 | Chattogram Grid Circle. | 4 | 3 | 91 | 98 | 11 | 3 | 83 | 97
4 | Cumilla Grid Circle. | 21 | 4 | 99 | 124 | 17 | 4 | 110 | 131
5 | Khulna Grid Circle. | 3 | 5 | 106 | 114 | 10 | 6 | 52 | 68
6 | HVDC Grid Circle | 3 | - | 53 | 56 | 4 | 2 | 34 | 40
7 | Bogura Grid Circle. | 10 | 2 | 41 | 53 | 3 | 3 | 28 | 34
8 | Others |  |  | 3 | 3 |  | 1 | 5 | 6
9 | Total | 57 | 23 | 751 | 831 | 67 | 24 | 542 | 633
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:February 2022
| Area | Previous Month (January' 2022) |  |  |  | Current Month (February '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | - | 82.97 | 1112.0833 | 1195.0533 | 18.67 |  | 1174.2 | 1192.87
2 | Dhaka (South) Grid Circle. | - | 50 | 716.27 | 766.27 | 987.2 | 93 |  | 1080.2
3 | Chattogram Grid Circle. | 18.37 | 14.25 | 1367.61 | 1400.23 | 157.75 | 40 | 418.92 | 616.67
4 | Cumilla Grid Circle. | 483.4 |  | 15.47 | 498.87 | 480.85 |  | 45.8 | 526.65
5 | Khulna Grid Circle. | - | 3.33 |  | 3.33 | 27.19 | 80.67 | 259.33 | 367.19
6 | HVDC Grid Circle |  |  | 570.33 | 570.33 |  | 9.33 | 123.75 | 133.08
7 | Bogura Grid Circle. | 110.85 |  | 1301.75 | 1412.6 | 5.2 |  | 664.42 | 669.62
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 612.62 | 150.55 | 5083.5133 | 5846.6833 | 1676.86 | 223 | 2686.42 | 4586.28
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:February 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 1 | 4 | 5 |  | 1 | 4 | 1192.87
2 | Dhaka (South) | 5031.6 | 2 |  | 2 | 2 | - | - | 10
3 | Chattogram | 2042 | 2 | 2 | 4 | 1 | 1 | 2 | 486.95
4 | Khulna | 2434 | 5 | 3 | 8 | 2 |  | 6 | 367.2
5 | HVDC | 5954.3 | 1 | 1 | 2 |  | 1 | 1 | 133.08 |  | 58.03
6 | Bogura | 3145.6 |  | 6 | 6 |  | 1 | 6 | 664.42
7 | Cumilla | 2981 | 1 | 3 | 4 | 1 |  | 3 | 49.05
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 2903.57
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.8%
3 | Chattogram | 99.89%
4 | Khulna | 99.97%
5 | HVDC | 99.99% | [6 empty] | Executive Engineer
6 | Bogura | 99.96% | [6 empty] | Information Management Division
7 | Cumilla | 98.89% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:February 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | - | - | - | - | - | -
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | - | - | 2 | 1070.2
3 | Chattogram | 917 | - | 2 |  | 2 | 1 |  | 1 | 129.72
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 |  | 1 | 1 |  |  | 5.2
7 | Cumilla | 1648.16 | - | 1 |  | 1 |  |  | 1 | 477.6
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 1682.72
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.86%
3 | Chattogram | 99.9%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 99.93% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:February 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-02-01 | 13 | - | - | - | 1 | 01hr'33 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:February 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tongi | 1 | 0:35 | 32 | 18.6667 | Due to tripping of 132/33 kV transformer T-1
Sherpur | 1 | 9:01 | 102 | 919.7 | Due to S/D of all 33 kV feeder
Jamalpur | 1 | 2:58 | 20 | 59.3333 | Due to S/D of 132/33 kV Transformers T1 & T4
Kabirpur | 1 | 1:01 | 30 | 30.5 | Due to S/D of 132/33 kV Transformer T1 & T3
Bhluka | 1 | 4:07 | 40 | 164.6667 | Due to S/D of 132/33 kV Transformer T1 with 33 kV bus
Ghorashal | 2 | 0:10 | 55 | 9.1667 | Due to tripping of 132/33 kV transformers T-1 & T2
Sreenagar |  | 0:10 | 5 | 0.83333 | Due to red-hot maint of 33 kV side
Shyampur(N) | 1 | 1:33 | 60 | 93 | Due to red-hot maint of Shyampur(N)-Shyampur(O) 132 kV Ckt-2
Shyampur(O) | 2 | 5:49 | 168 | 977.2 | Due to tripping of Shyampur(O)-Shyampur(N) 132 kV Ckt-2
Hathazari |  | 0:58 | 22 | 21.2667 | Due to tripping of 132/33 kV transformer T-1
Bakulia | 2 | 4:00 | 10 | 40 | Due to Oil leakage of 132/33 kV transformer T3
|  | 0:14 | 29 | 6.7667 | Due to tripping of 132/33 kV transformer T-1
Dohazari | 1 | 3:47 | 15 | 56.75 | Due to tripping of Dohazari-Cox'sbazar 132 kV Ckt-1
Hathazari | 2 | 0:11 | 398 | 72.9667 | Due to tripping of Hathazari-Baroerhat 132 kV Ckt-1
|  | 2:56 | 20 | 12.3333 | Due to S/D of 132 kV main Bus-2
Dohazari | 1 | 3:25 | 119 | 406.5833 | Due to S/D of 132 kV main Bus
Sylhet | 1 | 0:15 | 13 | 3.25 | Due to tripping of 132/33 kV transformer T4
Tripura | 1 | 6:38 | 72 | 477.6 | Due to tripping Tripura-Cumilla(S) 132 kV Ckt-1 & 2
Chandpur | 1 | 1:31 | 8 | 12.1333 | Due to tripping of 132/33 kV transformer T1
Sylhet | 1 | 0:04 | 30 | 2.3333 | Due to S/D of 132/33 kV Transformer T1
Sunamganj | 1 | 1:34 | 20 | 31.3333 | Due to S/D of 132/33 kV Transformers T1 & T2
Madaripur | 1 | 0:14 | 4 | 0.93333 | Due to tripping of 132/33 kV transformers T1 & 2
Barisal | 1 | 1:29 | 48 | 71.2 | Due to red-hot maint 132/33 kV Transformer T2
Satkhira | 1 | 0:32 | 43 | 22.9333 | Due to tripping of 132/33 kV transformers T1 & 2
Mongla | 1 | 1:11 | 8 | 9.4667 | Due to tripping of 132/33 kV transformers T1 & T2
Madaripur | 1 | 0:10 | 20 | 3.3333 | Due to tripping of 132/33 kV transformers T1,T2 & T3
Patuakhali | 1 | 3:00 | 35 | 102.6667 | Due to S/D of 132 kV full Bus
| 1 | 3:31 | 40 | 140.6667 | Due to S/D of 33 kV Bus
Gopalganj(O) | 1 | 1:36 | 10 | 16 | Due to S/D of 132/33 kV TransformerT1
Bottail | 1 | 0:35 | 16 | 9.3333 | Due to red-hot maint of 132/33 kV Transformer T2
Ishurdi | 1 | 2:56 | 40 | 117.3333 | Due to S/D of 132/33 kV Transformer T2
Bheramara GK | 1 | 1:17 | 5 | 6.4167 | Due to S/D of 132/33 kV Transformer T3
Bogura | 1 | 0:13 | 24 | 5.2 | Due to tripping of Bogura -Sirajganj 230 kV Ckt-1 & 2
Rajshahi(O) | 1 | 2:10 | 50 | 108.3333 | Due to S/D of 132 kV Bus
Mohasthangarh | 1 | 3:09 | 15 | 47.25 | Due to S/D of 132/33 kV TransformerT2
Rajshahi | 1 | 4:12 | 60 | 252 | Due to S/D of 132 kV Bus
Niyamatpur |  | 0:40 | 20 | 13.3333 | Due to S/D of 132 kV Bus-2
Purbasadipur | 1 | 1:43 | 130 | 223.1667 | Due to S/D of 132 kV Bus
Rajshahi | 1 | 2:02 | 10 | 20.3333 | Due to S/D of 132/33 kV Transformer T1
| Total Unserved energy : |  |  | 4586.2833 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: February '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Aftabnagar | 19 | 12 | 2022-02-02 | 13:00
2 | Agargaon | 54 | 16 | 2022-02-02 | 13:00
3 | Agrabad | 56 | 15 | 2022-02-02 | 19:00
4 | AKS | 0 | 11 | 2022-02-02 | 23:00
5 | AKSML | 27 | 14 | 2022-02-02 | 09:00
6 | Amnura | 43 | 18 | 2022-02-02 | 20:00
7 | Ashugonj | 30 | 17 | 2022-02-02 | 23:00
8 | Bagerhat | 83 | 16 | 2022-02-02 | 18:30
9 | Bakulia | 95 | 15 | 2022-02-02 | 18:30
10 | Banani | 36 | 14 | 2022-02-02 | 14:00
11 | Bangabhaban | 7 | 15 | 2022-02-02 | 12:00
12 | Barapukuria | 53 | 16 | 2022-02-02 | 09:00
13 | Sreenagar | 12 | 11 | 2022-02-02 | 21:00
14 | Barishal | 30 | 11 | 2022-02-02 | 20:00
15 | Baroaulia | 93 | 19 | 2022-02-02 | 09:00
16 | Baroirhat | 44 | 13 | 2022-02-02 | 18:30
17 | Bashundhara | 98 | 17 | 2022-02-02 | 18:30
18 | BashundharaCement | 45 | 16 | 2022-02-02 | 10:00
19 | Benapole | 52 | 17 | 2022-02-02 | 09:00
20 | Bhandaria | 42 | 16 | 2022-02-02 | 20:00
21 | Bhangura | 28 | 15 | 2022-02-02 | 19:00
22 | Bheramara(GK) | 41 | 15 | 2022-02-02 | 19:00
23 | Bhulta | 220 | 14 | 2022-02-02 | 19:30
24 | Bog-Sherpur | 52 | 12 | 2022-02-02 | 19:00
25 | Bogura | 116 | 14 | 2022-02-02 | 19:00
26 | Borhanuddin | 32 | 13 | 2022-02-02 | 22:00
27 | Cantonment | 86 | 16 | 2022-02-02 | 13:00
28 | Chandpur | 49 | 12 | 2022-02-02 | 20:00
29 | Chandraghona | 22 | 11 | 2022-02-02 | 19:00
30 | Chapai | 56 | 16 | 2022-02-02 | 08:00
31 | Charsaidpur | 42 | 15 | 2022-02-02 | 12:00
32 | Chauddagram | 44 | 18 | 2022-02-02 | 19:30
33 | Chhatak | 19 | 12 | 2022-02-02 | 19:30
34 | Chowmuhani | 134 | 14 | 2022-02-02 | 19:30
35 | Chuadanga | 67 | 14 | 2022-02-02 | 18:30
36 | Coxsbazar | 96 | 15 | 2022-02-02 | 19:00
37 | Cumilla(N) | 74 | 16 | 2022-02-02 | 11:00
38 | Cumilla(S) | 120 | 14 | 2022-02-02 | 18:00
39 | Daudkandi | 100 | 14 | 2022-02-02 | 20:00
40 | Daudkandi | 100 | 14 | 2022-02-02 | 20:00
41 | Dhaka | 20 | 14 | 2022-02-02 | 13:00
42 | Dhamrai | 94 | 14 | 2022-02-02 | 12:00
43 | Dhanmondi | 121 | 16 | 2022-02-02 | 13:00
44 | Dohazari | 82 | 19 | 2022-02-02 | 18:00
45 | Faridpur | 97 | 16 | 2022-02-02 | 19:30
46 | Goalpara | 63 | 19 | 2022-02-02 | 19:30
47 | Gollamari | 31 | 14 | 2022-02-02 | 13:00
48 | Gopalganj | 71 | 17 | 2022-02-02 | 19:00
49 | GPH | 105 | 12 | 2022-02-02 | 22:00
50 | Gulshan | 97 | 19 | 2022-02-02 | 18:00
51 | Halishahar | 62 | 17 | 2022-02-02 | 19:30
52 | Haripur | 109 | 15 | 2022-02-02 | 12:00
53 | Hasnabad | 67 | 15 | 2022-02-02 | 11:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: December '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Hathazari | 67 | 19 | 2022-02-02 | 18:30
56 | Ishurdi | 63 | 11 | 2022-02-02 | 00:00
57 | Jaldhaka | 52 | 14 | 2022-02-02 | 08:00
58 | Jamalpur | 133 | 13 | 2022-02-02 | 08:00
59 | Jashore | 86 | 15 | 2022-02-02 | 19:30
60 | Jhenaidah | 85 | 12 | 2022-02-02 | 19:00
61 | Joydebpur | 148 | 14 | 2022-02-02 | 12:00
62 | Joypurhat | 53 | 14 | 2022-02-02 | 08:00
63 | Juldah | 27 | 15 | 2022-02-02 | 15:00
64 | Kabirpur | 213 | 16 | 2022-02-02 | 10:00
65 | Kachua | 42 | 16 | 2022-02-02 | 21:00
66 | Kallyanpur | 60 | 15 | 2022-02-02 | 19:30
68 | Kamrangirchar | 60 | 17 | 2022-02-02 | 12:00
69 | Kaptai | 5 | 19 | 2022-02-02 | 19:00
70 | Kazla | 68 | 14 | 2022-02-02 | 12:00
71 | Keranigonj | 52 | 14 | 2022-02-02 | 19:00
72 | Khagrachori | 22 | 11 | 2022-02-02 | 18:30
73 | Khulna | 90 | 15 | 2022-02-02 | 13:00
74 | Khulshi | 158 | 17 | 2022-02-02 | 18:00
75 | Kishoreganj | 110 | 19 | 2022-02-02 | 20:00
76 | Kodda | 223 | 14 | 2022-02-02 | 18:30
77 | KSRM | 68.82 | 13 | 2022-02-02 | 13:00
78 | Kulaura | 42 | 12 | 2022-02-02 | 18:30
79 | Kurigram | 56 | 15 | 2022-02-02 | 19:00
80 | Kushtia | 99 | 12 | 2022-02-02 | 19:00
81 | Lalbag | 77 | 15 | 2022-02-02 | 13:00
82 | Lalmonirhat | 38 | 16 | 2022-02-02 | 18:30
83 | Madanganj | 90 | 19 | 2022-02-02 | 19:00
84 | Madaripur | 68 | 19 | 2022-02-02 | 21:00
85 | Madartek | 51 | 11 | 2022-02-02 | 13:00
86 | Madunaghat | 42 | 11 | 2022-02-02 | 13:00
87 | Magura | 42 | 13 | 2022-02-02 | 19:00
88 | Mahasthangarh | 48 | 19 | 2022-02-02 | 19:00
89 | Manikganj | 66 | 17 | 2022-02-02 | 20:00
90 | Maniknagar | 48 | 12 | 2022-02-02 | 13:00
91 | Matarbari | 27 | 14 | 2022-02-02 | 18:30
92 | Matuail | 136 | 16 | 2022-02-02 | 21:00
93 | Millgate | 38 | 12 | 2022-02-02 | 19:00
94 | Mirpur | 168.9 | 22 | 2022-02-02 | 13:00
96 | Mithapukur | 26 | 14 | 2022-02-02 | 08:00
97 | Mogbazar | 82 | 14 | 2022-02-02 | 15:00
98 | Mongla | 42 | 13 | 2022-02-02 | 12:00
99 | Motijheel | 21 | 16 | 2022-02-02 | 20:00
100 | Munshiganj | 64 | 13 | 2022-02-02 | 21:00
101 | Mymensingh | 192 | 11 | 2022-02-02 | 13:00
101 | Naogaon | 102 | 19 | 2022-02-02 | 13:00
102 | Narail | 38 | 13 | 2022-02-02 | 19:00
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: December '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | Narinda | 68 | 19 | 2022-02-02 | 17:00
104 | Narshingdi | 136 | 17 | 2022-02-02 | 19:00
105 | Nawabganj | 33.1 | 11 | 2022-02-02 | 13:00
106 | Netrakona | 123 | 11 | 2022-02-02 | 13:00
107 | New | 65.2 | 17 | 2022-02-02 | 12:00
108 | Niamatpur | 94 | 18 | 2022-02-02 | 08:00
109 | Noapara | 46 | 14 | 2022-02-02 | 18:30
110 | Pabna | 73 | 14 | 2022-02-02 | 19:00
111 | Palashbari | 102 | 19 | 2022-02-02 | 19:00
112 | Panchagarh | 49 | 17 | 2022-02-02 | 19:00
113 | Patuakhali | 84 | 17 | 2022-02-02 | 21:00
114 | PHP | 9 | 13 | 2022-02-02 | 18:00
115 | Purbachal | 15 | 19 | 2022-02-02 | 13:00
116 | Purbasadipur | 103 | 17 | 2022-02-02 | 13:00
117 | RahimSteel | 21 | 13 | 2022-02-02 | 14:00
118 | Rajbari | 46 | 12 | 2022-02-02 | 19:00
119 | Rajendrapur | 120 | 14 | 2022-02-02 | 05:00
120 | Rajshahi | 89 | 12 | 2022-02-02 | 19:00
121 | Rajshahi | 34 | 11 | 2022-02-02 | 13:00
122 | Ramganj | 56 | 17 | 2022-02-02 | 21:00
123 | Rangamati | 10 | 11 | 2022-02-02 | 18:30
124 | Rangpur | 114 | 15 | 2022-02-02 | 19:30
125 | Ruppur | 3.4 | 13 | 2022-02-02 | 18:00
126 | Saidpur | 99 | 17 | 2022-02-02 | 09:00
127 | Satkhira | 80 | 12 | 2022-02-02 | 19:00
128 | Satmasjid | 70 | 18 | 2022-02-02 | 13:00
129 | Savar | 145 | 16 | 2022-02-02 | 12:00
130 | SevenRings | 23 | 15 | 2022-02-02 | 11:00
131 | Shahjadpur | 84 | 14 | 2022-02-02 | 19:30
132 | Shahjibazar | 85 | 13 | 2022-02-02 | 19:00
133 | Shahmirpur | 40 | 13 | 2022-02-02 | 18:30
134 | Shariatpur | 44 | 13 | 2022-02-02 | 21:00
135 | Sherpur | 126 | 11 | 2022-02-02 | 19:00
136 | Shikalbaha | 25 | 13 | 2022-02-02 | 19:00
137 | Shitalakhya | 94 | 16 | 2022-02-02 | 12:00
139 | Shyampur | 180 | 16 | 2022-02-02 | 12:00
140 | Siddhirganj | 106 | 15 | 2022-02-02 | 12:00
141 | Sirajganj | 87 | 15 | 2022-02-02 | 20:00
142 | Sonargaon | 73 | 17 | 2022-02-02 | 10:00
143 | Sreemongol | 35 | 19 | 2022-02-02 | 19:30
144 | Srinagar | 28.51 | 16 | 2022-02-02 | 20:00
146 | Sunamganj | 33 | 12 | 2022-02-02 | 19:00
147 | Sylhet | 106 | 12 | 2022-02-02 | 18:30
148 | Mitha Pukur | 180 | 14 | 2022-02-02 | 18:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:February 2022
Area | MW | Date | Hour | Remarks
Dhaka | 3955 | 28/02/2022 | 18:30
Chattogram | 1214 | 24/02/2022 | 18:30
Khulna | 1184 | 24/02/2022 | 19:00
Rajshahi | 1074 | 28/02/2022 | 19:00
Cumilla | 863 | 28/02/2022 | 18:30
Mymensingh | 1147.8 | 14/02/2022 | 19:00
Sylhet | 360 | 27/02/2022 | 18:30
Barisal | 1035.2 | 14/02/2022 | 19:00
Rangpur | 744 | 2022-02-02 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: February '2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 445 | 17 | 2022-02-02 | 20:00 | 410 | 13 | 2022-02-02 | 11:00
2 | Bheramara | 400 | 408 | 11 | 2022-02-02 | 13:00 | 394 | 12 | 2022-02-02 | 11:00
3 | Ashuganj(N) | 400 | 430 | 11 | 2022-02-02 | 15:00 | 403 | 14 | 2022-02-02 | 16:00
4 | Payra | 400 | 421 | 12 | 2022-02-02 | 6:00 | 410 | 17 | 2022-02-02 | 1:00
5 | Kaliakoir | 400 | 419 | 11 | 2022-02-02 | 2:00 | 397 | 17 | 2022-02-02 | 12:00
6 | Bhulta | 400 | 434 | 11 | 2022-02-02 | 8:00 | 400 | 14 | 2022-02-02 | 11:00
7 | Gopalganj | 400 | 422 | 11 | 2022-02-02 | 15:00 | 405 | 15 | 2022-02-02 | 13:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2022-02-02 | 20:00 | 227 | 2 | 2022-02-02 | 10:00
2 | Ishurdi | 230 | 247 | 11 | 2022-02-02 | 15:00 | 228 | 19 | 2022-02-02 | 19:00
3 | Ashuganj | 230 | 250 | 11 | 2022-02-02 | 1:00 | 240 | 12 | 2022-02-02 | 12:00
4 | Serajganj | 230 | 246 | 11 | 2022-02-02 | 15:00 | 232 | 18 | 2022-02-02 | 11:00
5 | Baghabari | 230 | 244 | 11 | 2022-02-02 | 1:00 | 230 | 18 | 2022-02-02 | 7:00
6 | Barapukuria | 230 | 238 | 13 | 2022-02-02 | 19:30 | 219 | 17 | 2022-02-02 | 9:00
7 | Bogura | 230 | 240 | 11 | 2022-02-02 | 14:00 | 222 | 18 | 2022-02-02 | 11:00
8 | Rajshahi | 230 | 245 | 11 | 2022-02-02 | 14:00 | 225 | 13 | 2022-02-02 | 8:00
9 | Khulna South | 230 | 248 | 11 | 2022-02-02 | 4:00 | 223 | 19 | 2022-02-02 | 18:30
10 | Rampura | 230 | 244 | 11 | 2022-02-02 | 8:00 | 230 | 12 | 2022-02-02 | 14:00
11 | Haripur | 230 | 246 | 11 | 2022-02-02 | 8:00 | 229 | 12 | 2022-02-02 | 15:00
12 | Hasnabad | 230 | 249 | 11 | 2022-02-02 | 6:00 | 231 | 12 | 2022-02-02 | 12:00
13 | Shyampur | 230 | 245 | 11 | 2022-02-02 | 21:00 | 231 | 12 | 2022-02-02 | 12:00
14 | Aminbazar | 230 | 248 | 11 | 2022-02-02 | 1:00 | 228 | 17 | 2022-02-02 | 2:00
15 | Tongi | 230 | 244 | 11 | 2022-02-02 | 13:00 | 230 | 12 | 2022-02-02 | 15:00
16 | Comilla (N) | 230 | 244 | 11 | 2022-02-02 | 8:00 | 233 | 14 | 2022-02-02 | 16:00
17 | Hathazari | 230 | 244 | 14 | 2022-02-02 | 19:00 | 229 | 15 | 2022-02-02 | 10:00
18 | Megnaghat | 230 | 248 | 11 | 2022-02-02 | 11:00 | 241 | 13 | 2022-02-02 | 15:00
19 | Fenchuganj | 230 | 249 | 15 | 2022-02-02 | 5:00 | 242 | 12 | 2022-02-02 | 16:00
20 | Siddhirganj | 230 | 246 | 15 | 2022-02-02 | 5:00 | 223 | 15 | 2022-02-02 | 17:00 |  | 7345
21 | Maniknagar | 230 | 245 | 11 | 2022-02-02 | 8:00 | 231 | 12 | 2022-02-02 | 12:00
22 | Old Airport | 230 | 247 | 11 | 2022-02-02 | 3:00 | 232 | 12 | 2022-02-02 | 12:00
23 | Barisal | 230 | 250 | 15 | 2022-02-02 | 13:00 | 240 | 19 | 2022-02-02 | 13:00
24 | Bhola 225 MW | 230 | 249 | 11 | 2022-02-02 | 1:00 | 243 | 19 | 2022-02-02 | 20:00
25 | AKSML | 230 | 246 | 14 | 2022-02-02 | 18:30 | 220 | 12 | 2022-02-02 | 3:00
26 | BSRM | 230 | 245 | 13 | 2022-02-02 | 19:00 | 227 | 12 | 2022-02-02 | 3:00
27 | Bibiyana | 230 | 248 | 17 | 2022-02-02 | 7:00 | 240 | 11 | 2022-02-02 | 5:00
28 | Bhulta | 230 | 246 | 11 | 2022-02-02 | 8:00 | 231 | 12 | 2022-02-02 | 12:00
29 | Ashuganj (S) | 230 | 247 | 11 | 2022-02-02 | 2:00 | 236 | 12 | 2022-02-02 | 12:00
30 | Kaliakoir | 230 | 246 | 11 | 2022-02-02 | 8:00 | 231 | 12 | 2022-02-02 | 12:00
31 | GPH | 230 | 245 | 14 | 2022-02-02 | 19:00 | 221 | 12 | 2022-02-02 | 3:00
132 kV Substation
1 | AKS | 132 | 144 | 1 | 2022-02-02 | 1:00 | 133 | 16 | 2022-02-02 | 11:00
2 | Aftabnagar | 132 | 136 | 18 | 2022-02-02 | 06:00 | 123 | 28 | 2022-02-02 | 10:00
3 | Agargaon | 132 | 140 | 28 | 2022-02-02 | 20:00 | 121 | 28 | 2022-02-02 | 15:00
4 | Agrabad | 132 | 143 | 14 | 2022-02-02 | 00:00 | 121 | 28 | 2022-02-02 | 15:00
5 | Agrabad | 132 | 141 | 20 | 2022-02-02 | 18:00 | 121 | 28 | 2022-02-02 | 10:00
6 | Amnura | 132 | 140 | 1 | 2022-02-02 | 22:00 | 122 | 22 | 2022-02-02 | 8:00
7 | Ashugonj | 132 | 144 | 5 | 2022-02-02 | 8:00 | 132 | 28 | 2022-02-02 | 15:00
8 | Bagerhat | 132 | 143 | 4 | 2022-02-02 | 15:00 | 124 | 19 | 2022-02-02 | 18:00
9 | Banani | 132 | 141 | 6 | 2022-02-02 | 8:00 | 121 | 28 | 2022-02-02 | 11:00
10 | Bangabhaban | 132 | 138 | 5 | 2022-02-02 | 2:00 | 125 | 28 | 2022-02-02 | 11:00
11 | Bhangura | 132 | 145 | 4 | 2022-02-02 | 21:00 | 129 | 23 | 2022-02-02 | 10:00
12 | Barapukuria | 132 | 140 | 4 | 2022-02-02 | 15:00 | 122 | 9 | 2022-02-02 | 18:30
13 | Baroaulia | 132 | 144 | 19 | 2022-02-02 | 07:00 | 129 | 12 | 2022-02-02 | 04:00
14 | Barisal(N) | 132 | 148 | 3 | 2022-02-02 | 5:00 | 129 | 24 | 2022-02-02 | 23:00
15 | Barishal(S) | 132 | 146 | 4 | 2022-02-02 | 16:00 | 135 | 26 | 2022-02-02 | 18:30
16 | Baroirhat | 132 | 142 | 1 | 2022-02-02 | 23:00 | 132 | 25 | 2022-02-02 | 11:00
17 | Bashundhara Cement | 132 | 144 | 11 | 2022-02-02 | 09:00 | 116 | 16 | 2022-02-02 | 18:30
18 | Basundhara | 132 | 137 | 4 | 2022-02-02 | 0:00 | 122 | 28 | 2022-02-02 | 12:00
19 | Benapol | 132 | 142 | 5 | 2022-02-02 | 3:00 | 122 | 23 | 2022-02-02 | 12:00
20 | Bhandaria | 132 | 146 | 5 | 2022-02-02 | 7:00 | 126 | 24 | 2022-02-02 | 23:00
21 | Bhasantec | 132 | 139 | 28 | 2022-02-02 | 20:00 | 120 | 28 | 2022-02-02 | 15:00
22 | Bhulta | 132 | 139 | 10 | 2022-02-02 | 21:00 | 125 | 5 | 2022-02-02 | 16:00
23 | Biani Bazar | 132 | 140 | 5 | 2022-02-02 | 3:00 | 133 | 24 | 2022-02-02 | 12:00
24 | Bogra | 132 | 143 | 4 | 2022-02-02 | 21:00 | 130 | 3 | 2022-02-02 | 9:00
25 | Borguna | 132 | 148 | 4 | 2022-02-02 | 15:00 | 137 | 24 | 2022-02-02 | 18:30
26 | Bottail | 132 | 142 | 4 | 2022-02-02 | 15:00 | 126 | 23 | 2022-02-02 | 11:00
27 | Brahminbaria | 132 | 140 | 7 | 2022-02-02 | 5:00 | 126 | 28 | 2022-02-02 | 15:00
28 | C.Nawabganj | 132 | 143 | 14 | 2022-02-02 | 19:30 | 132 | 4 | 2022-02-02 | 13:00
29 | Chaddagram | 132 | 144 | 1 | 2022-02-02 | 19:00 | 132 | 4 | 2022-02-02 | 13:00
30 | Chandpur | 132 | 144 | 7 | 2022-02-02 | 17:00 | 131 | 25 | 2022-02-02 | 22:00
31 | Chandraghona | 132 | 144 | 7 | 2022-02-02 | 20:00 | 124 | 28 | 2022-02-02 | 21:00
32 | Char Saidpur | 132 | 141 | 4 | 2022-02-02 | 20:00 | 127 | 28 | 2022-02-02 | 15:00
33 | Chattak | 132 | 140 | 4 | 2022-02-02 | 23:00 | 132 | 24 | 2022-02-02 | 12:00
34 | Chowmuhani | 132 | 140 | 1 | 2022-02-02 | 10:00 | 125 | 25 | 2022-02-02 | 13:00
35 | Chuadanga | 132 | 142 | 24 | 2022-02-02 | 22:00 | 120 | 23 | 2022-02-02 | 12:00
36 | Cox'sbazar | 132 | 136 | 21 | 2022-02-02 | 5:00 | 117 | 16 | 2022-02-02 | 18:00
37 | Daudkandi | 132 | 142 | 1 | 2022-02-02 | 19:00 | 128 | 28 | 2022-02-02 | 15:00
38 | Dhaka University | 132 | 140 | 11 | 2022-02-02 | 08:00 | 120 | 6 | 2022-02-02 | 18:30
39 | Dhamrai | 132 | 142 | 6 | 2022-02-02 | 11:00 | 123 | 28 | 2022-02-02 | 15:00
40 | Dhanmondi | 132 | 142 | 1 | 2022-02-02 | 19:00 | 125 | 28 | 2022-02-02 | 16:00
41 | Dohazari | 132 | 141 | 5 | 2022-02-02 | 7:00 | 128 | 4 | 2022-02-02 | 16:00
42 | Faridpur | 132 | 143 | 4 | 2022-02-02 | 16:00 | 130 | 1 | 2022-02-02 | 9:00
43 | Fatullah | 132 | 138 | 4 | 2022-02-02 | 19:30 | 123 | 28 | 2022-02-02 | 11:00
44 | Fenchuganj | 132 | 142 | 20 | 2022-02-02 | 6:00 | 135 | 9 | 2022-02-02 | 8:00
45 | Feni | 132 | 142 | 1 | 2022-02-02 | 18:00 | 128 | 25 | 2022-02-02 | 21:00
46 | G.K Project | 132 | 145 | 4 | 2022-02-02 | 21:00 | 130 | 1 | 2022-02-02 | 9:00
47 | Gallamari | 132 | 148 | 4 | 2022-02-02 | 16:00 | 131 | 25 | 2022-02-02 | 11:00
48 | Ghorasal | 132 | 148 | 12 | 2022-02-02 | 00:00 | 124 | 28 | 2022-02-02 | 11:00
49 | Goalpara | 132 | 143 | 4 | 2022-02-02 | 15:00 | 127 | 4 | 2022-02-02 | 10:00
50 | Gulshan | 132 | 135 | 5 | 2022-02-02 | 6:00 | 121 | 28 | 2022-02-02 | 11:00
51 | Halishahar | 132 | 143 | 3 | 2022-02-02 | 19:00 | 129 | 12 | 2022-02-02 | 05:00
52 | Haripur (SBU) | 132 | 140 | 4 | 2022-02-02 | 20:00 | 127 | 28 | 2022-02-02 | 15:00
53 | Hasnabad | 132 | 142 | 4 | 2022-02-02 | 1:00 | 126 | 28 | 2022-02-02 | 16:00
54 | Hathazari | 132 | 144 | 3 | 2022-02-02 | 18:00 | 134 | 4 | 2022-02-02 | 16:00
55 | Ishurdi | 132 | 143 | 4 | 2022-02-02 | 21:00 | 129 | 22 | 2022-02-02 | 8:00
56 | Jessore | 132 | 141 | 4 | 2022-02-02 | 17:00 | 113 | 13 | 2022-02-02 | 14:00
57 | Jhenaidah(New) | 132 | 142 | 4 | 2022-02-02 | 15:00 | 123 | 20 | 2022-02-02 | 12:00
58 | Jhenida | 132 | 140 | 4 | 2022-02-02 | 15:00 | 114 | 19 | 2022-02-02 | 09:00
59 | Joldhaka | 132 | 145 | 11 | 2022-02-02 | 07:00 | 122 | 28 | 2022-02-02 | 16:00
60 | Joydevpur | 132 | 145 | 11 | 2022-02-02 | 07:00 | 122 | 28 | 2022-02-02 | 16:00
61 | Joypurhat | 132 | 144 | 4 | 2022-02-02 | 12:00 | 119 | 22 | 2022-02-02 | 8:00
62 | Julda | 132 | 143 | 14 | 2022-02-02 | 21:00 | 130 | 4 | 2022-02-02 | 16:00
63 | Kabirpur | 132 | 141 | 18 | 2022-02-02 | 19:30 | 122 | 28 | 2022-02-02 | 15:00
64 | Kalyanpur | 132 | 138 | 11 | 2022-02-02 | 08:00 | 127 | 7 | 2022-02-02 | 13:00
65 | Kamrangirchar | 132 | 142 | 11 | 2022-02-02 | 08:00 | 125 | 7 | 2022-02-02 | 12:00
66 | Kaptai | 132 | 146 | 15 | 2022-02-02 | 09:00 | 132 | 8 | 2022-02-02 | 10:00
67 | Kazla | 132 | 137 | 24 | 2022-02-02 | 4:00 | 125 | 2 | 2022-02-02 | 11:00
69 | Keraniganj | 132 | 144 | 4 | 2022-02-02 | 19:00 | 125 | 9 | 2022-02-02 | 13:00
70 | Khagrachhari | 132 | 144 | 5 | 2022-02-02 | 7:00 | 131 | 4 | 2022-02-02 | 17:00
71 | Khulawara | 132 | 142 | 5 | 2022-02-02 | 1:00 | 135 | 9 | 2022-02-02 | 8:00
72 | Khulna Central | 132 | 141 | 4 | 2022-02-02 | 13:00 | 122 | 20 | 2022-02-02 | 18:30
73 | Khulshi | 132 | 142 | 14 | 2022-02-02 | 22:00 | 130 | 4 | 2022-02-02 | 16:00
74 | Kishorganj | 132 | 139 | 5 | 2022-02-02 | 6:00 | 122 | 26 | 2022-02-02 | 18:30
75 | Kochua | 132 | 143 | 7 | 2022-02-02 | 2:00 | 131 | 25 | 2022-02-02 | 21:00
76 | Kodda | 132 | 140 | 21 | 2022-02-02 | 18:00 | 120 | 28 | 2022-02-02 | 16:00
77 | Kurigram | 132 | 140 | 4 | 2022-02-02 | 21:00 | 116 | 3 | 2022-02-02 | 8:00
78 | Lalbag | 132 | 142 | 6 | 2022-02-02 | 13:00 | 124 | 28 | 2022-02-02 | 11:00
79 | Lalmonirhat | 132 | 140 | 4 | 2022-02-02 | 15:00 | 116 | 19 | 2022-02-02 | 10:00
80 | Madanganj | 132 | 142 | 10 | 2022-02-02 | 22:00 | 125 | 28 | 2022-02-02 | 16:00
81 | Madanhat | 132 | 144 | 2 | 2022-02-02 | 20:00 | 131 | 8 | 2022-02-02 | 13:00
82 | Madaripur | 132 | 149 | 4 | 2022-02-02 | 16:00 | 132 | 4 | 2022-02-02 | 18:30
83 | Madartek | 132 | 140 | 6 | 2022-02-02 | 5:00 | 121 | 28 | 2022-02-02 | 11:00
84 | Magbazar | 132 | 137.5 | 6 | 2022-02-02 | 8:00 | 121 | 28 | 2022-02-02 | 11:00
85 | Magura | 132 | 143 | 4 | 2022-02-02 | 15:00 | 121 | 20 | 2022-02-02 | 18:30
86 | Manikganj | 132 | 141 | 4 | 2022-02-02 | 19:30 | 123 | 28 | 2022-02-02 | 15:00
87 | Maniknagar | 132 | 139 | 11 | 2022-02-02 | 08:00 | 0 | 1 | 2022-02-02 | 0:00
88 | Matarbari | 132 | 138 | 4 | 2022-02-02 | 7:00 | 121 | 17 | 2022-02-02 | 18:30
89 | Mirpur | 132 | 137 | 6 | 2022-02-02 | 4:00 | 122 | 28 | 2022-02-02 | 11:00
90 | Mithapukur | 132 | 143 | 5 | 2022-02-02 | 6:00 | 122 | 19 | 2022-02-02 | 10:00
91 | Modern Steel | 132 | 143 | 4 | 2022-02-02 | 12:00 | 132 | 4 | 2022-02-02 | 17:00
92 | Mohastangor | 132 | 143 | 4 | 2022-02-02 | 15:00 | 127 | 22 | 2022-02-02 | 8:00
93 | Mongla | 132 | 142 | 4 | 2022-02-02 | 14:00 | 124 | 4 | 2022-02-02 | 10:00
94 | Motijheel | 132 | 139 | 11 | 2022-02-02 | 08:00 | 120 | 16 | 2022-02-02 | 16:00
95 | Munsiganj | 132 | 142 | 2 | 2022-02-02 | 22:00 | 127 | 28 | 2022-02-02 | 15:00
96 | Mymensing | 132 | 138 | 5 | 2022-02-02 | 6:00 | 116 | 3 | 2022-02-02 | 13:00
98 | Narsinghdi | 132 | 139 | 5 | 2022-02-02 | 7:00 | 123 | 28 | 2022-02-02 | 11:00
99 | Natore | 132 | 143 | 11 | 2022-02-02 | 03:00 | 128 | 22 | 2022-02-02 | 8:00
100 | Nawabganj | 132 | 142 | 11 | 2022-02-02 | 08:00 | 124 | 28 | 2022-02-02 | 11:00
101 | Netrokona | 132 | 136 | 5 | 2022-02-02 | 6:00 | 112 | 2 | 2022-02-02 | 13:00
102 | New Tongi | 132 | 141 | 11 | 2022-02-02 | 04:00 | 126 | 27 | 2022-02-02 | 16:00
103 | Niyamatpur | 132 | 142 | 4 | 2022-02-02 | 15:00 | 115 | 22 | 2022-02-02 | 8:00
104 | Noagaon | 132 | 141 | 4 | 2022-02-02 | 15:00 | 121 | 22 | 2022-02-02 | 8:00
105 | Noapara | 132 | 143 | 4 | 2022-02-02 | 15:00 | 122 | 20 | 2022-02-02 | 18:30
106 | Norail | 132 | 141 | 4 | 2022-02-02 | 15:00 | 121 | 20 | 2022-02-02 | 18:00
107 | Pabna | 132 | 142 | 4 | 2022-02-02 | 15:00 | 128 | 23 | 2022-02-02 | 10:00
108 | Palashbari | 132 | 141 | 4 | 2022-02-02 | 15:00 | 122 | 23 | 2022-02-02 | 8:00
109 | Panchagar | 132 | 139 | 26 | 2022-02-02 | 3:00 | 115 | 3 | 2022-02-02 | 18:30
110 | Patuakhali | 132 | 143 | 14 | 2022-02-02 | 18:00 | 127 | 4 | 2022-02-02 | 18:30
111 | PHP | 132 | 141 | 1 | 2022-02-02 | 5:00 | 131 | 23 | 2022-02-02 | 16:00
112 | Purbachal | 132 | 146 | 4 | 2022-02-02 | 15:00 | 132 | 4 | 2022-02-02 | 18:30
113 | Purbasadipur | 132 | 138 | 24 | 2022-02-02 | 14:00 | 116 | 3 | 2022-02-02 | 9:00
114 | Rahim Steal | 132 | 140 | 4 | 2022-02-02 | 20:00 | 125 | 28 | 2022-02-02 | 16:00
115 | Rajbari | 132 | 144 | 4 | 2022-02-02 | 15:00 | 128 | 1 | 2022-02-02 | 9:00
116 | Rajendrapur | 132 | 141 | 6 | 2022-02-02 | 5:00 | 128 | 14 | 2022-02-02 | 16:00
117 | Rajshahi | 132 | 142 | 4 | 2022-02-02 | 21:00 | 126 | 22 | 2022-02-02 | 7:00
118 | Ramganj | 132 | 143 | 1 | 2022-02-02 | 19:00 | 127 | 4 | 2022-02-02 | 13:00
119 | Rangamati | 132 | 143 | 2 | 2022-02-02 | 20:00 | 131 | 4 | 2022-02-02 | 16:00
120 | Rangpur | 132 | 140 | 4 | 2022-02-02 | 15:00 | 119 | 19 | 2022-02-02 | 10:00
121 | Ruppur paromanobik | 132 | 143 | 4 | 2022-02-02 | 15:00 | 129 | 23 | 2022-02-02 | 10:00
122 | Saidpur | 132 | 138 | 4 | 2022-02-02 | 7:00 | 114 | 19 | 2022-02-02 | 10:00
123 | Sariatpur | 132 | 150 | 4 | 2022-02-02 | 16:00 | 134 | 25 | 2022-02-02 | 12:00
124 | Satmosjid | 132 | 140 | 28 | 2022-02-02 | 22:00 | 120 | 28 | 2022-02-02 | 15:00
125 | Savar | 132 | 139 | 1 | 2022-02-02 | 2:00 | 125 | 28 | 2022-02-02 | 11:00
126 | Serajganj | 132 | 143 | 4 | 2022-02-02 | 21:00 | 127 | 22 | 2022-02-02 | 8:00
127 | Shahjadpur | 132 | 148 | 11 | 2022-02-02 | 02:00 | 132 | 23 | 2022-02-02 | 9:00
128 | Shahjibazar | 132 | 140 | 4 | 2022-02-02 | 23:00 | 130 | 28 | 2022-02-02 | 16:00
129 | Sherpur | 132 | 139 | 1 | 2022-02-02 | 21:00 | 115 | 9 | 2022-02-02 | 7:00
130 | Sherpur(Bogura) | 132 | 144 | 4 | 2022-02-02 | 15:00 | 128 | 22 | 2022-02-02 | 8:00
131 | Shitalakhya | 132 | 145 | 0 | 2022-02-02 | 1:00 | 119 | 12 | 2022-02-02 | 21:00
132 | Siddhirganj | 132 | 140 | 4 | 2022-02-02 | 19:00 | 125 | 28 | 2022-02-02 | 15:00
133 | Sikalbaha | 132 | 149 | 28 | 2022-02-02 | 18:00 | 132 | 23 | 2022-02-02 | 16:00
134 | Sonargaon | 132 | 140 | 21 | 2022-02-02 | 8:00 | 126 | 28 | 2022-02-02 | 11:00
135 | Sreenagar | 132 | 147 | 4 | 2022-02-02 | 23:00 | 125 | 28 | 2022-02-02 | 15:00
136 | Srimongal | 132 | 143 | 22 | 2022-02-02 | 6:00 | 134 | 28 | 2022-02-02 | 15:00
137 | Sunamganj | 132 | 138 | 4 | 2022-02-02 | 17:00 | 131 | 24 | 2022-02-02 | 13:00
138 | Sylhet | 132 | 139 | 22 | 2022-02-02 | 1:00 | 133 | 24 | 2022-02-02 | 13:00
139 | Tangail | 132 | 138 | 4 | 2022-02-02 | 18:00 | 120 | 28 | 2022-02-02 | 14:00
140 | TK Chemical | 132 | 144 | 5 | 2022-02-02 | 6:00 | 128 | 4 | 2022-02-02 | 17:00
141 | Tongi | 132 | 141 | 1 | 2022-02-02 | 23:00 | 125 | 28 | 2022-02-02 | 15:00
142 | Tongi Millgate | 132 | 141 | 6 | 2022-02-02 | 4:00 | 123 | 28 | 2022-02-02 | 16:00
143 | Ullon | 132 | 138 | 6 | 2022-02-02 | 8:00 | 113 | 3 | 2022-02-02 | 18:30
144 | Uttara | 132 | 143 | 4 | 2022-02-02 | 12:00 | 123 | 28 | 2022-02-02 | 11:00
145 | Uttara(New) | 132 | 140 | 7 | 2022-02-02 | 20:00 | 123 | 28 | 2022-02-02 | 15:00
146 | Valuka | 132 | 135 | 7 | 2022-02-02 | 6:00 | 108 | 3 | 2022-02-02 | 13:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:February 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 34 | 75
Hasnabad | TR2 | 225 | 34 | 75 | 25.02.2022 | 24:00
| TR3 | 225 | 34 | 75
| TR1 | 225 | 140 | 365 | 24.02.2022 | 16:00
Tongi | TR2 | 225 | 140 | 365
| TR3 | 225 | 140 | 365
Haripur | TR1 | 225 | 116 | 246
| TR2 | 225 | 116 | 246 | 27.02.2022 | 23:00
| TR3 | 225 | 116 | 246
| TR1 | 225 | 140 | 380
Rampura | TR2 | 225 | 140 | 305 | 28.02.2022 | 15:00
| TR3 | 225 | 140 | 305
Keraniganj | ATR1 | 300 | 93 | 235
| ATR2 | 300 | 93 | 235 | 04.02.2022 | 13:00
| ATR3 | 300 | 93 | 235
| TR1 | 225 | 77 | 193
Aminbazar | TR2 | 225 | 77 | 193 | 07.02.2022 | 12:00
| TR3 | 225 | 83 | 206
Agargaon | TR1 | 300 | 118 | 315
| TR2 | 300 | 118 | 315 | '28/2/2022 | 13:00
Maniknagar | TR1 | 300 | 104 | 300 | 28/02/2022 | 13:00
| TR2 | 300 | 104 | 300
Cumilla (N) | TR1 | 225 | 148 | 380 | '25/2/2022 | 21:00
| TR2 | 225 | 144 | 367
Fenchuganj | AT2 | 300 | 167 | 431 | 23/02/2022 | 19:00
| MT1 | 150 | 70 | 294
Hathazari | MT2 | 150 | 70 | 294 | 24/02/2022 | 17:00
| MT3 | 150 | 70 | 294
| MT4 | 150 | 70 | 294
| TR1 | 225 | 83 | 205
Ishurdi | TR2 | 225 | 83 | 205 | 04/02/2022 | 18:30
| TR3 | 225 | 83 | 205
Khulna(S) | TR1 | 225 | 71 | 193
| TR2 | 225 | 71 | 193 | 10/02/2022 | 8:00
| TR3 | 300 | 89 | 246
Bogura | TR1 | 225 | 91 | 250 | 21.02.22 | 8:00
| TR2 | 225 | 91 | 250
| TR3 | 225 | 124 | 328
Baghabari | TR1 | 300 | 130 | 360 | 20.02.22 | 8:00
| TR2 | 225 | 96 | 270
Rajshahi | ATR-01 | 300 | 84 | 212 | 24.02.2022 | 8:00
| ATR-02 | 300 | 84 | 212
Barapukuria | TR1 | 225 | 174 | 800 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 150 | 720 | 16.02.2022 | 9:00 | 132 kV current is being provided
| TR6 | 300 | 193 | 928
Bheramara | Transformer-1 | 225 | 96 | 229 | 04.02.2022 | 19:00
| Transformer-2 | 225 | 96 | 229
Shyampur | ATR-01 | 300 | 96 | 239 | 07.02.2022 | 10:00
| ATR-02 | 300 | 96 | 239
Kaliakoir | TR1 | 300 | 114.2 | 341 | 28.02.2022 | 12:30
Sikalbaha | ATR-1 | 300 | 143 | 395 | 24.02.2022 | 18:00
| ATR-2 | 300 | 143 | 395
Jhenaidah | T1(230/132 kV) | 300 | 116 | 505 | 14.02.2022 | 19:00
| T2(230/132 kV) | 300 | 116 | 505
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:February 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 208.2 | 301 | 05.02.2022 | 12:15
| TR2(400/230 kV) | 520 | 210.5 | 307.6
| TR1(400/132 kV) | 325 | 248.3 | 397.6 | 28.02.2022 | 18:45
| TR2(400/132 kV) | 325 | 250.2 | 399.7
Bibiyana | ICT1(400/230 kV) | 520 | 75 | 106
| ICT2(400/230kV) | 520 | 73 | 104 | 08.02.2022 | 11:00
Bhulta | ATR1(400/230 kV) | 520 | 272 | 428 | 17.02.2022 | 12:15
| ATR2(400/230kV) | 520 | 272 | 428
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 391 | 536 | 15.02.2022 | 7:32
Gopalganj | ATR1(400/138 kV) | 325 | 270 | 389 | 02.02.2022 | 19:00
| ATR2(400/138kV) | 325 | 270 | 389
Payra | GSUT1 | 270 | 197.56 | 847 | 21/02/2022 | 22:00
| GSUT2 | 270 | 197.56 | 845
| GSUT3 | 270 | 197.56 | 839
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:February2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:February2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-02-01 | 9775 | 9775 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-01 | 8977 | 8977 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-02 | 10011 | 10011 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-02 | 8934 | 8934 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-03 | 9784 | 9784 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-03 | 9086 | 9086 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-04 | 7350 | 7350 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-04 | 6344 | 6344 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-05 | 9073 | 9073 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-05 | 7466 | 7466 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-06 | 9448 | 9448 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-06 | 8023 | 8023 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-07 | 9478 | 9478 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-07 | 8198 | 8198 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-08 | 9671 | 9671 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-08 | 8339 | 8339 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-09 | 9748 | 9748 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-09 | 8610 | 8610 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-10 | 9596 | 9596 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-10 | 8698 | 8698 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-11 | 8555 | 8555 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-11 | 7479 | 7479 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-12 | 9667 | 9667 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-12 | 7982 | 7982 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-13 | 9873 | 9873 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-13 | 8773 | 8773 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-14 | 10004 | 10004 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-14 | 8748 | 8748 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-15 | 9913 | 9913 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-15 | 8913 | 8913 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-16 | 9951 | 9951 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-16 | 8992 | 8992 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-17 | 10099 | 10099 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-17 | 9145 | 9145 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-18 | 8785 | 8785 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-18 | 7737 | 7737 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-19 | 10000 | 10000 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-19 | 8582 | 8582 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-20 | 9542 | 9542 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-20 | 9002 | 9002 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-21 | 8561 | 8561 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-21 | 7730 | 7730 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-22 | 9947 | 9947 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-22 | 8832 | 8832 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-23 | 10262 | 10262 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-23 | 9090 | 9090 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-24 | 10225 | 10225 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-24 | 9254 | 9254 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-25 | 8937 | 8937 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-25 | 7966 | 7966 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-26 | 10381 | 10381 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-26 | 9028 | 9028 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-27 | 9939 | 9939 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-27 | 9422 | 9422 | - | - | - | - | - | - | - | - | - | - | - | -
2022-02-28 | 10737 | 10737 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-02-28 | 9529 | 9529 | - | - | - | - | - | - | - | - | - | - | - | -
Evening Peak | Max. L/S | 0 | - | -
| Min. L/S | 0 | - | -
| No. of Days | - | [12 empty] | 0 | 0 | 1
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:February 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 10737 | 2022-02-28 | 19:00
2 | Maximum Day Peak Genaration | MW | 9529 | 2022-02-28 | 12:00
3 | Maximum Evening Peak Demand | MW | 10737 | 2022-02-28 | 12:00
4 | Minimum Generation | MW | 4663 | 2022-02-05 | 6:00
5 | Average of the daily evening peak Genaration | MW | 9618.2857
6 | Average of the daily day peak Genaration | MW | 8531.3929
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 28 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 5348.2536
12 | Total Generation by BPDB | MkWh | 1150.9855 | % of total Gen. | 21.52%
13 | Total Generation by IPP | MkWh | 1986.8654 | '' | 37.15%
14 | A) Total Generation by Generation Companies | MkWh | 1234.0733 | '' | 23.07%
| B) Total Generation by REB | MkWh | 126.4229 | " | 2.364%
| C) Total Generation by RENTAL | MkWh | 320.0645 | " | 5.984%
| D) Total Imported from India (BIPTC) | MkWh | 471.5229 | " | 8.816%
| E) Total Imported from Tripura, India (A.C) | MkWh | 58.319 | " | 1.09%
15 | Fuel wise Generation.
| A) Gas | MkWh | 2892.5467 | % of total Gen. | 54.08%
| B) Oil | MkWh | 1481.7153 | '' | 27.7%
| C) Hydro | MkWh | 33.9959 | '' | 0.6356%
| D) Solar | MkWh | 33.0046 | '' | 0.6171%
| E) Coal | MkWh | 377.1491 | '' | 7.052%
| F) BIPTC (Import from India) | MkWh | 471.5229 | '' | 8.816%
| G) A.C (Import from Tripura, India) | MkWh | 58.319 | '' | 1.09%
16 | Maximun of the daily total Generation . | MkWh | 212.4134 | 2022-02-28
17 | Monthly Load factor | % | 74.1352
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 18557.4113
| A) Gas | M.Taka | 3061.2938
| B) Liquid fuel | M.Taka | 10875.9154
| C) Coal | M.Taka | 1796.7047
| D) BIPTC (Import from India) | M.Taka | 2404.7668
| E) Tripura(Import from India) | M.Taka | 418.7307
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 675.8059 | 2022-02-21
| A) Gas | M.Taka | 107.6623 | 2022-02-09
| B) Liquid fuel | M.Taka | 517.4849 | 2022-02-23
| C) Coal | M.Taka | 76.8092 | 2022-02-16
| D) BIPTC (Import from India) | M.Taka | 89.8935 | 2022-02-06
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.9478
| B) Excluding Hydro & Solar | Taka/kWhR | 5.0098
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 93.32 | 28/02/2022 | 06:00
b) | Actual | FT (MSL) | 90.53 | 28/02/2022 | 06:00
22 | Peak Genaration of February 2021 | MW | 10603 | 28-02.2021 | 19:00
23 | Peak Demand of February 2021 | MW | 10603 | 28-02.2021 | 19:00
24 | Maximum peak Generation recorded upto 28/02/2022 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 28/02/2022 | MW | 14097 | 27/04/21 | 12:00
26 | Maximum load shed recorded upto 28/02/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.