## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-14 | Sunday
|  | Date (day): | 2023-05-14 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10891.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12563 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-05-13 | 2023-05-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 263 | 220 | 220 | 82 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 213 | 131 | 0 | 0 | 360 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 130 | 85 | 85 | 85 | 325 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 26 | 26 | 26 | 74 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 20 | 17 | 17 | 17 |  | 5 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 19 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | GT-1 Under maint & Gas Shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 37 | 42 | 35 | 40 | 60 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 41 | 92 | 40 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 146 | 100 | 148
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 35 | 20 |  | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 49 | 50 | 50 |  | 30 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 12 | 12 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 49 | 16 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 97 | 277 | 97 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 210 | 306 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 86 | 80 | 70 | 80 | 20 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 75 | 82 | 75 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 34 | 133 | 116 | 116
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 35 | 52 | 54 | 54 | 50 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 135 | 54 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 17 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2139 | 2613 | 1967 | 2494 | 1938 | 1157
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 4 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 40 | 6 | 44 | 6 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 0 | 0 | 0 | 0 | 225 |  | Gas shortage
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 28 | 85 | 17 | 105
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 53 | 55 | 54 | 57 |  | 41 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 84 | 84 | 84 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 9 | 0 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 30 | 0 | 30 | 78 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 87 | 262 | 88 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 105 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 51 | 65 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 163 | 36 | 163 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 501 | 985 | 530 | 1037 | 1055 | 389
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 203 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 310 | 310 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 315 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 28 | 40 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 185 | 189 | 180 | 180 | 15
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 20 | 145 | 20 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 38 | 35 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 68 | 34 | 68 | 132 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 6 | 7 | 7 |  | 4 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 142 | 118 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 7 | 0 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 24 | 96 | 26 | 96 | 17 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 95 | 54 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1461 | 1739 | 1484 | 1781 | 299 | 620
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 47 | 84 | 35 | 90 | 112 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 18 | 18 | 4 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 49 | 87 | 48 | 85 | 115 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 48 | 89 | 48 | 85 | 30 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 225 | 291 | 212.6 | 290 | 116 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 29 | 30 | 30 |  | 60 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 46 | 49 | 44 | 44
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 3 | 3 | 3
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 61 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 77 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 203 | 202 | 201 | 201 |  | 30 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 17 | 17 | 17
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 285 | 290 | 280 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 367 | 390 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 380 | 375 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1562 | 1615 | 1639 | 1659 | 9 | 710
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 923 | 819 | 940 | 940
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 47 | 81 | 49 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 14 | 31 | 20 | 43 |  | 11 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 45 | 80 | 60 | 82 |  | 27 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 32 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 55 | 17 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 105 | 85 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 82 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1186 | 1203 | 1279 | 1363 | 806 | 55
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 0 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 31 | 22 | 32 |  | 8 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 178 | 178 | 175 | 175
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1050 | 1244 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 250 | 307 | 300 | 300
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1515 | 1926 | 1758 | 1917 | 94 | 228
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 21 | 28 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 34 | 34 | 15 | 31 |  | 40 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 28 | 21 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 32 | 40 | 24 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 179 | 164 | 170 | 170 | 40 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 139 | 139 | 150 | 150 | 70 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 383 | 351 | 380 | 380 | 34 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 34 | 34 | 34 | 34 |  | 16 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 20 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 58 | 80 | 80 | 83 |  | 21 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 482 | 404 | 400 | 400 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1532 | 1478 | 1450 | 1522 | 856 | 122
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 75 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 260 | 260 | 260 | 260
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 34 | 50 |  |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 37 | 115 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 184 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 628 | 499 | 572 | 500 | 50 | 85
| Total |  |  |  |  | 23332 | 22566 | 10749 | 12349 | 10891.6 | 12563 | 5223 | 3366
A. |  | 2023-05-13 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 12349 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9766 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14400 | MW
3 | Day peak Generation : |  |  | 10749 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13630.65 | MW
4 | Evening peak Generation : |  |  | 12349 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 1959 | MW
5 | Total Energy Generation : |  | 264.8912 | MKWHr | By Solar | 2.7059 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 119.8808 | MKWHr |  | By Oil: | 61.6436 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 55.5369 | MKWHr |  | By Hydro: | 0.39378 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5223 | MW | Dhaka | 5140.75 | 4290.75 |  | 850 |  | 18:00 |  | 2049.43
|  |  | For Plants S/D or M/C prob = |  |  | 3366 | MW | Chittagong | 989.7 | 938.7 |  | 51 |  | 19:00 |  | 2053.25
|  |  | Total = |  |  | 8589 | MW | Khulna | 1761.6 | 1697.6 |  | 64 |  | 19:30 |  | 2012.185
7 | Total Gas Supplied : |  |  | 878.64 | MMCFD |  |  | Rajshahi | 1389.2 | 1199.2 |  | 190 |  | 20:00 |  | 2080.945
8 | Fuel Cost : | i) Gas : | Taka | 135730399.172 | ii) Oil : | Taka | 894406557.89 | Comilla | 1311 | 1011 |  | 300 |  | 21:00 |  | 1959
|  | iii) Coal : | Taka | 317389349.9 | Total | Taka | 1347526306.962 | Mymensingh | 1122 | 932 |  | 190 |  | 22:00 |  | 2032.24
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 568 | 449 |  | 119 |  | 23:00 |  | 2348.345
| ii) During Peak Demand : |  |  | 420 | MW (E to W) at | 21:00 | hrs | Barisal | 430.4 | 430.4 |  | 0 |  | 24:00 |  | 2925.165
| iii) Maximum : |  |  | 290 | MW at | 22:00 | hrs | Rangpur | 918 | 723 |  | 195
10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 13630.65 | 11671.65 |  | 1959
B. |  | 2023-05-14 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12563 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 12200 | MW
4 | Reserve(Generation end) |  |  |  | 63 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 268.1302 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9616 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6553 | MKWHr. | ii) HVDC Flow at Peak Time |  | 819 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0749 | MKWHr. | iii) Maximum HVDC Flow : |  | 923 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.04 |  | (b) Today: | 73.92 |  | (c) Rule Curve: |  | 79.53
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-05-13 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 121 | 180 | 0 | 22 | 0 | 368 | 324 |  | 0 | 360 | 148 | 9 | 97 | 15 | 150 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 23 | 27 | 33 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 0 | 0 | 0 |  | 6 | 57 | 84 | 10 | 0 | 6 | 8 | 31 | 0 | 0 | 0 | 310 | 315 | 209 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 120 | 94 | 0 | 17 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 59 | 80 | 0 | 202 | 0 | 0 | 10 | 275 | 16 | 5 | 0 | 95 | 156 | 80 | 48 | 75 | 35 | 0 | 12 | 17 | 18 | 407 | 28 | 88 | 51 | 0 | 87 | 17 | 92 | 114 | 9 | 12 | 398 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 28 | 17 | 0 | 0 | 0 |  | 827 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 19 | 73 | 32 | 85 | 33 | 0 | 0 | 0 | 0 | 21 | 0 | 66 | 21 | 42 | 32 | 0 | 34 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 421 | 17 | 0 | 35 | 85 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 533 | 0 | 0 |  | 6509 | 4612 | 11121 | 3612 | 827 | 2061 | 311 | 1440 | 2285 | 0 | 0 | 465 | 120 | 0 | 1794.445 | 74.09
2:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 403 | 264 |  | 0 | 330 | 151 | 9 | 97 | 15 | 131 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 23 | 27 | 33 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 57 | 84 | 10 | 0 | 6 | 8 | 22 | 0 | 0 | 0 | 310 | 305 | 210 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 130 | 94 | 0 | 17 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 59 | 80 | 0 | 208 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 95 | 208 | 80 | 48 | 75 | 35 | 0 | 12 | 17 | 20 | 415 | 28 | 88 | 51 | 0 | 87 | 17 | 92 | 114 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 0 | 0 |  | 827 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 19 | 73 | 8 | 180 | 32 | 0 | 0 | 0 | 0 | 21 | 0 | 66 | 21 | 42 | 32 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 424 | 17 | 0 | 35 | 85 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203 | 527 | 0 | 0 |  | 6474 | 4702 | 11176 | 3709 | 827 | 1972 | 363 | 1408 | 2309 | 0 | 0 | 458 | 130 | 0 | 1646.42 | 74.08
3:00 | 0 | 0 | 121 | 180 | 0 | 22 | 0 | 399 | 234 |  | 0 | 300 | 149 | 9 | 97 | 15 | 92 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 23 | 27 | 33 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 48 | 84 | 10 | 0 | 6 | 8 | 10 | 0 | 0 | 0 | 310 | 305 | 210 | 187 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 124 | 95 | 0 | 17 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 59 | 80 | 0 | 208 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 95 | 212 | 80 | 48 | 75 | 35 | 0 | 12 | 17 | 20 | 408 | 28 | 88 | 51 | 0 | 87 | 17 | 92 | 72 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 15 | 73 | 8 | 180 | 31 | 0 | 0 | 0 | 0 | 21 | 5 | 66 | 21 | 42 | 32 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 423 | 17 | 0 | 0 | 85 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 520 | 0 | 0 |  | 6297 | 4749 | 11046 | 3664 | 922 | 1894 | 367 | 1296 | 2329 | 0 | 0 | 450 | 124 | 0 | 1675.07 | 74.07
4:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 356 | 275 |  | 0 | 310 | 128 | 8 | 97 | 15 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 21 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 56 | 84 | 10 | 0 | 6 | 8 | 5 | 0 | 0 | 0 | 310 | 305 | 211 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 128 | 95 | 0 | 17 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 59 | 80 | 0 | 208 | 0 | 0 | 10 | 275 | 16 | 5 | 0 | 95 | 302 | 80 | 48 | 75 | 35 | 0 | 12 | 17 | 18 | 416 | 28 | 88 | 51 | 0 | 87 | 17 | 85 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 15 | 73 | 8 | 180 | 30 | 0 | 0 | 0 | 0 | 21 | 7 | 66 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 427 | 17 | 0 | 0 | 85 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 287 | 514 | 0 | 0 |  | 6177 | 4796 | 10973 | 3537 | 921 | 1919 | 457 | 1179 | 2380 | 0 | 0 | 452 | 128 | 0 | 1649.285 | 74.06
5:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 350 | 264 |  | 0 | 300 | 127 | 9 | 97 | 15 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 56 | 84 | 10 | 0 | 6 | 8 | 3 | 0 | 0 | 0 | 310 | 305 | 211 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 134 | 95 | 0 | 17 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 59 | 80 | 0 | 208 | 0 | 0 | 10 | 275 | 16 | 5 | 0 | 95 | 120 | 80 | 48 | 75 | 35 | 0 | 12 | 17 | 20 | 410 | 28 | 88 | 17 | 0 | 87 | 17 | 92 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 18 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 15 | 73 | 8 | 180 | 28 | 0 | 0 | 0 | 0 | 21 | 14 | 66 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 426 | 17 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 306 | 522 | 0 | 0 |  | 5940 | 4799 | 10739 | 3529 | 922 | 1892 | 275 | 1121 | 2407 | 0 | 0 | 459 | 134 | 0 | 1825.005 | 74.05
6:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 350 | 228 |  | 0 | 260 | 90 | 8 | 97 | 15 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 |  | 6 | 56 | 84 | 10 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 345 | 320 | 208 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 134 | 86 | 0 | 17 | 1 | 43 | 28 | 53 | 50 | 0 | 0 | 59 | 80 | 0 | 208 | 0 | 0 | 10 | 265 | 16 | 5 | 0 | 95 | 0 | 50 | 48 | 50 | 35 | 0 | 12 | 17 | 18 | 408 | 28 | 88 | 17 | 0 | 87 | 17 | 92 | 0 | 7 | 12 | 397 | 17 | 3 | 17 | 17 | 0 | 35 | 1 | 17 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 15 | 73 | 8 | 180 | 24 | 0 | 0 | 0 | 0 | 21 | 16 | 66 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 422 | 17 | 0 | 0 | 85 | 0 | 0 | 0 | 35 | 1244 | 0 | 0 | 17 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 308 | 451 | 11 | 0 |  | 5668 | 4775 | 10443 | 3563 | 922 | 1760 | 100 | 1145 | 2338 | 0 | 0 | 461 | 134 | 20 | 1439.185 | 74.04
7:00 | 0 | 0 | 121 | 180 | 0 | 22 | 0 | 351 | 203 |  | 0 | 235 | 0 | 9 | 75 | 15 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 23 | 27 | 33 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 6 | 54 | 84 | 10 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 310 | 305 | 211 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 20 | 134 | 47 | 0 | 17 | 0 | 43 | 28 | 53 | 50 | 0 | 0 | 56 | 77 | 0 | 208 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 95 | 0 | 25 | 48 | 25 | 35 | 1 | 12 | 17 | 20 | 402 | 28 | 88 | 17 | 0 | 87 | 0 | 92 | 0 | 7 | 12 | 400 | 17 | 10 | 17 | 17 | 0 | 35 | 4 | 18 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 15 | 73 | 8 | 180 | 20 | 0 | 0 | 0 | 0 | 21 | 20 | 53 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 397 | 17 | 0 | 13 | 85 | 0 | 0 | 2 | 35 | 1244 | 0 | 0 | 17 | 0 | 15 | 0 | 0 | 0 | 0 | 6 | 302 | 449 | 41 | 0 |  | 5385 | 4788 | 10173 | 3470 | 922 | 1593 | 50 | 1145 | 2330 | 0 | 0 | 450 | 134 | 79 | 1267.285 | 74.03
8:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 344 | 193 |  | 0 | 200 | 0 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 23 | 27 | 33 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 54 | 84 | 10 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 310 | 305 | 212 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 0 | 132 | 43 | 0 | 17 | 1 | 43 | 28 | 53 | 50 | 0 | 0 | 62 | 77 | 0 | 208 | 0 | 0 | 10 | 270 | 16 | 5 | 0 | 95 | 0 | 25 | 48 | 25 | 35 | 3 | 12 | 17 | 20 | 396 | 28 | 88 | 17 | 1 | 87 | 0 | 81 | 0 | 0 | 12 | 400 | 17 | 17 | 17 | 17 | 0 | 35 | 9 | 17 | 17 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 15 | 73 | 8 | 174 | 20 | 0 | 0 | 0 | 0 | 21 | 20 | 52 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 380 | 17 | 0 | 35 | 85 | 33 | 0 | 3 | 35 | 1140 | 0 | 0 | 17 | 1 | 31 | 0 | 0 | 0 | 0 | 12 | 306 | 394 | 68 | 0 |  | 5225 | 4716 | 9941 | 3407 | 921 | 1529 | 50 | 1132 | 2175 | 0 | 0 | 449 | 132 | 146 | 1775.345 | 74.03
9:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 329 | 199 |  | 0 | 130 | 0 | 9 | 34 | 15 | 0 | 0 | 0 | 13 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 23 | 27 | 0 | 14 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 54 | 84 | 10 | 0 | 6 | 8 | 0 | 0 | 0 | 0 | 310 | 305 | 208 | 187 | 0 | 33 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 25 | 12 | 118 | 43 | 0 | 17 | 1 | 43 | 28 | 53 | 50 | 0 | 0 | 61 | 77 | 0 | 209 | 0 | 0 | 10 | 280 | 16 | 5 | 0 | 95 | 0 | 25 | 48 | 25 | 35 | 3 | 12 | 21 | 18 | 391 | 28 | 88 | 17 | 2 | 87 | 0 | 75 | 0 | 0 | 12 | 394 | 34 | 38 | 17 | 17 | 0 | 35 | 12 | 18 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 15 | 36 | 8 | 174 | 19 | 0 | 0 | 0 | 0 | 21 | 20 | 52 | 21 | 42 | 24 | 0 | 27 | 21 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 390 | 17 | 0 | 35 | 85 | 28 | 0 | 5 | 35 | 1040 | 0 | 0 | 17 | 2 | 40 | 0 | 0 | 0 | 0 | 20 | 268 | 423 | 126 | 0 |  | 5169 | 4597 | 9766 | 3293 | 922 | 1481 | 50 | 1150 | 2066 | 25 | 0 | 412 | 118 | 249 | 2037.97 | 74.02
10:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 347 | 200 |  | 0 | 130 | 0 | 8 | 34 | 15 | 0 | 0 | 0 | 34 | 16 | 62 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 23 | 25 | 0 | 14 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 12 | 54 | 84 | 10 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 310 | 305 | 209 | 187 | 0 | 31 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 16 | 12 | 132 | 43 | 0 | 17 | 2 | 43 | 28 | 53 | 47 | 0 | 0 | 61 | 77 | 0 | 206 | 0 | 0 | 10 | 280 | 16 | 0 | 0 | 96 | 0 | 25 | 48 | 25 | 35 | 5 | 12 | 34 | 20 | 390 | 28 | 88 | 17 | 3 | 87 | 8 | 74 | 0 | 9 | 12 | 380 | 50 | 39 | 54 | 17 | 0 | 35 | 15 | 20 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 15 | 36 | 8 | 174 | 21 | 0 | 0 | 0 | 0 | 21 | 26 | 52 | 21 | 42 | 24 | 0 | 28 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 137 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 419 | 17 | 0 | 35 | 85 | 28 | 0 | 5 | 35 | 1040 | 0 | 0 | 17 | 3 | 35 | 0 | 0 | 0 | 0 | 25 | 269 | 445 | 167 | 0 |  | 5296 | 4714 | 10010 | 3271 | 922 | 1509 | 50 | 1275 | 2089 | 30 | 0 | 433 | 132 | 299 | 1995.95 | 74.02
11:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 351 | 208 |  | 0 | 130 | 0 | 8 | 20 | 15 | 0 | 0 | 0 | 34 | 41 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 10 | 10 | 23 | 25 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 |  | 12 | 53 | 75 | 22 | 0 | 15 | 8 | 0 | 0 | 0 | 0 | 320 | 320 | 204 | 187 | 0 | 33 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 13 | 20 | 128 | 47 | 0 | 16 | 2 | 43 | 28 | 53 | 43 | 0 | 0 | 60 | 77 | 0 | 203 | 0 | 0 | 10 | 270 | 16 | 0 | 0 | 96 | 35 | 84 | 48 | 75 | 35 | 3 | 25 | 34 | 18 | 386 | 46 | 88 | 17 | 1 | 87 | 17 | 54 | 0 | 9 | 25 | 380 | 52 | 51 | 54 | 17 | 0 | 35 | 27 | 37 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 14 | 30 | 8 | 178 | 21 | 0 | 0 | 0 | 0 | 21 | 31 | 52 | 28 | 42 | 30 | 0 | 28 | 19 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 390 | 17 | 0 | 35 | 85 | 34 | 0 | 6 | 35 | 1040 | 0 | 0 | 17 | 4 | 31 | 17 | 0 | 0 | 0 | 31 | 250 | 398 | 166 | 0 |  | 5662 | 4694 | 10356 | 3385 | 922 | 1473 | 194 | 1416 | 2023 | 30 | 0 | 463 | 128 | 322 | 1952.02 | 74.01
12:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 370 | 213 |  | 0 | 130 | 0 | 9 | 20 | 15 | 0 | 0 | 0 | 37 | 41 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 10 | 23 | 25 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 53 | 84 | 22 | 0 | 18 | 9 | 0 | 0 | 0 | 0 | 310 | 305 | 204 | 185 | 0 | 28 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 7 | 15 | 142 | 47 | 0 | 16 | 2 | 43 | 28 | 53 | 46 | 0 | 0 | 58 | 73 | 0 | 203 | 0 | 0 | 10 | 285 | 16 | 0 | 0 | 97 | 210 | 86 | 49 | 75 | 34 | 4 | 25 | 34 | 20 | 367 | 48 | 88 | 28 | 3 | 87 | 17 | 54 | 0 | 24 | 25 | 380 | 35 | 51 | 54 | 17 | 0 | 35 | 25 | 53 | 17 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 14 | 45 | 8 | 178 | 20 | 0 | 0 | 0 | 0 | 21 | 34 | 58 | 28 | 42 | 32 | 0 | 34 | 18 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 383 | 17 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 1050 | 0 | 0 | 17 | 4 | 82 | 37 | 0 | 0 | 0 | 31 | 250 | 482 | 184 | 0 |  | 5888 | 4861 | 10749 | 3338 | 923 | 1481 | 371 | 1450 | 2117 | 30 | 0 | 504 | 142 | 393 | 1959 | 74.01
13:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 358 | 203 |  | 0 | 130 | 0 | 9 | 17 | 30 | 0 | 0 | 0 | 37 | 48 | 98 | 4 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 23 | 25 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 54 | 84 | 22 | 0 | 19 | 9 | 0 | 0 | 0 | 0 | 325 | 320 | 201 | 185 | 0 | 33 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 0 | 6 | 15 | 136 | 47 | 0 | 15 | 2 | 43 | 28 | 50 | 45 | 0 | 0 | 55 | 73 | 0 | 202 | 0 | 0 | 10 | 285 | 16 | 0 | 0 | 96 | 303 | 85 | 57 | 75 | 35 | 6 | 25 | 34 | 20 | 380 | 48 | 88 | 42 | 2 | 87 | 17 | 54 | 0 | 47 | 25 | 370 | 35 | 51 | 54 | 17 | 0 | 35 | 31 | 54 | 17 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 14 | 30 | 8 | 178 | 23 | 0 | 0 | 0 | 0 | 21 | 34 | 66 | 28 | 42 | 32 | 0 | 34 | 18 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 359 | 17 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 1060 | 0 | 0 | 17 | 0 | 52 | 37 | 0 | 0 | 0 | 31 | 271 | 413 | 156 | 0 |  | 6083 | 4728 | 10811 | 3345 | 921 | 1446 | 463 | 1555 | 2079 | 30 | 0 | 498 | 136 | 338 | 1994.995 | 74
14:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 331 | 187 |  | 0 | 120 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 34 | 48 | 113 | 7 | 0 | 0 | 0 | 17 | 35 | 35 | 10 | 23 | 25 | 33 | 8 | 8 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 53 | 84 | 22 | 9 | 21 | 9 | 0 | 0 | 0 | 0 | 325 | 315 | 201 | 185 | 0 | 32 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 0 | 15 | 118 | 47 | 0 | 15 | 2 | 43 | 28 | 50 | 48 | 0 | 0 | 60 | 73 | 0 | 202 | 0 | 0 | 10 | 290 | 0 | 0 | 0 | 96 | 180 | 86 | 48 | 74 | 34 | 5 | 25 | 34 | 18 | 387 | 48 | 88 | 51 | 1 | 87 | 17 | 54 | 0 | 55 | 25 | 370 | 48 | 41 | 54 | 17 | 0 | 35 | 15 | 53 | 17 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 13 | 30 | 8 | 178 | 23 | 0 | 0 | 0 | 0 | 28 | 34 | 72 | 28 | 42 | 32 | 0 | 34 | 17 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 345 | 17 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 1090 | 0 | 0 | 17 | 0 | 81 | 37 | 0 | 0 | 0 | 28 | 270 | 404 | 141 | 0 |  | 5867 | 4755 | 10622 | 3302 | 923 | 1413 | 340 | 1552 | 2099 | 30 | 0 | 524 | 118 | 321 | 2079.99 | 74.01
15:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 311 | 167 |  | 0 | 120 | 0 | 9 | 17 | 0 | 0 | 0 | 0 | 34 | 48 | 130 | 0 | 0 | 0 | 0 | 17 | 35 | 45 | 10 | 23 | 25 | 33 | 12 | 12 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 53 | 84 | 22 | 12 | 25 | 9 | 0 | 0 | 0 | 0 | 320 | 320 | 201 | 185 | 0 | 30 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 6 | 0 | 15 | 136 | 46 | 0 | 15 | 1 | 39 | 28 | 47 | 45 | 0 | 0 | 55 | 73 | 0 | 200 | 17 | 0 | 10 | 290 | 8 | 0 | 0 | 96 | 30 | 86 | 48 | 75 | 71 | 2 | 25 | 34 | 18 | 374 | 48 | 88 | 51 | 1 | 87 | 17 | 54 | 0 | 57 | 25 | 369 | 52 | 35 | 54 | 17 | 0 | 35 | 10 | 54 | 17 | 0 | 0 | 0 |  | 922 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 16 | 45 | 8 | 178 | 23 | 0 | 0 | 0 | 0 | 28 | 34 | 80 | 28 | 42 | 32 | 0 | 34 | 17 | 0 | 8 | 76 | 0 | 260 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 343 | 17 | 0 | 35 | 50 | 34 | 0 | 6 | 35 | 1090 | 0 | 0 | 17 | 2 | 39 | 37 | 0 | 0 | 0 | 20 | 270 | 404 | 115 | 0 |  | 5751 | 4693 | 10444 | 3271 | 922 | 1385 | 191 | 1611 | 2100 | 30 | 0 | 567 | 136 | 231 | 2154.48 | 73.99
16:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 287 | 157 |  | 0 | 105 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 37 | 48 | 146 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 10 | 23 | 25 | 33 | 12 | 33 | 0 | 30 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 |  | 12 | 48 | 74 | 22 | 12 | 25 | 9 | 0 | 0 | 0 | 0 | 310 | 310 | 202 | 187 | 0 | 34 | 0 | 0 | 43 | 0 | 31 | 0 | 17 | 6 | 0 | 9 | 120 | 46 | 0 | 17 | 1 | 40 | 28 | 50 | 48 | 0 | 0 | 58 | 72 | 0 | 198 | 17 | 0 | 10 | 295 | 8 | 0 | 0 | 96 | 301 | 85 | 48 | 75 | 88 | 1 | 25 | 34 | 20 | 374 | 49 | 88 | 51 | 0 | 87 | 17 | 70 | 0 | 58 | 25 | 370 | 36 | 21 | 54 | 17 | 0 | 19 | 10 | 54 | 17 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 17 | 60 | 8 | 177 | 22 | 0 | 0 | 0 | 0 | 28 | 34 | 72 | 28 | 42 | 32 | 0 | 34 | 17 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 324 | 17 | 0 | 35 | 15 | 34 | 0 | 4 | 35 | 1190 | 0 | 0 | 17 | 2 | 29 | 37 | 0 | 0 | 0 | 14 | 241 | 402 | 61 | 0 |  | 5969 | 4638 | 10607 | 3227 | 921 | 1352 | 461 | 1609 | 2168 | 30 | 0 | 576 | 120 | 143 | 1903.315 | 73.99
17:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 269 | 145 |  | 0 | 90 | 0 | 8 | 17 | 0 | 0 | 0 | 0 | 34 | 48 | 146 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 23 | 26 | 33 | 12 | 33 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 55 | 68 | 22 | 29 | 25 | 0 | 0 | 0 | 0 | 0 | 310 | 305 | 204 | 187 | 0 | 34 | 0 | 0 | 43 | 0 | 31 | 0 | 17 | 6 | 0 | 20 | 122 | 46 | 0 | 19 | 0 | 40 | 28 | 50 | 48 | 0 | 0 | 60 | 76 | 0 | 198 | 17 | 0 | 10 | 295 | 16 | 0 | 0 | 96 | 170 | 87 | 57 | 50 | 88 | 0 | 25 | 44 | 36 | 368 | 49 | 88 | 56 | 0 | 87 | 17 | 80 | 0 | 58 | 25 | 374 | 35 | 14 | 54 | 17 | 0 | 35 | 4 | 54 | 26 | 0 | 0 | 0 |  | 921 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 24 | 60 | 8 | 177 | 20 | 0 | 0 | 0 | 0 | 28 | 34 | 72 | 28 | 42 | 32 | 0 | 34 | 17 | 0 | 8 | 76 | 0 | 260 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 129 | 0 | 328 | 17 | 0 | 35 | 15 | 40 | 0 | 2 | 35 | 1190 | 0 | 0 | 17 | 1 | 8 | 37 | 0 | 0 | 0 | 7 | 240 | 441 | 31 | 0 |  | 5855 | 4626 | 10481 | 3204 | 921 | 1331 | 307 | 1708 | 2207 | 30 | 0 | 584 | 122 | 67 | 1880.395 | 73.98
18:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 259 | 138 |  | 0 | 85 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 34 | 90 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 23 | 26 | 33 | 12 | 37 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 55 | 84 | 22 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 305 | 305 | 207 | 187 | 0 | 38 | 0 | 0 | 43 | 0 | 38 | 0 | 17 | 6 | 0 | 20 | 126 | 46 | 0 | 19 | 0 | 40 | 28 | 53 | 48 | 0 | 0 | 61 | 76 | 0 | 198 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 96 | 130 | 50 | 58 | 50 | 98 | 0 | 25 | 68 | 85 | 368 | 49 | 88 | 78 | 0 | 119 | 17 | 92 | 0 | 58 | 25 | 374 | 35 | 2 | 54 | 17 | 0 | 35 | 1 | 54 | 34 | 0 | 20 | 0 |  | 920 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 27 | 59 | 8 | 178 | 21 | 0 | 0 | 0 | 0 | 28 | 34 | 72 | 28 | 34 | 40 | 0 | 34 | 19 | 0 | 8 | 74 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 332 | 19 | 0 | 35 | 15 | 49 | 0 | 1 | 35 | 1170 | 0 | 0 | 17 | 0 | 2 | 37 | 0 | 0 | 0 | 2 | 240 | 456 | 6 | 0 |  | 6056 | 4598 | 10654 | 3196 | 920 | 1334 | 230 | 1967 | 2200 | 30 | 0 | 637 | 126 | 14 | 2049.43 | 73.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 258 | 137 |  | 0 | 90 | 0 | 25 | 17 | 10 | 0 | 0 | 0 | 42 | 92 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 23 | 20 | 33 | 12 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 55 | 84 | 22 | 29 | 35 | 0 | 0 | 0 | 0 | 0 | 330 | 315 | 203 | 187 | 0 | 36 | 0 | 0 | 43 | 0 | 38 | 0 | 18 | 6 | 0 | 20 | 122 | 68 | 0 | 19 | 0 | 40 | 28 | 53 | 48 | 0 | 0 | 55 | 77 | 0 | 202 | 17 | 0 | 10 | 285 | 16 | 0 | 0 | 260 | 204 | 88 | 86 | 84 | 132 | 0 | 25 | 68 | 137 | 395 | 87 | 88 | 87 | 0 | 257 | 17 | 102 | 0 | 95 | 25 | 348 | 53 | 0 | 162 | 17 | 0 | 35 | 0 | 64 | 34 | 0 | 43 | 0 |  | 921 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 28 | 63 | 32 | 178 | 28 | 16 | 0 | 0 | 0 | 21 | 38 | 80 | 21 | 34 | 40 | 8 | 34 | 19 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 333 | 35 | 0 | 35 | 36 | 49 | 0 | 0 | 55 | 1190 | 0 | 0 | 37 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 272 | 401 | 0 | 0 |  | 6942 | 4758 | 11700 | 3240 | 921 | 1332 | 376 | 2811 | 2198 | 30 | 0 | 670 | 122 | 0 | 2053.25 | 73.96
19:30 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 266 | 137 |  | 0 | 90 | 0 | 25 | 17 | 15 | 0 | 0 | 0 | 42 | 92 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 21 | 26 | 0 | 12 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 55 | 84 | 22 | 27 | 39 | 0 | 0 | 0 | 0 | 0 | 325 | 315 | 204 | 187 | 0 | 40 | 0 | 0 | 43 | 0 | 38 | 0 | 18 | 6 | 0 | 20 | 130 | 84 | 0 | 19 | 0 | 43 | 29 | 53 | 48 | 0 | 0 | 58 | 77 | 0 | 202 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 277 | 205 | 88 | 86 | 83 | 133 | 0 | 25 | 68 | 137 | 378 | 88 | 88 | 87 | 0 | 262 | 17 | 102 | 0 | 95 | 25 | 348 | 53 | 0 | 162 | 17 | 0 | 35 | 0 | 94 | 35 | 0 | 80 | 0 |  | 921 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 30 | 70 | 32 | 178 | 30 | 16 | 0 | 0 | 0 | 21 | 34 | 80 | 21 | 34 | 40 | 8 | 34 | 19 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 351 | 55 | 0 | 50 | 85 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 81 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 306 | 399 | 0 | 0 |  | 7029 | 5064 | 12093 | 3225 | 921 | 1367 | 376 | 3048 | 2284 | 30 | 0 | 712 | 130 | 0 | 2012.185 | 0
20:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 266 | 133 |  | 0 | 85 | 0 | 25 | 17 | 15 | 0 | 0 | 0 | 42 | 92 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 23 | 26 | 33 | 12 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 55 | 84 | 22 | 26 | 39 | 0 | 0 | 0 | 0 | 0 | 305 | 305 | 205 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 38 | 0 | 18 | 6 | 0 | 20 | 112 | 85 | 0 | 19 | 0 | 43 | 29 | 53 | 48 | 0 | 0 | 61 | 76 | 0 | 202 | 17 | 0 | 10 | 295 | 16 | 3 | 0 | 277 | 206 | 88 | 86 | 83 | 134 | 0 | 25 | 68 | 142 | 367 | 89 | 88 | 85 | 0 | 262 | 17 | 105 | 0 | 96 | 25 | 348 | 53 | 0 | 162 | 17 | 0 | 35 | 0 | 94 | 34 | 0 | 130 | 0 |  | 819 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 34 | 85 | 32 | 178 | 31 | 16 | 0 | 0 | 0 | 28 | 34 | 80 | 21 | 34 | 40 | 8 | 34 | 19 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 128 | 0 | 352 | 55 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 100 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 307 | 404 | 0 | 0 |  | 7077 | 5044 | 12121 | 3246 | 819 | 1356 | 377 | 3103 | 2290 | 30 | 0 | 788 | 112 | 0 | 2080.945 | 73.97
21:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 263 | 131 |  | 0 | 85 | 0 | 26 | 17 | 15 | 0 | 0 | 0 | 42 | 92 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 23 | 26 | 33 | 12 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 55 | 84 | 22 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 310 | 315 | 203 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 38 | 0 | 18 | 6 | 0 | 20 | 118 | 84 | 0 | 19 | 0 | 43 | 29 | 53 | 49 | 0 | 0 | 61 | 77 | 0 | 202 | 17 | 0 | 10 | 290 | 16 | 3 | 0 | 277 | 306 | 80 | 87 | 82 | 133 | 0 | 25 | 68 | 145 | 390 | 89 | 88 | 85 | 0 | 262 | 17 | 105 | 0 | 96 | 25 | 375 | 52 | 0 | 135 | 17 | 0 | 35 | 0 | 95 | 34 | 0 | 163 | 0 |  | 819 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 31 | 80 | 32 | 178 | 31 | 16 | 0 | 0 | 0 | 28 | 34 | 80 | 21 | 42 | 40 | 8 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 351 | 55 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 307 | 404 | 0 | 0 |  | 7243 | 5106 | 12349 | 3316 | 819 | 1351 | 468 | 3144 | 2290 | 30 | 0 | 813 | 118 | 0 | 1959 | 73.96
22:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 245 | 102 |  | 0 | 85 | 0 | 25 | 17 | 15 | 0 | 0 | 0 | 42 | 92 | 148 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 23 | 27 | 33 | 12 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 56 | 84 | 22 | 30 | 9 | 0 | 0 | 0 | 0 | 0 | 315 | 310 | 205 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 0 | 18 | 6 | 0 | 20 | 114 | 84 | 0 | 19 | 0 | 43 | 29 | 53 | 49 | 0 | 0 | 61 | 77 | 0 | 202 | 17 | 0 | 10 | 290 | 16 | 3 | 0 | 277 | 300 | 80 | 78 | 83 | 133 | 0 | 25 | 68 | 143 | 390 | 89 | 88 | 85 | 0 | 123 | 17 | 107 | 0 | 98 | 25 | 375 | 47 | 0 | 72 | 17 | 0 | 35 | 0 | 95 | 34 | 0 | 163 | 0 |  | 819 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 24 | 76 | 32 | 178 | 32 | 16 | 0 | 0 | 0 | 28 | 34 | 72 | 21 | 42 | 40 | 8 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 355 | 55 | 0 | 50 | 105 | 48 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 307 | 403 | 0 | 0 |  | 6907 | 5065 | 11972 | 3316 | 819 | 1327 | 463 | 2820 | 2289 | 30 | 0 | 794 | 114 | 0 | 2032.24 | 73.96
23:00 | 0 | 0 | 100 | 180 | 0 | 22 | 0 | 241 | 103 |  | 0 | 85 | 0 | 10 | 7 | 15 | 0 | 0 | 0 | 19 | 32 | 148 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 23 | 27 | 33 | 13 | 50 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 10 | 56 | 84 | 22 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 340 | 330 | 203 | 199 | 0 | 41 | 0 | 0 | 43 | 0 | 39 | 0 | 18 | 6 | 0 | 20 | 132 | 84 | 0 | 19 | 0 | 43 | 29 | 53 | 49 | 0 | 0 | 60 | 77 | 0 | 204 | 17 | 0 | 10 | 295 | 16 | 3 | 0 | 277 | 300 | 80 | 48 | 84 | 64 | 0 | 25 | 68 | 60 | 391 | 28 | 88 | 85 | 0 | 87 | 17 | 107 | 0 | 26 | 25 | 375 | 20 | 0 | 17 | 17 | 0 | 35 | 0 | 95 | 34 | 0 | 163 | 0 |  | 819 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 24 | 76 | 32 | 178 | 32 | 0 | 0 | 0 | 0 | 28 | 34 | 72 | 21 | 34 | 32 | 0 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 345 | 55 | 0 | 35 | 85 | 49 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 307 | 403 | 0 | 0 |  | 6381 | 4910 | 11291 | 3339 | 819 | 1333 | 464 | 2125 | 2289 | 0 | 0 | 790 | 132 | 0 | 2348.345 | 73.95
24:00 | 0 | 0 | 100 | 180 | 0 | 22 | 0 | 240 | 92 |  | 0 | 85 | 0 | 8 | 0 | 15 | 0 | 0 | 0 | 9 | 32 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 19 | 23 | 27 | 33 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 56 | 84 | 22 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 340 | 340 | 205 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 39 | 0 | 18 | 6 | 0 | 20 | 136 | 84 | 0 | 19 | 0 | 43 | 29 | 50 | 49 | 0 | 0 | 61 | 77 | 0 | 204 | 18 | 0 | 10 | 290 | 16 | 3 | 0 | 278 | 300 | 80 | 48 | 76 | 35 | 0 | 12 | 53 | 18 | 390 | 28 | 88 | 74 | 0 | 87 | 17 | 107 | 0 | 9 | 12 | 378 | 17 | 0 | 17 | 17 | 0 | 35 | 0 | 75 | 17 | 0 | 40 | 0 |  | 820 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 29 | 76 | 32 | 178 | 30 | 0 | 0 | 0 | 0 | 28 | 34 | 72 | 21 | 42 | 32 | 0 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 341 | 55 | 0 | 35 | 85 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 403 | 0 | 0 |  | 5936 | 4701 | 10637 | 3352 | 820 | 1298 | 456 | 1614 | 2289 | 0 | 0 | 672 | 136 | 0 | 2925.165 | 73.95
KWH | 0 | 0 | 2849906 | 4252500 | 0 | 529000 | 0 | 7780350 | 4630000 |  | 0 | 3916000 | 885260 | 271680 | 926634 | 308893 | 436164 | 0 | 0 | 565440 | 989136 | 2297760 | 15000 | 0 | 0 | 0 | 260280 | 643681 | 635575 | 298692 | 552000 | 608400 | 739080 | 346000 | 525600 | 0 | 393780 | 0 | 0 | 0 | 525877 | 199169 | 0 | 0 | 0 |  | 236400 | 1292832 | 1977976 | 412320 | 218880 | 432480 | 139008 | 114720 | 0 | 0 | 0 | 8132800 | 7741000 | 4981000 | 4516363 | 0 | 848736 | 0 | 0 | 968102 | 0 | 801152 | 0 | 420480 | 164340 | 283600 | 424540 | 3074880 | 1534080 | 0 | 383652 | 14650 | 1009000 | 635400 | 1252800 | 1160568 | 0 | 0 | 1397088 | 1834560 | 0 | 5139060 | 163000 | 0 | 252900 | 6897500 | 354336 | 64992 | 0 | 3412364 | 4131569 | 1688701 | 1334400 | 1539404 | 1487808 | 36180 | 452160 | 917280 | 1078909 | 9393000 | 1066800 | 2114477 | 1228618 | 13199 | 2679709 | 380988 | 2039046 | 352260 | 813120 | 470400 | 9033400 | 792000 | 362340 | 1124640 | 417764 | 0 | 870480 | 147148 | 1131840 | 553320 | 0 | 744363 | 0 |  | 21655272 | 0 | 0 | 0 | 1106880 | 0 | 0 | 0 | 435840 | 1433344 | 354375 | 4209374 | 623532 | 60768 | 0 | 0 | 0 | 570992 | 496577 | 1583792 | 550960 | 932528 | 616956 | 25430 | 743170 | 456720 | 0 | 196056 | 1736290 | 0 | 6256100 | 0 | 0 | 4333618 | 0 | 0 | 0 | 0 | 0 | 3761209 | 0 | 9037745 | 627360 | 0 | 801696 | 1773072 | 794294 | 0 | 58597 | 825984 | 30433600 | 0 | 0 | 962400 | 22620 | 522720 | 787200 | 0 | 0 | 0 | 231713 | 6436400 | 10674545 | 1296700 | 0 |  | 147464739 | 117426429 | 264891168 | 82805030 | 21655272 | 37075770 | 7359674 | 41289206 | 55536935 | 393780 | 0 | 12994754 | 3074880 | 2705867 | 0
Fuel Cost | 0 | 0 | 4160862.76 | 6336225 | 0 | 703570 | 0 | 8169367.5 | 5000400 |  | 0 | 4268440 | 982638.6 | 3037382.4 | 12277900.5 | 4092832.25 | 488503.68 | 0 | 0 | 8266732.8 | 13917143.52 | 37246689.6 | 138300 | 0 | 0 | 0 | 3310761.6 | 8689693.5 | 8523060.75 | 224019 | 414000 | 0 | 0 | 0 | 8940456 | 0 | 106320.6 | 0 | 0 | 0 | 8598088.95 | 207135.76 | 0 | 0 | 0 |  | 3085020 | 21564437.76 | 33665151.52 | 5570443.2 | 2775398.4 | 5003793.6 | 176540.16 | 382017.6 | 0 | 0 | 0 | 9027408 | 8437690 | 5777960 | 5826108.27 | 0 | 959071.68 | 0 | 0 | 1616730.34 | 0 | 13835895.04 | 0 | 576057.6 | 123255 | 496300 | 318405 | 22077638.4 | 1672147.2 | 0 | 521766.72 | 233521 | 1382330 | 838728 | 2179872 | 2007782.64 | 0 | 0 | 2710350.72 | 4182796.8 | 0 | 5190450.6 | 350450 | 0 | 500742 | 6897500 | 265752 | 49393.92 | 0 | 46578768.6 | 86597686.24 | 34905449.67 | 17987712 | 31819480.68 | 20606140.8 | 422944.2 | 4666291.2 | 12530044.8 | 14317122.43 | 8641560 | 12972288 | 30575337.42 | 15542017.7 | 0 | 31459783.66 | 4148959.32 | 21675058.98 | 4780168.2 | 10481116.8 | 5541312 | 8310728 | 10256400 | 5235813 | 14271681.6 | 4754154.32 | 0 | 11368468.8 | 1758418.6 | 16943644.8 | 7287224.4 | 0 | 0 | 0 |  | 64965816 | 0 | 0 | 0 | 11522620.8 | 0 | 0 | 0 | 7849478.4 | 25800192 | 5092368.75 | 4714498.88 | 1209652.08 | 662371.2 | 0 | 0 | 0 | 9575535.84 | 8685131.73 | 24770506.88 | 4242392 | 15442663.68 | 10432725.96 | 346610.9 | 12537277.9 | 945410.4 | 0 | 148414.392 | 10087844.9 | 0 | 33094769 | 0 | 0 | 5026996.88 | 0 | 0 | 0 | 0 | 0 | 4363002.44 | 0 | 8947367.55 | 8431718.4 | 0 | 9484063.68 | 25620890.4 | 10087533.8 | 0 | 647496.85 | 10027445.76 | 274206736 | 0 | 0 | 7121760 | 255832.2 | 6131505.6 | 12067776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 814815206.16 | 634546407.252 | 1449361613.412 | 90079370.892 | 64965816 | 45651028.28 | 153322616.59 | 535120918.67 | 317389349.9 | 106320.6 | 0 | 205963022.63 | 22077638.4 | 14685531.45 | 0
Yesterday Day Peak | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 370 | 213 |  | 0 | 130 | 0 | 9 | 20 | 15 | 0 | 0 | 0 | 37 | 41 | 98 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 10 | 23 | 25 | 33 | 12 | 8 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 |  | 12 | 53 | 84 | 22 | 0 | 18 | 9 | 0 | 0 | 0 | 0 | 310 | 305 | 204 | 185 | 0 | 28 | 0 | 0 | 43 | 0 | 31 | 0 | 18 | 7 | 7 | 15 | 142 | 47 | 0 | 16 | 2 | 43 | 28 | 53 | 46 | 0 | 0 | 58 | 73 | 0 | 203 | 0 | 0 | 10 | 285 | 16 | 0 | 0 | 97 | 210 | 86 | 49 | 75 | 34 | 4 | 25 | 34 | 20 | 367 | 48 | 88 | 28 | 3 | 87 | 17 | 54 | 0 | 24 | 25 | 380 | 35 | 51 | 54 | 17 | 0 | 35 | 25 | 53 | 17 | 0 | 0 | 0 |  | 923 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 14 | 45 | 8 | 178 | 20 | 0 | 0 | 0 | 0 | 21 | 34 | 58 | 28 | 42 | 32 | 0 | 34 | 18 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 383 | 17 | 0 | 35 | 50 | 34 | 0 | 7 | 35 | 1050 | 0 | 0 | 17 | 4 | 82 | 37 | 0 | 0 | 0 | 31 | 250 | 482 | 184 | 0 |  | 10749 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 263 | 131 | 0 | 0 | 85 | 0 | 26 | 17 | 15 | 0 | 0 | 0 | 42 | 92 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 23 | 26 | 33 | 12 | 49 | 0 | 30 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 55 | 84 | 22 | 30 | 40 | 0 | 0 | 0 | 0 | 0 | 310 | 315 | 203 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 38 | 0 | 18 | 6 | 0 | 20 | 118 | 84 | 0 | 19 | 0 | 43 | 29 | 53 | 49 | 0 | 0 | 61 | 77 | 0 | 202 | 17 | 0 | 10 | 290 | 16 | 3 | 0 | 277 | 306 | 80 | 87 | 82 | 133 | 0 | 25 | 68 | 145 | 390 | 89 | 88 | 85 | 0 | 262 | 17 | 105 | 0 | 96 | 25 | 375 | 52 | 0 | 135 | 17 | 0 | 35 | 0 | 95 | 34 | 0 | 163 | 0 |  | 819 | 0 | 0 | 0 | 81 | 0 | 0 | 0 | 31 | 80 | 32 | 178 | 31 | 16 | 0 | 0 | 0 | 28 | 34 | 80 | 21 | 42 | 40 | 8 | 34 | 20 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 351 | 55 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 307 | 404 | 0 | 0 |  | 12349 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 220 | 0 | 0 | 0 | 85 | 0 | 26 | 17 | 15 | 0 | 0 | 0 | 40 | 92 | 148 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 23 | 27 | 33 | 33 | 52 | 0 | 25 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 57 | 84 | 22 | 30 | 44 | 10 | 0 | 0 | 0 | 0 | 310 | 300 | 200 | 180 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 0 | 18 | 7 | 33 | 20 | 152 | 90 | 0 | 18 | 0 | 43 | 30 | 51 | 44 | 0 | 0 | 60 | 84 | 0 | 201 | 17 | 0 | 10 | 300 | 16 | 3 | 0 | 300 | 300 | 80 | 85 | 80 | 116 | 0 | 25 | 68 | 150 | 400 | 85 | 88 | 105 | 0 | 300 | 17 | 54 | 0 | 96 | 25 | 400 | 54 | 0 | 162 | 51 | 0 | 35 |  | 94 | 34 | 0 | 163 |  |  | 940 | 0 | 0 |  | 98 | 0 | 0 | 0 | 43 | 82 | 40 | 175 | 32 | 16 | 0 | 0 | 0 | 28 | 31 | 83 | 21 | 42 | 40 | 8 | 34 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 170 |  | 0 | 0 | 0 | 0 | 150 | 0 | 380 | 55 | 0 | 50 | 105 | 50 | 0 | 0 | 55 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 300 | 400 |  | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 220 | 0 | 0 | 0 | 85 | 0 | 26 | 17 | 15 | 0 | 0 | 0 | 35 | 40 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 22 | 23 | 27 | 33 | 33 | 16 | 0 | 25 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 12 | 54 | 84 | 22 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 310 | 300 | 200 | 180 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 0 | 18 | 7 | 33 | 20 | 129 | 35 | 0 | 18 | 1.6 | 43 | 30 | 51 | 44 | 0 | 0 | 60 | 84 | 0 | 201 | 17 | 0 | 10 | 280 | 16 | 3 | 0 | 97 | 300 | 70 | 48 | 75 | 116 | 20 | 25 | 34 | 20 | 400 | 48 | 88 | 17 | 5 | 88 | 17 | 54 | 0 | 26 | 25 | 400 | 54 | 50 | 54 | 17 | 0 | 35 | 30 | 54 | 17 | 0 | 36 |  |  | 940 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 20 | 60 | 8 | 175 | 22 | 0 | 0 | 0 | 0 | 28 | 15 | 80 | 21 | 42 | 24 | 0 | 34 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 380 | 17 | 0 | 35 | 85 | 34 | 0 | 8 | 35 | 1244 | 0 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 300 | 400 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 100 | 180 | 0 | 22 | 0 | 252 | 80 | 0 | 0 | 85 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 19 | 23 | 27 | 33 | 12 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 6 | 55 | 84 | 10 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 325 | 320 | 207 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 37 | 0 | 15 | 3 | 0 | 18 | 132 | 31 | 0 | 19 | 1 | 43 | 29 | 50 | 49 | 0 | 0 | 61 | 77 | 0 | 204 | 17 | 0 | 10 | 285 | 16 | 3 | 0 | 97 | 156 | 80 | 48 | 75 | 17 | 1 | 12 | 17 | 20 | 391 | 28 | 88 | 17 | 0 | 87 | 17 | 40 | 0 | 9 | 12 | 368 | 8 | 12 | 17 | 17 | 0 | 35 | 8 | 18 | 17 | 0 | 36 | 0 | 0 | 921 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 19 | 70 | 8 | 180 | 17 | 0 | 0 | 0 | 0 | 28 | 0 | 76 | 28 | 42 | 32 | 0 | 34 | 19 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 326 | 17 | 0 | 35 | 15 | 22 | 0 | 3 | 35 | 1160 | 0 | 0 | 17 | 2 | 27 | 0 | 0 | 0 | 0 | 13 | 178 | 401 | 72 | 0 | 0 |  |  |  | 119.8808 | 21.6553 | 61.6436 | 55.5369 | 0.39378 | 3.0749 | 2.7059
264.8912
| Minimum Generation |  | 9766 | 9:00
| Highest Generation |  | 12349 | 21:00
| Day Peak Generation |  | 10749 | 12:00
| Evening Peak Generation |  | 12349 | 21:00
| HVDC Max Flow |  | 923 | 12:00
| HVDC EvPeak Flow |  | 819 | 21:00
| Load factor L.F |  | 89.38% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-14
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-05-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10749 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9616
Evening Peak Generation : |  |  | 12349 | MW Hour : | 21:00 | Available Max Generation : |  | 12563
E.P. Demand (at gen end) : |  |  | 14400 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12500
Maximum Generation : |  |  | 12349 | MW Hour : | 21:00 | Reserve(Generation end) |  | 63
Total Gen. (MKWH) : |  |  | 264.8912 | System Load Factor : | 89.38% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 290 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-14
Actual : |  | 73.92 | Ft.(MSL) , | Rule curve : | 79.53 | Ft.( MSL )
Gas Consumed : |  | Total = | 878.64 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 135730399.172
: |  |  | Coal : | 317389349.9 | Oil : | 894406557.89 | Total : | 1347526306.962
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 850 | 20400:00 | 4211.0089 |  |  | 0 | 0%
Chittagong Area |  | 51 | 1224:00 | 1154.9 |  |  | 0 | 0%
Khulna Area |  | 64 | 1536:00 | 1617.1353 |  |  | 0 | 0%
Rajshahi Area |  | 190 | 4560:00 | 1404.9812 |  |  | 0 | 0%
Cumilla Area |  | 300 | 7200:00 | 1156.3575 |  |  | 0 | 0%
Mymensingh Area |  | 190 | 4560:00 | 859.7216 |  |  | 0 | 0%
Sylhet Area |  | 119 | 2856:00 | 482.2394 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 401.5794 |  |  | 0 | 0%
Rangpur Area |  | 195 | 4680:00 | 785.4259 |  |  | 0 | 0%
Total |  | 1959 |  | 12073.3492 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:15 | 13:56 | Bheramara 230/132kV S/S Transformer-2 HT Scheduled S/D Due to fire Extinguishing Water pipe maintenance.
8:15 | 13:58 | Bheramara 230/132kV S/S Transformer-2 LT Scheduled S/D Due to fire Extinguishing Water pipe maintenance.
9:08 | 15:22 | Chhatak 132/33kV S/S T-2 LT Scheduled S/D Due to DS Change of SPPM 33kv feeder. | [5 empty] | 5.0MW load interrup.
9:10 | 15:21 | Chhatak 132/33kV S/S T-2 HT Scheduled S/D Due to 33 kv SPPM Feeder DS Change. | [5 empty] | 5.0MW load interrup.
9:31 | 11:45 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D Due to Red Hot Remove & various nut bolt tightning .
9:40 | 9:55 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Forced S/D Due to Tr-3 33kV Breaker SF6 Gass refill work.
9:40 | 9:55 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Forced S/D Due to Tr-3 33kV Breaker SF6 Gass refill work.
10:08 | 17:45 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to TR-04,33 kv Bus maintenance by BPDB. | [5 empty] | 40.0MW load interrup.
10:10 | 17:42 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to None.
10:18 | 13:12 | Barishal 230/132kV S/S 230kV BUS Project Work S/D Due to Connecting 230kv BUS-1 to GIS Bay.
10:40 | - | Sholoshohor 132/33 kV T-2 was shutdown due to auxiliary transformer maintenance.
10:40 | 1:40 | Sholoshohor 132/33kV T-2 was shutdown due to auxiliary transformer maintenance.
10:50 | - | Sholosohor 132/33kV S/S TRAFO-01 HT Forced S/D Due to auxliary transformer -2 fuse maintenance.
12:12 | 13:46 | Manikganj 132/33kV S/S 132/33 kV Transformer GT-4 (50/75 MVA) LT Scheduled S/D Due to Red Hot Remove & various nut bolt tightning.
- | 13:12 | Barishal 230/132kV S/S 230kV BUS is restored.
- | 13:41 | Joypurhat 132/33kV S/S Transformer T-4 (437 T) HT is restored.
14:18 | 19:11 | Joydebpur 132/33kV S/S GT-2 HT Forced S/D Due to GT-2 Fault. | [5 empty] | 50.0MW load interrup.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-05-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2849906 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4252500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 529000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 263 | 7780350 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 131 | 4630000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 85 | 3916000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 26 | 271680 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 885260 | Fuel shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 926634 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 308893 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 15000 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 298692 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 42 | 565440 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 436164 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 92 | 989136 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 260280 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 146 | 2297760
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 643681
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 635575 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1160400 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 739080
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 346000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 525600 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 277 | 3412364 | Machine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 306 | 4131569
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 1688701 | Engine problem
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 82 | 1539404 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 133 | 1487808 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2114477 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 52 | 792000 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 135 | 1124640 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 147148
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 553320 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2613 | 52254462
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 525877
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 36180
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 40 | 432480 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 393780 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 0 | 199169
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 1228618 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 55 | 1292832 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1977976 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 412320 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 452160 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 139008 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 114720
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 30 | 218880 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 13199
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 262 | 2679709 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 380988 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 2039046
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 470400
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 417764 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 163 | 744363
| Chattogram area Total |  |  |  | 2382 | 985 | 14169469
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 203 | 4981000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 8132800 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 315 | 7741000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 40 | 848736 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 189 | 4516363
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 968102 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 1078909
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 801152 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 68 | 917280 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 420480 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 6 | 164340 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 118 | 3074880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 0 | 283600 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 424540 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 352260 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 813120 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 870480 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 95 | 1131840 | Fuel shortage
| Cumilla Area Total |  |  |  | 3151 | 1739 | 37520882
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 84 | 1534080 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 383652 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14650
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 87 | 1334400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 89 | 1066800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 362340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 236400 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 291 | 4932322
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1009000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 635400 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1252800
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 1160568
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 3 | 64992 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1397088
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1834560
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 202 | 5139060
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 163000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 354336 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6897500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 390 | 9393000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252900
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 375 | 9033400
| Sylhet Area Total |  |  |  | 2427 | 1615 | 38587604
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 819 | 21655272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 81 | 1106880 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 31 | 435840 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 80 | 1433344 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 354375 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 627360 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 1773072
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 522720
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1203 | 27908863
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 60768 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 31 | 623532 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 178 | 4209374 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 30433600
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 962400
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 307 | 6436400
| Barisal Area Total |  |  |  | 2265 | 1926 | 42726074
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 570992 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 496577 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 21 | 550960 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 932528 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 616956 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 164 | 4333618 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 139 | 3761209 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 351 | 9037745 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 743170 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 456720
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 196056 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 25430 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 80 | 1583792 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 801696 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 825984 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 22620
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 404 | 10674545 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1478 | 35630598
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1736290
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 6256100
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 794294 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 58597
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 787200
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 231713
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1296700
| Rangpur Area Total |  |  |  | 750 | 499 | 11160894
| Total |  |  |  | 22566 | 12349 | 264891168
| Eastern Grid Total |  |  |  | 14421 | 7243 | 147464739
| Western Grid Total |  |  |  | 8145 | 5106 | 117426429
| National Grid Total |  |  |  | 22566 | 12349 | 264891168
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-05-13
| (a) ENTIRE EASTERN GRID : |  | 7621.45 | MW | (b) ENTIRE WESTERN GRID : |  | 4050.2 | MW
| i) Dhaka area |  | 4290.75 | MW | i) Khulna area |  | 1697.6 | MW
| ii) Chittagong area |  | 938.7 | MW | ii) Rajshahi area |  | 1199.2 | MW
| iii) Comilla area |  | 1011 | MW | iii) Barisal area |  | 430.4 | MW
| iv) Mymensingh area |  | 932 | MW | iv) Rangpur area |  | 723 | MW
| v) Sylhet area |  | 449 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11671.65 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 3 | 14:00 | Chhatak | 27 | 00:00 | Kamrangirchar | 47 | 00:00 | Natore | 114 | 21:00 | Shitalakhya | 98 | 19:00
2 | AKSML | 7 | 02:00 | Chowmuhani | 170 | 21:00 | Kaptai | 4 | 18:00 | Nawabganj | 37.6 | 22:00 | Sholosohor | 30 | 22:00
3 | Aftabnagar | 50 | 21:00 | Chuadanga | 111 | 20:00 | Kazla | 89 | 00:00 | Netrakona | 113 | 21:00 | Shyampur | 156 | 06:00
4 | Agargaon | 81 | 00:00 | Coxsbazar | 110 | 19:30 | Keranigonj | 68 | 20:00 | New | 73.4 | 22:00 | Siddhirganj | 104 | 00:00
5 | Agrabad | 56 | 18:00 | Cumilla(N) | 150 | 21:00 | Khagrachori | 28 | 22:00 | Niamatpur | 80 | 22:00 | Sirajganj | 93 | 21:00
6 | Amnura | 56 | 00:00 | Cumilla(S) | 142 | 12:00 | Khulna | 104 | 20:00 | Noapara | 46 | 19:00 | Sonargaon | 82 | 20:00
7 | Ashuganj | 72 | 00:00 | Daudkandi | 114 | 00:00 | Khulshi | 119 | 18:00 | PHP | 3 | 10:00 | Sreemongol | 65 | 00:00
8 | BIPTC | N/A | N/A | Dhaka | 30 | 13:00 | Kishoreganj | 124 | 18:30 | Pabna | 95 | 20:00 | Sreepur | 46 | 14:00
9 | BSRM | 5 | 11:00 | Dhamrai | 96 | 18:30 | Kodda | 252 | 18:30 | Palashbari | 112 | 13:00 | Srinagar | 39.15 | 05:00
10 | Bagerhat | 102 | 20:00 | Dhanmondi | 128 | 12:00 | Kulaura | 42 | 00:00 | Panchagarh | 41 | 03:00 | Sunamganj | 51 | 00:00
11 | Bakulia | 86 | 00:00 | Dohazari | 72 | 20:00 | Kurigram | 53 | 21:00 | Patuakhali | 104 | 22:00 | Sylhet | 151 | 20:00
12 | Banani | 58 | 15:00 | Faridpur | 159 | 20:00 | Kushtia | 148 | 19:30 | Payra | 18 | 00:00 | TK | 26 | 22:00
13 | Bangabhaban | 11 | 11:00 | Fatullah | 63 | 12:00 | Lalbag | 60 | 00:00 | Postogola | 60 | 00:00 | Tangail | 191 | 19:30
14 | Barapukuria | 59 | 19:00 | Fenchuganj | 46 | 00:00 | Lalmonirhat | 38 | 22:00 | Purbachal | 22 | 21:00 | Thakurgaon | 84 | 22:00
15 | Barguna | 20 | 21:00 | Feni | 98 | 00:00 | Madanganj | 46 | 18:30 | Purbasadipur | 102 | 05:00 | Tongi | 101 | 20:00
16 | Barishal | 106 | 20:00 | GPH | 20 | 23:00 | Madaripur | 108 | 19:00 | Rahanpur_I | 0 | 00:00 | Ullon | 46 | 00:00
17 | Barishal-230 | 94 | 22:00 | Ghorashal | 139 | 01:00 | Madartek | 94 | 00:00 | Rahim | 52 | 18:30 | Uttara | 65 | 00:00
18 | Baroaulia | 59 | 23:00 | Goalpara | 38 | 19:00 | Madunaghat | 52 | 21:00 | Rajbari | 70 | 20:00 | UttaraNew | 53 | 00:00
19 | Baroirhat | 56 | 22:00 | Gollamari | 48 | 00:00 | Magura | 62 | 19:30 | Rajendrapur | 90 | 19:00 | Zigatola | 78 | 00:00
20 | Bashundhara | 164 | 00:00 | Gopalganj | 105.6 | 21:00 | Mahasthangarh | 60 | 03:00 | Rajshahi | 160 | 20:00
21 | BashundharaCement | 6 | 10:00 | Gulshan | 58 | 19:00 | Manikganj | 85 | 20:00 | Rajshahi-230 | 35 | 22:00
22 | Beanibazar | 62 | 00:00 | Halishahar | 126 | 10:00 | Maniknagar | 80 | 13:00 | Ramganj | 88 | 00:00
23 | Benapole | 64 | 19:30 | HaripurSBU | 132 | 05:00 | Matarbari | 39 | 20:00 | Rampur | 27 | 03:00
24 | Bhaluka | 130 | 21:00 | Hasnabad | 106 | 19:00 | Matuail | 61 | 00:00 | Rangamati | 12 | 21:00
25 | Bhandaria | 51 | 21:00 | Hathazari | 72 | 21:00 | Millgate | 94 | 15:00 | Rangpur | 104 | 22:00
26 | Bhangura | 34 | 10:00 | Ishurdi | 56 | 00:00 | Mirpur | 151 | 00:00 | Ruppur | 4.2 | 15:00
27 | Bheramara(GK) | 64 | 20:00 | Jaldhaka | 56 | 19:00 | Mirsorai | 5.5 | 19:30 | SSM | 16 | 14:00
28 | Bhulta | 202 | 12:00 | Jamalpur | 117 | 18:30 | Mithapukur | 34 | 19:00 | Saidpur | 93 | 11:00
29 | Bog-Sherpur | 54 | 13:00 | Jashore | 138 | 20:00 | Modern | 0 | 00:00 | Satkhira | 125 | 20:00
30 | Bogura | 138 | 12:00 | Jhenaidah | 130 | 19:30 | Mogbazar | 111 | 00:00 | Satmasjid | 115 | 01:00
31 | Borhanuddin | 54 | 22:00 | Joydebpur | 179 | 11:00 | Mongla | 26 | 09:00 | Savar | 151 | 20:00
32 | Brahmanbaria | 148 | 00:00 | Joypurhat | 50 | 19:00 | Motijheel | 40 | 20:00 | Shahjadpur | 82 | 21:00
33 | Cantonment | 132 | 00:00 | Juldah | 24 | 00:00 | Munshiganj | 81 | 21:00 | Shahjibazar | 95 | 00:00
34 | Chandpur | 64 | 00:00 | KSRM | 70 | 18:00 | Mymensingh | 180 | 21:00 | Shahmirpur | 40 | 15:00
35 | Chandraghona | 26 | 18:30 | Kabirpur | 237 | 21:00 | Naogaon | 112 | 21:00 | Shariatpur | 78 | 21:00
36 | Chapai | 61 | 19:00 | Kachua | 67 | 00:00 | Narail | 57 | 20:00 | Sherpur | 104 | 19:30
37 | Charsaidpur | 41 | 00:00 | Kallyanpur | 105 | 00:00 | Narinda | 62 | 17:00 | Shikalbaha | 26 | 03:00
38 | Chauddagram | 54 | 00:00 | Kalurghat | 32 | 11:00 | Narshingdi | 127 | 21:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-05-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 402 | 18:00 | 389 | 12:00 | Kaliakoir | 394 | 19:00 | 385 | 14:00
| Bhulta | 390 | 19:00 | 377 | 12:00 | Madunaghat_I | 418 | 19:30 | 241 | 20:00
| Bibiana | 408 | 00:00 | 397 | 08:00 | Payra | 412 | 00:00 | 407 | 06:00
| BIPTC | 399 | 10:00 | 387 | 12:00 | Rahanpur_I | 421 | 16:00 | 415 | 02:00
| Gopalganj | 406 | 00:00 | 392 | 13:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 233 | 20:00 | 225 | 12:00 | Hathazari | 243 | 20:00 | 206 | 08:00
| AKSML | 242 | 21:00 | 212 | 06:00 | Ishurdi | 234 | 18:00 | 220 | 15:00
| Aminbazar | 236 | 19:00 | 227 | 16:00 | Jhenaidah | 248 | 19:30 | 218 | 13:00
| Ashuganj | 239 | 19:30 | 230 | 07:00 | Kaliakoir | 235 | 19:00 | 227 | 14:00
| Baghabari | 232 | 23:00 | 226 | 06:00 | Keranigonj | 233 | 20:00 | 225 | 12:00
| Barapukuria | 224 | 23:00 | 216 | 05:00 | Khulna(S) | 238 | 00:00 | 224 | 13:00
| Barishal | 235 | 18:00 | 227 | 23:00 | Madunaghat_I | 243 | 20:00 | 202 | 08:00
| Bheramara | 232 | 18:00 | 221 | 03:00 | Maniknagar | 231 | 00:00 | 224 | 12:00
| Bhulta | 234 | 22:00 | 226 | 12:00 | Meghnaghat | 236 | 21:00 | 228 | 11:00
| Bibiana | 240 | 00:00 | 232 | 04:00 | Mirsorai | 240 | 19:30 | 210 | 08:00
| BIPTC | 234 | 18:00 | 222 | 03:00 | Rajshahi | 233 | 00:00 | 224 | 12:00
| Bogura | 229 | 08:00 | 222 | 05:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 236 | 00:00 | 228 | 03:00 | Rampura | 232 | 19:00 | 223 | 12:00
| BSRM | 243 | 21:00 | 206 | 08:00 | Shikalbaha | 242 | 19:30 | 211 | 08:00
| Cumilla(N) | 236 | 19:30 | 222 | 08:00 | Shyampur | 233 | 21:00 | 225 | 12:00
| Fenchuganj | 242 | 10:00 | 237 | 12:00 | Siddhirganj | 234 | 19:00 | 227 | 10:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 239 | 18:00 | 234 | 04:00
| GPH | 243 | 21:00 | 212 | 07:00 | Sreepur | 230 | 00:00 | 230 | 00:00
| Haripur | 231 | 00:00 | 223 | 12:00 | Tongi | 233 | 21:00 | 221 | 13:00
| Hasnabad | 235 | 21:00 | 225 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 02:00 | 132 | 12:00 | Lalbag | 140 | 19:30 | 135 | 07:00
| Agargaon | 133 | 09:00 | 129 | 14:00 | Lalmonirhat | 131 | 08:00 | 124 | 05:00
| Agrabad | 140 | 19:30 | 116 | 08:00 | Madanganj | 136 | 20:00 | 129 | 11:00
| AKS | 137 | 19:00 | 124 | 06:00 | Madaripur | 131 | 00:00 | 125 | 14:00
| Aminbazar | 133 | 18:30 | 128 | 12:00 | Madartek | 138 | 20:00 | 133 | 12:00
| Amnura | 140 | 00:00 | 128 | 01:00 | Madunaghat | 141 | 19:30 | 124 | 08:00
| Ashuganj | 139 | 19:30 | 135 | 01:00 | Magura | 135 | 00:00 | 124 | 19:30
| Bagerhat | 137 | 00:00 | 125 | 13:00 | Mahasthangarh | 135 | 23:00 | 128 | 03:00
| Bakulia | 141 | 21:00 | 118 | 08:00 | Manikganj | 138 | 18:00 | 129 | 07:00
| Banani | 137 | 19:00 | 133 | 11:00 | Maniknagar | 134 | 19:00 | 129 | 12:00
| Bangabhaban | 134 | 19:00 | 129 | 12:00 | Matarbari | 134 | 09:00 | 111 | 08:00
| Barapukuria | 139 | 23:00 | 132 | 04:00 | Matuail | 135.2 | 22:00 | 130 | 13:00
| Barguna | 138 | 09:00 | 131 | 00:00 | Millgate | 136 | 19:00 | 128 | 14:00
| Barishal | 137 | 08:00 | 123 | 23:00 | Mirpur | 132 | 20:00 | 126 | 06:00
| Barishal-230 | 132 | 00:00 | 124 | 19:00 | Mithapukur | 134 | 23:00 | 126 | 03:00
| Baroaulia | 141 | 21:00 | 124 | 06:00 | Modern | 141 | 19:00 | 123 | 06:00
| Baroirhat | 137 | 19:30 | 117 | 08:00 | Mogbazar | 139 | 20:00 | 134 | 13:00
| Bashundhara | 136 | 19:00 | 128 | 13:00 | Mongla | 137 | 00:00 | 126 | 19:30
| BashundharaCement | 136 | 20:00 | 129 | 11:00 | Motijheel | 134 | 19:00 | 129 | 12:00
| Beanibazar | 131 | 07:00 | 127 | 00:00 | Munshiganj | 135 | 19:30 | 129 | 14:00
| Benapole | 133 | 00:00 | 122 | 13:00 | Mymensingh | 134 | 10:00 | 108 | 13:00
| Bhaluka | 130 | 09:00 | 116 | 16:00 | Naogaon | 132 | 18:00 | 125 | 03:00
| Bhandaria | 138 | 10:00 | 126 | 03:00 | Narail | 132 | 02:00 | 124 | 19:00
| Bhangura | 136 | 00:00 | 132 | 11:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 132 | 18:00 | 126 | 03:00 | Narshingdi | 132 | 19:00 | 125 | 11:00
| Bheramara(GK) | 132 | 00:00 | 126 | 12:00 | Natore | 133 | 17:00 | 127 | 03:00
| Bhulta | 128 | 03:00 | 121 | 12:00 | Nawabganj | 140 | 19:30 | 135 | 06:00
| Bog-Sherpur | 135 | 00:00 | 130 | 05:00 | Netrakona | 133 | 00:00 | 119 | 17:00
| Bogura | 136 | 17:00 | 130 | 02:00 | New | 136 | 18:30 | 128 | 13:00
| Bogura-230 | 137 | 18:00 | 130 | 05:00 | Niamatpur | 130 | 14:00 | 124 | 13:00
| Brahmanbaria | 135 | 19:30 | 130 | 01:00 | Noapara | 139 | 00:00 | 127 | 13:00
| Cantonment | 132 | 00:00 | 129 | 12:00 | Pabna | 133 | 23:00 | 127 | 13:00
| Chandpur | 139 | 19:30 | 116 | 06:00 | Palashbari | 132 | 23:00 | 125 | 02:00
| Chandraghona | 141 | 19:30 | 126 | 06:00 | Panchagarh | 140 | 19:00 | 123 | 03:00
| Chapai | 134 | 14:00 | 131 | 00:00 | Patuakhali | 139 | 22:00 | 134 | 06:00
| Charsaidpur | 136 | 20:00 | 130 | 07:00 | Payra | 139 | 09:00 | 137 | 03:00
| Chauddagram | 134 | 19:00 | 117 | 07:00 | PHP | 135 | 19:00 | 114 | 06:00
| Chhatak | 132 | 07:00 | 127 | 00:00 | Postogola | 135 | 20:00 | 130 | 07:00
| Chowmuhani | 135 | 19:00 | 112 | 06:00 | Purbachal | 136 | 01:00 | 128 | 14:00
| Chuadanga | 130 | 00:00 | 116 | 19:30 | Purbasadipur | 136 | 19:00 | 121 | 05:00
| Coxsbazar | 132 | 00:00 | 115 | 08:00 | Rahim | 136 | 20:00 | 131 | 11:00
| Cumilla(N) | 137 | 19:00 | 126 | 06:00 | Rajbari | 128 | 00:00 | 122 | 19:00
| Cumilla(S) | 136 | 19:30 | 122 | 06:00 | Rajendrapur | 138 | 19:30 | 131 | 06:00
| Daudkandi | 135 | 19:00 | 126 | 06:00 | Rajshahi | 134 | 18:00 | 128 | 04:00
| Dhaka | 138 | 19:00 | 133 | 13:00 | Rajshahi-230 | 134 | 00:00 | 128 | 05:00
| Dhamrai | 160 | 13:00 | 130 | 12:00 | Ramganj | 135 | 19:00 | 112 | 06:00
| Dhanmondi | 135 | 22:00 | 129 | 12:00 | Rampur | 140 | 20:00 | 121 | 06:00
| Dohazari | 140 | 00:00 | 121 | 07:00 | Rampura | 138 | 19:00 | 132 | 12:00
| Faridpur | 128 | 00:00 | 123 | 15:00 | Rangamati | 140 | 20:00 | 117 | 08:00
| Fatullah | 137 | 20:00 | 131 | 07:00 | Rangpur | 133 | 14:00 | 127 | 05:00
| Fenchuganj | 137 | 19:30 | 135 | 11:00 | Ruppur | 134 | 00:00 | 128 | 12:00
| Feni | 136 | 19:30 | 116 | 06:00 | Saidpur | 135 | 19:00 | 126 | 04:00
| Ghorashal | 140 | 22:00 | 136 | 11:00 | Satkhira | 136 | 18:00 | 119 | 21:00
| Goalpara | 141 | 00:00 | 130 | 13:00 | Satmasjid | 133 | 18:00 | 129 | 06:00
| Gollamari | 132 | 00:00 | 124 | 13:00 | Savar | 134 | 20:00 | 127 | 06:00
| Gopalganj | 134 | 00:00 | 126 | 13:00 | Shahjadpur | 139 | 00:00 | 134 | 03:00
| Gopalganj-400 | 130 | 00:00 | 125 | 13:00 | Shahjibazar | 137 | 10:00 | 132 | 02:00
| Gulshan | 138 | 22:00 | 133 | 11:00 | Shahmirpur | 140 | 19:30 | 117 | 07:00
| Halishahar | 141 | 21:00 | 117 | 08:00 | Shariatpur | 130 | 00:00 | 121 | 23:00
| Haripur | 136 | 20:00 | 131 | 11:00 | Sherpur | 129 | 08:00 | 117 | 12:00
| HaripurSBU | 136 | 20:00 | 131 | 11:00 | Shikalbaha | 143 | 21:00 | 118 | 08:00
| Hasnabad | 135 | 20:00 | 129 | 12:00 | Shikalbaha-230 | 140 | 00:00 | 123 | 08:00
| Hathazari | 142 | 20:00 | 121 | 8:00 | Shitalakhya | 136 | 20:00 | 130 | 11:00
| Ishurdi | 134 | 18:00 | 129 | 03:00 | Sholosohor | 140 | 21:00 | 117 | 08:00
| Jaldhaka | 134 | 19:00 | 124 | 05:00 | Shyampur | 135 | 19:00 | 130 | 06:00
| Jamalpur | 131 | 00:00 | 119 | 15:00 | Shyampur-230 | 136 | 19:30 | 131 | 06:00
| Jashore | 132 | 00:00 | 124 | 13:00 | Siddhirganj | 135 | 19:00 | 130 | 12:00
| Jhenaidah | 136 | 00:00 | 126 | 13:00 | Sirajganj | 135 | 00:00 | 130 | 12:00
| Jhenaidah-230 | 135 | 00:00 | 126 | 19:30 | Sonargaon | 135 | 19:30 | 124 | 12:00
| Joydebpur | 141 | 00:00 | 134 | 11:00 | Sreemongol | 134 | 07:00 | 131 | 01:00
| Joypurhat | 131 | 08:00 | 126 | 11:00 | Sreepur | 130 | 00:00 | 130 | 00:00
| Juldah | 140 | 21:00 | 124 | 06:00 | Srinagar | 140 | 20:00 | 134 | 11:00
| Kabirpur | 139 | 00:00 | 126 | 13:00 | SSM | 145 | 21:00 | 129 | 06:00
| Kachua | 136 | 19:00 | 117 | 06:00 | Sunamganj | 130 | 09:00 | 124 | 00:00
| Kaliakoir | 142 | 19:30 | 133 | 14:00 | Sylhet | 132 | 07:00 | 131 | 00:00
| Kallyanpur | 135 | 00:00 | 127 | 02:00 | Tangail | 134 | 10:00 | 125 | 06:00
| Kalurghat | 140 | 19:30 | 121 | 08:00 | Thakurgaon | 136 | 19:00 | 121 | 03:00
| Kamrangirchar | 130 | 09:00 | 125 | 05:00 | TK | 141 | 20:00 | 126 | 06:00
| Kaptai | 138 | 00:00 | 135 | 01:00 | Tongi | 136 | 18:30 | 129 | 00:00
| Kazla | 134 | 22:00 | 128 | 13:00 | Ullon | 138 | 19:00 | 133 | 13:00
| Keranigonj | 140 | 20:00 | 135 | 07:00 | Uttara | 132 | 20:00 | 127 | 11:00
| Khagrachori | 140 | 20:00 | 117 | 08:00 | UttaraNew | 135 | 20:00 | 125 | 23:00
| Khulna | 140 | 00:00 | 129 | 06:00 | Zigatola | 140 | 19:30 | 135 | 07:00
| Khulna(S) | 140 | 00:00 | 131 | 06:00
| Khulshi | 140 | 21:00 | 115 | 08:00
| Kishoreganj | 130 | 08:00 | 118 | 19:00
| Kodda | 141 | 19:00 | 131 | 06:00
| KSRM | 141 | 21:00 | 118 | 08:00
| Kulaura | 136 | 08:00 | 134 | 00:00
| Kurigram | 133 | 14:00 | 125 | 03:00
| Kushtia | 132 | 00:00 | 124 | 19:30
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-05-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 676 | 5936 | 4701 | 10637 |  |  |  | QF-LDC-11
0:30 | 668 | 6222.5 | 4656.5 | 10879 | Date: | 2023-05-13
1:00 | 660 | 6509 | 4612 | 11121
1:30 | 670 | 6491.5 | 4657 | 11148.5
2:00 | 680 | 6474 | 4702 | 11176
2:30 | 685 | 6385.5 | 4725.5 | 11111 | [5 empty] | Gen. at Eve. Peak | 12349 | 12349 MW (21:00 )
3:00 | 690 | 6297 | 4749 | 11046 | [6 empty] | 21:00
3:30 | 705 | 6237 | 4772.5 | 11009.5 | [5 empty] | Gen. at Day Peak | 10749 | 10749 MW (12:00 )
4:00 | 720 | 6177 | 4796 | 10973 | [6 empty] | 12:00
4:30 | 740 | 6058.5 | 4797.5 | 10856 | [5 empty] | Highest Generation | 12349
5:00 | 760 | 5940 | 4799 | 10739 | [6 empty] | 21:00
5:30 | 865 | 5804 | 4787 | 10591
6:00 | 970 | 5668 | 4775 | 10443
6:30 | 935 | 5526.5 | 4781.5 | 10308
7:00 | 900 | 5385 | 4788 | 10173
7:30 | 915 | 5305 | 4752 | 10057
8:00 | 930 | 5225 | 4716 | 9941
8:30 | 945 | 5197 | 4656.5 | 9853.5
9:00 | 960 | 5169 | 4597 | 9766
9:30 | 950 | 5232.5 | 4655.5 | 9888
10:00 | 940 | 5296 | 4714 | 10010
10:30 | 980 | 5479 | 4704 | 10183
11:00 | 1020 | 5662 | 4694 | 10356
11:30 | 1030 | 5775 | 4777.5 | 10552.5
12:00 | 1040 | 5888 | 4861 | 10749
12:30 | 950 | 5985.5 | 4794.5 | 10780
13:00 | 860 | 6083 | 4728 | 10811
13:30 | 920 | 5975 | 4741.5 | 10716.5
14:00 | 980 | 5867 | 4755 | 10622
14:30 | 970 | 5809 | 4724 | 10533
15:00 | 960 | 5751 | 4693 | 10444
15:30 | 935 | 5860 | 4665.5 | 10525.5
16:00 | 910 | 5969 | 4638 | 10607
16:30 | 915 | 5912 | 4632 | 10544
17:00 | 920 | 5855 | 4626 | 10481
17:30 | 835 | 5955.5 | 4612 | 10567.5
18:00 | 750 | 6056 | 4598 | 10654
18:30 | 643 | 6499 | 4678 | 11177
19:00 | 536 | 6942 | 4758 | 11700
19:30 | 480 | 7029 | 5064 | 12093
20:00 | 404 | 7077 | 5044 | 12121 |  |  |  | Executive Engineer
20:30 | 412 | 7160 | 5075 | 12235 |  |  |  | Network Operation Division
21:00 | 420 | 7243 | 5106 | 12349
21:30 | 355 | 7075 | 5085.5 | 12160.5
22:00 | 290 | 6907 | 5065 | 11972 |  |  |  |  | Page 6 of 7
22:30 | 500 | 6644 | 4987.5 | 11631.5
23:00 | 710 | 6381 | 4910 | 11291
23:30 | 693 | 6158.5 | 4805.5 | 10964
24:00 | 676 | 5936 | 4701 | 10637
12349 MW (21:00 )
10749 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-05-13 |  | Energy |  | 264891168
[13 empty] | 2023-05-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3352 | 820 | 1298 | 456 | 1614 | 2289 | 0 | 0 | 672 | 136 | 0 | 0
0:30 | 3482 | 823.5 | 1679.5 | 383.5 | 1527 | 2287 | 0 | 0 | 568.5 | 128 | 0 | 897.2225 |  | Date: | 43597
1:00 | 3612 | 827 | 2061 | 311 | 1440 | 2285 | 0 | 0 | 465 | 120 | 0 | 1794.445
1:30 | 3660.5 | 827 | 2016.5 | 337 | 1424 | 2297 | 0 | 0 | 461.5 | 125 | 0 | 1720.4325 | [8 empty] | Total Energy | 264.8912 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 264.891 MKWHr Energy Not Served 43.999 MKWHr Energy Requirement 308.890 MKWHr
2:00 | 3709 | 827 | 1972 | 363 | 1408 | 2309 | 0 | 0 | 458 | 130 | 0 | 1646.42 | [8 empty] | Energy not Served | 43.9989
2:30 | 3686.5 | 874.5 | 1933 | 365 | 1352 | 2319 | 0 | 0 | 454 | 127 | 0 | 1660.745 | [8 empty] | Energy Requirement | 308.8901
3:00 | 3664 | 922 | 1894 | 367 | 1296 | 2329 | 0 | 0 | 450 | 124 | 0 | 1675.07
3:30 | 3600.5 | 921.5 | 1906.5 | 412 | 1237.5 | 2354.5 | 0 | 0 | 451 | 126 | 0 | 1662.1775 | [7 empty] | Shortage
4:00 | 3537 | 921 | 1919 | 457 | 1179 | 2380 | 0 | 0 | 452 | 128 | 0 | 1649.285
4:30 | 3533 | 921.5 | 1905.5 | 366 | 1150 | 2393.5 | 0 | 0 | 455.5 | 131 | 0 | 1737.145
5:00 | 3529 | 922 | 1892 | 275 | 1121 | 2407 | 0 | 0 | 459 | 134 | 0 | 1825.005
5:30 | 3546 | 922 | 1826 | 187.5 | 1133 | 2372.5 | 0 | 0 | 460 | 134 | 10 | 1632.095
6:00 | 3563 | 922 | 1760 | 100 | 1145 | 2338 | 0 | 0 | 461 | 134 | 20 | 1439.185
6:30 | 3516.5 | 922 | 1676.5 | 75 | 1145 | 2334 | 0 | 0 | 455.5 | 134 | 49.5 | 1353.235 | [6 empty] | Coal
7:00 | 3470 | 922 | 1593 | 50 | 1145 | 2330 | 0 | 0 | 450 | 134 | 79 | 1267.285
7:30 | 3438.5 | 921.5 | 1561 | 50 | 1138.5 | 2252.5 | 0 | 0 | 449.5 | 133 | 112.5 | 1521.315 | [5 empty] | Oil
8:00 | 3407 | 921 | 1529 | 50 | 1132 | 2175 | 0 | 0 | 449 | 132 | 146 | 1775.345
8:30 | 3350 | 921.5 | 1505 | 50 | 1141 | 2120.5 | 12.5 | 0 | 430.5 | 125 | 197.5 | 1906.6575
9:00 | 3293 | 922 | 1481 | 50 | 1150 | 2066 | 25 | 0 | 412 | 118 | 249 | 2037.97
9:30 | 3282 | 922 | 1495 | 50 | 1212.5 | 2077.5 | 27.5 | 0 | 422.5 | 125 | 274 | 2016.96
10:00 | 3271 | 922 | 1509 | 50 | 1275 | 2089 | 30 | 0 | 433 | 132 | 299 | 1995.95
10:30 | 3328 | 922 | 1491 | 122 | 1345.5 | 2056 | 30 | 0 | 448 | 130 | 310.5 | 1973.985
11:00 | 3385 | 922 | 1473 | 194 | 1416 | 2023 | 30 | 0 | 463 | 128 | 322 | 1952.02
11:30 | 3361.5 | 922.5 | 1477 | 282.5 | 1433 | 2070 | 30 | 0 | 483.5 | 135 | 357.5 | 1955.51
12:00 | 3338 | 923 | 1481 | 371 | 1450 | 2117 | 30 | 0 | 504 | 142 | 393 | 1959
12:30 | 3341.5 | 922 | 1463.5 | 417 | 1502.5 | 2098 | 30 | 0 | 501 | 139 | 365.5 | 2019.495
13:00 | 3345 | 921 | 1446 | 463 | 1555 | 2079 | 30 | 0 | 498 | 136 | 338 | 2079.99
13:30 | 3345 | 921 | 1446 | 463 | 1555 | 2079 | 30 | 0 | 498 | 136 | 338 | 2079.99
14:00 | 3345 | 921 | 1446 | 463 | 1555 | 2079 | 30 | 0 | 498 | 136 | 338 | 2079.99
14:30 | 3308 | 921.5 | 1415.5 | 327 | 1583 | 2089.5 | 30 | 0 | 532.5 | 136 | 284.5 | 2117.235
15:00 | 3271 | 922 | 1385 | 191 | 1611 | 2100 | 30 | 0 | 567 | 136 | 231 | 2154.48
15:30 | 3249 | 921.5 | 1368.5 | 326 | 1610 | 2134 | 30 | 0 | 571.5 | 128 | 187 | 2028.8975
16:00 | 3227 | 921 | 1352 | 461 | 1609 | 2168 | 30 | 0 | 576 | 120 | 143 | 1903.315
16:30 | 3215.5 | 921 | 1341.5 | 384 | 1658.5 | 2187.5 | 30 | 0 | 580 | 121 | 105 | 1891.855
17:00 | 3204 | 921 | 1331 | 307 | 1708 | 2207 | 30 | 0 | 584 | 122 | 67 | 1880.395 | [10 empty] | 472
17:30 | 3200 | 920.5 | 1332.5 | 268.5 | 1837.5 | 2203.5 | 30 | 0 | 610.5 | 124 | 40.5 | 1964.9125 | [10 empty] | 100
18:00 | 3196 | 920 | 1334 | 230 | 1967 | 2200 | 30 | 0 | 637 | 126 | 14 | 2049.43 | [10 empty] | 20
18:30 | 3218 | 920.5 | 1333 | 303 | 2389 | 2199 | 30 | 0 | 653.5 | 124 | 7 | 2051.34 | [10 empty] | 592
19:00 | 3240 | 921 | 1332 | 376 | 2811 | 2198 | 30 | 0 | 670 | 122 | 0 | 2053.25
19:30 | 3225 | 921 | 1367 | 376 | 3048 | 2284 | 30 | 0 | 712 | 130 | 0 | 2067.0975
20:00 | 3246 | 819 | 1356 | 377 | 3103 | 2290 | 30 | 0 | 788 | 112 | 0 | 2080.945
20:30 | 3281 | 819 | 1353.5 | 422.5 | 3123.5 | 2290 | 30 | 0 | 800.5 | 115 | 0 | 2019.9725
21:00 | 3316 | 819 | 1351 | 468 | 3144 | 2290 | 30 | 0 | 813 | 118 | 0 | 1959
21:30 | 3316 | 819 | 1339 | 465.5 | 2982 | 2289.5 | 30 | 0 | 803.5 | 116 | 0 | 1995.62
22:00 | 3316 | 819 | 1327 | 463 | 2820 | 2289 | 30 | 0 | 794 | 114 | 0 | 2032.24
22:30 | 3327.5 | 819 | 1330 | 463.5 | 2472.5 | 2289 | 15 | 0 | 792 | 123 | 0 | 2190.2925
23:00 | 3339 | 819 | 1333 | 464 | 2125 | 2289 | 0 | 0 | 790 | 132 | 0 | 2348.345
23:30 | 3345.5 | 819.5 | 1315.5 | 460 | 1869.5 | 2289 | 0 | 0 | 731 | 134 | 0 | 2636.755 |  | Max Temp. in Dhaka |  | 35.5° C
24:00 | 3352 | 820 | 1298 | 456 | 1614 | 2289 | 0 | 0 | 672 | 136 | 0 | 2925.165
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 264.891 MKWHr Energy Not Served 43.999 MKWHr Energy Requirement 308.890 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-05-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [8 empty] | 25 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 0 |  | 393780
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 20 | 25 |  |  | 0 | 19 | 25 | 25 | 25 | 25 | 20 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 525877
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 3 | 3 | 5 | 3 | 4 | 6 | 5 | 2 | 1 | 0 | [9 empty] | 36180
6 | Sikalbaha 225MW CCPP (Gas) | 20 | 0 | [24 empty] | 199169
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 75 | 84 | 84 | 84 | 84 | 74 | 68 | 84 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1977976
12 | Hathazari 100 MW peaking PP | 57 | 57 | 48 | 56 | 56 | 56 | 54 | 54 | 54 | 54 | 53 | 53 | 54 | 53 | 53 | 48 | 55 | 55 |  | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 1292832
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 42 | 51 | 51 | 51 | 56 | 78 |  | 87 | 87 | 85 | 85 | 85 | 85 | 74 | 1228618
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 38 |  | 38 | 38 | 38 | 38 | 35 | 39 | 39 | 801152
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 150 | 131 | 92 | 0 | [22 empty] | 436164
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 96 | 96 | 97 | 96 | 96 | 96 | 96 | 96 | 96 |  | 260 | 277 | 277 | 277 | 277 | 277 | 278 | 3412364
19 | Ashuganj 195MW PP (APSCL-United) | 189 | 189 | 187 | 189 | 189 | 189 | 189 | 189 | 187 | 187 | 187 | 185 | 185 | 185 | 185 | 187 | 187 | 187 |  | 187 | 187 | 189 | 189 | 189 | 199 | 189 | 4516363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 121 | 120 | 121 | 120 | 120 | 120 | 121 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 2849906
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4252500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 33 | 31 | 33 | 28 | 33 | 32 | 30 | 34 | 34 | 38 |  | 36 | 40 | 40 | 40 | 41 | 41 | 41 | 848736
33 | Ashuganj 225 MW CCPP | 209 | 210 | 210 | 211 | 211 | 208 | 211 | 212 | 208 | 209 | 204 | 204 | 201 | 201 | 201 | 202 | 204 | 207 |  | 203 | 204 | 205 | 203 | 205 | 203 | 205 | 4981000
34 | Ashuganj 450 MW CCPP(South) | 315 | 305 | 305 | 305 | 305 | 320 | 305 | 305 | 305 | 305 | 320 | 305 | 320 | 315 | 320 | 310 | 305 | 305 |  | 315 | 315 | 305 | 315 | 310 | 330 | 340 | 7741000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 345 | 310 | 310 | 310 | 310 | 320 | 310 | 325 | 325 | 320 | 310 | 310 | 305 |  | 330 | 325 | 305 | 310 | 315 | 340 | 340 | 8132800
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 368 | 403 | 399 | 356 | 350 | 350 | 351 | 344 | 329 | 347 | 351 | 370 | 358 | 331 | 311 | 287 | 269 | 259 |  | 258 | 266 | 266 | 263 | 245 | 241 | 240 | 7780350
40 | Meghnaghat 450 MW CCPP(MPL) | 360 | 330 | 300 | 310 | 300 | 260 | 235 | 200 | 130 | 130 | 130 | 130 | 130 | 120 | 120 | 105 | 90 | 85 |  | 90 | 90 | 85 | 85 | 85 | 85 | 85 | 3916000
41 | Haripur 360MW CCPP(HPL) | 324 | 264 | 234 | 275 | 264 | 228 | 203 | 193 | 199 | 200 | 208 | 213 | 203 | 187 | 167 | 157 | 145 | 138 |  | 137 | 137 | 133 | 131 | 102 | 103 | 92 | 4630000
42 | RPCL 210MW CCPP | 94 | 94 | 95 | 95 | 95 | 86 | 47 | 43 | 43 | 43 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 46 |  | 68 | 84 | 85 | 84 | 84 | 84 | 84 | 1534080
43 | Sutiakhali 50 MW Solar PP |  |  |  |  | 0 | 3 | 10 | 17 | 38 | 39 | 51 | 51 | 51 | 41 | 35 | 21 | 14 | 2 | [8 empty] | 362340
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 39 | 40 | 40 | 40 |  | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 1009000
45 | Fenchugonj CCPP Phase-2 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 635400
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 59 | 59 | 59 | 59 | 56 | 62 | 61 | 61 | 60 | 58 | 55 | 60 | 55 | 58 | 60 | 61 |  | 55 | 58 | 61 | 61 | 61 | 60 | 61 | 1397088
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 77 | 77 | 77 | 77 | 77 | 73 | 73 | 73 | 73 | 72 | 76 | 76 |  | 77 | 77 | 76 | 77 | 77 | 77 | 77 | 1834560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 202 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 209 | 206 | 203 | 203 | 202 | 202 | 200 | 198 | 198 | 198 |  | 202 | 202 | 202 | 202 | 202 | 204 | 204 | 5139060
51 | Sylhet 20 MW GTPP | [14 empty] | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 163000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 252900
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [12 empty] | 3 | 3 | 3 | 3 | 3 | 64992
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 47 | 50 | 50 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 1252800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 354336
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 280 | 275 | 275 | 265 | 270 | 270 | 280 | 280 | 270 | 285 | 285 | 290 | 290 | 295 | 295 | 300 |  | 285 | 300 | 295 | 290 | 290 | 295 | 290 | 6897500
| Bibiyana South 400 MW | 398 | 400 | 400 | 400 | 400 | 397 | 400 | 400 | 394 | 380 | 380 | 380 | 370 | 370 | 369 | 370 | 374 | 374 |  | 348 | 348 | 348 | 375 | 375 | 375 | 378 | 9033400
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 0 | [6 empty] | 10 | 17 | 35 | 35 | 45 | 55 | 55 | 55 |  | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 635575
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 10 | 11 | 236400
60 | Barabkunda 22 MW PP (Regent) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 9 | 9 | 9 | 9 | 9 | [10 empty] | 139008
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 298692
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 15 | 15 | 15 | 17 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 383652
63 | Impoprt (Tripura) | 120 | 130 | 124 | 128 | 134 | 134 | 134 | 132 | 118 | 132 | 128 | 142 | 136 | 118 | 136 | 120 | 122 | 126 |  | 122 | 130 | 112 | 118 | 114 | 132 | 136 | 3074880
64 | Malancha, Ctg. EPZ (United) | 31 | 22 | 10 | 5 | 3 | 2 | 2 | [19 empty] | 114720
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 420480
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 164340
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 13 | 7 | 6 | 0 | [6 empty] | 0 | [5 empty] | 283600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 12 | 12 | 20 | 15 | 15 | 15 | 15 | 9 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 424540
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 21 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 26 | 26 |  | 20 | 26 | 26 | 26 | 27 | 27 | 27 | 608400
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 739080
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 14 | 14 | 14 | 12 | 12 | 12 | 8 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 13 | 10 | 346000
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 529000
| Feni Lanka Power | 114 | 114 | 72 | 0 | [22 empty] | 352260
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 7 | 7 |  |  | 9 | 9 | 24 | 47 | 55 | 57 | 58 | 58 | 58 |  | 95 | 95 | 96 | 96 | 98 | 26 | 9 | 813120
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 162 | 162 | 162 | 135 | 72 | 17 | 17 | 1124640
77 | Siddhirganj 100 PP(Dutch Bangla) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 13 | 34 | 34 | 37 | 37 | 34 | 34 | 37 | 34 | 34 |  | 42 | 42 | 42 | 42 | 42 | 19 | 9 | 565440
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 33 | 33 | 37 |  | 49 | 49 | 49 | 49 | 49 | 50 | 16 | 525600
79 | Kodda 150 MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 62 | 98 | 98 | 98 | 113 | 130 | 146 | 146 | 146 |  | 146 | 146 | 146 | 146 | 148 | 148 | 148 | 2297760
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [26 empty] | 0
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2114477
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 1 | 3 | 2 | 1 | 1 | 0 | 0 | [9 empty] | 13199
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 0 |  |  | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 380988
| Karnaphuli Power Ltd. | 92 | 92 | 92 | 85 | 92 | 92 | 92 | 81 | 75 | 74 | 54 | 54 | 54 | 54 | 54 | 70 | 80 | 92 |  | 102 | 102 | 105 | 105 | 107 | 107 | 107 | 2039046
82 | Madanganj 102 PP(Summit) | 97 | 97 | 97 | 97 | 97 | 97 | 75 | 34 | 34 | 34 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 7 |  | 926634
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 4 | 7 | [12 empty] | 15000
86 | Meghnaghat CCPP ( Summit) | 148 | 151 | 149 | 128 | 127 | 90 | 0 | [19 empty] | 885260
87 | Meghnaghat 100 MW(IEL) | 9 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 9 | 8 | 9 | 8 | 8 | 15 |  | 25 | 25 | 25 | 26 | 25 | 10 | 8 | 271680
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 50 | 52 | 35 | 35 | 48 | 52 | 36 | 35 | 35 |  | 53 | 53 | 53 | 52 | 47 | 20 | 17 | 792000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 412320
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 43 | 46 | 45 | 48 | 45 | 48 | 48 | 48 |  | 48 | 48 | 48 | 49 | 49 | 49 | 49 | 1160568
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 968102
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 41 | 41 | 48 | 48 | 48 | 48 | 48 | 90 |  | 92 | 92 | 92 | 92 | 92 | 32 | 32 | 989136
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 15 | 18 | 19 | 21 | 25 | 25 | 25 | 32 |  | 35 | 39 | 39 | 40 | 9 | 41 | 6 | 432480
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 9 | 12 | 12 | 29 | 30 |  | 29 | 27 | 26 | 30 | 30 |  |  | 218880
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | [6 empty] | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 308893
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 |  | 643681
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 1 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 14650
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 17 |  |  | 260280
104 | Keranigonj 300 MW PP (APR) | 156 | 208 | 212 | 302 | 120 | 0 |  |  |  |  | 35 | 210 | 303 | 180 | 30 | 301 | 170 | 130 |  | 204 | 205 | 206 | 306 | 300 | 300 | 300 | 4131569
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 | 50 | 25 | 25 | 25 | 25 | 84 | 86 | 85 | 86 | 86 | 85 | 87 | 50 |  | 88 | 88 | 88 | 80 | 80 | 80 | 80 | 1688701
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 57 | 48 | 48 | 48 | 57 | 58 |  | 86 | 86 | 86 | 87 | 78 | 48 | 48 | 1334400
112 | Aurahati 100MW PP (Aggreko) | 75 | 75 | 75 | 75 | 75 | 50 | 25 | 25 | 25 | 25 | 75 | 75 | 75 | 74 | 75 | 75 | 50 | 50 |  | 84 | 83 | 83 | 82 | 83 | 84 | 76 | 1539404
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 34 | 35 | 34 | 71 | 88 | 88 | 98 |  | 132 | 133 | 134 | 133 | 133 | 64 | 35 | 1487808
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 452160
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 44 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 53 | 917280
117 | Ashuganj 150MW PP (Midland) | 18 | 20 | 20 | 18 | 20 | 18 | 20 | 20 | 18 | 20 | 18 | 20 | 20 | 18 | 18 | 20 | 36 | 85 |  | 137 | 137 | 142 | 145 | 143 | 60 | 18 | 1078909
118 | Bibiyana-III 400 MW CCPP | 407 | 415 | 408 | 416 | 410 | 408 | 402 | 396 | 391 | 390 | 386 | 367 | 380 | 387 | 374 | 374 | 368 | 368 |  | 395 | 378 | 367 | 390 | 390 | 391 | 390 | 9393000
| Jamalpur 115 MW PP (United) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 46 | 48 | 48 | 48 | 48 | 49 | 49 | 49 |  | 87 | 88 | 89 | 89 | 89 | 28 | 28 | 1066800
| Anwara 300 MW PP (United) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 119 |  | 257 | 262 | 262 | 262 | 123 | 87 | 87 | 2679709
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 12 | 470400
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 417764
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 19 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 870480
| Spectra Solar Plant Ltd. |  |  |  |  | 0 | 1 | 4 | 9 | 12 | 15 | 27 | 25 | 31 | 15 | 10 | 10 | 4 | 1 | [8 empty] | 147148
| Chandpur 115(Doreen) | 28 | 18 | 18 | 18 | 18 | 17 | 18 | 17 | 18 | 20 | 37 | 53 | 54 | 53 | 54 | 54 | 54 | 54 |  | 64 | 94 | 94 | 95 | 95 | 95 | 75 | 1131840
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 34 |  | 34 | 35 | 34 | 34 | 34 | 34 | 17 | 553320
| Mirsharai 150 MW (Oil) | [17 empty] | 20 |  | 43 | 80 | 130 | 163 | 163 | 163 | 40 | 744363
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6509 | 6474 | 6297 | 6177 | 5940 | 5668 | 5385 | 5225 | 5169 | 5296 | 5662 | 5888 | 6083 | 5867 | 5751 | 5969 | 5855 | 6056 |  | 6942 | 7029 | 7077 | 7243 | 6907 | 6381 | 5936 | 147464739
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 36 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 46 |  | 63 | 71 | 80 | 81 | 82 | 50 | 35 | 1106880
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 13 | 16 | 17 | 24 | 27 |  | 28 | 30 | 34 | 31 | 24 | 24 | 29 | 435840
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 627360
130 | Mongla Orion 100 MW Solar PP |  |  |  |  | 0 | 3 | 15 | 31 | 40 | 35 | 31 | 82 | 52 | 81 | 39 | 29 | 8 | 2 | [8 empty] | 522720
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 37 | 81 | 100 | 150 | 150 | 150 | 17 | 962400
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 | 16 | 16 |  |  | 60768
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 173 | 203 | 230 | 287 | 306 | 308 | 302 | 306 | 268 | 269 | 250 | 250 | 271 | 270 | 270 | 241 | 240 | 240 |  | 272 | 306 | 307 | 307 | 307 | 307 | 307 | 6436400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 85 | 180 | 180 | 180 | 180 | 180 | 180 | 174 | 174 | 174 | 178 | 178 | 178 | 178 | 178 | 177 | 177 | 178 |  | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 4209374
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 31 | 30 | 28 | 24 | 20 | 20 | 19 | 21 | 21 | 20 | 23 | 23 | 23 | 22 | 20 | 21 |  | 28 | 30 | 31 | 31 | 32 | 32 | 30 | 623532
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 354375
143 | Gopalganj 100 MW Peaking PP | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 36 | 36 | 30 | 45 | 30 | 30 | 45 | 60 | 60 | 59 |  | 63 | 70 | 85 | 80 | 76 | 76 | 76 | 1433344
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 | 50 | 50 | 50 | 15 | 15 | 15 |  | 36 | 85 | 105 | 105 | 105 | 85 | 85 | 1773072
146 | Bheramara HVDC | 827 | 827 | 922 | 921 | 922 | 922 | 922 | 921 | 922 | 922 | 922 | 923 | 921 | 923 | 922 | 921 | 921 | 920 |  | 921 | 921 | 819 | 819 | 819 | 819 | 820 | 21655272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1140 | 1040 | 1040 | 1040 | 1050 | 1060 | 1090 | 1090 | 1190 | 1190 | 1170 |  | 1190 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 30433600
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 75 | 76 | 74 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1736290
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6256100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 28 | 28 | 28 | 28 | 28 |  | 21 | 21 | 28 | 28 | 28 | 28 | 28 | 570992
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 4 | 0 | 0 | 2 | 2 | 1 | 0 | [8 empty] | 22620
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 178 | 178 | 178 | 178 | 178 | 179 | 181 | 184 | 130 | 137 | 179 | 179 | 180 | 179 | 171 | 169 | 165 | 164 |  | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 4333618
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 158 | 158 | 161 | 161 | 166 | 166 | 161 | 160 | 155 | 151 | 144 | 139 | 135 | 133 | 130 | 130 | 129 | 128 |  | 128 | 128 | 128 | 139 | 153 | 154 | 155 | 3761209
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 421 | 424 | 423 | 427 | 426 | 422 | 397 | 380 | 390 | 419 | 390 | 383 | 359 | 345 | 343 | 324 | 328 | 332 |  | 333 | 351 | 352 | 351 | 355 | 345 | 341 | 9037745
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP |  | 0 | 5 | 7 | 14 | 16 | 20 | 20 | 20 | 26 | 31 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 38 | 34 | 34 | 34 | 34 | 34 | 34 | 496577
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 19 | 18 | 18 | 17 | 17 | 17 | 17 | 19 |  | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 456720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 196056
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 550960
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 34 |  | 34 | 34 | 34 | 42 | 42 | 34 | 42 | 932528
167 | Katakhali 50 MW Peaking PP | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 40 |  | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 616956
168 | Santahar 50 MW Peaking PP | 34 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 743170
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | 8 | 8 | 8 | 8 |  |  | 25430
170 | Chapainawabganj 100 MW Peaking PP | 66 | 66 | 66 | 66 | 66 | 66 | 53 | 52 | 52 | 52 | 52 | 58 | 66 | 72 | 80 | 72 | 72 | 72 |  | 80 | 80 | 80 | 80 | 72 | 72 | 72 | 1583792
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 0 |  |  | 0 | 13 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 801696
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 |  | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 825984
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 0 |  |  | 33 | 28 | 28 | 34 | 34 | 34 | 34 | 34 | 34 | 40 | 49 |  | 49 | 49 | 49 | 49 | 48 | 49 | 34 | 794294
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 2 | 3 | 5 | 5 | 6 | 7 | 7 | 7 | 6 | 4 | 2 | 1 | [8 empty] | 58597
178 | Energypac Power Venture Thakurgaon Ltd. | [10 empty] | 17 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 56 | 115 | 115 | 115 | 75 | 55 | 0 | 787200
| Intraco Solar 30 MW |  |  |  |  | 0 | 1 | 6 | 12 | 20 | 25 | 31 | 31 | 31 | 28 | 20 | 14 | 7 | 2 | [8 empty] | 231713
| Adani Power Jharkhanda Ltd | 533 | 527 | 520 | 514 | 522 | 451 | 449 | 394 | 423 | 445 | 398 | 482 | 413 | 404 | 404 | 402 | 441 | 456 |  | 401 | 399 | 404 | 404 | 403 | 403 | 403 | 10674545
178 | Teesta Solar Limited |  |  |  |  | 0 | 11 | 41 | 68 | 126 | 167 | 166 | 184 | 156 | 141 | 115 | 61 | 31 | 6 | [8 empty] | 1296700