## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-01 | Monday
|  | Date (day): | 2023-05-01 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12614.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14950 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-04-30 | 2023-05-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 110 | 110 | 110 | 70 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 16 | 70 |  | 38 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 378 | 356 | 360 | 360 | 52
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 330 | 255 | 300 | 300 | 60
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 370 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 67 | 24 | 25 | 70 | 30 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 298 | 286 | 300 | 300 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 72 | 66 | 90 | 90 |  | 12 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 30 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 10 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 10 | 10 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 65 | 40 | 90 | 100 |  | 110 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 55 | 30 | 90 | 90 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 217 | 190 | 220 | 220 |  | 115 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 66 | 83 | 48 | 83 |  | 19 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 17 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 150 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 50 | 37 | 55 |  |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 47 | 43 | 47 |  | 33 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 25 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 32 | 32 | 32 | 32
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 16 | 49 | 41 | 49
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 145 | 45 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 149 | 50 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 105 | 105 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 50 | 45 | 54 | 70 |  | 34 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 162 | 72 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 34 | 34 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 3020 | 3023 | 3651 | 4217 | 327 | 1260
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 38 | 26 | 38 | 12 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 217 | 223 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 57 | 46 | 45 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 63 | 84 | 66 | 84 |  | 18 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 44 | 56 | 50 | 70 | 30 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 38 | 76 | 38 | 76 | 24 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 21 | 15 | 30
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 31 | 0 | 50 | 58 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 122 | 190 | 120 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 35 | 54
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 51 | 54 | 51 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 88 | 63 | 90 |  | 10 | Engine problem
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 34 | 34 | 34 | 82 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 0 | 0 | 163 | 54 | 162 | 162
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 1074 | 1280 | 1152 | 1558 | 773 | 216
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 188 | 200 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 300 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 300 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 39 | 40 | 40
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 148 | 78 | 68 | 69 | 126 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 73 | 140 | 80 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 38 | 38 | 31 | 38 |  | 14 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 100 | 120 | 17 | 150 | 50 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 7 | 7 | 7 |  | 4 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 140 | 143 | 165
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 41 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 36 | 17 | 0 | 114 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 78 | 9 | 55 | 58 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 59 | 115 | 94 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1580 | 1800 | 1514 | 1808 | 348 | 609
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 29 | 47 | 50 | 80 | 122 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 5 | 11 | 0 | 0 | 22 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 158 | 173 | 160 | 173 |  | 27 | Engine prolem
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 99 | 108 | 75 | 115
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 356 | 351 | 348.6 | 380 | 144 | 27
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 29 | 29 | 29 |  | 61 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 42 | 48 | 46 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 61 | 62
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 79 | 85 | 85
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 135 | 130 | 130 | 130 |  | 101 | ST Under S/D
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 300 | 310 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 370 | 410 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 383 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1479 | 1540 | 1554 | 1569 | 9 | 828
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 485 | 913 | 496 | 930
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 59 | 16 | 85 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 22 | 38 |  | 16 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 55 | 70 |  | 39 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 200 | 170 | 200 | 250 | 160 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 32 | 0 | 0 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 17 | 17 | 88 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 67 | 15 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 90 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 933 | 1169 | 975 | 1543 | 594 | 72
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 16 | 16 | 64
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 21 | 24 | 25 | 30 |  | 10 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 178 | 183 | 180 | 183
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 900 | 1200 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 14 | 17 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1489 | 1140 | 1438 | 1671 | 307 | 230
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 24 | 0 | 26 | 26 |  | 26 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 4 | 0 | 34 |  | 37 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 14
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 0 | 34 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 24 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 166 | 150 | 150 | 160 | 50 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 151 | 136 | 140 | 150 | 70 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 275 | 253 | 300 | 350 | 64 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 0 | 0 | 43 | 9 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 24 | 80 | 80 |  | 24 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 35 | 50 | 113
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 0 | 95 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 186 | 407 | 500 | 500 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1043 | 1114 | 1470 | 1730 | 784 | 123
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 75 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 150 | 180 | 200
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 34 | 34 | 84 | 29 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 75 | 36 | 55 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 23 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 163 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 375 | 295 | 512 | 474 | 79 | 85
| Total |  |  |  |  | 23332 | 22566 | 11349 | 11712 | 12614.6 | 14950 | 3365 | 3450
A. |  | 2023-04-30 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 12171 | MW at | 15:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 8596 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11801 | MW
3 | Day peak Generation : |  |  | 11349 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11282.4 | MW
4 | Evening peak Generation : |  |  | 11712 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 85 | MW
5 | Total Energy Generation : |  | 254.6954 | MKWHr | By Solar | 2.6032 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 149.8385 | MKWHr |  | By Oil: | 47.803 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 37.1533 | MKWHr |  | By Hydro: | 0.308 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3365 | MW | Dhaka | 4280.8 | 4280.8 |  | 0 |  | 18:00 |  | 85
|  |  | For Plants S/D or M/C prob = |  |  | 3450 | MW | Chittagong | 1307.6 | 1307.6 |  | 0 |  | 19:00 |  | 111.735
|  |  | Total = |  |  | 6815 | MW | Khulna | 1110.2 | 1110.2 |  | 0 |  | 19:30 |  | 84.995
7 | Total Gas Supplied : |  |  | 1121.26 | MMCFD |  |  | Rajshahi | 546.8 | 546.8 |  | 0 |  | 20:00 |  | 84.995
8 | Fuel Cost : | i) Gas : | Taka | 173027212.06 | ii) Oil : | Taka | 608629089.91 | Comilla | 1310 | 1290 |  | 20 |  | 21:00 |  | 54
|  | iii) Coal : | Taka | 281063639.84 | Total | Taka | 1062719941.81 | Mymensingh | 1033 | 978 |  | 55 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 528 | 518 |  | 10 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 612 | MW (E to W) at | 19:30 | hrs | Barisal | 413 | 413 |  | 0 |  | 24:00 |  | 115
| iii) Maximum : |  |  | -150 | MW at | 6:00 | hrs | Rangpur | 753 | 753 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 11282.4 | 11197.4 |  | 85
B. |  | 2023-05-01 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14950 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
4 | Reserve(Generation end) |  |  |  | 3450 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 240.6538 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8365 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.9367 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0528 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.15 |  | (b) Today: | 75.13 |  | (c) Rule Curve: |  | 82.2
.

## YesterdayGen
2023-04-30 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 180 | 180 | 0 | 75 | 0 | 399 | 346 |  | 0 | 450 | 265 | 4 | 0 | 0 | 170 | 0 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 20 | 25 | 25 | 16 | 0 | 0 | 0 | 120 | 0 | 8 | 227 | 0 | 0 | 0 |  | 6 | 0 | 84 | 55 | 25 | 6 | 10 | 38 | 0 | 0 | 0 | 310 | 300 | 217 | 150 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 48 | 18 | 7 | 33 | 20 | 126 | 75 | 0 | 19 | 0 | 0 | 31 | 50 | 46 | 0 | 0 | 62 | 81 | 0 | 130 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 38 | 17 | 0 | 367 | 30 | 17 | 17 | 0 | 88 | 35 | 53 | 106 | 9 | 38 | 400 | 34 | 0 | 80 | 34 | 0 | 35 | 0 | 71 | 17 | 0 | 54 | 0 |  | 486 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 208 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 359 | 10 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1202 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6578 | 3223 | 9801 | 4472 | 486 | 2249 | 0 | 1053 | 1277 | 0 | 0 | 138 | 126 | 0 | 50 | 75.15
2:00 | 0 | 0 | 180 | 180 | 0 | 75 | 0 | 396 | 352 |  | 0 | 400 | 280 | 25 | 0 | 0 | 170 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 20 | 25 | 25 | 16 | 0 | 0 | 0 | 120 | 0 | 8 | 227 | 0 | 0 | 0 |  | 0 | 0 | 51 | 55 | 25 | 6 | 10 | 36 | 0 | 0 | 0 | 310 | 300 | 216 | 150 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 7 | 33 | 20 | 122 | 74 | 0 | 19 | 0 | 0 | 31 | 50 | 46 | 0 | 0 | 62 | 81 | 0 | 130 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 38 | 17 | 0 | 367 | 16 | 0 | 17 | 0 | 88 | 35 | 54 | 90 | 9 | 38 | 400 | 53 | 0 | 0 | 34 | 0 | 35 | 0 | 19 | 0 | 0 | 54 | 0 |  | 485 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 206 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 304 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 1162 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6301 | 3100 | 9401 | 4441 | 485 | 2168 | 0 | 843 | 1237 | 0 | 0 | 105 | 122 | 0 | 50 | 75.15
3:00 | 0 | 0 | 180 | 180 | 0 | 75 | 0 | 397 | 304 |  | 0 | 350 | 290 | 25 | 0 | 0 | 170 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 20 | 25 | 25 | 16 | 0 | 0 | 0 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 51 | 55 | 0 | 6 | 10 | 38 | 0 | 0 | 0 | 310 | 300 | 215 | 150 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 7 | 33 | 20 | 120 | 75 | 0 | 19 | 0 | 0 | 31 | 50 | 46 | 0 | 0 | 63 | 81 | 0 | 130 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 17 | 0 | 365 | 16 | 0 | 17 | 0 | 88 | 35 | 54 | 62 | 9 | 38 | 400 | 53 | 0 | 0 | 34 | 0 | 28 | 0 | 21 | 0 | 0 | 54 | 0 |  | 485 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 321 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6131 | 2904 | 9035 | 4344 | 485 | 2086 | 0 | 698 | 1197 | 0 | 0 | 105 | 120 | 0 | 50 | 75.15
4:00 | 0 | 0 | 180 | 180 | 0 | 75 | 0 | 397 | 303 |  | 0 | 350 | 275 | 24 | 0 | 0 | 170 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 20 | 25 | 25 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 51 | 55 | 0 | 6 | 10 | 38 | 0 | 0 | 0 | 310 | 300 | 217 | 150 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 7 | 33 | 20 | 118 | 73 | 0 | 19 | 0 | 0 | 31 | 50 | 46 | 0 | 0 | 63 | 30 | 0 | 130 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 17 | 0 | 365 | 16 | 0 | 17 | 0 | 88 | 35 | 54 | 45 | 9 | 25 | 400 | 52 | 0 | 0 | 34 | 0 | 17 | 0 | 18 | 0 | 0 | 54 | 0 |  | 485 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5996 | 2789 | 8785 | 4330 | 485 | 1992 | 0 | 628 | 1127 | 0 | 0 | 105 | 118 | 0 | 50 | 75.15
5:00 | 0 | 0 | 140 | 180 | 0 | 72 | 0 | 397 | 303 |  | 0 | 350 | 280 | 25 | 0 | 0 | 172 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 23 | 20 | 25 | 25 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 229 | 0 | 0 | 0 |  | 0 | 0 | 34 | 55 | 0 | 6 | 10 | 39 | 0 | 0 | 0 | 310 | 300 | 217 | 150 | 0 | 42 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 7 | 33 | 20 | 114 | 74 | 0 | 19 | 0 | 0 | 31 | 50 | 46 | 0 | 0 | 62 | 30 | 0 | 130 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 17 | 0 | 365 | 16 | 0 | 17 | 0 | 88 | 35 | 54 | 35 | 9 | 25 | 400 | 52 | 0 | 0 | 34 | 0 | 17 | 0 | 18 | 0 | 0 | 108 | 0 |  | 485 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5991 | 2712 | 8703 | 4283 | 485 | 2009 | 0 | 593 | 1077 | 0 | 0 | 142 | 114 | 0 | 46 | 75.15
6:00 | 0 | 0 | 140 | 180 | 0 | 72 | 0 | 364 | 305 |  | 0 | 350 | 310 | 25 | 0 | 0 | 170 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | 20 | 25 | 25 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 0 | 0 | 0 | 55 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 320 | 315 | 189 | 150 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 7 | 33 | 20 | 106 | 34 | 0 | 19 | 0 | 0 | 31 | 47 | 46 | 0 | 0 | 62 | 30 | 0 | 130 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 38 | 17 | 0 | 365 | 18 | 0 | 17 | 0 | 88 | 35 | 54 | 17 | 9 | 25 | 370 | 45 | 3 | 0 | 34 | 0 | 17 | 1 | 18 | 0 | 0 | 108 | 0 |  | 485 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2 | 0 |  | 5857 | 2739 | 8596 | 4154 | 485 | 2081 | 0 | 573 | 1077 | 0 | 0 | 108 | 106 | 12 | 36 | 75.15
7:00 | 0 | 0 | 110 | 180 | 0 | 72 | 0 | 353 | 303 |  | 0 | 350 | 260 | 24 | 0 | 0 | 170 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | 20 | 25 | 32 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 228 | 0 | 0 | 0 |  | 0 | 0 | 0 | 55 | 0 | 6 | 10 | 38 | 0 | 0 | 0 | 300 | 300 | 179 | 150 | 0 | 44 | 0 | 0 | 51 | 0 | 0 | 52 | 18 | 7 | 33 | 20 | 96 | 33 | 0 | 19 | 0 | 0 | 31 | 47 | 46 | 0 | 0 | 62 | 81 | 0 | 130 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 22 | 0 | 7 | 6 | 38 | 17 | 0 | 365 | 47 | 0 | 17 | 1 | 88 | 35 | 51 | 17 | 9 | 25 | 360 | 53 | 11 | 5 | 34 | 0 | 17 | 6 | 18 | 7 | 0 | 108 | 0 |  | 485 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 416 | 0 | 0 | 10 | 0 | 29 | 0 | 0 | 20 | 1080 | 0 | 0 | 0 | 0 | 12 | 15 | 0 | 0 | 0 | 5 | 0 | 0 | 41 | 0 |  | 5836 | 3012 | 8848 | 4064 | 485 | 2139 | 0 | 718 | 1156 | 0 | 0 | 108 | 96 | 82 | 0 | 75.15
8:00 | 0 | 0 | 100 | 180 | 0 | 52 | 0 | 350 | 308 |  | 0 | 320 | 310 | 25 | 0 | 0 | 140 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 23 | 20 | 25 | 32 | 2 | 0 | 0 | 0 | 120 | 0 | 0 | 227 | 0 | 0 | 0 |  | 5 | 0 | 0 | 55 | 0 | 6 | 10 | 14 | 0 | 0 | 0 | 300 | 310 | 189 | 150 | 0 | 43 | 0 | 0 | 51 | 0 | 0 | 24 | 18 | 7 | 33 | 20 | 104 | 33 | 0 | 17 | 0 | 0 | 31 | 47 | 46 | 0 | 0 | 62 | 81 | 0 | 130 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 55 | 0 | 17 | 4 | 38 | 17 | 0 | 380 | 56 | 0 | 17 | 2 | 88 | 35 | 51 | 17 | 9 | 25 | 370 | 52 | 13 | 17 | 34 | 0 | 17 | 15 | 18 | 17 | 0 | 108 | 0 |  | 484 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 415 | 0 | 0 | 35 | 0 | 33 | 0 | 3 | 35 | 1172 | 0 | 0 | 0 | 0 | 38 | 55 | 0 | 0 | 0 | 13 | 0 | 0 | 76 | 0 |  | 5884 | 3233 | 9117 | 4042 | 484 | 2113 | 0 | 855 | 1247 | 0 | 0 | 108 | 104 | 164 | 0 | 75.14
9:00 | 0 | 0 | 110 | 180 | 0 | 52 | 0 | 383 | 310 |  | 0 | 450 | 280 | 25 | 0 | 0 | 200 | 0 | 40 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 23 | 20 | 25 | 32 | 10 | 0 | 0 | 0 | 120 | 0 | 0 | 225 | 0 | 0 | 0 |  | 6 | 0 | 0 | 55 | 0 | 6 | 10 | 5 | 0 | 0 | 0 | 310 | 300 | 183 | 150 | 0 | 40 | 0 | 0 | 51 | 0 | 0 | 26 | 18 | 7 | 33 | 20 | 110 | 32 | 0 | 17 | 1 | 0 | 30 | 47 | 46 | 0 | 0 | 61 | 78 | 0 | 137 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 0 | 0 | 0 | 55 | 0 | 17 | 14 | 38 | 27 | 0 | 368 | 56 | 10 | 17 | 2 | 88 | 35 | 51 | 17 | 9 | 25 | 400 | 52 | 33 | 18 | 34 | 0 | 17 | 23 | 18 | 17 | 0 | 108 | 0 |  | 485 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 156 | 0 | 370 | 0 | 0 | 35 | 0 | 34 | 0 | 4 | 35 | 1170 | 0 | 0 | 0 | 0 | 69 | 55 | 0 | 0 | 0 | 20 | 0 | 0 | 101 | 0 |  | 6188 | 3264 | 9452 | 4148 | 485 | 2159 | 0 | 913 | 1246 | 0 | 0 | 124 | 110 | 267 | 0 | 75.14
10:00 | 0 | 0 | 180 | 180 | 0 | 52 | 0 | 402 | 340 |  | 0 | 450 | 299 | 52 | 0 | 7 | 222 | 0 | 98 | 1 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 23 | 20 | 25 | 32 | 16 | 0 | 0 | 0 | 120 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 10 | 0 | 55 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 330 | 340 | 191 | 150 | 0 | 35 | 0 | 0 | 43 | 0 | 0 | 34 | 18 | 7 | 33 | 20 | 116 | 32 | 0 | 17 | 2 | 0 | 30 | 47 | 43 | 0 | 0 | 60 | 80 | 0 | 135 | 17 | 0 | 9 | 275 | 16 | 8 | 0 | 30 | 160 | 0 | 72 | 0 | 17 | 17 | 38 | 100 | 8 | 377 | 63 | 51 | 17 | 4 | 88 | 35 | 51 | 0 | 8 | 25 | 390 | 52 | 42 | 54 | 34 | 0 | 17 | 18 | 19 | 17 | 0 | 108 | 0 |  | 485 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 153 | 0 | 332 | 0 | 0 | 35 | 0 | 34 | 0 | 5 | 70 | 1200 | 0 | 0 | 0 | 0 | 92 | 60 | 36 | 0 | 0 | 19 | 0 | 15 | 103 | 0 |  | 6919 | 3328 | 10247 | 4330 | 485 | 2157 | 160 | 1221 | 1290 | 0 | 36 | 150 | 116 | 302 | 0 | 75.14
11:00 | 0 | 0 | 130 | 170 | 0 | 52 | 0 | 388 | 275 |  | 0 | 370 | 304 | 63 | 32 | 15 | 170 | 0 | 40 | 24 | 50 | 82 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 15 | 23 | 20 | 18 | 32 | 16 | 0 | 0 | 25 | 120 | 0 | 8 | 221 | 0 | 0 | 0 |  | 6 | 46 | 55 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 335 | 345 | 194 | 149 | 0 | 40 | 0 | 0 | 43 | 0 | 21 | 43 | 15 | 7 | 33 | 20 | 126 | 28 | 0 | 10 | 2 | 0 | 30 | 52 | 42 | 0 | 0 | 40 | 80 | 0 | 135 | 17 | 0 | 9 | 280 | 16 | 8 | 0 | 120 | 0 | 0 | 157 | 0 | 34 | 18 | 38 | 100 | 42 | 369 | 98 | 92 | 17 | 4 | 121 | 35 | 51 | 0 | 8 | 38 | 370 | 34 | 20 | 72 | 34 | 0 | 17 | 30 | 51 | 17 | 0 | 163 | 0 |  | 484 | 0 | 195 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 34 | 0 | 17 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 330 | 0 | 0 | 50 | 50 | 34 | 0 | 4 | 75 | 1232 | 0 | 0 | 0 | 0 | 102 | 115 | 30 | 0 | 0 | 27 | 0 | 108 | 161 | 0 |  | 7137 | 3692 | 10829 | 4048 | 484 | 2025 | 0 | 1941 | 1415 | 25 | 30 | 367 | 126 | 368 | 0 | 75.14
12:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 378 | 330 |  | 0 | 400 | 298 | 67 | 72 | 15 | 217 | 0 | 65 | 55 | 66 | 98 | 10 | 0 | 0 | 0 | 0 | 35 | 17 | 15 | 23 | 20 | 25 | 32 | 16 | 0 | 0 | 25 | 120 | 0 | 8 | 217 | 0 | 0 | 0 |  | 10 | 57 | 63 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 310 | 188 | 148 | 0 | 33 | 0 | 0 | 51 | 0 | 38 | 43 | 17 | 7 | 33 | 20 | 130 | 29 | 0 | 5 | 1 | 0 | 30 | 50 | 42 | 0 | 0 | 60 | 80 | 0 | 135 | 16 | 0 | 9 | 280 | 16 | 8 | 0 | 145 | 0 | 0 | 158 | 0 | 35 | 19 | 38 | 100 | 73 | 370 | 99 | 105 | 17 | 5 | 122 | 35 | 51 | 0 | 8 | 38 | 383 | 50 | 54 | 72 | 34 | 0 | 17 | 33 | 59 | 34 | 0 | 163 | 0 |  | 485 | 0 | 200 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 32 | 178 | 21 | 32 | 0 | 0 | 0 | 24 | 4 | 0 | 0 | 42 | 0 | 43 | 0 | 19 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 275 | 0 | 0 | 50 | 67 | 34 | 0 | 6 | 75 | 1244 | 0 | 0 | 14 | 0 | 90 | 75 | 0 | 0 | 0 | 23 | 0 | 186 | 163 | 0 |  | 7509 | 3840 | 11349 | 4070 | 485 | 2017 | 0 | 2277 | 1504 | 25 | 0 | 447 | 130 | 394 | 0 | 75.14
13:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 399 | 330 |  | 0 | 450 | 291 | 68 | 68 | 15 | 212 | 0 | 95 | 75 | 66 | 98 | 9 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 23 | 20 | 25 | 32 | 16 | 0 | 0 | 25 | 120 | 0 | 14 | 218 | 0 | 0 | 0 |  | 12 | 57 | 77 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 300 | 184 | 173 | 0 | 39 | 0 | 0 | 51 | 0 | 37 | 50 | 17 | 7 | 33 | 20 | 136 | 26 | 0 | 8 | 1 | 0 | 29 | 50 | 46 | 0 | 0 | 60 | 79 | 0 | 135 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 150 | 0 | 0 | 160 | 0 | 34 | 19 | 38 | 100 | 85 | 369 | 98 | 105 | 17 | 4 | 122 | 35 | 51 | 0 | 8 | 38 | 383 | 52 | 52 | 72 | 34 | 0 | 17 | 32 | 76 | 34 | 0 | 163 | 0 |  | 485 | 0 | 200 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 32 | 176 | 24 | 32 | 0 | 0 | 0 | 32 | 4 | 0 | 0 | 42 | 0 | 43 | 0 | 20 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 308 | 0 | 0 | 70 | 85 | 34 | 0 | 6 | 75 | 1244 | 0 | 0 | 54 | 0 | 63 | 75 | 0 | 0 | 0 | 31 | 0 | 370 | 160 | 0 |  | 7736 | 4158 | 11894 | 4133 | 485 | 2126 | 0 | 2465 | 1688 | 25 | 0 | 468 | 136 | 368 | 0 | 75.14
14:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 401 | 295 |  | 0 | 450 | 300 | 67 | 80 | 15 | 212 | 0 | 95 | 75 | 48 | 98 | 4 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 23 | 20 | 25 | 32 | 16 | 0 | 0 | 25 | 120 | 0 | 24 | 212 | 0 | 0 | 0 |  | 12 | 55 | 78 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 340 | 335 | 199 | 173 | 0 | 38 | 0 | 0 | 51 | 0 | 38 | 46 | 17 | 7 | 33 | 20 | 140 | 25 | 0 | 8 | 2 | 0 | 29 | 51 | 46 | 0 | 0 | 59 | 79 | 0 | 25 | 17 | 0 | 10 | 285 | 16 | 8 | 0 | 150 | 0 | 0 | 160 | 0 | 22 | 17 | 38 | 100 | 99 | 398 | 98 | 105 | 17 | 4 | 124 | 35 | 51 | 0 | 9 | 38 | 360 | 52 | 40 | 72 | 34 | 0 | 17 | 28 | 86 | 34 | 0 | 163 | 0 |  | 485 | 0 | 195 | 0 | 80 | 0 | 0 | 0 | 16 | 0 | 32 | 176 | 24 | 32 | 0 | 0 | 0 | 32 | 10 | 0 | 14 | 42 | 0 | 35 | 0 | 18 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 152 | 0 | 302 | 0 | 0 | 70 | 85 | 34 | 0 | 4 | 75 | 1230 | 0 | 0 | 63 | 4 | 10 | 75 | 0 | 0 | 0 | 12 | 0 | 413 | 136 | 0 |  | 7686 | 4128 | 11814 | 4100 | 485 | 2098 | 0 | 2502 | 1717 | 25 | 0 | 490 | 140 | 257 | 0 | 75.14
15:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 400 | 298 |  | 0 | 450 | 296 | 67 | 97 | 15 | 213 | 0 | 95 | 75 | 48 | 98 | 12 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 23 | 20 | 33 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 24 | 218 | 0 | 0 | 0 |  | 12 | 54 | 61 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 300 | 300 | 206 | 173 | 0 | 35 | 0 | 0 | 51 | 0 | 36 | 40 | 15 | 7 | 33 | 20 | 144 | 26 | 0 | 8 | 1 | 0 | 29 | 50 | 41 | 0 | 0 | 55 | 79 | 0 | 20 | 17 | 0 | 9 | 280 | 16 | 8 | 0 | 148 | 296 | 0 | 146 | 0 | 17 | 13 | 38 | 100 | 102 | 368 | 98 | 105 | 17 | 3 | 123 | 45 | 53 | 0 | 8 | 38 | 360 | 52 | 37 | 72 | 34 | 0 | 17 | 23 | 115 | 34 | 0 | 163 | 0 |  | 485 | 0 | 190 | 0 | 80 | 0 | 0 | 0 | 23 | 25 | 32 | 181 | 24 | 32 | 0 | 0 | 0 | 32 | 28 | 0 | 27 | 42 | 20 | 43 | 0 | 19 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 290 | 0 | 0 | 70 | 85 | 67 | 0 | 5 | 75 | 1244 | 0 | 0 | 118 | 4 | 22 | 74 | 0 | 0 | 0 | 17 | 0 | 414 | 101 | 0 |  | 7880 | 4291 | 12171 | 4000 | 485 | 2074 | 296 | 2650 | 1731 | 25 | 0 | 540 | 144 | 226 | 77.355 | 75.14
16:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 406 | 298 |  | 0 | 450 | 283 | 64 | 97 | 15 | 213 | 0 | 96 | 75 | 48 | 98 | 19 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 23 | 20 | 33 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 24 | 222 | 0 | 0 | 0 |  | 12 | 14 | 77 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 300 | 300 | 207 | 173 | 0 | 38 | 0 | 0 | 51 | 0 | 36 | 30 | 15 | 7 | 33 | 20 | 124 | 29 | 0 | 8 | 1 | 0 | 29 | 50 | 43 | 0 | 0 | 55 | 79 | 0 | 20 | 17 | 0 | 9 | 270 | 16 | 8 | 0 | 145 | 21 | 0 | 114 | 0 | 17 | 8 | 38 | 100 | 104 | 368 | 49 | 105 | 17 | 1 | 123 | 54 | 54 | 0 | 8 | 38 | 365 | 45 | 16 | 72 | 34 | 0 | 24 | 15 | 115 | 34 | 0 | 163 | 0 |  | 485 | 0 | 190 | 0 | 96 | 0 | 0 | 0 | 29 | 75 | 40 | 180 | 22 | 32 | 0 | 0 | 0 | 32 | 28 | 30 | 27 | 42 | 40 | 43 | 0 | 19 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 281 | 0 | 0 | 70 | 100 | 84 | 0 | 3 | 75 | 1244 | 0 | 0 | 137 | 1 | 10 | 74 | 0 | 0 | 0 | 15 | 0 | 408 | 30 | 0 |  | 7449 | 4364 | 11813 | 4022 | 485 | 2042 | 21 | 2647 | 1725 | 25 | 0 | 622 | 124 | 100 | 163.305 | 75.14
17:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 405 | 298 |  | 0 | 450 | 262 | 64 | 97 | 15 | 214 | 0 | 62 | 45 | 48 | 128 | 0 | 0 | 0 | 0 | 17 | 40 | 35 | 16 | 23 | 20 | 33 | 30 | 16 | 0 | 0 | 25 | 120 | 0 | 25 | 220 | 0 | 0 | 0 |  | 12 | 36 | 78 | 56 | 3 | 6 | 10 | 8 | 0 | 0 | 0 | 300 | 300 | 208 | 175 | 0 | 38 | 0 | 0 | 51 | 0 | 36 | 32 | 16 | 7 | 33 | 20 | 122 | 30 | 0 | 11 | 0 | 0 | 29 | 50 | 43 | 0 | 0 | 60 | 79 | 0 | 90 | 17 | 0 | 9 | 270 | 16 | 8 | 0 | 150 | 0 | 0 | 117 | 0 | 17 | 3 | 38 | 100 | 107 | 368 | 49 | 105 | 28 | 0 | 123 | 54 | 54 | 70 | 8 | 38 | 331 | 45 | 9 | 72 | 34 | 0 | 35 | 2 | 115 | 34 | 0 | 163 | 0 |  | 487 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 29 | 75 | 8 | 180 | 23 | 32 | 0 | 0 | 0 | 32 | 28 | 52 | 21 | 42 | 40 | 43 | 12 | 20 | 0 | 8 | 76 | 0 | 76 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 268 | 0 | 0 | 35 | 32 | 34 | 0 | 2 | 35 | 1030 | 0 | 0 | 150 | 0 | 3 | 75 | 0 | 0 | 0 | 3 | 0 | 407 | 5 | 0 |  | 7528 | 3910 | 11438 | 4018 | 487 | 2018 | 0 | 2443 | 1589 | 25 | 0 | 709 | 122 | 27 | 135.61 | 75.14
18:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 333 | 255 |  | 0 | 350 | 276 | 67 | 77 | 15 | 130 | 0 | 39 | 30 | 48 | 150 | 0 | 0 | 0 | 0 | 17 | 43 | 35 | 0 | 23 | 20 | 33 | 30 | 41 | 0 | 0 | 25 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 12 | 42 | 68 | 10 | 19 | 16 | 10 | 13 | 0 | 0 | 0 | 300 | 300 | 180 | 127 | 0 | 38 | 0 | 0 | 51 | 0 | 36 | 36 | 18 | 7 | 33 | 20 | 138 | 29 | 0 | 11 | 0 | 0 | 30 | 50 | 44 | 0 | 0 | 61 | 78 | 0 | 125 | 17 | 0 | 10 | 260 | 16 | 8 | 0 | 145 | 0 | 0 | 135 | 0 | 49 | 0 | 38 | 34 | 115 | 368 | 70 | 105 | 17 | 0 | 122 | 54 | 54 | 70 | 50 | 38 | 355 | 35 | 0 | 35 | 34 | 0 | 35 | 0 | 50 | 34 | 0 | 54 | 0 |  | 905 | 0 | 180 | 0 | 32 | 0 | 0 | 0 | 32 | 74 | 8 | 181 | 23 | 32 | 0 | 0 | 0 | 31 | 28 | 52 | 21 | 42 | 40 | 16 | 32 | 20 | 0 | 8 | 76 | 0 | 150 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 253 | 0 | 0 | 35 | 32 | 34 | 0 | 1 | 35 | 800 | 0 | 0 | 72 | 0 | 1 | 36 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 |  | 7008 | 4017 | 11025 | 3856 | 905 | 1822 | 0 | 2205 | 1433 | 25 | 0 | 639 | 138 | 2 | 85 | 75.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 312 | 255 |  | 0 | 370 | 233 | 67 | 68 | 15 | 190 | 0 | 40 | 30 | 64 | 150 | 0 | 0 | 0 | 0 | 35 | 47 | 45 | 0 | 23 | 19 | 33 | 32 | 41 | 0 | 0 | 25 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 12 | 46 | 83 | 56 | 31 | 38 | 10 | 21 | 0 | 0 | 0 | 295 | 300 | 206 | 120 | 0 | 38 | 0 | 0 | 51 | 0 | 36 | 50 | 18 | 7 | 33 | 20 | 154 | 45 | 0 | 11 | 0 | 0 | 29 | 51 | 47 | 0 | 0 | 61 | 76 | 0 | 130 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 145 | 0 | 0 | 173 | 0 | 88 | 0 | 76 | 52 | 122 | 402 | 108 | 105 | 28 | 0 | 190 | 54 | 54 | 70 | 73 | 75 | 365 | 45 | 0 | 60 | 34 | 0 | 35 | 0 | 70 | 34 | 0 | 54 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 43 | 75 | 8 | 183 | 28 | 32 | 0 | 0 | 0 | 31 | 15 | 50 | 0 | 8 | 40 | 8 | 35 | 20 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 253 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 35 | 900 | 0 | 0 | 60 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 |  | 7664 | 3989 | 11653 | 3934 | 913 | 1817 | 0 | 2619 | 1533 | 25 | 0 | 658 | 154 | 0 | 111.735 | 75.14
19:30 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 356 | 255 |  | 0 | 370 | 286 | 24 | 66 | 30 | 190 | 0 | 40 | 30 | 83 | 150 | 0 | 0 | 0 | 0 | 35 | 50 | 55 | 10 | 23 | 24 | 33 | 32 | 49 | 0 | 0 | 25 | 120 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 46 | 84 | 56 | 31 | 38 | 10 | 21 | 0 | 0 | 0 | 300 | 300 | 200 | 78 | 0 | 39 | 0 | 0 | 51 | 0 | 38 | 52 | 18 | 7 | 33 | 20 | 140 | 47 | 0 | 11 | 0 | 0 | 29 | 53 | 48 | 0 | 0 | 60 | 79 | 0 | 130 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 45 | 0 | 0 | 173 | 0 | 149 | 0 | 76 | 120 | 140 | 410 | 108 | 105 | 51 | 0 | 190 | 54 | 54 | 36 | 78 | 88 | 400 | 45 | 0 | 162 | 34 | 0 | 35 | 0 | 115 | 34 | 0 | 54 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 183 | 24 | 16 | 0 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 40 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 253 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 0 | 900 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 |  | 7994 | 3718 | 11712 | 4033 | 913 | 1842 | 0 | 2714 | 1532 | 25 | 0 | 513 | 140 | 0 | 84.995 | 0
20:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 358 | 322 |  | 0 | 420 | 304 | 24 | 52 | 22 | 218 | 0 | 98 | 24 | 48 | 150 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 10 | 23 | 24 | 33 | 32 | 49 | 0 | 0 | 25 | 120 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 47 | 84 | 56 | 30 | 38 | 10 | 26 | 0 | 0 | 0 | 345 | 255 | 199 | 35 | 0 | 39 | 0 | 0 | 51 | 0 | 38 | 43 | 18 | 7 | 33 | 20 | 144 | 47 | 0 | 12 | 0 | 0 | 29 | 53 | 48 | 0 | 0 | 60 | 79 | 0 | 130 | 17 | 0 | 10 | 275 | 16 | 8 | 0 | 45 | 0 | 0 | 173 | 0 | 149 | 0 | 76 | 120 | 100 | 391 | 108 | 105 | 51 | 0 | 190 | 54 | 54 | 17 | 77 | 88 | 385 | 40 | 0 | 162 | 34 | 0 | 35 | 0 | 115 | 34 | 0 | 54 | 0 |  | 912 | 0 | 175 | 0 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 180 | 29 | 16 | 0 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 40 | 0 | 35 | 22 | 0 | 0 | 76 | 0 | 150 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 243 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 0 | 900 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 404 | 0 | 0 |  | 7936 | 3707 | 11643 | 4084 | 912 | 1929 | 0 | 2505 | 1530 | 25 | 0 | 514 | 144 | 0 | 84.995 | 75.14
21:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 395 | 309 |  | 0 | 450 | 268 | 8 | 34 | 30 | 150 | 0 | 92 | 16 | 40 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 10 | 23 | 24 | 33 | 32 | 49 | 0 | 0 | 25 | 120 | 0 | 25 | 224 | 0 | 0 | 0 |  | 0 | 47 | 84 | 22 | 31 | 39 | 10 | 26 | 0 | 0 | 0 | 295 | 255 | 209 | 35 | 0 | 39 | 0 | 0 | 51 | 0 | 35 | 31 | 18 | 7 | 32 | 20 | 146 | 52 | 0 | 0 | 0 | 0 | 29 | 53 | 45 | 0 | 0 | 61 | 80 | 0 | 133 | 17 | 0 | 10 | 270 | 16 | 8 | 0 | 45 | 0 | 0 | 88 | 0 | 118 | 0 | 76 | 120 | 100 | 368 | 47 | 98 | 51 | 0 | 278 | 54 | 54 | 34 | 78 | 32 | 370 | 17 | 0 | 35 | 34 | 0 | 35 | 0 | 114 | 34 | 0 | 54 | 0 |  | 818 | 0 | 180 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 30 | 16 | 0 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 238 | 17 | 0 | 35 | 15 | 24 | 0 | 0 | 0 | 1030 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 403 | 0 | 0 |  | 7306 | 3684 | 10990 | 4001 | 818 | 1899 | 0 | 2112 | 1658 | 25 | 0 | 331 | 146 | 0 | 54 | 75.14
22:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 348 | 308 |  | 0 | 450 | 264 | 9 | 20 | 15 | 150 | 0 | 41 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 23 | 24 | 17 | 32 | 49 | 0 | 0 | 25 | 120 | 0 | 25 | 226 | 0 | 0 | 0 |  | 0 | 47 | 84 | 10 | 31 | 39 | 10 | 26 | 0 | 0 | 0 | 295 | 255 | 213 | 35 | 0 | 39 | 0 | 0 | 51 | 0 | 38 | 52 | 18 | 7 | 33 | 20 | 150 | 52 | 0 | 0 | 0 | 0 | 29 | 53 | 49 | 0 | 0 | 62 | 80 | 0 | 130 | 17 | 0 | 10 | 255 | 16 | 8 | 0 | 15 | 0 | 0 | 24 | 0 | 71 | 0 | 12 | 120 | 50 | 368 | 47 | 88 | 17 | 0 | 285 | 17 | 34 | 34 | 75 | 12 | 370 | 16 | 0 | 17 | 34 | 0 | 35 | 0 | 115 | 34 | 0 | 34 | 0 |  | 825 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 28 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 35 | 20 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 196 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 265 | 17 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 1050 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 406 | 0 | 0 |  | 6675 | 3666 | 10341 | 3895 | 825 | 1906 | 0 | 1601 | 1681 | 25 | 0 | 258 | 150 | 0 | 0 | 75.14
23:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 366 | 350 |  | 0 | 450 | 303 | 8 | 17 | 15 | 222 | 0 | 99 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 23 | 24 | 25 | 32 | 25 | 0 | 0 | 0 | 120 | 0 | 25 | 222 | 0 | 0 | 0 |  | 0 | 47 | 84 | 20 | 31 | 39 | 10 | 24 | 0 | 0 | 0 | 315 | 250 | 212 | 35 | 0 | 43 | 0 | 0 | 51 | 0 | 39 | 38 | 18 | 7 | 33 | 20 | 142 | 51 | 0 | 0 | 0 | 0 | 29 | 53 | 49 | 0 | 0 | 61 | 81 | 0 | 130 | 18 | 0 | 10 | 260 | 16 | 8 | 0 | 15 | 0 | 0 | 26 | 0 | 65 | 0 | 20 | 100 | 10 | 381 | 49 | 88 | 17 | 0 | 231 | 17 | 34 | 88 | 20 | 26 | 393 | 16 | 0 | 17 | 34 | 0 | 0 | 0 | 115 | 34 | 0 | 18 | 0 |  | 827 | 0 | 185 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 28 | 16 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 0 | 0 | 76 | 0 | 150 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 250 | 17 | 0 | 35 | 15 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 |  | 6755 | 3614 | 10369 | 4106 | 827 | 1978 | 0 | 1439 | 1634 | 0 | 0 | 243 | 142 | 0 | 0 | 75.14
24:00 | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 405 | 352 |  | 0 | 450 | 286 | 23 | 17 | 15 | 222 | 0 | 42 | 20 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 23 | 24 | 25 | 33 | 16 | 0 | 0 | 0 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 2 | 47 | 84 | 33 | 0 | 6 | 10 | 29 | 0 | 0 | 0 | 295 | 250 | 211 | 35 | 0 | 43 | 0 | 0 | 51 | 0 | 39 | 46 | 18 | 7 | 33 | 20 | 144 | 52 | 0 | 0 | 0 | 0 | 29 | 53 | 49 | 0 | 0 | 61 | 81 | 0 | 130 | 18 | 0 | 10 | 275 | 16 | 8 | 0 | 15 | 0 | 0 | 46 | 0 | 37 | 0 | 25 | 51 | 10 | 367 | 49 | 88 | 17 | 0 | 88 | 17 | 51 | 114 | 9 | 38 | 400 | 44 | 0 | 17 | 34 | 0 | 16 | 0 | 115 | 34 | 0 | 50 | 0 |  | 827 | 0 | 185 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 27 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 76 | 0 | 177 | 0 | 0 | 197 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 264 | 17 | 0 | 57 | 0 | 31 | 0 | 0 | 35 | 1170 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 408 | 0 | 0 |  | 6598 | 3859 | 10457 | 4074 | 827 | 1995 | 0 | 1330 | 1831 | 0 | 0 | 256 | 144 | 0 | 115 | 75.14
KWH | 0 | 0 | 3117281 | 4158000 | 0 | 955545 | 0 | 9254910 | 7450000 |  | 0 | 9565250 | 6980625 | 911040 | 783907 | 256332 | 4578675 | 0 | 1786560 | 541440 | 674640 | 1295520 | 60959 | 0 | 0 | 0 | 259560 | 439560 | 382542 | 234072 | 552000 | 502200 | 631440 | 745700 | 451680 | 0 | 0 | 308000 | 2800000 | 0 | 331885 | 5256283 | 0 | 0 | 0 |  | 148800 | 635088 | 1284345 | 1107480 | 241920 | 333120 | 233952 | 491040 | 0 | 0 | 0 | 7790000 | 7259000 | 4883000 | 3161454 | 0 | 949536 | 0 | 0 | 1160468 | 0 | 463568 | 1050994 | 409068 | 167400 | 803000 | 482720 | 3052800 | 1024320 | 0 | 240372 | 14900 | 0 | 662520 | 1201200 | 1094328 | 0 | 0 | 1420800 | 1776960 | 0 | 2837140 | 399000 | 0 | 238140 | 6654000 | 370344 | 183392 | 0 | 1550618 | 450336 | 0 | 1958400 | 0 | 828580 | 139455 | 943680 | 1627680 | 1226109 | 9034000 | 1455600 | 1500125 | 531090 | 31078 | 3138873 | 974827 | 1270430 | 899460 | 541800 | 869760 | 9202600 | 1057920 | 368140 | 1127520 | 840545 | 0 | 595800 | 222609 | 1586880 | 573120 | 0 | 2276581 | 0 |  | 13936727 | 0 | 5767488 | 0 | 563520 | 0 | 0 | 0 | 215520 | 313648 | 164250 | 4313000 | 552300 | 340032 | 0 | 0 | 0 | 229350 | 145948 | 202888 | 100240 | 290434 | 215752 | 294216 | 209387 | 472560 | 0 | 117900 | 1756364 | 0 | 1053200 | 0 | 0 | 4591364 | 0 | 0 | 0 | 0 | 0 | 3825882 | 0 | 7499672 | 113760 | 0 | 962400 | 637488 | 711513 | 0 | 37998 | 760128 | 29443700 | 0 | 0 | 732000 | 9700 | 532080 | 1062336 | 58043 | 0 | 0 | 200125 | 0 | 4900000 | 1047110 | 0 |  | 166315391 | 88380023 | 254695414 | 100584919 | 13936727 | 49253542 | 450336 | 39806993 | 37153264 | 308000 | 58043 | 7487595 | 3052800 | 2603195 | 0
Fuel Cost | 0 | 0 | 4551230.26 | 6195420 | 0 | 1270874.85 | 0 | 9717655.5 | 8046000 |  | 0 | 10426122.5 | 7748493.75 | 10185427.2 | 10386767.75 | 3396399 | 5128116 | 0 | 3126480 | 7915852.8 | 9492184.8 | 21000379.2 | 562041.98 | 0 | 0 | 0 | 3301603.2 | 5934060 | 5129888.22 | 175554 | 414000 | 0 | 0 | 0 | 7683076.8 | 0 | 0 | 83160 | 5292000 | 0 | 5426319.75 | 5466534.32 | 0 | 0 | 0 |  | 1941840 | 10593267.84 | 21859551.9 | 14962054.8 | 3067545.6 | 3854198.4 | 297119.04 | 1635163.2 | 0 | 0 | 0 | 8646900 | 7912310 | 5664280 | 4078275.66 | 0 | 1072975.68 | 0 | 0 | 1937981.56 | 0 | 8005819.36 | 14135869.3 | 560423.16 | 125550 | 1405250 | 362040 | 21919104 | 1116508.8 | 0 | 326905.92 | 237506 | 0 | 874526.4 | 2090088 | 1893187.44 | 0 | 0 | 2756352 | 4051468.8 | 0 | 2865511.4 | 857850 | 0 | 471517.2 | 6654000 | 277758 | 139377.92 | 0 | 21165935.7 | 9439042.56 | 0 | 26399232 | 0 | 11475833 | 1630228.95 | 9738777.6 | 22234108.8 | 16270466.43 | 8311280 | 17700096 | 21691807.5 | 6718288.5 | 0 | 36850369.02 | 10615866.03 | 13504670.9 | 12205672.2 | 6983802 | 10245772.8 | 8466392 | 13700064 | 5319623 | 14308228.8 | 9565402.1 | 0 | 7781148 | 2660177.55 | 23755593.6 | 7547990.4 | 0 | 0 | 0 |  | 41810181 | 0 | 6459586.56 | 0 | 5866243.2 | 0 | 0 | 0 | 3881515.2 | 5645664 | 2360272.5 | 4830560 | 1071462 | 3706348.8 | 0 | 0 | 0 | 3846199.5 | 2552630.52 | 3173168.32 | 771848 | 4809587.04 | 3648366.32 | 4010164.08 | 3532358.69 | 978199.2 | 0 | 89250.3 | 10204474.84 | 0 | 5571428 | 0 | 0 | 5325982.24 | 0 | 0 | 0 | 0 | 0 | 4438023.12 | 0 | 7424675.28 | 1528934.4 | 0 | 11385192 | 9211701.6 | 9036215.1 | 0 | 419877.9 | 9227953.92 | 265287737 | 0 | 0 | 5416800 | 109707 | 6241298.4 | 16285610.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 672991588.7 | 470159216.91 | 1143150805.61 | 113249702.62 | 41810181 | 59777509.44 | 9439042.56 | 511451126.5 | 281063639.84 | 83160 | 0 | 87738920.85 | 21919104 | 16618418.8 | 0
Yesterday Day Peak | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 378 | 330 |  | 0 | 400 | 298 | 67 | 72 | 15 | 217 | 0 | 65 | 55 | 66 | 98 | 10 | 0 | 0 | 0 | 0 | 35 | 17 | 15 | 23 | 20 | 25 | 32 | 16 | 0 | 0 | 25 | 120 | 0 | 8 | 217 | 0 | 0 | 0 |  | 10 | 57 | 63 | 44 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 310 | 188 | 148 | 0 | 33 | 0 | 0 | 51 | 0 | 38 | 43 | 17 | 7 | 33 | 20 | 130 | 29 | 0 | 5 | 1 | 0 | 30 | 50 | 42 | 0 | 0 | 60 | 80 | 0 | 135 | 16 | 0 | 9 | 280 | 16 | 8 | 0 | 145 | 0 | 0 | 158 | 0 | 35 | 19 | 38 | 100 | 73 | 370 | 99 | 105 | 17 | 5 | 122 | 35 | 51 | 0 | 8 | 38 | 383 | 50 | 54 | 72 | 34 | 0 | 17 | 33 | 59 | 34 | 0 | 163 | 0 |  | 485 | 0 | 200 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 32 | 178 | 21 | 32 | 0 | 0 | 0 | 24 | 4 | 0 | 0 | 42 | 0 | 43 | 0 | 19 | 0 | 8 | 74 | 0 | 0 | 0 | 0 | 166 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 275 | 0 | 0 | 50 | 67 | 34 | 0 | 6 | 75 | 1244 | 0 | 0 | 14 | 0 | 90 | 75 | 0 | 0 | 0 | 23 | 0 | 186 | 163 | 0 |  | 11349 | DayPeak
Yesterday Evening Peak | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 356 | 255 | 0 | 0 | 370 | 286 | 24 | 66 | 30 | 190 | 0 | 40 | 30 | 83 | 150 | 0 | 0 | 0 | 0 | 35 | 50 | 55 | 10 | 23 | 24 | 33 | 32 | 49 | 0 | 0 | 25 | 120 | 0 | 25 | 223 | 0 | 0 | 0 | 0 | 12 | 46 | 84 | 56 | 31 | 38 | 10 | 21 | 0 | 0 | 0 | 300 | 300 | 200 | 78 | 0 | 39 | 0 | 0 | 51 | 0 | 38 | 52 | 18 | 7 | 33 | 20 | 140 | 47 | 0 | 11 | 0 | 0 | 29 | 53 | 48 | 0 | 0 | 60 | 79 | 0 | 130 | 17 | 0 | 10 | 280 | 16 | 8 | 0 | 45 | 0 | 0 | 173 | 0 | 149 | 0 | 76 | 120 | 140 | 410 | 108 | 105 | 51 | 0 | 190 | 54 | 54 | 36 | 78 | 88 | 400 | 45 | 0 | 162 | 34 | 0 | 35 | 0 | 115 | 34 | 0 | 54 | 0 |  | 913 | 0 | 170 | 0 | 16 | 0 | 0 | 0 | 38 | 0 | 0 | 183 | 24 | 16 | 0 | 0 | 0 | 0 | 4 | 24 | 0 | 0 | 40 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 253 | 17 | 0 | 35 | 15 | 34 | 0 | 0 | 0 | 900 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 407 | 0 | 0 |  | 11712 | EvPeak
Forecast for Evening | 0 | 0 | 110 | 170 | 0 | 70 | 0 | 360 | 300 | 0 | 0 | 450 | 300 | 70 | 90 | 30 | 220 | 0 | 100 | 90 | 83 | 149 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 18 | 23 | 24 | 33 | 32 | 49 | 0 | 0 | 25 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 60 | 84 | 70 | 50 | 38 | 10 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 69 | 0 | 40 | 0 | 0 | 51 | 0 | 38 | 52 | 18 | 7 | 33 | 20 | 165 | 80 | 0 | 0 | 0 | 0 | 29 | 51 | 50 | 0 | 0 | 62 | 85 | 0 | 130 | 18 | 0 | 10 | 310 | 16 | 8 | 0 | 300 | 300 | 100 | 173 | 80 | 149 | 0 | 76 | 150 | 150 | 400 | 115 | 105 | 51 | 0 | 300 | 54 | 54 | 0 | 55 | 90 | 400 | 70 | 0 | 162 | 34 | 0 | 35 |  | 115 | 35 | 0 | 162 |  |  | 930 | 0 | 250 |  | 98 | 0 | 0 | 0 | 38 | 70 | 40 | 183 | 30 | 64 | 0 | 0 | 0 | 26 | 34 | 80 | 14 | 42 | 40 | 43 | 35 | 22 | 0 | 8 | 75 | 0 | 200 | 0 | 0 | 160 |  | 0 | 0 | 0 | 0 | 150 | 0 | 350 | 17 | 0 | 113 | 100 | 84 | 0 | 0 | 113 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 500 |  | 0
Forecast for Day | 0 | 0 | 110 | 170 | 0 | 16 | 0 | 360 | 300 | 0 | 0 | 450 | 300 | 25 | 90 | 15 | 220 | 0 | 90 | 90 | 48 | 149 | 0 | 0 | 0 | 0 | 17 | 37 | 35 | 10 | 23 | 20 | 25 | 32 | 41 | 0 | 0 | 25 | 120 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 45 | 66 | 50 | 0 | 26 | 10 | 15 | 0 | 0 | 0 | 300 | 300 | 210 | 68 | 0 | 40 | 0 | 0 | 51 | 0 | 31 | 41 | 18 | 7 | 33 | 20 | 143 | 50 | 0 | 0 | 1.6 | 0 | 29 | 51 | 46 | 0 | 0 | 61 | 85 | 0 | 130 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 300 | 300 | 50 | 160 | 0 | 50 | 20 | 38 | 17 | 80 | 400 | 75 | 105 | 17 | 5 | 120 | 35 | 51 | 17 | 9 | 63 | 400 | 54 | 50 | 72 | 34 | 0 | 35 | 30 | 94 | 17 | 0 | 162 |  |  | 496 | 0 | 200 | 0 | 85 | 0 | 0 | 0 | 22 | 55 | 0 | 180 | 25 | 16 | 0 | 0 | 0 | 26 | 0 | 80 | 0 | 34 | 24 | 0 | 35 | 22 | 0 | 8 | 75 | 0 | 180 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 300 | 17 | 0 | 50 | 0 | 34 | 0 | 8 | 95 | 1200 | 0 |  | 17 | 6 | 100 | 55 | 0 |  | 0 | 30 | 0 | 500 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 110 | 170 | 0 | 12 | 0 | 344 | 260 | 0 | 0 | 330 | 280 | 0 | 0 | 0 | 150 | 0 | 39 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 24 | 25 | 33 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 226 | 0 | 0 | 0 | 0 | 6 | 33 | 17 | 10 | 0 | 6 | 10 | 42 | 0 | 0 | 0 | 280 | 270 | 180 | 8 | 0 | 41 | 0 | 0 | 10 | 0 | 39 | 43 | 18 | 7 | 33 | 20 | 108 | 52 | 0 | 0 | 1 | 0 | 29 | 11 | 10 | 0 | 0 | 40 | 40 | 0 | 130 | 17 | 0 | 10 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 46 | 0 | 17 | 9 | 12 | 17 | 0 | 319 | 49 | 0 | 17 | 1 | 65 | 17 | 17 | 17 | 9 | 12 | 350 | 17 | 30 | 0 | 34 | 0 | 17 | 11 | 18 | 0 | 0 | 18 | 0 | 0 | 910 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 75 | 0 | 200 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 570 | 0 | 0 | 0 | 1 | 36 | 0 | 0 | 0 | 0 | 17 | 0 | 409 | 55 | 0 | 0 |  |  |  | 149.8385 | 13.9367 | 47.803 | 37.1533 | 0.308 | 3.0528 | 2.6032
254.6954
| Minimum Generation |  | 8596 | 6:00
| Highest Generation |  | 12171 | 15:00
| Day Peak Generation |  | 11349 | 12:00
| Evening Peak Generation |  | 11712 | 19:30
| HVDC Max Flow |  | 913 | 19:00
| HVDC EvPeak Flow |  | 913 | 19:30
| Load factor L.F |  | 87.19% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-01
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-04-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 11349 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8365
Evening Peak Generation : |  |  | 11712 | MW Hour : | 19:30 | Available Max Generation : |  | 14950
E.P. Demand (at gen end) : |  |  | 11801 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11500
Maximum Generation : |  |  | 12171 | MW Hour : | 15:00 | Reserve(Generation end) |  | 3450
Total Gen. (MKWH) : |  |  | 254.6954 | System Load Factor : | 87.19% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | -150 | MW at | 6:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-01
Actual : |  | 75.13 | Ft.(MSL) , | Rule curve : | 82.2 | Ft.( MSL )
Gas Consumed : |  | Total = | 1121.26 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 173027212.06
: |  |  | Coal : | 281063639.84 | Oil : | 608629089.91 | Total : | 1062719941.81
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4277.4276 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1183.5628 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1555.8063 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1372.6427 |  |  | 0 | 0%
Cumilla Area |  | 20 | 480:00 | 1171.9796 |  |  | 0 | 0%
Mymensingh Area |  | 55 | 1320:00 | 963.3164 |  |  | 0 | 0%
Sylhet Area |  | 10 | 240:00 | 435.3258 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 351.1605 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 760.6533 |  |  | 0 | 0%
Total |  | 85 |  | 12071.875 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:14 | 13:15 | Hathazari 230/132/33kV S/S T-01 LT Scheduled S/D Due to T-01 transformer (80/120MVA) 132/33kv, 33kv side cable laying.
08:14 | 13:15 | Hathazari 230/132/33kV S/S T-01 HT Scheduled S/D Due to T-01 transformer (80/120MVA) 132/33kv, 33kv side cable laying.
08:30 | 13:46 | Bheramara 230/132kV S/S Transformer-1 HT Scheduled S/D Due to Annual maintenance.
08:30 | 13:46 | Bheramara 230/132kV S/S Transformer-1 LT Scheduled S/D Due to Annual maintenance
09:08 |  | Khulshi-Madunaghat 132kV Ckt-2 Project Work S/D from Madunaghat 132/33kV end Due to For GNDP project work.
09:33 | 16:44 | Haripur 230/132kV S/S Ullon (Maniknagar-2) Scheduled S/D
10:11 | 16:18 | Siddhirganj-Ullon (T at Haripur) 132kV Ckt-2 Forced S/D from Siddhirganj 132/33kV end Due to Maintanances Work in Ullon ends
| 10:33 | Naogaon 132/33kV S/S T-3 HT is restored.
| 10:36 | Naogaon 132/33kV S/S T-3 LT is restored.
10:54 | 15:11 | Fenchuganj 230/132/33kV S/S AT-02 HT Scheduled S/D Due to Annual Maintenance
10:54 | 15:11 | Fenchuganj 230/132/33kV S/S AT-02 LT Scheduled S/D Due to Annual Maintenance
11:00 | 16:31 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Maintanances Work for EGCB ends
| 11:25 | Faridpur 132/33kV S/S Transformer-2 LT is restored.
| 11:25 | Faridpur 132/33kV S/S Transformer-2 HT is restored.
11:30 |  | Rampal 230/132KV ICT-2 SD by P/S.
11:33 | 14:47 | Mongla 132/33kV S/S T-2 LT Forced S/D Due to 33 kV bus section ds maintenance | [5 empty] | 20 MW load interrupt.
11:33 | 12:34 | Mongla 132/33kV S/S T-1 LT Tripped showing OC/EF(50) relays Due to BICL feeder trip | [5 empty] | 36 MW load interrupt.
11:33 | 14:47 | Mongla 132/33kV S/S T-2 LT Tripped showing OC/EF(50) relays Due to BICL feeder fault
11:34 | 16:49 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T LT Scheduled S/D Due to Red Hot Maintenance
11:35 | 16:48 | Barapukuria 230/132/33kV S/S 230/132 KV T-01, 703T HT Scheduled S/D Due to Red Hot Maintenance
11:56 | 12:04 | Barishal-Bhandaria 132 kV Ckt-1 Tripped from Barishal 132/33kV end showing Phase A relays Due to Un Known. | [5 empty] | 30 MW load interrupt.
12:00 |  | Day Peak Generation = 11,099MW
| 12:30 | Bhaluka-Mymensingh 132 kV Ckt-2 is restored.
| 12:30 | Bhaluka-Mymensingh 132 kV Ckt-1 is restored.
| 12:31 | Bhaluka 132/33kV S/S Transformer- 02 HT is restored.
| 12:31 | Bhaluka 132/33kV S/S Transformer- 01 HT is restored.
12:33 | 14:47 | Mongla 132/33kV S/S T-2 HT Forced S/D Due to 33 kV bus section ds loop maintenance. | [5 empty] | 20 MW load interrupt.
| 12:36 | Bhaluka 132/33kV S/S Transformer- 01 LT is restored.
| 12:37 | Bhaluka 132/33kV S/S Transformer- 02 LT is restored.
12:43 | 13:14 | Gopalganj(N)-Madaripur 132kV Ckt-1 Tripped from Madaripur 132/33kV end showing SIEMENS SIPROTEC 7SA52 relays Due to | [5 empty] | 50 MW load interrupt.
No and from Gopalganj 400/132kV end showing DIR OC (67) Inverse relays Due to 19.8km, Phase C,zone1
12:59 | 18:18 | Aminbazar 400/230/132kV S/S 132 kv Bus 02 Scheduled S/D Due to 400/132 kV Interim ATR bus DS maintenance.
15:50 |  | Mymensingh 132 kV bus coupler was opened
16:01 | 16:20 | Bogura-Sirajganj 230 kV Ckt-1 Tripped from Sirajgonj 230 end showing Main-1(REL316*4)distance relay,
Main-2(REL521) distance relay relays Due to L2-N fault
16:14 |  | Bhola CCPP GT1 was sync.
| 16:46 | BIPTC S/S 20DF24 is restored.
16:57 |  | Bogura west- Adani Power Ltd. 400 kv line Trip ( Distance relay Y- phase)
16:57 | 17:14 | Chapainawabganj-Rahanpur 132kV Ckt-1 Tripped from Rahanpur_I 400/132kV end showing M1 Main protection Relay | [5 empty] | 120 MW load interrupt.
relays Due to Thunderstorm
| 17:05 | Kodda 132/33kV S/S Tr-3 (426T) HT is restored.
| 17:06 | Kodda 132/33kV S/S Tr-4 (436T) HT is restored.
| 17:08 | Kodda 132/33kV S/S Tr-3 (426T) LT is restored.
| 17:09 | Kodda 132/33kV S/S Tr-4 (436T) LT is restored.
17:24 |  | Bhola CCPP GT2 was sync.
17:46 | 19:05 | BIPTC S/S 21T01 LT Tripped showing TDC (ACF Main protection) relays Due to Pole-01 tripped by 00X00.B-A1RPC RPC NO AC Filter | [5 empty] | 485 MW load interrupt.
17:55 | 18:15 | Haripur-Madanganj 132kV Ckt-1 Tripped from Madanganj 132/33kV end showing Main Protection Relay relays. and from
|  | Haripur 230/132kV end showing Distance Zone-1, BN (Y Phase N) relays Due to Rain | [5 empty] | 42 MW load interrupt.
19:21 | 20:10 | Ashugonj-Sreepur ckt-1 tripped at both sides showing distance relay.
19:41 |  | Bogura west- Adani Power Ltd. 400 KV line Syn.
20:37 | 22:17 | Chattak-Sylhet 132 kV Ckt-2 Tripped from Sylhet 132/33kV end showing Distance Protection trip Z-1, C-Phase. relays. | [5 empty] | 1.0 MW load interrupt.
20:38 | 21:12 | Chattak-Sunamganj 132 kV Ckt-1 Tripped from Sunamganj 132/33kV end showing REL-670 relays.
21:00 |  | Evening peak generation: 9235 MW. System Demand drastically reduced due to Bad weather all over the Country.
21:58 | 04:10 | Rangpur 132/33kV S/S T-1(414T) LT Tripped showing O/C ,E/F relays Due to Due to 33 kv T-6 Feeder Fault | [5 empty] | 60 MW load interrupt.
21:58 | 04:10 | Rangpur 132/33kV S/S T-2 (404T) LT Tripped showing O/C ,E/F relays Due to Due to33kv T-6 feeder Breaker Fault
22:23 | 22:50 | Ramganj 132/33kV S/S Transformer -02 LT Scheduled S/D Due to None | [5 empty] | 50 MW load interrupt.
22:42 |  | Gulsan-Rampura 132kV Ckt-1 Scheduled S/D from Gulshan 132/33kV end Due to 132 kV 0.9 km underground cable
replacement work. and from Rampura 230/132kV end Due to XLPE cable replacement work of 132 KV Gulshan ckt-1.
00:30 |  | Bhola 225MW CCPP ST was sync.
06:00 |  | minimum generation 8596 MW

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-04-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 110 | 3117281 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4158000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 955545 | Bad weather
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 356 | 9254910 | Bad weather
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 255 | 7450000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 370 | 9565250 | Bad weather
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 24 | 911040 | Low Demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 286 | 6980625 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 66 | 783907 | Low Demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 30 | 256332 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 60959 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 10 | 234072 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 40 | 1786560 | Bad weather
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 30 | 541440 | Low Demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 190 | 4578675 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 83 | 674640 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 259560 | Low Demand
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1295520
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 50 | 439560
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 382542
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1054200 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 631440
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 32 | 745700
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 49 | 451680 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 45 | 1550618 | Low Demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 450336 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 149 | 828580
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1500125
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 45 | 1057920 | Low Demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1127520
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 222609
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 573120 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3023 | 63880266
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 331885
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 139455
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 38 | 333120 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 308000 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 5256283
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 531090 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 46 | 635088 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 84 | 1284345 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 56 | 1107480 | Low Demand
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 76 | 943680 | Engine problem
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 233952 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 21 | 491040
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 31 | 241920 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31078
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 190 | 3138873 | Low Demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 974827
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 54 | 1270430 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 869760
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 34 | 840545 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 54 | 2276581 | On test.
| Chattogram area Total |  |  |  | 2382 | 1280 | 24039432
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 200 | 4883000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7790000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7259000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 39 | 949536
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 78 | 3161454 | Bad weather
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1160468
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 1226109 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 463568 | Low Demand
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 120 | 1627680 | Low Demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 409068 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 167400 | 33 kV feeder fault.
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 3052800
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 803000
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1050994
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 482720 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 36 | 899460 | Low Demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 78 | 541800 | Low Demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 595800 | Low Demand
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 115 | 1586880
| Cumilla Area Total |  |  |  | 3151 | 1800 | 38110737
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 47 | 1024320 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 11 | 240372 | 33 kV feeder fault.
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14900
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 173 | 1958400 | Engine problem
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 108 | 1455600 | Engine problem
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 368140
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 148800 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 351 | 5210532
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 29 | 662520 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1201200
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 48 | 1094328
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 183392
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1420800
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1776960
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 130 | 2837140 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 399000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 370344 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6654000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 410 | 9034000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238140
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9202600
| Sylhet Area Total |  |  |  | 2427 | 1540 | 35074424
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 13936727
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 563520 | Low Demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 215520 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 313648 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 170 | 5767488 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 164250 | Reserve
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 113760 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 637488 | Low Demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 532080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 58043 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1169 | 22302524
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 340032 | Low Demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 552300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 183 | 4313000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 900 | 29443700 | Bad weather
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 732000 | Low Demand
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1140 | 35381032
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 229350 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 4 | 145948 | Low Demand
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 100240 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 290434 | Reserve
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 215752 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 150 | 4591364 | FGMO
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 136 | 3825882 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 253 | 7499672 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 209387 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 472560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 117900 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 294216 | Reserve
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 24 | 202888 | Low Demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 962400 | Low Demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 760128 | Low Demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 9700
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 407 | 4900000 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1114 | 24827821
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1756364 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 1053200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 34 | 711513 | Low Demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 37998
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 36 | 1062336 | Low Demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 200125
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1047110
| Rangpur Area Total |  |  |  | 750 | 295 | 5868646
| Total |  |  |  | 22566 | 11712 | 254695414
| Eastern Grid Total |  |  |  | 14421 | 7994 | 166315391
| Western Grid Total |  |  |  | 8145 | 3718 | 88380023
| National Grid Total |  |  |  | 22566 | 11712 | 254695414
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-04-30
| (a) ENTIRE EASTERN GRID : |  | 8374.4 | MW | (b) ENTIRE WESTERN GRID : |  | 2823 | MW
| i) Dhaka area |  | 4280.8 | MW | i) Khulna area |  | 1110.2 | MW
| ii) Chittagong area |  | 1307.6 | MW | ii) Rajshahi area |  | 546.8 | MW
| iii) Comilla area |  | 1290 | MW | iii) Barisal area |  | 413 | MW
| iv) Mymensingh area |  | 978 | MW | iv) Rangpur area |  | 753 | MW
| v) Sylhet area |  | 518 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11197.4 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 30 | 20:00 | Kamrangirchar | 40 | 13:00 | Natore | 113 | 13:00 | Shitalakhya | 110 | 15:00
2 | AKSML | 98.5 | 13:00 | Chowmuhani | 230 | 21:00 | Kaptai | 4 | 18:30 | Nawabganj | 51.1 | 19:30 | Sholosohor | 32 | 00:00
3 | Aftabnagar | 56 | 15:00 | Chuadanga | 85 | 15:00 | Kazla | 61 | 22:00 | Netrakona | 130 | 19:30 | Shyampur | 110 | 14:00
4 | Agargaon | 73 | 13:00 | Coxsbazar | 136 | 20:00 | Keranigonj | 52 | 13:00 | New | 66 | 19:00 | Siddhirganj | 96 | 11:00
5 | Agrabad | 70 | 11:00 | Cumilla(N) | 175 | 22:00 | Khagrachori | 30 | 19:30 | Niamatpur | 78 | 13:00 | Sirajganj | 97 | 19:00
6 | Amnura | 45 | 14:00 | Cumilla(S) | 154 | 18:30 | Khulna | 91 | 19:00 | Noapara | 40 | 19:00 | Sonargaon | 75 | 11:00
7 | Ashuganj | 66 | 21:00 | Daudkandi | 144 | 19:30 | Khulshi | 192 | 19:00 | PHP | 9 | 16:00 | Sreemongol | 65 | 19:00
8 | BIPTC | N/A | N/A | Dhaka | 28 | 13:00 | Kishoreganj | 118 | 21:00 | Pabna | 87 | 15:00 | Sreepur | 60 | 19:00
9 | BSRM | 108 | 00:00 | Dhamrai | 112 | 19:30 | Kodda | 283 | 18:30 | Palashbari | 124 | 18:30 | Srinagar | 38.7 | 22:00
10 | Bagerhat | 87 | 19:30 | Dhanmondi | 137 | 13:00 | Kulaura | 48 | 19:00 | Panchagarh | 54 | 19:00 | Sunamganj | 51 | 21:00
11 | Bakulia | 97 | 17:00 | Dohazari | 98 | 19:00 | Kurigram | 67 | 19:00 | Patuakhali | 101 | 20:00 | Sylhet | 144 | 18:30
12 | Banani | 60 | 15:00 | Faridpur | 126 | 18:30 | Kushtia | 110 | 17:00 | Payra | 20 | 21:00 | TK | 30.5 | 21:00
13 | Bangabhaban | 23 | 10:00 | Fatullah | 52 | 15:00 | Lalbag | 53 | 17:00 | Postogola | 45 | 18:30 | Tangail | 220 | 18:30
14 | Barapukuria | 60 | 20:00 | Fenchuganj | 49 | 18:30 | Lalmonirhat | 46 | 19:00 | Purbachal | 18 | 19:00 | Thakurgaon | 83 | 19:00
15 | Barguna | 20 | 21:00 | Feni | 123 | 19:00 | Madanganj | 30 | 21:00 | Purbasadipur | 112 | 12:00 | Tongi | 106 | 12:00
16 | Barishal | 107 | 19:00 | GPH | 79 | 17:00 | Madaripur | 96 | 20:00 | Rahanpur_I | 20 | 09:00 | Ullon | 35 | 19:30
17 | Barishal-230 | 90 | 20:00 | Ghorashal | 65 | 15:00 | Madartek | 68 | 20:00 | Rahim | 34 | 04:00 | Uttara | 60 | 16:00
18 | Baroaulia | 56 | 21:00 | Goalpara | 30 | 13:00 | Madunaghat | 52 | 19:00 | Rajbari | 50 | 21:00 | UttaraNew | 47 | 13:00
19 | Baroirhat | 60 | 19:00 | Gollamari | 52 | 13:00 | Magura | 47 | 20:00 | Rajendrapur | 84 | 19:00 | Zigatola | 67 | 19:00
20 | Bashundhara | 147 | 16:00 | Gopalganj | 93 | 19:00 | Mahasthangarh | 54 | 18:00 | Rajshahi | 128 | 14:00
21 | BashundharaCement | 6 | 00:00 | Gulshan | 80 | 09:00 | Manikganj | 105 | 19:30 | Rajshahi-230 | 27 | 00:00
22 | Beanibazar | 68 | 19:00 | Halishahar | 88 | 15:00 | Maniknagar | 80 | 13:00 | Ramganj | 112 | 21:00
23 | Benapole | 38 | 12:00 | HaripurSBU | 117 | 16:00 | Matarbari | 46 | 19:00 | Rampur | 30 | 19:00
24 | Bhaluka | 150 | 20:00 | Hasnabad | 71 | 17:00 | Matuail | 48 | 15:00 | Rangamati | 16 | 18:30
25 | Bhandaria | 44 | 19:00 | Hathazari | 73 | 19:30 | Millgate | 82 | 16:00 | Rangpur | 99 | 16:00
26 | Bhangura | 32 | 14:00 | Ishurdi | 58 | 18:00 | Mirpur | 115 | 19:00 | Ruppur | 5 | 15:00
27 | Bheramara(GK) | 46 | 15:00 | Jaldhaka | 68 | 19:00 | Mirsorai | 3 | 06:00 | SSM | 0 | 00:00
28 | Bhulta | 190 | 15:00 | Jamalpur | 143 | 19:30 | Mithapukur | 54 | 07:00 | Saidpur | 104 | 15:00
29 | Bog-Sherpur | 52 | 18:30 | Jashore | 112 | 13:00 | Modern | 0 | 00:00 | Satkhira | 90 | 13:00
30 | Bogura | 138 | 18:30 | Jhenaidah | 88 | 18:30 | Mogbazar | 108 | 15:00 | Satmasjid | 101 | 19:00
31 | Borhanuddin | 66 | 23:00 | Joydebpur | 143 | 18:30 | Mongla | 30 | 12:00 | Savar | 168 | 16:00
32 | Brahmanbaria | 165 | 22:00 | Joypurhat | 49 | 20:00 | Motijheel | 36 | 15:00 | Shahjadpur | 83 | 18:30
33 | Cantonment | 116 | 19:00 | Juldah | 23 | 09:00 | Munshiganj | 97 | 15:00 | Shahjibazar | 121 | 22:00
34 | Chandpur | 68 | 21:00 | KSRM | 26 | 23:00 | Mymensingh | 174 | 18:00 | Shahmirpur | 49 | 00:00
35 | Chandraghona | 31 | 19:00 | Kabirpur | 281 | 19:00 | Naogaon | 106 | 13:00 | Shariatpur | 75 | 20:00
36 | Chapai | 55 | 13:00 | Kachua | 69 | 20:00 | Narail | 47 | 19:00 | Sherpur | 126 | 20:00
37 | Charsaidpur | 27 | 03:00 | Kallyanpur | 90 | 19:00 | Narinda | 54 | 13:00 | Shikalbaha | 37 | 21:00
38 | Chauddagram | 62 | 19:30 | Kalurghat | 34 | 15:00 | Narshingdi | 152 | 19:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-04-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 414 | 04:00 | 402 | 14:00 | Kaliakoir | 396 | 04:00 | 389 | 13:00
| Bhulta | 400 | 05:00 | 389 | 15:00 | Madunaghat_I | 403 | 21:00 | 385 | 10:00
| Bibiana | 409 | 05:00 | 400 | 16:00 | Payra | 419 | 18:00 | 411 | 16:00
| BIPTC | 408 | 04:00 | 398 | 19:30 | Rahanpur_I | 425 | 11:00 | 413 | 06:00
| Gopalganj | 416 | 18:00 | 400 | 20:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 05:00 | 228 | 07:00 | Hathazari | 233 | 17:00 | 223 | 10:00
| AKSML | 234 | 17:00 | 211 | 23:00 | Ishurdi | 237 | 04:00 | 230 | 13:00
| Aminbazar | 241 | 07:00 | 233 | 23:00 | Jhenaidah | 234 | 18:00 | 223 | 12:00
| Ashuganj | 242 | 05:00 | 236 | 23:00 | Kaliakoir | 236 | 02:00 | 231 | 10:00
| Baghabari | 234 | 15:00 | 230 | 13:00 | Keranigonj | 237 | 04:00 | 230 | 10:00
| Barapukuria | 226 | 22:00 | 209 | 06:00 | Khulna(S) | 239 | 18:00 | 229 | 00:00
| Barishal | 244 | 18:00 | 234 | 20:00 | Madunaghat_I | 232 | 21:00 | 222 | 10:00
| Bheramara | 236 | 17:00 | 229 | 13:00 | Maniknagar | 238 | 04:00 | 136 | 01:00
| Bhulta | 239 | 01:00 | 233 | 15:00 | Meghnaghat | 241 | 17:00 | 236 | 23:00
| Bibiana | 240 | 07:00 | 233 | 19:30 | Mirsorai | 235 | 19:30 | 224 | 10:00
| BIPTC | 238 | 18:00 | 227 | 13:00 | Rajshahi | 241 | 19:00 | 228 | 12:00
| Bogura | 232 | 22:00 | 220 | 14:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 243 | 19:30 | 235 | 23:00 | Rampura | 236 | 01:00 | 231 | 15:00
| BSRM | 237 | 17:00 | 226 | 23:00 | Shikalbaha | 231 | 21:00 | 221 | 10:00
| Cumilla(N) | 236 | 07:00 | 227 | 23:00 | Shyampur | 237 | 04:00 | 220 | 19:00
| Fenchuganj | 245 | 07:00 | 236 | 16:00 | Siddhirganj | 240 | 03:00 | 235 | 14:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 241 | 22:00 | 236 | 06:00
| GPH | 232 | 19:30 | 221 | 10:00 | Sreepur | 237 | 04:00 | 232 | 16:00
| Haripur | 236 | 03:00 | 231 | 00:00 | Tongi | 232 | 00:00 | 226 | 11:00
| Hasnabad | 239 | 07:00 | 232 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 01:00 | 124 | 14:00 | Lalbag | 133 | 21:00 | 128 | 10:00
| Agargaon | 138 | 05:00 | 132 | 10:00 | Lalmonirhat | 135 | 22:00 | 121 | 06:00
| Agrabad | 134 | 17:00 | 128 | 09:00 | Madanganj | 137 | 07:00 | 133 | 10:00
| AKS | 133 | 17:00 | 125 | 23:00 | Madaripur | 135 | 06:00 | 130 | 20:00
| Aminbazar | 134 | 02:00 | 129 | 13:00 | Madartek | 138 | 04:00 | 130 | 13:00
| Amnura | 137 | 17:00 | 127 | 00:00 | Madunaghat | 136 | 19:30 | 128 | 10:00
| Ashuganj | 141 | 07:00 | 138 | 14:00 | Magura | 138 | 18:00 | 130 | 14:00
| Bagerhat | 136 | 05:00 | 130 | 00:00 | Mahasthangarh | 137 | 22:00 | 129 | 13:00
| Bakulia | 135 | 18:00 | 129 | 09:00 | Manikganj | 138 | 21:00 | 126 | 15:00
| Banani | 139 | 07:00 | 130 | 15:00 | Maniknagar | 139 | 05:00 | 134 | 13:00
| Bangabhaban | 139 | 07:00 | 135 | 10:00 | Matarbari | 125 | 17:00 | 111 | 23:00
| Barapukuria | 140 | 22:00 | 128 | 06:00 | Matuail | 138 | 04:00 | 134.3 | 10:00
| Barguna | 140 | 17:00 | 132 | 23:00 | Millgate | 136 | 01:00 | 129 | 10:00
| Barishal | 139 | 17:00 | 127 | 23:00 | Mirpur | 133 | 07:00 | 128 | 13:00
| Barishal-230 | 136 | 05:00 | 129 | 19:30 | Mithapukur | 136 | 22:00 | 125 | 13:00
| Baroaulia | 135 | 21:00 | 128 | 22:00 | Modern | 135 | 18:00 | 125 | 00:00
| Baroirhat | 133 | 18:00 | 122 | 23:00 | Mogbazar | 140 | 07:00 | 133 | 10:00
| Bashundhara | 136 | 03:00 | 129 | 14:00 | Mongla | 135 | 18:00 | 130 | 00:00
| BashundharaCement | 137 | 07:00 | 133 | 10:00 | Motijheel | 139 | 07:00 | 135 | 12:00
| Beanibazar | 135 | 05:00 | 126 | 22:00 | Munshiganj | 138 | 18:00 | 133 | 10:00
| Benapole | 136 | 18:00 | 129 | 13:00 | Mymensingh | 135 | 10:00 | 111 | 20:00
| Bhaluka | 134 | 21:00 | 108 | 19:30 | Naogaon | 136 | 22:00 | 123 | 14:00
| Bhandaria | 137 | 17:00 | 126 | 19:30 | Narail | 137 | 04:00 | 128 | 13:00
| Bhangura | 140 | 19:00 | 134 | 14:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 137 | 18:00 | 133 | 13:00 | Narshingdi | 136 | 07:00 | 129 | 20:00
| Bheramara(GK) | 138 | 06:00 | 136 | 11:00 | Natore | 138 | 19:00 | 131 | 13:00
| Bhulta | 131 | 17:00 | 126 | 10:00 | Nawabganj | 132 | 05:00 | 126 | 10:00
| Bog-Sherpur | 137 | 22:00 | 132 | 13:00 | Netrakona | 133 | 10:00 | 112 | 19:30
| Bogura | 138 | 22:00 | 131 | 06:00 | New | 137 | 07:00 | 130 | 14:00
| Bogura-230 | 139 | 22:00 | 130 | 07:00 | Niamatpur | 135 | 22:00 | 118 | 13:00
| Brahmanbaria | 136 | 05:00 | 133 | 13:00 | Noapara | 138 | 05:00 | 132 | 10:00
| Cantonment | 137 | 04:00 | 131 | 13:00 | Pabna | 140 | 19:00 | 132 | 13:00
| Chandpur | 135 | 17:00 | 124 | 05:00 | Palashbari | 136 | 22:00 | 124 | 14:00
| Chandraghona | 135 | 17:00 | 128 | 10:00 | Panchagarh | 139 | 22:00 | 126 | 14:00
| Chapai | 136 | 18:00 | 128 | 13:00 | Patuakhali | 142 | 17:00 | 134 | 00:00
| Charsaidpur | 138 | 18:00 | 134 | 03:00 | Payra | 141 | 18:00 | 137 | 00:00
| Chauddagram | 135 | 18:00 | 124 | 15:00 | PHP | 133 | 18:00 | 121 | 23:00
| Chhatak | 136 | 01:00 | 126 | 18:30 | Postogola | 137 | 21:00 | 133 | 10:00
| Chowmuhani | 131 | 18:00 | 127 | 05:00 | Purbachal | 138 | 03:00 | 127 | 14:00
| Chuadanga | 138 | 18:00 | 125 | 14:00 | Purbasadipur | 135 | 22:00 | 120 | 06:00
| Coxsbazar | 124 | 17:00 | 110 | 03:00 | Rahim | 138 | 05:00 | 135 | 10:00
| Cumilla(N) | 137 | 07:00 | 130 | 23:00 | Rajbari | 135 | 04:00 | 130 | 13:00
| Cumilla(S) | 136 | 17:00 | 126 | 18:30 | Rajendrapur | 139 | 21:00 | 127 | 09:00
| Daudkandi | 136 | 18:00 | 128 | 23:00 | Rajshahi | 137 | 18:00 | 128 | 13:00
| Dhaka | 139 | 07:00 | 132 | 14:00 | Rajshahi-230 | 137 | 19:00 | 128 | 12:00
| Dhamrai | 135 | 21:00 | 127 | 15:00 | Ramganj | 132 | 17:00 | 118 | 23:00
| Dhanmondi | 139 | 05:00 | 134 | 10:00 | Rampur | 139 | 00:00 | 128 | 10:00
| Dohazari | 133 | 17:00 | 123 | 23:00 | Rampura | 136 | 01:00 | 132 | 13:00
| Faridpur | 135 | 03:00 | 130 | 23:00 | Rangamati | 134 | 17:00 | 129 | 00:00
| Fatullah | 138 | 07:00 | 134 | 10:00 | Rangpur | 135 | 22:00 | 124 | 14:00
| Fenchuganj | 140 | 00:00 | 133 | 18:30 | Ruppur | 139 | 18:00 | 133 | 14:00
| Feni | 134 | 18:00 | 123 | 15:00 | Saidpur | 135 | 22:00 | 123 | 06:00
| Ghorashal | 142 | 01:00 | 139 | 10:00 | Satkhira | 138 | 18:00 | 130 | 14:00
| Goalpara | 140 | 18:00 | 135 | 00:00 | Satmasjid | 137 | 04:00 | 132 | 10:00
| Gollamari | 138 | 16:00 | 129 | 19:30 | Savar | 136 | 09:00 | 127 | 10:00
| Gopalganj | 139 | 16:00 | 129 | 19:30 | Shahjadpur | 143 | 00:00 | 140 | 07:00
| Gopalganj-400 | 137 | 04:00 | 131 | 20:00 | Shahjibazar | 138 | 07:00 | 132 | 22:00
| Gulshan | 137 | 03:00 | 131 | 14:00 | Shahmirpur | 135 | 18:00 | 129 | 09:00
| Halishahar | 135 | 17:00 | 127 | 10:00 | Shariatpur | 135 | 04:00 | 129 | 22:00
| Haripur | 138 | 05:00 | 135 | 10:00 | Sherpur | 137 | 10:00 | 117 | 06:00
| HaripurSBU | 139 | 21:00 | 133 | 10:00 | Shikalbaha | 137 | 17:00 | 121 | 15:00
| Hasnabad | 136 | 02:00 | 133 | 23:00 | Shikalbaha-230 | 136 | 18:00 | 132 | 13:00
| Hathazari | 136 | 17:00 | 130 | 07:00 | Shitalakhya | 137 | 05:00 | 133 | 10:00
| Ishurdi | 138 | 04:00 | 133 | 01:00 | Sholosohor | 135 | 21:00 | 127 | 10:00
| Jaldhaka | 134 | 22:00 | 117 | 06:00 | Shyampur | 136 | 01:00 | 134 | 09:00
| Jamalpur | 140 | 19:00 | 121 | 06:00 | Shyampur-230 | 137 | 04:00 | 133 | 10:00
| Jashore | 137 | 04:00 | 129 | 14:00 | Siddhirganj | 138 | 05:00 | 135 | 10:00
| Jhenaidah | 139 | 05:00 | 132 | 13:00 | Sirajganj | 140 | 22:00 | 133 | 06:00
| Jhenaidah-230 | 139 | 04:00 | 131 | 14:00 | Sonargaon | 138 | 18:00 | 133 | 00:00
| Joydebpur | 144 | 21:00 | 133 | 08:00 | Sreemongol | 136 | 05:00 | 131 | 23:00
| Joypurhat | 133 | 22:00 | 122 | 13:00 | Sreepur | 134 | 03:00 | 130 | 16:00
| Juldah | 136 | 17:00 | 129 | 09:00 | Srinagar | 132 | 05:00 | 126 | 10:00
| Kabirpur | 141 | 21:00 | 125 | 15:00 | SSM | 138 | 21:00 | 130 | 22:00
| Kachua | 136 | 17:00 | 124 | 23:00 | Sunamganj | 135 | 07:00 | 123 | 18:30
| Kaliakoir | 138 | 05:00 | 132 | 09:00 | Sylhet | 135 | 00:00 | 130 | 18:30
| Kallyanpur | 134 | 04:00 | 129 | 15:00 | Tangail | 140 | 21:00 | 123 | 15:00
| Kalurghat | 136 | 17:00 | 128 | 10:00 | Thakurgaon | 136 | 10:00 | 122 | 06:00
| Kamrangirchar | 133 | 07:00 | 128 | 14:00 | TK | 135 | 17:00 | 127 | 10:00
| Kaptai | 132 | 00:00 | 128 | 09:00 | Tongi | 136 | 21:00 | 132 | 04:00
| Kazla | 139 | 03:00 | 134 | 13:00 | Ullon | 138 | 07:00 | 132 | 10:00
| Keranigonj | 133 | 07:00 | 128 | 10:00 | Uttara | 133 | 06:00 | 128 | 10:00
| Khagrachori | 133 | 18:00 | 127 | 10:00 | UttaraNew | 133 | 03:00 | 128 | 14:00
| Khulna | 139 | 18:00 | 132 | 00:00 | Zigatola | 133 | 05:00 | 128 | 10:00
| Khulna(S) | 140 | 04:00 | 134 | 10:00
| Khulshi | 133 | 18:00 | 124 | 10:00
| Kishoreganj | 133 | 22:00 | 123 | 13:00
| Kodda | 141 | 21:00 | 125 | 15:00
| KSRM | 134 | 18:00 | 129 | 00:00
| Kulaura | 138 | 05:00 | 133 | 18:30
| Kurigram | 133 | 22:00 | 120 | 14:00
| Kushtia | 138 | 18:00 | 132 | 13:00
Page 7 of 7

## L-Curve
Date | 2023-04-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1060 | 6598 | 3859 | 10457 |  |  |  | QF-LDC-11
0:30 | 590 | 6588 | 3541 | 10129 | Date: | 2023-04-30
1:00 | 120 | 6578 | 3223 | 9801
1:30 | 125 | 6439.5 | 3161.5 | 9601
2:00 | 130 | 6301 | 3100 | 9401
2:30 | 135 | 6216 | 3002 | 9218 | [5 empty] | Gen. at Eve. Peak | 11712 | 11712 MW (19:30 )
3:00 | 140 | 6131 | 2904 | 9035 | [6 empty] | 19:30
3:30 | 95 | 6063.5 | 2846.5 | 8910 | [5 empty] | Gen. at Day Peak | 11349 | 11349 MW (12:00 )
4:00 | 50 | 5996 | 2789 | 8785 | [6 empty] | 12:00
4:30 | 93 | 5993.5 | 2750.5 | 8744 | [5 empty] | Highest Generation | 12171
5:00 | 136 | 5991 | 2712 | 8703 | [6 empty] | 15:00
5:30 | 143 | 5924 | 2725.5 | 8649.5
6:00 | 150 | 5857 | 2739 | 8596
6:30 | 88 | 5846.5 | 2875.5 | 8722
7:00 | 26 | 5836 | 3012 | 8848
7:30 | 71 | 5860 | 3122.5 | 8982.5
8:00 | 116 | 5884 | 3233 | 9117
8:30 | 135 | 6036 | 3248.5 | 9284.5
9:00 | 154 | 6188 | 3264 | 9452
9:30 | 154 | 6553.5 | 3296 | 9849.5
10:00 | 154 | 6919 | 3328 | 10247
10:30 | 127 | 7028 | 3510 | 10538
11:00 | 100 | 7137 | 3692 | 10829
11:30 | 112 | 7323 | 3766 | 11089
12:00 | 124 | 7509 | 3840 | 11349
12:30 | 96 | 7622.5 | 3999 | 11621.5
13:00 | 68 | 7736 | 4158 | 11894
13:30 | 107 | 7711 | 4143 | 11854
14:00 | 146 | 7686 | 4128 | 11814
14:30 | 295 | 7783 | 4209.5 | 11992.5
15:00 | 444 | 7880 | 4291 | 12171
15:30 | 488 | 7664.5 | 4327.5 | 11992
16:00 | 532 | 7449 | 4364 | 11813
16:30 | 504 | 7488.5 | 4137 | 11625.5
17:00 | 476 | 7528 | 3910 | 11438
17:30 | 778 | 7268 | 3963.5 | 11231.5
18:00 | 1080 | 7008 | 4017 | 11025
18:30 | 930 | 7336 | 4003 | 11339
19:00 | 780 | 7664 | 3989 | 11653
19:30 | 612 | 7994 | 3718 | 11712
20:00 | 610 | 7936 | 3707 | 11643 |  |  |  | Executive Engineer
20:30 | 580 | 7621 | 3695.5 | 11316.5 |  |  |  | Network Operation Division
21:00 | 550 | 7306 | 3684 | 10990
21:30 | 675 | 6990.5 | 3675 | 10665.5
22:00 | 800 | 6675 | 3666 | 10341 |  |  |  |  | Page 6 of 7
22:30 | 778 | 6715 | 3640 | 10355
23:00 | 756 | 6755 | 3614 | 10369
23:30 | 908 | 6676.5 | 3736.5 | 10413
24:00 | 1060 | 6598 | 3859 | 10457
11712 MW (19:30 )
11349 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-04-30 |  | Energy |  | 254695414
[13 empty] | 2023-04-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 4074 | 827 | 1995 | 0 | 1330 | 1831 | 0 | 0 | 256 | 144 | 0 | 0
0:30 | 4273 | 656.5 | 2122 | 0 | 1191.5 | 1554 | 0 | 0 | 197 | 135 | 0 | 25 |  | Date: | 43584
1:00 | 4472 | 486 | 2249 | 0 | 1053 | 1277 | 0 | 0 | 138 | 126 | 0 | 50
1:30 | 4456.5 | 485.5 | 2208.5 | 0 | 948 | 1257 | 0 | 0 | 121.5 | 124 | 0 | 50 | [8 empty] | Total Energy | 254.6954 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 254.695 MKWHr Energy Not Served 1.037 MKWHr Energy Requirement 255.732 MKWHr
2:00 | 4441 | 485 | 2168 | 0 | 843 | 1237 | 0 | 0 | 105 | 122 | 0 | 50 | [8 empty] | Energy not Served | 1.037
2:30 | 4392.5 | 485 | 2127 | 0 | 770.5 | 1217 | 0 | 0 | 105 | 121 | 0 | 50 | [8 empty] | Energy Requirement | 255.7325
3:00 | 4344 | 485 | 2086 | 0 | 698 | 1197 | 0 | 0 | 105 | 120 | 0 | 50
3:30 | 4337 | 485 | 2039 | 0 | 663 | 1162 | 0 | 0 | 105 | 119 | 0 | 50 | [7 empty] | Shortage
4:00 | 4330 | 485 | 1992 | 0 | 628 | 1127 | 0 | 0 | 105 | 118 | 0 | 50
4:30 | 4306.5 | 485 | 2000.5 | 0 | 610.5 | 1102 | 0 | 0 | 123.5 | 116 | 0 | 48
5:00 | 4283 | 485 | 2009 | 0 | 593 | 1077 | 0 | 0 | 142 | 114 | 0 | 46
5:30 | 4218.5 | 485 | 2045 | 0 | 583 | 1077 | 0 | 0 | 125 | 110 | 6 | 41
6:00 | 4154 | 485 | 2081 | 0 | 573 | 1077 | 0 | 0 | 108 | 106 | 12 | 36
6:30 | 4109 | 485 | 2110 | 0 | 645.5 | 1116.5 | 0 | 0 | 108 | 101 | 47 | 18 | [6 empty] | Coal
7:00 | 4064 | 485 | 2139 | 0 | 718 | 1156 | 0 | 0 | 108 | 96 | 82 | 0
7:30 | 4053 | 484.5 | 2126 | 0 | 786.5 | 1201.5 | 0 | 0 | 108 | 100 | 123 | 0 | [5 empty] | Oil
8:00 | 4042 | 484 | 2113 | 0 | 855 | 1247 | 0 | 0 | 108 | 104 | 164 | 0
8:30 | 4095 | 484.5 | 2136 | 0 | 884 | 1246.5 | 0 | 0 | 116 | 107 | 215.5 | 0
9:00 | 4148 | 485 | 2159 | 0 | 913 | 1246 | 0 | 0 | 124 | 110 | 267 | 0
9:30 | 4239 | 485 | 2158 | 80 | 1067 | 1268 | 0 | 18 | 137 | 113 | 284.5 | 0
10:00 | 4330 | 485 | 2157 | 160 | 1221 | 1290 | 0 | 36 | 150 | 116 | 302 | 0
10:30 | 4189 | 484.5 | 2091 | 80 | 1581 | 1352.5 | 12.5 | 33 | 258.5 | 121 | 335 | 0
11:00 | 4048 | 484 | 2025 | 0 | 1941 | 1415 | 25 | 30 | 367 | 126 | 368 | 0
11:30 | 4059 | 484.5 | 2021 | 0 | 2109 | 1459.5 | 25 | 15 | 407 | 128 | 381 | 0
12:00 | 4070 | 485 | 2017 | 0 | 2277 | 1504 | 25 | 0 | 447 | 130 | 394 | 0
12:30 | 4101.5 | 485 | 2071.5 | 0 | 2371 | 1596 | 25 | 0 | 457.5 | 133 | 381 | 0
13:00 | 4133 | 485 | 2126 | 0 | 2465 | 1688 | 25 | 0 | 468 | 136 | 368 | 0
13:30 | 4133 | 485 | 2126 | 0 | 2465 | 1688 | 25 | 0 | 468 | 136 | 368 | 0
14:00 | 4133 | 485 | 2126 | 0 | 2465 | 1688 | 25 | 0 | 468 | 136 | 368 | 0
14:30 | 4066.5 | 485 | 2100 | 148 | 2557.5 | 1709.5 | 25 | 0 | 504 | 140 | 297 | 38.6775
15:00 | 4000 | 485 | 2074 | 296 | 2650 | 1731 | 25 | 0 | 540 | 144 | 226 | 77.355
15:30 | 4011 | 485 | 2058 | 158.5 | 2648.5 | 1728 | 25 | 0 | 581 | 134 | 163 | 120.33
16:00 | 4022 | 485 | 2042 | 21 | 2647 | 1725 | 25 | 0 | 622 | 124 | 100 | 163.305
16:30 | 4020 | 486 | 2030 | 10.5 | 2545 | 1657 | 25 | 0 | 665.5 | 123 | 63.5 | 149.4575
17:00 | 4018 | 487 | 2018 | 0 | 2443 | 1589 | 25 | 0 | 709 | 122 | 27 | 135.61 | [10 empty] | 472
17:30 | 3937 | 696 | 1920 | 0 | 2324 | 1511 | 25 | 0 | 674 | 130 | 14.5 | 110.305 | [10 empty] | 100
18:00 | 3856 | 905 | 1822 | 0 | 2205 | 1433 | 25 | 0 | 639 | 138 | 2 | 85 | [10 empty] | 20
18:30 | 3895 | 909 | 1819.5 | 0 | 2412 | 1483 | 25 | 0 | 648.5 | 146 | 1 | 98.3675 | [10 empty] | 592
19:00 | 3934 | 913 | 1817 | 0 | 2619 | 1533 | 25 | 0 | 658 | 154 | 0 | 111.735
19:30 | 4033 | 913 | 1842 | 0 | 2714 | 1532 | 25 | 0 | 513 | 140 | 0 | 98.365
20:00 | 4084 | 912 | 1929 | 0 | 2505 | 1530 | 25 | 0 | 514 | 144 | 0 | 84.995
20:30 | 4042.5 | 865 | 1914 | 0 | 2308.5 | 1594 | 25 | 0 | 422.5 | 145 | 0 | 69.4975
21:00 | 4001 | 818 | 1899 | 0 | 2112 | 1658 | 25 | 0 | 331 | 146 | 0 | 54
21:30 | 3948 | 821.5 | 1902.5 | 0 | 1856.5 | 1669.5 | 25 | 0 | 294.5 | 148 | 0 | 27
22:00 | 3895 | 825 | 1906 | 0 | 1601 | 1681 | 25 | 0 | 258 | 150 | 0 | 0
22:30 | 4000.5 | 826 | 1942 | 0 | 1520 | 1657.5 | 12.5 | 0 | 250.5 | 146 | 0 | 0
23:00 | 4106 | 827 | 1978 | 0 | 1439 | 1634 | 0 | 0 | 243 | 142 | 0 | 0
23:30 | 4090 | 827 | 1986.5 | 0 | 1384.5 | 1732.5 | 0 | 0 | 249.5 | 143 | 0 | 57.5 |  | Max Temp. in Dhaka |  | 35.5° C
24:00 | 4074 | 827 | 1995 | 0 | 1330 | 1831 | 0 | 0 | 256 | 144 | 0 | 115
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 254.695 MKWHr Energy Not Served 1.037 MKWHr Energy Requirement 255.732 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-04-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | [9 empty] | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 0 |  | 308000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | [6 empty] | 0 | 8 | 8 | 8 | 14 | 24 | 24 | 24 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 331885
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 4 | 14 | 17 | 18 | 19 | 19 | 17 | 13 | 8 | 3 | 0 | [8 empty] | 139455
6 | Sikalbaha 225MW CCPP (Gas) | 227 | 227 | 229 | 229 | 229 | 227 | 228 | 227 | 225 | 222 | 221 | 217 | 218 | 212 | 218 | 222 | 220 | 225 |  | 225 | 223 | 223 | 224 | 226 | 222 | 225 | 5256283
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 84 | 51 | 51 | 51 | 34 | [5 empty] | 55 | 63 | 77 | 78 | 61 | 77 | 78 | 68 |  | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 1284345
12 | Hathazari 100 MW peaking PP | [9 empty] | 10 | 46 | 57 | 57 | 55 | 54 | 14 | 36 | 42 |  | 46 | 46 | 47 | 47 | 47 | 47 | 47 | 635088
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 17 |  | 28 | 51 | 51 | 51 | 17 | 17 | 17 | 531090
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | [10 empty] | 21 | 38 | 37 | 38 | 36 | 36 | 36 | 36 |  | 36 | 38 | 38 | 35 | 38 | 39 | 39 | 463568
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 104 | 59 | 61 | 59 | 60 | 61 | 59 | 63 | 40 | 98 | 40 | 65 | 95 | 95 | 95 | 96 | 62 | 39 |  | 40 | 40 | 98 | 92 | 41 | 99 | 42 | 1786560
17 | Siddhirganj 335 MW CCPP | 170 | 170 | 170 | 170 | 172 | 170 | 170 | 140 | 200 | 222 | 170 | 217 | 212 | 212 | 213 | 213 | 214 | 130 |  | 190 | 190 | 218 | 150 | 150 | 222 | 222 | 4578675
18 | Kodda 300 MW PP Unit-2 (Summit) | [9 empty] | 30 | 120 | 145 | 150 | 150 | 148 | 145 | 150 | 145 |  | 145 | 45 | 45 | 45 | 15 | 15 | 15 | 1550618
19 | Ashuganj 195MW PP (APSCL-United) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 148 | 173 | 173 | 173 | 173 | 175 | 127 |  | 120 | 78 | 35 | 35 | 35 | 35 | 35 | 3161454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 180 | 180 | 180 | 140 | 140 | 110 | 100 | 110 | 180 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3117281
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4158000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 44 | 44 | 42 | 42 | 42 | 44 | 44 | 43 | 40 | 35 | 40 | 33 | 39 | 38 | 35 | 38 | 38 | 38 |  | 38 | 39 | 39 | 39 | 39 | 43 | 43 | 949536
33 | Ashuganj 225 MW CCPP | 217 | 216 | 215 | 217 | 217 | 189 | 179 | 189 | 183 | 191 | 194 | 188 | 184 | 199 | 206 | 207 | 208 | 180 |  | 206 | 200 | 199 | 209 | 213 | 212 | 211 | 4883000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 315 | 300 | 310 | 300 | 340 | 345 | 310 | 300 | 335 | 300 | 300 | 300 | 300 |  | 300 | 300 | 255 | 255 | 255 | 250 | 250 | 7259000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 320 | 300 | 300 | 310 | 330 | 335 | 305 | 305 | 340 | 300 | 300 | 300 | 300 |  | 295 | 300 | 345 | 295 | 295 | 315 | 295 | 7790000
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 399 | 396 | 397 | 397 | 397 | 364 | 353 | 350 | 383 | 402 | 388 | 378 | 399 | 401 | 400 | 406 | 405 | 333 |  | 312 | 356 | 358 | 395 | 348 | 366 | 405 | 9254910
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 400 | 350 | 350 | 350 | 350 | 350 | 320 | 450 | 450 | 370 | 400 | 450 | 450 | 450 | 450 | 450 | 350 |  | 370 | 370 | 420 | 450 | 450 | 450 | 450 | 9565250
41 | Haripur 360MW CCPP(HPL) | 346 | 352 | 304 | 303 | 303 | 305 | 303 | 308 | 310 | 340 | 275 | 330 | 330 | 295 | 298 | 298 | 298 | 255 |  | 255 | 255 | 322 | 309 | 308 | 350 | 352 | 7450000
42 | RPCL 210MW CCPP | 75 | 74 | 75 | 73 | 74 | 34 | 33 | 33 | 32 | 32 | 28 | 29 | 26 | 25 | 26 | 29 | 30 | 29 |  | 45 | 47 | 47 | 52 | 52 | 51 | 52 | 1024320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 11 | 13 | 33 | 42 | 20 | 54 | 52 | 40 | 37 | 16 | 9 | 0 | [8 empty] | 368140
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 30 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 662520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 63 | 63 | 62 | 62 | 62 | 62 | 61 | 60 | 40 | 60 | 60 | 59 | 55 | 55 | 60 | 61 |  | 61 | 60 | 60 | 61 | 62 | 61 | 61 | 1420800
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 30 | 30 | 30 | 81 | 81 | 78 | 80 | 80 | 80 | 79 | 79 | 79 | 79 | 79 | 78 |  | 76 | 79 | 79 | 80 | 80 | 81 | 81 | 1776960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 137 | 135 | 135 | 135 | 135 | 25 | 20 | 20 | 90 | 125 |  | 130 | 130 | 130 | 133 | 130 | 130 | 130 | 2837140
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 399000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 9 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238140
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 183392
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 52 | 50 | 50 | 51 | 50 | 50 | 50 | 50 |  | 51 | 53 | 53 | 53 | 53 | 53 | 53 | 1201200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 370344
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 275 | 270 | 275 | 280 | 275 | 270 | 275 | 275 | 280 | 280 | 280 | 285 | 280 | 270 | 270 | 260 |  | 270 | 280 | 275 | 270 | 255 | 260 | 275 | 6654000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 370 | 360 | 370 | 400 | 390 | 370 | 383 | 383 | 360 | 360 | 365 | 331 | 355 |  | 365 | 400 | 385 | 370 | 370 | 393 | 400 | 9202600
58 | Nababganj 55 MW PP (Southern power ) | [11 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 |  | 45 | 55 | 17 | 17 | 17 | 17 | 18 | 382542
59 | Tangail Palli Power Gen 22 MW | 6 | [6 empty] | 5 | 6 | 6 | 6 | 10 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 0 |  |  | 2 | 148800
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 233952
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 8 | 8 | 8 | 8 | 8 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 0 |  |  | 10 | 10 | 10 |  |  |  | 234072
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 10 | 5 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 12 | 0 |  |  |  | 240372
63 | Impoprt (Tripura) | 126 | 122 | 120 | 118 | 114 | 106 | 96 | 104 | 110 | 116 | 126 | 130 | 136 | 140 | 144 | 124 | 122 | 138 |  | 154 | 140 | 144 | 146 | 150 | 142 | 144 | 3052800
64 | Malancha, Ctg. EPZ (United) | 38 | 36 | 38 | 38 | 39 | 42 | 38 | 14 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 13 |  | 21 | 21 | 26 | 26 | 26 | 24 | 29 | 491040
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 17 | 17 | 17 | 15 | 15 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 409068
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 167400
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 32 | 33 | 33 | 33 | 803000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 482720
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 19 | 24 | 24 | 24 | 24 | 24 | 24 | 502200
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 18 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 17 | 25 | 25 | 631440
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 |  | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 745700
73 | Ghorashal 108MW PP (Regent) | 75 | 75 | 75 | 75 | 72 | 72 | 72 | 52 | 52 | 52 | 52 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 955545
| Feni Lanka Power | 106 | 90 | 62 | 45 | 35 | 17 | 17 | 17 | 17 | [6 empty] | 0 | 70 | 70 |  | 70 | 36 | 17 | 34 | 34 | 88 | 114 | 899460
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 9 | 8 | 8 | 8 | 50 |  | 73 | 78 | 77 | 78 | 75 | 20 | 9 | 541800
| Manikgonj 162MW PP(MPGL) | 80 | [5 empty] | 5 | 17 | 18 | 54 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 35 |  | 60 | 162 | 162 | 35 | 17 | 17 | 17 | 1127520
77 | Siddhirganj 100 PP(Dutch Bangla) | [9 empty] | 1 | 24 | 55 | 75 | 75 | 75 | 75 | 45 | 30 |  | 30 | 30 | 24 | 16 | 16 | 16 | 20 | 541440
78 | Gazipur 52 MW PP | 16 | 16 | 16 |  |  |  |  | 2 | 10 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 41 |  | 41 | 49 | 49 | 49 | 49 | 25 | 16 | 451680
79 | Kodda 150 MW PP | [8 empty] | 16 | 32 | 82 | 98 | 98 | 98 | 98 | 98 | 128 | 150 |  | 150 | 150 | 150 | 48 | 16 | 16 | 32 | 1295520
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 24 | 26 | 34 | 43 | 43 | 50 | 46 | 40 | 30 | 32 | 36 |  | 50 | 52 | 43 | 31 | 52 | 38 | 46 | 1050994
| Gazipur 100 MW PP | 17 | [7 empty] | 10 | 51 | 92 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 98 | 88 | 88 | 88 | 1500125
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 4 | 5 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 31078
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 974827
| Karnaphuli Power Ltd. | 53 | 54 | 54 | 54 | 54 | 54 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 34 | 34 | 51 | 1270430
82 | Madanganj 102 PP(Summit) | [10 empty] | 32 | 72 | 68 | 80 | 97 | 97 | 97 | 77 |  | 68 | 66 | 52 | 34 | 20 | 17 | 17 | 783907
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 10 | 9 | 4 | 12 | 19 | 0 | [9 empty] | 60959
86 | Meghnaghat CCPP ( Summit) | 265 | 280 | 290 | 275 | 280 | 310 | 260 | 310 | 280 | 299 | 304 | 298 | 291 | 300 | 296 | 283 | 262 | 276 |  | 233 | 286 | 304 | 268 | 264 | 303 | 286 | 6980625
87 | Meghnaghat 100 MW(IEL) | 4 | 25 | 25 | 24 | 25 | 25 | 24 | 25 | 25 | 52 | 63 | 67 | 68 | 67 | 67 | 64 | 64 | 67 |  | 67 | 24 | 24 | 8 | 9 | 8 | 23 | 911040
| Meghnaghat 104 MW PP (OPCL) | 34 | 53 | 53 | 52 | 52 | 45 | 53 | 52 | 52 | 52 | 34 | 50 | 52 | 52 | 52 | 45 | 45 | 35 |  | 45 | 45 | 40 | 17 | 16 | 16 | 44 | 1057920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 44 | 44 | 44 | 44 | 44 | 44 | 56 | 10 |  | 56 | 56 | 56 | 22 | 10 | 20 | 33 | 1107480
92 | Fenchuganj 44MW (Energyprima) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 43 | 42 | 42 | 46 | 46 | 41 | 43 | 43 | 44 |  | 47 | 48 | 48 | 45 | 49 | 49 | 49 | 1094328
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1160468
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 8 | 24 | 50 | 66 | 66 | 48 | 48 | 48 | 48 | 48 |  | 64 | 83 | 48 | 40 | 16 | 16 | 16 | 674640
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 16 |  | 38 | 38 | 38 | 39 | 39 | 39 | 6 | 333120
96 | Chattogram 108 MW PP (ECPV) | 25 | 25 | [14 empty] | 3 | 19 |  | 31 | 31 | 30 | 31 | 31 | 31 |  | 241920
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [9 empty] | 7 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 30 | 22 | 30 | 15 | 15 | 15 | 256332
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 43 |  | 47 | 50 | 17 | 17 | 17 | 17 |  | 439560
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | [9 empty] | 14900
103 | Kamalaghat 54 MW PP(Banco Energy) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 | 17 |  | 259560
104 | Keranigonj 300 MW PP (APR) | [9 empty] | 160 |  |  |  | 0 | 296 | 21 | 0 | [9 empty] | 450336
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 | 8 |  |  |  | 3 | 22 | 55 | 55 | 72 | 157 | 158 | 160 | 160 | 146 | 114 | 117 | 135 |  | 173 | 173 | 173 | 88 | 24 | 26 | 46 | 1958400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [6 empty] | 7 | 17 | 17 | 17 | 34 | 35 | 34 | 22 | 17 | 17 | 17 | 49 |  | 88 | 149 | 149 | 118 | 71 | 65 | 37 | 828580
115 | Juldah 100 MW PP Unit-3 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 76 | 76 | 76 | 76 | 12 | 20 | 25 | 943680
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 34 |  | 52 | 120 | 120 | 120 | 120 | 100 | 51 | 1627680
117 | Ashuganj 150MW PP (Midland) | [9 empty] | 8 | 42 | 73 | 85 | 99 | 102 | 104 | 107 | 115 |  | 122 | 140 | 100 | 100 | 50 | 10 | 10 | 1226109
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 365 | 365 | 365 | 365 | 365 | 380 | 368 | 377 | 369 | 370 | 369 | 398 | 368 | 368 | 368 | 368 |  | 402 | 410 | 391 | 368 | 368 | 381 | 367 | 9034000
| Jamalpur 115 MW PP (United) | 30 | 16 | 16 | 16 | 16 | 18 | 47 | 56 | 56 | 63 | 98 | 99 | 98 | 98 | 98 | 49 | 49 | 70 |  | 108 | 108 | 108 | 47 | 47 | 49 | 49 | 1455600
| Anwara 300 MW PP (United) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 121 | 122 | 122 | 124 | 123 | 123 | 123 | 122 |  | 190 | 190 | 190 | 278 | 285 | 231 | 88 | 3138873
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 75 | 88 | 88 | 32 | 12 | 26 | 38 | 869760
| Anlima Energy Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 840545
| Bhairob 54.5 MW | 35 | 35 | 28 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 |  | 16 | 595800
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 15 | 23 | 18 | 30 | 33 | 32 | 28 | 23 | 15 | 2 | 0 | [8 empty] | 222609
| Chandpur 115(Doreen) | 71 | 19 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 51 | 59 | 76 | 86 | 115 | 115 | 115 | 50 |  | 70 | 115 | 115 | 114 | 115 | 115 | 115 | 1586880
| Kanchan Purbachal Power Generation Ltd. | 17 | [5 empty] | 7 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 573120
| Mirsharai 150 MW (Oil) | 54 | 54 | 54 | 54 | 108 | 108 | 108 | 108 | 108 | 108 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 54 |  | 54 | 54 | 54 | 54 | 34 | 18 | 50 | 2276581
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 6578 | 6301 | 6131 | 5996 | 5991 | 5857 | 5836 | 5884 | 6188 | 6919 | 7137 | 7509 | 7736 | 7686 | 7880 | 7449 | 7528 | 7008 |  | 7664 | 7994 | 7936 | 7306 | 6675 | 6755 | 6598 | 166315391
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [10 empty] | 49 | 59 | 67 | 80 | 80 | 96 | 32 | 32 |  | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 563520
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [9 empty] | 36 | 30 | [15 empty] | 58043
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [13 empty] | 16 | 23 | 29 | 29 | 32 |  | 43 | 38 | 38 | 0 |  |  |  | 215520
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 10 | [18 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 113760
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 4 | 12 | 38 | 69 | 92 | 102 | 90 | 63 | 10 | 22 | 10 | 3 | 1 |  | 0 | [6 empty] | 532080
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [11 empty] | 14 | 54 | 63 | 118 | 137 | 150 | 72 |  | 60 | 17 | 17 | 17 | 17 | 17 | 0 | 732000
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [11 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 16 | 16 | 16 | 16 | 16 |  | 340032
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 162 | 193 | 192 | 192 | 192 | 192 | 191 | 189 | 189 | 179 | 176 | 178 | 176 | 176 | 181 | 180 | 180 | 181 |  | 183 | 183 | 180 | 180 | 180 | 180 | 183 | 4313000
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 23 | 22 | 23 | 20 | 18 | 17 | 17 | 18 | 20 | 21 | 24 | 24 | 24 | 22 | 23 | 23 |  | 28 | 24 | 29 | 30 | 28 | 28 | 27 | 552300
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [11 empty] | 32 | 32 | 32 | 32 | 40 | 8 | 8 |  | 8 | 0 | [5 empty] | 164250
143 | Gopalganj 100 MW Peaking PP | [14 empty] | 25 | 75 | 75 | 74 |  | 75 | 0 | [5 empty] | 313648
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [10 empty] | 50 | 67 | 85 | 85 | 85 | 100 | 32 | 32 |  | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 637488
146 | Bheramara HVDC | 486 | 485 | 485 | 485 | 485 | 485 | 485 | 484 | 485 | 485 | 484 | 485 | 485 | 485 | 485 | 485 | 487 | 905 |  | 913 | 913 | 912 | 818 | 825 | 827 | 827 | 13936727
147 | Bheramara 410 MW CCPP | 350 | 340 | 325 | 310 | 300 | 285 | 275 | 250 | 230 | 200 | 195 | 200 | 200 | 195 | 190 | 190 | 180 | 180 |  | 170 | 170 | 175 | 180 | 185 | 185 | 185 | 5767488
148 | Payra 1320 MW | 1202 | 1162 | 1122 | 1050 | 1000 | 1000 | 1080 | 1172 | 1170 | 1200 | 1232 | 1244 | 1244 | 1230 | 1244 | 1244 | 1030 | 800 |  | 900 | 900 | 900 | 1030 | 1050 | 1000 | 1170 | 29443700
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 75 | 77 | 77 | 77 | 76 | 75 | 76 | 75 | 75 | 74 | 74 | 74 | 73 | 73 | 76 | 76 |  | 75 | 75 | 76 | 75 | 75 | 76 | 76 | 1756364
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | [16 empty] | 76 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 177 | 1053200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 24 | 32 | 32 | 32 | 32 | 32 | 31 |  | 31 | 0 | [5 empty] | 229350
| Sirajgonj 6.55 MW Solar | [13 empty] | 4 | 4 | 1 | 0 | 0 | [8 empty] | 9700
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 208 | 206 | 160 | 160 | 160 | 160 | 163 | 160 | 195 | 195 | 150 | 166 | 192 | 190 | 190 | 194 | 194 | 190 |  | 150 | 150 | 153 | 184 | 196 | 197 | 197 | 4591364
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 177 | 177 | 140 | 140 | 140 | 140 | 149 | 156 | 156 | 153 | 150 | 151 | 152 | 152 | 151 | 147 | 141 | 138 |  | 138 | 136 | 136 | 135 | 131 | 136 | 142 | 3825882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 359 | 304 | 321 | 300 | 308 | 346 | 416 | 415 | 370 | 332 | 330 | 275 | 308 | 302 | 290 | 281 | 268 | 253 |  | 253 | 253 | 243 | 238 | 265 | 250 | 264 | 7499672
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [11 empty] | 4 | 4 | 10 | 28 | 28 | 28 | 28 |  | 15 | 4 | 4 | 4 | 4 | 4 | 4 | 145948
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 17 | 17 | 19 | 20 | 18 | 19 | 19 | 20 | 20 |  | 20 | 22 | 22 | 22 | 20 | 22 | 21 | 472560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 0 |  |  |  |  | 117900
165 | Amnura 50 MW PP(Sinha) | [13 empty] | 14 | 27 | 27 | 21 | 21 |  | 0 | [6 empty] | 100240
166 | Katakhali 50 MW PP (Northern) | [10 empty] | 16 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 8 | 0 | [5 empty] | 290434
167 | Katakhali 50 MW Peaking PP | [14 empty] | 20 | 40 | 40 | 40 |  | 40 | 40 | 40 | 0 |  |  |  | 215752
168 | Santahar 50 MW Peaking PP | [16 empty] | 12 | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 0 | 209387
169 | Natore 52 MW PP (Rajlanka) | [10 empty] | 34 | 43 | 43 | 35 | 43 | 43 | 43 | 16 |  | 8 | 0 | [5 empty] | 294216
170 | Chapainawabganj 100 MW Peaking PP | [15 empty] | 30 | 52 | 52 |  | 50 | 24 | 24 | 24 |  |  |  | 202888
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  |  | 10 | 35 | 35 | 35 | 50 | 50 | 70 | 70 | 70 | 70 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 57 | 962400
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [5 empty] | 20 | 35 | 35 | 70 | 75 | 75 | 75 | 75 | 75 | 75 | 35 | 35 |  | 35 | 0 |  |  |  |  | 35 | 760128
173 | Rangpur 20 MW GTPP | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 26 |  |  | 29 | 33 | 34 | 34 | 34 | 34 | 34 | 34 | 67 | 84 | 34 | 34 |  | 34 | 34 | 34 | 24 |  |  | 31 | 711513
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 3 | 4 | 5 | 4 | 6 | 6 | 4 | 5 | 3 | 2 | 1 |  | 0 | [6 empty] | 37998
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 36 |  |  |  |  | 15 | 55 | 55 | 60 | 115 | 75 | 75 | 75 | 74 | 74 | 75 | 36 |  | 36 | 36 | 36 | 36 |  |  | 6 | 1062336
| Intraco Solar 30 MW | [5 empty] | 1 | 5 | 13 | 20 | 19 | 27 | 23 | 31 | 12 | 17 | 15 | 3 | 0 | [8 empty] | 200125
| Adani Power Jharkhanda Ltd | [9 empty] | 15 | 108 | 186 | 370 | 413 | 414 | 408 | 407 | 407 |  | 408 | 407 | 404 | 403 | 406 | 408 | 408 | 4900000
178 | Teesta Solar Limited | [5 empty] | 2 | 41 | 76 | 101 | 103 | 161 | 163 | 160 | 136 | 101 | 30 | 5 | 0 | [8 empty] | 1047110