## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-08-13 | Monday
|  | Date (day): | 2018-08-13 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11053 | MW |  |  | (b) At Evening Peak Hour : |  | 12396 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-08-12 | 2018-08-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 100 | 100 | 100 | 100 | 70 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 100 | 100 | 100 | 90 |  | Gas shortage
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 20 | 0 | 0 | 0
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 374 | 412 | 412
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 75 | 96 | 110 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 211 | 221 | 232 | 250 | 139 |  | Gas shortage
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 340 | 340 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 100 | 100 | 100 |  | 10
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 305 | 305 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 65 | 65 | 84 |  | 16 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 75 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 15 | 100 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 85 | 100 | 100 | 100
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 212 | 214 | 215 | 215
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 51 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 35 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 132 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 8 | 8 | 8 |  | 100 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 57 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 37 | 51 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 210 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 54 | 0 | 300
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 96 | 100 | 100 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 97 | 99 | 100 | 100
37 | Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 149 | 149 | 115 | 149 | 150 | 150
| Dhaka area Total |  |  |  |  | 5784 | 5548 | 3663 | 4010 | 4239 | 4576 | 772 | 445
38 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
39 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
40 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 44 | 45 | 45 |  | 5
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 189 | 200 | 190 | 200
42 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
43 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 220
44 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 135 | 135 | 135
45 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 50 | 50 | 50
46 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 16 | 80 | 40 | 80
47 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 45 | 50 | 50
48 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 90 | 100 | 100
49 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 8 | 10 | 10
50 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 86 | 93 | 100 | 100
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 653 | 780 | 755 | 1025 | 360 | 54
51 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 100 | 120 | 120 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Under maint.
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 130 | 130 | 0 | 0 | 134
52 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 178 | 225 | 225 |  |  | FGMO
53 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 360 | 360 |  | 360
54 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 334 | 334 | 360 | 360 |  |  | FGMO
55 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 33 | 40
56 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 4 | 6 | 20 |  | 51
57 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 5 | 30 | 30 | 48 |  | Gas shortage
58 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 108 | 110 | 75 | 110 | 85
59 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 38 | 45 | 45 | 45 |  | 6 | Engine problem
60 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
61 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
62 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 57 | ST under maint.
63 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
64 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 126 | 172 | 126 | 174
65 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
66 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 52 | 52
67 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 21 | 22 | 22
68 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 83 | 200 | 100 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1449 | 1643 | 1805 | 2059 | 431 | 474
69 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 48 | 47 | 50 | 50 | 152 |  | Gas shortage
70 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
71 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 83 | 90 | 90 | 90
72 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 2 | 0
73 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 122 | 129 | 135 | 135
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 276.9 | 288 | 299 | 297 | 152 | 0
74 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 65 | 68 | 70 | 70
75 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 62 | 62 | 62 | 62
76 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 10 | 163 | 163 | 163
77 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 314 | 339 | 330 | 330
78 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 53 | 51 | 51
79 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 44 | 47 | 50 | 50
80 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
81 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 30 | 32 | 32 |  |  | GT-9 under maint.
82 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 83 | 86 | 86 | 86
83 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 47 | 48 | 48
84 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 127 | 130 | 130 | 130
85 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 19 | 19 | 19
86 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 43 | 48 | 48
87 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 23 | 23 | 23
88 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 325 | 341 | 341 |  |  | FGMO
89 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 6 | 7 | 8 | 8
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1208 | 1453 | 1472 | 1472 | 0 | 0
90 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 48 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 494 | 496 | 499 | 498
91 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 73 | 97 | 100 | 100 |  | 10 | Engine problem
92 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 80 | 115 | 115 | 115
93 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 49 | 0 | 48
94 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0
95 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 91 | 0 | 80
96 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 410 | 410 | 410
97 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 32 | 40 | 40
98 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Experied
99 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 94 | 100 | 100 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 1183 | 1438 | 1264 | 1439 | 0 | 10
100 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 110 | 110 | 110
101 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
102 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 36 | 33 | 33
103 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 187 | 185 | 100 | 194
104 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 97 | 98 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 371 | 429 | 338 | 462 | 0 | 0
105 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
106 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
107 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 36 | 0 | 32
108 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 20 | 50 | 50 | 50
109 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
110 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 43 | 46 | 44 | 44
111 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 205 | 220 | 215 | 215
112 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 173 | 220 | 150 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 148 | 151 | 154 | 154
113 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 40
114 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18
115 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
116 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
117 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 51 | 52 | 52 | 52
118 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 33 | 100 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 755 | 1039 | 847 | 1032 | 71 | 107
119 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal shortage
120 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 274 |  | Coal shortage
121 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 16 | 16
122 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 0 | 17 | 34 | 34 | 359 | 85
| Total |  |  |  |  | 16102 | 15559 | 9558.9 | 11097 | 11053 | 12396 | 2145 | 1175
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9098.9151 | 10563 | 10521.1173 | 11799.4907
A. |  | 2018-08-12 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11097 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
2 | Minimum Generation : |  |  | 8570.6 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11097 | MW
3 | Day peak Generation : |  |  | 9558.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10563 | MW
4 | Evening peak Generation : |  |  | 11097 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 234.2529 | MKWHr | By Solar | 0.01195 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 133.7787 | MKWHr |  | By Oil: | 80.8164 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 0 | MKWHr |  | By Hydro: | 4.4523 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2145 | MW | Dhaka | 4148 | 4148 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1175 | MW | Chittagong | 1010 | 1010 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3320 | MW | Khulna | 1396 | 1396 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1165.05 | MMCFD |  |  | Rajshahi | 1147 | 1147 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 93508621.69 | ii) Oil : | Taka | 819755754.08 | Comilla | 954 | 954 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 0 | Total | Taka | 913264375.77 | Mymensingh | 710 | 710 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 5.897 | MKWHr. | Sylhet | 446 | 446 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -580 | MW at | 19:30 | hrs | Barisal | 260 | 260 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -600 | MW at | 20:00 | hrs | Rangpur | 492 | 492 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 10563 | 10563 |  | 0
B. |  | 2018-08-13 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12396 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9700 | MW
4 | Reserve(Generation end) |  |  |  | 596 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 249.0929 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8491.4 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.8124 | MKWHr. | ii) HVDC Flow at Peak Time |  | 496 | MW at | 19:30 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3811 | MKWHr. | iii) Maximum HVDC Flow : |  | 496 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.91 |  | (b) Today: | 104.99 |  | (c) Rule Curve: |  | 92.84
.

## YesterdayGen
2018-08-12
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 390 | 273 | 96 | 0 | 370 | 200 | 100 | 64 | 55 | 218 | 0 | 0 | 52 | 100 | 102 | 132 | 60 | 8 | 10 | 40 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 107 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 40 | 81 | 47 | 90 | 88 | 45 | 19 | 34 | 120 | 0 | 130 | 0 | 312 | 220 | 109 | 100 | 40 | 0 | 10 | 45 | 85 | 41 | 0 | 19 | 11 | 33 | 15 | 158 | 48 | 91 | 22 | 0 | 70 | 62 | 50 | 50 | 10 | 300 | 32 | 86 | 48 | 117 | 19 | 46 | 8 | 7 | 23 | 11 | 140 | 180 | 166 | 50 | 130 | 51 | 125 |  | 495 | 0 | 410 | 92 | 112 | 0 | 0 | 0 | 34 | 65 | 40 | 187 | 33 | 96 | 0 | 0 | 0 | 43 | 31 | 100 | 50 | 43 | 43 | 52 | 38 | 18 | 10 | 11 | 0 | 0 | 0 | 15 | 14 | 217 | 0 | 0 | 173 | 98 | 98 | 152 | 0 |  | 7648 | 2770 | 10418 | 4088 | 495 | 1410 | 2861 | 0 | 187 | 1219 | 158 | 0 | 0 | 104.91
2:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 393 | 292 | 96 | 0 | 380 | 200 | 100 | 64 | 55 | 218 | 0 | 0 | 50 | 100 | 102 | 132 | 60 | 8 | 10 | 40 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 105 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 100 | 0 | 40 | 81 | 46 | 90 | 94 | 45 | 19 | 35 | 120 | 0 | 130 | 0 | 301 | 220 | 109 | 100 | 40 | 0 | 10 | 45 | 85 | 41 | 0 | 19 | 11 | 33 | 15 | 154 | 48 | 91 | 22 | 0 | 70 | 62 | 50 | 50 | 15 | 302 | 32 | 86 | 48 | 98 | 19 | 46 | 8 | 35 | 23 | 11 | 50 | 180 | 57 | 10 | 122 | 21 | 106 |  | 495 | 0 | 412 | 92 | 113 | 0 | 0 | 0 | 34 | 65 | 40 | 187 | 31 | 98 | 0 | 0 | 0 | 43 | 31 | 100 | 50 | 43 | 43 | 52 | 38 | 18 | 10 | 11 | 0 | 0 | 0 | 15 | 14 | 218 | 0 | 0 | 172 | 97 | 98 | 153 | 0 |  | 7352 | 2773 | 10125 | 4067 | 495 | 1470 | 2572 | 0 | 185 | 1182 | 154 | 0 | 0 | 104.91
3:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 400 | 292 | 96 | 0 | 400 | 200 | 100 | 64 | 55 | 216 | 0 | 0 | 0 | 100 | 102 | 132 | 60 | 8 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 103 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 70 | 0 | 40 | 81 | 46 | 90 | 99 | 45 | 19 | 34 | 120 | 0 | 130 | 0 | 305 | 220 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 41 | 0 | 19 | 11 | 33 | 15 | 152 | 48 | 91 | 22 | 0 | 67 | 62 | 50 | 50 | 10 | 300 | 32 | 86 | 48 | 98 | 19 | 46 | 8 | 75 | 23 | 11 | 0 | 180 | 0 | 0 | 132 | 0 | 106 |  | 495 | 0 | 412 | 92 | 112 | 0 | 0 | 0 | 34 | 55 | 40 | 190 | 32 | 96 | 0 | 0 | 0 | 43 | 31 | 100 | 50 | 43 | 43 | 52 | 38 | 18 | 10 | 11 | 0 | 0 | 0 | 15 | 14 | 216 | 0 | 0 | 172 | 98 | 96 | 152 | 0 |  | 7192 | 2760 | 9952 | 4071 | 495 | 1525 | 2384 | 0 | 183 | 1142 | 152 | 0 | 0 | 104.91
4:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 405 | 292 | 29 | 0 | 400 | 200 | 100 | 64 | 55 | 222 | 0 | 0 | 0 | 50 | 102 | 132 | 60 | 8 | 0 | 40 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 101 | 80 | 0 | 0 | 16 | 0 | 228 | 0 | 50 | 0 | 40 | 82 | 46 | 90 | 98 | 45 | 19 | 38 | 120 | 0 | 130 | 0 | 300 | 222 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 148 | 48 | 91 | 22 | 0 | 65 | 62 | 50 | 50 | 10 | 300 | 32 | 86 | 48 | 98 | 19 | 46 | 8 | 180 | 23 | 11 | 0 | 180 | 0 | 0 | 132 | 0 | 106 |  | 495 | 0 | 417 | 92 | 101 | 0 | 0 | 0 | 34 | 45 | 40 | 162 | 31 | 87 | 0 | 0 | 0 | 43 | 31 | 100 | 50 | 43 | 43 | 52 | 38 | 18 | 10 | 11 | 0 | 0 | 0 | 15 | 14 | 217 | 0 | 0 | 172 | 98 | 0 | 156 | 0 |  | 7124 | 2615 | 9739 | 4059 | 495 | 1633 | 2150 | 0 | 181 | 1073 | 148 | 0 | 0 | 104.91
5:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 410 | 292 | 13 | 0 | 400 | 200 | 57 | 64 | 55 | 221 | 0 | 0 | 0 | 7 | 70 | 98 | 30 | 8 | 0 | 39 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 105 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 50 | 0 | 40 | 48 | 46 | 90 | 88 | 45 | 19 | 38 | 120 | 0 | 130 | 0 | 300 | 222 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 142 | 48 | 91 | 22 | 0 | 65 | 62 | 50 | 47 | 10 | 300 | 32 | 86 | 48 | 98 | 19 | 47 | 8 | 250 | 23 | 11 | 0 | 180 | 0 | 0 | 132 | 0 | 107 |  | 495 | 0 | 415 | 92 | 97 | 0 | 0 | 0 | 34 | 45 | 40 | 165 | 32 | 81 | 0 | 0 | 0 | 43 | 31 | 100 | 50 | 43 | 43 | 52 | 38 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 172 | 96 | 0 | 156 | 0 |  | 6951 | 2577 | 9528 | 4065 | 495 | 1700 | 1966 | 0 | 185 | 975 | 142 | 0 | 0 | 104.91
6:00 | 70 | 100 | 0 | 100 | 300 | 0 | 20 | 415 | 290 | 0 | 0 | 400 | 200 | 15 | 16 | 15 | 224 | 0 | 0 | 0 | 7 | 102 | 16 | 10 | 8 | 0 | 6 | 18 | 55 | 36 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 95 | 80 | 0 | 0 | 8 | 0 | 227 | 0 | 50 | 0 | 40 | 16 | 4 | 90 | 86 | 45 | 19 | 38 | 120 | 0 | 130 | 0 | 300 | 222 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 130 | 48 | 64 | 22 | 0 | 70 | 62 | 50 | 47 | 30 | 302 | 20 | 86 | 48 | 98 | 19 | 46 | 8 | 260 | 23 | 11 | 0 | 180 | 0 | 0 | 132 | 0 | 107 |  | 494 | 0 | 419 | 69 | 97 | 0 | 0 | 0 | 34 | 0 | 40 | 141 | 25 | 75 | 0 | 0 | 0 | 0 | 10 | 50 | 50 | 43 | 43 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 172 | 96 | 0 | 155 | 0 |  | 6492 | 2362 | 8854 | 3983 | 494 | 1720 | 1691 | 0 | 175 | 661 | 130 | 0 | 0 | 104.91
7:00 | 70 | 100 | 0 | 100 | 250 | 0 | 20 | 370 | 292 | 0 | 0 | 400 | 200 | 7 | 16 | 15 | 219 | 0 | 0 | 0 | 7 | 102 | 16 | 10 | 8 | 0 | 6 | 18 | 56 | 17 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 105 | 80 | 0 | 0 | 8 | 0 | 228 | 0 | 50 | 0 | 40 | 16 | 0 | 90 | 86 | 40 | 19 | 24 | 120 | 0 | 130 | 0 | 301 | 222 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 100 | 48 | 64 | 22 | 0.4 | 65 | 62 | 50 | 47 | 70 | 300 | 30 | 86 | 47 | 99 | 19 | 48 | 8 | 280 | 23 | 11 | 0 | 180 | 0 | 0 | 132 | 0 | 107 |  | 495 | 0 | 350 | 69 | 85 | 0 | 0 | 0 | 29 | 0 | 40 | 189 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 43 | 43 | 51 | 38 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 167 | 94 | 0 | 152 | 0 |  | 6392.4 | 2291 | 8683.4 | 3863 | 495 | 1767 | 1636 | 0 | 185 | 637 | 100 | 0.4 | 0 | 104.91
8:00 | 70 | 100 | 0 | 100 | 300 | 0 | 20 | 300 | 271 | 0 | 0 | 400 | 200 | 7 | 15 | 15 | 214 | 0 | 0 | 0 | 7 | 102 | 32 | 10 | 8 | 0 | 6 | 18 | 55 | 17 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 105 | 80 | 0 | 0 | 8 | 0 | 228 | 0 | 50 | 0 | 40 | 16 | 0 | 90 | 86 | 38 | 19 | 6 | 100 | 0 | 130 | 0 | 342 | 229 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 96 | 48 | 64 | 22 | 0.6 | 65 | 62 | 50 | 47 | 70 | 321 | 32 | 86 | 47 | 98 | 19 | 46 | 8 | 280 | 23 | 11 | 0 | 180 | 0 | 0 | 132 | 0 | 122 |  | 494 | 0 | 300 | 33 | 97 | 0 | 0 | 0 | 0 | 0 | 40 | 189 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 43 | 43 | 51 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 156 | 90 | 0 | 150 | 0 |  | 6399.6 | 2171 | 8570.6 | 3837 | 494 | 1721 | 1623 | 0 | 185 | 614 | 96 | 0.6 | 0 | 104.91
9:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 375 | 252 | 0 | 0 | 360 | 200 | 7 | 15 | 23 | 216 | 0 | 0 | 0 | 7 | 102 | 82 | 50 | 8 | 30 | 9 | 18 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 34 | 0 | 109 | 80 | 0 | 0 | 16 | 0 | 228 | 0 | 80 | 0 | 40 | 16 | 0 | 90 | 86 | 45 | 19 | 2 | 80 | 0 | 130 | 0 | 300 | 182 | 108 | 100 | 40 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 120 | 48 | 80 | 22 | 1.3 | 65 | 62 | 50 | 47 | 109 | 301 | 30 | 84 | 46 | 98 | 19 | 47 | 6 | 290 | 23 | 11 | 0 | 180 | 0 | 10 | 132 | 10 | 123 |  | 494 | 0 | 411 | 85 | 97 | 0 | 0 | 0 | 0 | 0 | 32 | 187 | 22 | 90 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 43 | 51 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 147 | 95 | 0 | 153 | 0 |  | 6682.3 | 2303 | 8985.3 | 3933 | 494 | 1706 | 1874 | 0 | 189 | 668 | 120 | 1.3 | 0 | 104.91
10:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 375 | 232 | 0 | 0 | 340 | 200 | 8 | 52 | 40 | 214 | 0 | 0 | 0 | 40 | 102 | 82 | 70 | 8 | 31 | 37 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 34 | 0 | 109 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 80 | 0 | 40 | 16 | 0 | 90 | 86 | 38 | 19 | 2 | 80 | 0 | 130 | 0 | 338 | 199 | 108 | 100 | 40 | 0 | 10 | 38 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 120 | 48 | 82 | 22 | 1.3 | 65 | 62 | 47 | 47 | 109 | 317 | 30 | 84 | 45 | 115 | 19 | 46 | 6 | 300 | 23 | 11 | 0 | 178 | 0 | 20 | 132 | 21 | 118 |  | 494 | 0 | 410 | 75 | 97 | 0 | 0 | 0 | 0 | 0 | 32 | 188 | 23 | 80 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 43 | 51 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 167 | 95 | 0 | 150 | 0 |  | 6846.3 | 2295 | 9141.3 | 4010 | 494 | 1665 | 1999 | 0 | 189 | 663 | 120 | 1.3 | 0 | 104.91
11:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 370 | 221 | 26 | 0 | 340 | 200 | 68 | 64 | 40 | 212 | 0 | 0 | 0 | 80 | 102 | 116 | 75 | 8 | 30 | 40 | 18 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 34 | 0 | 121 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 135 | 0 | 40 | 16 | 12 | 90 | 86 | 40 | 19 | 2 | 120 | 0 | 130 | 0 | 305 | 188 | 108 | 100 | 39 | 0 | 10 | 38 | 85 | 0 | 7 | 19 | 11 | 33 | 0 | 122 | 49 | 83 | 22 | 1.3 | 67 | 62 | 47 | 47 | 90 | 328 | 30 | 84 | 44 | 117 | 19 | 43 | 6 | 310 | 15 | 11 | 0 | 190 | 0 | 50 | 132 | 50 | 118 |  | 494 | 0 | 410 | 74 | 81 | 0 | 0 | 0 | 0 | 0 | 32 | 180 | 24 | 80 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 43 | 43 | 50 | 0 | 18 | 9 | 11 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 168 | 96 | 20 | 149 | 0 |  | 7137.3 | 2223 | 9360.3 | 3984 | 494 | 1642 | 2190 | 0 | 201 | 726 | 122 | 1.3 | 0 | 104.91
12:00 | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 370 | 211 | 75 | 0 | 340 | 305 | 90 | 48 | 40 | 212 | 0 | 0 | 15 | 85 | 102 | 133 | 75 | 8 | 51 | 35 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 37 | 0 | 109 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 40 | 16 | 16 | 90 | 86 | 44 | 19 | 2 | 120 | 0 | 130 | 0 | 334 | 205 | 108 | 100 | 39 | 0 | 10 | 38 | 85 | 0 | 8 | 19 | 11 | 33 | 0 | 126 | 48 | 83 | 22 | 1.9 | 65 | 62 | 44 | 44 | 10 | 314 | 30 | 83 | 44 | 127 | 0 | 43 | 6 | 310 | 15 | 11 | 83 | 195 | 0 | 96 | 122 | 97 | 115 |  | 494 | 0 | 410 | 73 | 80 | 0 | 0 | 0 | 0 | 0 | 32 | 187 | 23 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 43 | 43 | 51 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 173 | 97 | 94 | 148 | 0 |  | 7249.9 | 2309 | 9558.9 | 4027 | 494 | 1546 | 2626 | 0 | 189 | 549 | 126 | 1.9 | 0 | 104.91
13:00 | 70 | 100 | 0 | 100 | 330 | 0 | 0 | 360 | 201 | 96 | 0 | 340 | 200 | 100 | 52 | 40 | 209 | 0 | 0 | 70 | 99 | 102 | 133 | 86 | 8 | 46 | 35 | 18 | 56 | 55 | 22 | 25 | 22 | 33 | 33 | 43 | 0 | 107 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 60 | 28 | 80 | 86 | 40 | 19 | 8 | 120 | 0 | 130 | 0 | 300 | 184 | 157 | 100 | 39 | 0 | 20 | 38 | 85 | 0 | 0 | 19 | 11 | 33 | 0 | 134 | 48 | 82 | 22 | 1.9 | 66 | 62 | 44 | 47 | 10 | 298 | 30 | 83 | 44 | 114 | 0 | 45 | 7 | 300 | 22 | 11 | 100 | 190 | 0 | 92 | 122 | 99 | 144 |  | 494 | 0 | 410 | 80 | 80 | 0 | 0 | 0 | 0 | 0 | 32 | 173 | 11 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 0 | 50 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 152 | 94 | 94 | 149 | 0 |  | 7246.9 | 2262 | 9508.9 | 3889 | 494 | 1562 | 2700 | 0 | 187 | 541 | 134 | 1.9 | 0 | 104.91
14:00 | 70 | 100 | 0 | 100 | 330 | 0 | 0 | 320 | 210 | 96 | 0 | 340 | 200 | 100 | 65 | 40 | 170 | 0 | 0 | 100 | 100 | 102 | 133 | 86 | 8 | 49 | 40 | 18 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 42 | 0 | 107 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 32 | 90 | 86 | 43 | 19 | 2 | 120 | 0 | 130 | 0 | 300 | 182 | 197 | 100 | 39 | 0 | 53 | 38 | 85 | 0 | 0 | 19 | 11 | 33 | 0 | 134 | 48 | 82 | 22 | 0.8 | 66 | 62 | 44 | 47 | 30 | 300 | 30 | 84 | 45 | 114 | 0 | 45 | 7 | 290 | 23 | 3 | 50 | 183 | 0 | 93 | 131 | 98 | 144 |  | 494 | 0 | 350 | 85 | 96 | 0 | 0 | 0 | 0 | 0 | 32 | 173 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 0 | 51 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 118 | 96 | 45 | 151 | 0 |  | 7286.8 | 2158 | 9444.8 | 3745 | 494 | 1665 | 2688 | 0 | 187 | 531 | 134 | 0.8 | 0 | 104.91
15:00 | 70 | 100 | 0 | 100 | 330 | 0 | 0 | 370 | 212 | 96 | 0 | 340 | 200 | 99 | 60 | 44 | 208 | 0 | 0 | 100 | 100 | 102 | 133 | 86 | 8 | 30 | 40 | 18 | 37 | 55 | 22 | 25 | 22 | 33 | 33 | 42 | 0 | 102 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 34 | 90 | 85 | 44 | 0 | 2 | 120 | 0 | 130 | 0 | 338 | 206 | 195 | 100 | 39 | 0 | 53 | 38 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 142 | 47 | 82 | 22 | 1.2 | 67 | 62 | 44 | 47 | 40 | 330 | 30 | 86 | 45 | 118 | 0 | 42 | 7 | 310 | 23 | 8 | 20 | 178 | 0 | 98 | 127 | 99 | 144 |  | 494 | 0 | 410 | 83 | 95 | 0 | 0 | 0 | 0 | 0 | 32 | 183 | 26 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 0 | 51 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 118 | 96 | 20 | 148 | 0 |  | 7434.2 | 2199 | 9633.2 | 3997 | 494 | 1696 | 2588 | 0 | 182 | 533 | 142 | 1.2 | 0 | 104.92
16:00 | 70 | 100 | 0 | 100 | 330 | 0 | 0 | 380 | 211 | 96 | 0 | 340 | 200 | 100 | 48 | 55 | 208 | 0 | 0 | 100 | 100 | 102 | 133 | 100 | 8 | 31 | 40 | 18 | 37 | 55 | 22 | 25 | 30 | 0 | 33 | 44 | 0 | 100 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 33 | 90 | 85 | 44 | 19 | 2 | 120 | 0 | 130 | 0 | 334 | 199 | 194 | 100 | 39 | 3 | 53 | 38 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 140 | 47 | 82 | 22 | 1 | 66 | 62 | 47 | 47 | 130 | 318 | 30 | 86 | 45 | 128 | 0 | 45 | 7 | 310 | 23 | 11 | 20 | 175 | 0 | 98 | 127 | 98 | 144 |  | 494 | 0 | 410 | 84 | 92 | 0 | 0 | 0 | 4 | 8 | 24 | 184 | 25 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 0 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 118 | 98 | 20 | 152 | 0 |  | 7532 | 2208 | 9740 | 3995 | 494 | 1794 | 2592 | 0 | 180 | 544 | 140 | 1 | 0 | 104.92
17:00 | 70 | 100 | 0 | 100 | 280 | 0 | 0 | 376 | 211 | 96 | 0 | 340 | 200 | 100 | 48 | 55 | 209 | 0 | 0 | 50 | 100 | 102 | 145 | 100 | 8 | 20 | 40 | 18 | 37 | 55 | 22 | 25 | 30 | 17 | 33 | 51 | 0 | 110 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 79 | 33 | 90 | 85 | 44 | 19 | 5 | 120 | 0 | 130 | 0 | 300 | 182 | 195 | 100 | 39 | 3 | 53 | 45 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 142 | 47 | 90 | 22 | 0.5 | 70 | 62 | 53 | 47 | 130 | 302 | 30 | 86 | 46 | 80 | 18 | 43 | 7 | 290 | 23 | 11 | 0 | 175 | 0 | 70 | 127 | 72 | 144 |  | 495 | 0 | 350 | 89 | 115 | 0 | 0 | 0 | 12 | 25 | 24 | 184 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 50 | 43 | 12 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 120 | 98 | 0 | 152 | 0 |  | 7301.5 | 2191 | 9492.5 | 3808 | 495 | 1783 | 2480 | 0 | 190 | 594 | 142 | 0.5 | 0 | 104.92
18:00 | 70 | 100 | 0 | 100 | 250 | 0 | 0 | 300 | 212 | 96 | 0 | 360 | 200 | 100 | 60 | 55 | 120 | 0 | 0 | 50 | 100 | 102 | 140 | 100 | 8 | 20 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 116 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 80 | 0 | 50 | 80 | 33 | 90 | 86 | 44 | 19 | 2 | 120 | 0 | 130 | 0 | 301 | 194 | 199 | 100 | 39 | 6 | 10 | 45 | 51 | 0 | 0 | 19 | 11 | 33 | 15 | 132 | 48 | 90 | 22 | 0.1 | 70 | 62 | 53 | 47 | 130 | 313 | 30 | 50 | 20 | 78 | 19 | 43 | 7 | 280 | 23 | 11 | 0 | 178 | 0 | 50 | 129 | 51 | 149 |  | 495 | 0 | 250 | 95 | 115 | 0 | 0 | 0 | 13 | 40 | 32 | 184 | 24 | 64 | 0 | 0 | 0 | 0 | 10 | 33 | 50 | 43 | 43 | 52 | 8 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 120 | 71 | 0 | 151 | 0 |  | 6997.1 | 2129 | 9126.1 | 3535 | 495 | 1638 | 2530 | 0 | 196 | 600 | 132 | 0.1 | 0 | 104.92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.92
19:00 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 330 | 221 | 96 | 0 | 360 | 305 | 100 | 65 | 55 | 180 | 0 | 0 | 70 | 100 | 102 | 134 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 33 | 90 | 93 | 44 | 19 | 4 | 100 | 0 | 130 | 0 | 360 | 200 | 160 | 100 | 39 | 6 | 10 | 45 | 85 | 50 | 0 | 19 | 11 | 33 | 21 | 172 | 47 | 90 | 22 | 0 | 62 | 62 | 52 | 47 | 130 | 337 | 30 | 86 | 47 | 116 | 19 | 43 | 7 | 290 | 23 | 11 | 152 | 204 | 50 | 100 | 129 | 99 | 149 |  | 495 | 48 | 410 | 101 | 115 | 0 | 0 | 0 | 49 | 62 | 32 | 173 | 34 | 110 | 0 | 0 | 0 | 43 | 36 | 75 | 50 | 43 | 45 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 17 | 0 | 207 | 0 | 0 | 155 | 98 | 90 | 151 | 0 |  | 8020 | 2769 | 10789 | 4003 | 495 | 1753 | 3165 | 0 | 200 | 1001 | 172 | 0 | 0 | 104.93
19:30 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 374 | 221 | 96 | 0 | 340 | 305 | 100 | 65 | 55 | 214 | 0 | 0 | 100 | 100 | 102 | 132 | 100 | 8 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 45 | 90 | 93 | 44 | 19 | 8 | 100 | 0 | 130 | 0 | 334 | 178 | 110 | 100 | 39 | 4 | 5 | 45 | 85 | 49 | 8 | 19 | 11 | 33 | 21 | 172 | 47 | 90 | 22 | 0 | 68 | 62 | 53 | 47 | 163 | 339 | 30 | 86 | 47 | 130 | 19 | 43 | 7 | 325 | 23 | 11 | 200 | 210 | 54 | 100 | 129 | 99 | 149 |  | 496 | 48 | 410 | 97 | 115 | 0 | 0 | 0 | 49 | 91 | 32 | 185 | 36 | 110 | 0 | 0 | 0 | 43 | 36 | 100 | 50 | 43 | 46 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 17 | 0 | 220 | 0 | 0 | 220 | 98 | 100 | 151 | 0 |  | 8174 | 2923 | 11097 | 4080 | 496 | 1751 | 3268 | 0 | 200 | 1130 | 172 | 0 | 0 | 0
20:00 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 376 | 210 | 96 | 0 | 340 | 305 | 99 | 65 | 55 | 210 | 0 | 0 | 100 | 100 | 102 | 132 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 82 | 45 | 90 | 93 | 44 | 19 | 13 | 80 | 0 | 125 | 20 | 276 | 164 | 68 | 100 | 10 | 4 | 5 | 45 | 85 | 49 | 10 | 19 | 11 | 33 | 21 | 172 | 47 | 90 | 22 | 0 | 65 | 62 | 52 | 47 | 163 | 338 | 30 | 86 | 48 | 134 | 19 | 43 | 5 | 270 | 23 | 11 | 200 | 210 | 58 | 100 | 129 | 99 | 149 |  | 496 | 48 | 410 | 95 | 115 | 0 | 0 | 0 | 48 | 70 | 32 | 187 | 37 | 110 | 12 | 0 | 0 | 43 | 36 | 100 | 50 | 43 | 47 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 16 | 219 | 0 | 0 | 220 | 97 | 93 | 153 | 0 |  | 7967 | 2923 | 10890 | 3975 | 496 | 1646 | 3263 | 0 | 200 | 1138 | 172 | 0 | 0 | 104.93
21:00 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 370 | 191 | 96 | 0 | 340 | 305 | 99 | 65 | 55 | 210 | 0 | 0 | 100 | 100 | 102 | 132 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 82 | 42 | 90 | 93 | 34 | 19 | 23 | 80 | 10 | 125 | 20 | 276 | 186 | 68 | 100 | 10 | 8 | 5 | 45 | 85 | 49 | 30 | 19 | 11 | 33 | 21 | 172 | 47 | 90 | 22 | 0 | 65 | 62 | 52 | 47 | 163 | 330 | 30 | 86 | 48 | 133 | 19 | 43 | 5 | 320 | 23 | 11 | 200 | 214 | 87 | 100 | 129 | 99 | 148 |  | 496 | 48 | 410 | 96 | 115 | 0 | 0 | 0 | 48 | 70 | 32 | 188 | 39 | 110 | 12 | 0 | 0 | 43 | 38 | 100 | 50 | 43 | 45 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 17 | 17 | 218 | 0 | 0 | 220 | 98 | 79 | 154 | 0 |  | 8068 | 2916 | 10984 | 3993 | 496 | 1694 | 3292 | 0 | 200 | 1137 | 172 | 0 | 0 | 104.93
22:00 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 365 | 180 | 96 | 0 | 340 | 240 | 100 | 65 | 55 | 216 | 0 | 0 | 100 | 100 | 102 | 137 | 100 | 8 | 50 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 45 | 90 | 93 | 44 | 19 | 28 | 80 | 26 | 60 | 20 | 276 | 220 | 68 | 100 | 10 | 8 | 5 | 45 | 85 | 49 | 0 | 19 | 11 | 33 | 21 | 174 | 47 | 91 | 20 | 0 | 70 | 62 | 52 | 47 | 130 | 331 | 30 | 86 | 48 | 112 | 19 | 46 | 5 | 270 | 23 | 11 | 200 | 215 | 107 | 100 | 129 | 100 | 148 |  | 496 | 48 | 411 | 71 | 115 | 0 | 0 | 0 | 48 | 70 | 32 | 91 | 39 | 113 | 0 | 0 | 0 | 43 | 38 | 100 | 50 | 43 | 45 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 17 | 219 | 0 | 0 | 220 | 97 | 40 | 152 | 0 |  | 7898 | 2744 | 10642 | 3865 | 496 | 1607 | 3170 | 0 | 200 | 1130 | 174 | 0 | 0 | 104.93
23:00 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 360 | 170 | 96 | 0 | 340 | 270 | 100 | 65 | 55 | 216 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 40 | 18 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 109 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 136 | 0 | 50 | 80 | 46 | 90 | 93 | 45 | 19 | 28 | 80 | 65 | 0 | 75 | 250 | 222 | 68 | 100 | 10 | 8 | 5 | 45 | 85 | 49 | 0 | 19 | 11 | 33 | 16 | 168 | 48 | 90 | 20 | 0 | 70 | 62 | 52 | 47 | 163 | 330 | 30 | 86 | 48 | 112 | 19 | 45 | 5 | 270 | 23 | 11 | 200 | 205 | 124 | 100 | 137 | 100 | 148 |  | 496 | 48 | 414 | 70 | 115 | 0 | 0 | 0 | 48 | 62 | 32 | 88 | 38 | 113 | 0 | 0 | 0 | 43 | 37 | 100 | 50 | 43 | 44 | 51 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 16 | 219 | 0 | 0 | 220 | 98 | 30 | 154 | 0 |  | 7927 | 2723 | 10650 | 3867 | 496 | 1629 | 3168 | 0 | 189 | 1133 | 168 | 0 | 0 | 104.93
24:00 | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 360 | 196 | 96 | 0 | 340 | 270 | 100 | 65 | 55 | 216 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 40 | 18 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 109 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 130 | 0 | 50 | 80 | 46 | 90 | 93 | 44 | 19 | 27 | 120 | 70 | 0 | 18 | 250 | 212 | 68 | 100 | 31 | 8 | 5 | 45 | 85 | 49 | 0 | 19 | 11 | 33 | 15 | 164 | 47 | 91 | 20 | 0 | 70 | 62 | 50 | 47 | 163 | 330 | 30 | 86 | 48 | 115 | 19 | 45 | 5 | 290 | 21 | 11 | 200 | 163 | 125 | 99 | 136 | 100 | 150 |  | 495 | 32 | 416 | 70 | 115 | 0 | 0 | 0 | 48 | 62 | 32 | 84 | 36 | 110 | 10 | 0 | 0 | 43 | 37 | 100 | 50 | 43 | 45 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 16 | 218 | 0 | 0 | 220 | 98 | 76 | 154 | 0 |  | 7917 | 2756 | 10673 | 3862 | 495 | 1670 | 3171 | 0 | 189 | 1122 | 164 | 0 | 0 | 104.93
KWH | 1556000 | 2508660 | 0 | 2520000 | 8219999 | 0 | 363776 | 8965120 | 5652000 | 1538200 | 0 | 7860938 | 5673329 | 1879680 | 1306560 | 1121363 | 5055402 | 0 | 0 | 1248000 | 1929600 | 2418336 | 2773920 | 1756870 | 171840 | 652000 | 840048 | 595800 | 1242078 | 1238273 | 500076 | 600000 | 714600 | 741800 | 837000 | 1071864 | 0 | 2541749 | 1910600 | 0 | 0 | 333540 | 0 | 2490945 | 0 | 2530339 | 0 | 1088160 | 1401872 | 732570 | 2099760 | 2113960 | 1060320 | 439872 | 435840 | 2609904 | 128635 | 2855130 | 187600 | 7348000 | 4945000 | 2960727 | 2407480 | 812088 | 42720 | 392000 | 1007791 | 1306560 | 390240 | 70080 | 451728 | 249301 | 823400 | 322840 | 3381120 | 1150000 | 2041920 | 518292 | 11950 | 1593000 | 1474120 | 1189200 | 1137000 | 1953327 | 7178403 | 710000 | 2043840 | 1057680 | 2655710 | 350000 | 1071480 | 172260 | 6508900 | 526224 | 252336 | 1578240 | 4423500 | 833304 | 1294690 | 3105600 | 1354861 | 3142080 |  | 11812364 | 248300 | 9464832 | 1935840 | 2405760 | 0 | 0 | 0 | 512640 | 744960 | 813000 | 4231058 | 653486 | 2013120 | 30076 | 0 | 0 | 457352 | 390499 | 1516996 | 1097910 | 992000 | 799921 | 1228320 | 627345 | 428160 | 236160 | 184820 | 0 | 0 | 0 | 164000 | 139000 | 5313164 | 0 | 0 | 4160127 | 2283859 | 995520 | 3619363 | 0 |  | 174752920 | 59499952 | 234252872 | 95020957 | 11812364 | 38757704 | 60705326 | 0 | 4452349 | 20111102 | 3381120 | 11950 | 0
Fuel Cost | 1338160 | 2157447.6 | 0 | 2167200 | 5260799.36 | 0 | 341949.44 | 5468723.2 | 3447720 | 14782102 | 0 | 5266828.46 | 86177867.51 | 11804390.4 | 8727820.8 | 6851527.93 | 3286011.3 | 0 | 0 | 19418880 | 12060000 | 15936834.24 | 26823806.4 | 11191261.9 | 1029321.6 | 10425480 | 5603120.16 | 4248054 | 7762987.5 | 7763971.71 | 375057 | 450000 | 0 | 0 | 0 | 10139833.44 | 0 | 0 | 0 | 0 | 0 | 3158623.8 | 0 | 34001399.25 | 0 | 55439727.49 | 0 | 9564926.4 | 15098161.44 | 7127906.1 | 12997514.4 | 13656181.6 | 6934492.8 | 373891.2 | 0 | 2375012.64 | 117057.85 | 2598168.3 | 116312 | 5070120 | 3461500 | 2042901.63 | 2311180.8 | 544098.96 | 36739.2 | 360640 | 826388.62 | 1241232 | 4230201.6 | 519993.6 | 347830.56 | 186975.75 | 634018 | 242130 | 23126860.8 | 862500 | 18765244.8 | 399084.84 | 0 | 1656720 | 1533084.8 | 1141632 | 1023300 | 1523595.06 | 5024882.1 | 809400 | 2186908.8 | 1163448 | 3027509.4 | 448000 | 996476.4 | 160201.8 | 4165696 | 394668 | 191775.36 | 27350899.2 | 32114610 | 14441158.32 | 22074464.5 | 22205040 | 23100380.05 | 0 |  | 60243056.4 | 7237945 | 6341437.44 | 15506078.4 | 19943750.4 | 0 | 0 | 0 | 5772326.4 | 8775628.8 | 6406440 | 2919430.02 | 646951.14 | 14897088 | 1012959.68 | 0 | 0 | 5236680.4 | 4186149.28 | 13592284.16 | 9496921.5 | 8828800 | 8519158.65 | 12184934.4 | 7383850.65 | 470976 | 221990.4 | 139908.74 | 0 | 0 | 0 | 5285720 | 3721030 | 3612951.52 | 0 | 0 | 60987461.82 | 0 | 17252361.6 | 0 | 0 |  | 685810022.17 | 310824270.8 | 996634292.97 | 66243046.74 | 60243056.4 | 27265574.95 | 545323356.96 | 0 | 0 | 274432397.12 | 23126860.8 | 0 | 0
Yesterday Day Peak | 70 | 100 | 0 | 100 | 365 | 0 | 20 | 370 | 211 | 75 | 0 | 340 | 305 | 90 | 48 | 40 | 212 | 0 | 0 | 15 | 85 | 102 | 133 | 75 | 8 | 51 | 35 | 18 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 37 | 0 | 109 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 40 | 16 | 16 | 90 | 86 | 44 | 19 | 2 | 120 | 0 | 130 | 0 | 334 | 205 | 108 | 100 | 39 | 0 | 10 | 38 | 85 | 0 | 8 | 19 | 11 | 33 | 0 | 126 | 48 | 83 | 22 | 1.9 | 65 | 62 | 44 | 44 | 10 | 314 | 30 | 83 | 44 | 127 | 0 | 43 | 6 | 310 | 15 | 11 | 83 | 195 | 0 | 96 | 122 | 97 | 115 |  | 494 | 0 | 410 | 73 | 80 | 0 | 0 | 0 | 0 | 0 | 32 | 187 | 23 | 64 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 43 | 43 | 51 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 173 | 97 | 94 | 148 | 0 |  | 9558.9 | DayPeak
Yesterday Evening Peak | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 374 | 221 | 96 | 0 | 340 | 305 | 100 | 65 | 55 | 214 | 0 | 0 | 100 | 100 | 102 | 132 | 100 | 8 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 80 | 45 | 90 | 93 | 44 | 19 | 8 | 100 | 0 | 130 | 0 | 334 | 178 | 110 | 100 | 39 | 4 | 5 | 45 | 85 | 49 | 8 | 19 | 11 | 33 | 21 | 172 | 47 | 90 | 22 | 0 | 68 | 62 | 53 | 47 | 163 | 339 | 30 | 86 | 47 | 130 | 19 | 43 | 7 | 325 | 23 | 11 | 200 | 210 | 54 | 100 | 129 | 99 | 149 |  | 496 | 48 | 410 | 97 | 115 | 0 | 0 | 0 | 49 | 91 | 32 | 185 | 36 | 110 | 0 | 0 | 0 | 43 | 36 | 100 | 50 | 43 | 46 | 52 | 39 | 18 | 10 | 11 | 0 | 0 | 0 | 17 | 0 | 220 | 0 | 0 | 220 | 98 | 100 | 151 | 0 |  | 11097 | EvPeak
Forecast for Evening | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 412 | 250 | 110 | 0 | 450 | 305 | 100 | 84 | 55 | 215 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 120 | 80 | 0 | 0 | 16 | 0 | 220 | 0 | 135 | 0 | 50 | 80 | 50 | 100 | 100 | 45 | 19 | 10 | 120 | 0 | 0 | 360 | 360 | 225 | 110 | 100 | 40 | 20 | 30 | 45 | 85 | 50 | 52 | 22 | 11 | 33 | 22 | 174 | 50 | 90 | 22 | 0 | 70 | 62 | 51 | 50 | 163 | 330 | 32 | 86 | 48 | 130 | 19 | 48 | 8 | 341 | 23 | 11 | 200 | 300 | 300 | 100 | 135 | 100 | 150 |  | 498 | 48 | 410 | 100 | 115 | 0 | 0 | 0 | 48 | 80 | 40 | 194 | 33 | 110 | 30 | 0 | 0 | 43 | 32 | 100 | 50 | 43 | 44 | 52 | 40 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 18 | 215 | 0 | 0 | 220 | 95 | 100 | 154
Forecast for Day | 70 | 100 | 0 | 100 | 365 | 0 | 0 | 412 | 232 | 110 | 0 | 450 | 305 | 100 | 65 | 55 | 215 | 0 | 0 | 100 | 100 | 102 | 149 | 100 | 8 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 110 | 80 | 0 | 0 | 16 | 0 | 0 | 0 | 135 | 0 | 50 | 40 | 50 | 100 | 100 | 45 | 19 | 10 | 120 | 0 | 0 | 360 | 360 | 225 | 75 | 100 | 33 | 6 | 30 | 45 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 126 | 50 | 90 | 22 | 2 | 70 | 62 | 51 | 50 | 163 | 330 | 32 | 86 | 48 | 130 | 19 | 48 | 8 | 341 | 23 | 11 | 100 | 300 | 0 | 100 | 135 | 100 | 150 |  | 499 | 0 | 410 | 100 | 115 | 0 | 0 | 0 | 0 | 0 | 40 | 100 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 44 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 16 | 18 | 215 | 0 | 0 | 150 | 95 | 100 | 154
Generation at 08:00(Today) | 70 | 100 | 0 | 100 | 180 | 0 | 0 | 350 | 232 | 13 | 0 | 380 | 200 | 85 | 65 | 55 | 170 | 0 | 0 | 17 | 90 | 50 | 64 | 74 | 8 | 0 | 40 | 18 | 55 | 55 | 0 | 25 | 32 | 33 | 33 | 51 | 0 | 66 | 80 | 0 | 0 | 8 | 0 | 0 | 0 | 115 | 0 | 50 | 81 | 34 | 84 | 93 | 45 | 19 | 7 | 120 | 0 | 0 | 365 | 268 | 191 | 72 | 100 | 33 | 6 | 5 | 38 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 110 | 46 | 32 | 20 | 0.4 | 70 | 62 | 50 | 47 | 100 | 312 | 20 | 84 | 48 | 90 | 19 | 43 | 0 | 280 | 8 | 11 | 0 | 92 | 0 | 0 | 135 | 0 | 149 | 0 | 427 | 0 | 320 | 58 | 81 | 0 | 0 | 0 | 0 | 0 | 32 | 91 | 21 | 80 | 0 | 0 | 0 | 0 | 0 | 57 | 40 | 43 | 44 | 8 | 0 | 18 | 10 | 11 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 131 | 98 | 0 | 152 | 0 | 0
199
| Minimum Generation |  | 8570.6 | 8:00
| Highest Generation |  | 11097 | 19:30
| Day Peak Generation |  | 9558.9 | 12:00
| Evening Peak Generation |  | 11097 | 19:30
| HVDC Max Flow |  | 496 | 19:30
| HVDC EvPeak Flow |  | 496 | 19:30
| Load factor L.F |  | 87.96%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-08-13
Till now the maximum generation is : - |  |  | 11387 | 22:00 | Hrs on | 2018-07-18
The Summary of Yesterday's |  | 2018-08-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9558.9 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8491.4 | MW
Evening Peak Generation : |  | 11097 | MW Hour : | 19:30 | Available Max Generation : |  | 12396 | MW
E.P. Demand (at gen end) : |  | 11097 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11097 | MW Hour : | 19:30 | Reserve(Generation end) |  | 596 | MW
Total Gen. (MKWH) : |  | 234.2529 | System Load Factor : | 87.96% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -600 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-08-13
Actual : | 104.99 | Ft.(MSL) , | Rule curve : | 92.84 | Ft.( MSL )
Gas Consumed : | Total = | 1165.05 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 93508621.69
|  | Coal : | 0 | Oil : | 819755754.08 | Total : | 913264375.77
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4179.2695 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1422.8601 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1275.1343 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1152.2975 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1041.2561 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 840.261 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 467.6744 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 216.2875 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 648.0613 |  |  | 0 | 0%
Total | 0 |  | 11243.1017 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2,3
| Nil |  |  | 2) Khulna ST 110 MW |  | 10) Ashuganj Unit-4
3) Ghorasal Unit-4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Haripur GT-1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Kishoreganj 132/33 kV T2 transformer was under shut down from 09:24 to 11:31 for C/M.
b) Bibiyana-Kaliakoir 400 kV Ckt-1 was under shut down from 11:40 to 17:15 for D/W.
c) Sikalbaha 225 MW CCPP tripped at 11:04 due to generation protection operated.
d) After maint Ashuganj(N) CCPP 360 MW GT was synchronized at 20:59 & ST sync at 02:55(13/8/18).
e) After maint Ashuganj # 4 was synchronized at 20:59 and tripped at 00:08(13/8/18).
f) After maint Ashuganj precision 55 MW was synchronized at 15:05.
g) Jessore-Noapara 132 kV Ckt-1 & 2 tripped at 21:17 from Jessore end showing 3 phase O/C,E/F relay |  |  |  | About 360 MW Power interruption occurred under Jessore,
both line and were switched on at 21:42. |  |  |  | Jhenidah,Magura,Chuadanga S/S area from 21:17 to 21:42.
h) Bottail-Jhenidah 132 kV Ckt-1 & 2 tripped at 21:18 from Bottail end showing O/C,relay
and were switched on at 21:51.
i) Mirpur-Aminbazar 132 kV Ckt is under shut down since 06:11 due to project work.
j) Rampura-Bhulta 230 kV Ckt-4 tripped at 03:35(13/8/18) due to lightning arrestor burst at Rampura end.
k) Haripur-Siddhirganj 230 kV Ckt-1 tripped at 03:32 form Haripur end showing differential 3-phase trip
and was switched on at 06:05(13/8/18).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-08-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 70 | 1556000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 100 | 2508660
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 100 | 2520000
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8219999
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 363776 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 374 | 8965120 | Gas shortage
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 96 | 1538200 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 221 | 5652000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 340 | 7860938 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1879680
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 5673329
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 65 | 1306560 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1121363
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1756870
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 500076
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 1248000
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1929600
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 214 | 5055402
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 652000
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 2418336
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 840048 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 595800
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 132 | 2773920 | Engine problem
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1242078
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1238273
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 8 | 171840 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1314600 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 741800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 837000
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 1071864
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 210 | 4423500 | Engine problem
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 54 | 833304 | Line over load.
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 100 | 1294690
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 1354861
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 149 | 149 | 3142080
| Dhaka area Total |  |  |  | 5548 | 4010 | 84601567
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 333540 | Engine problem
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 44 | 1060320 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 200 | 4452349
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Gas shortage
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 2490945 | Tripped at 11:04.
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2530339
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 1088160
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 80 | 1401872
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 45 | 732570
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 2099760 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 439872
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 8 | 435840
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 93 | 2113960 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 780 | 19179527
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2609904 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 128635 | Under maint.
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 130 | 2855130
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 178 | 4945000 | Gas shortage
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 187600 | Under maint.
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 334 | 7348000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 39 | 812088
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 4 | 42720 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 392000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 110 | 2960727 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 1007791 | Engine problem
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1306560
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 390240
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2407480
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 451728
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249301
** | Tripura |  | Imported power | 0 | 160 | 172 | 3381120
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 823400
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 8 | 70080 | Line over load.
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 322840
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 200 | 1578240
| Comilla Area Total |  |  |  | 2541 | 1643 | 34270584
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 47 | 1150000 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 518292
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 90 | 2041920
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 11950
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 129 | 3105600 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 288 | 6827762
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 68 | 1593000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1474120
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 1953327
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 339 | 7178403 | FGMO
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1189200
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 47 | 1137000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 252336
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 30 | 710000 | GT-9 Under maint.
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 2043840
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 1057680
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 130 | 2655710
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 19 | 350000
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 43 | 1071480 | Engine problem
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 526224
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 325 | 6508900 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 7 | 172260 | Engine problem
| Sylhet Area Total |  |  |  | 1549 | 1453 | 29873480
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 48 | 248300
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 496 | 11812364
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 97 | 1935840 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 2405760
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 49 | 512640
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Engine problem
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 91 | 744960
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9464832
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 32 | 813000 | Engine problem
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 0 | 0 | Contract Experied
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 100 | 995520
| Khulna Area Total |  |  |  | 1769 | 1438 | 28933216
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2013120
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 30076 | Reserve
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 36 | 653486
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 185 | 4231058 | FGMO
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 2283859
| Barisal Area Total |  |  |  | 462 | 429 | 9211599
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 457352 | Engine problem
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 36 | 390499
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1097910
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 992000 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 46 | 799921
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 0
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 151 | 3619363 | On test
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 39 | 627345
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 428160 | Engine problem
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 236160
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 184820
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 1228320
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 1516996
| Rajshahi Area Total |  |  |  | 1123 | 819 | 11578846
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under overhauling
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Coal shortage
120 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 164000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 139000
| Rangpur Area Total |  |  |  | 484 | 17 | 303000
| Total |  |  |  | 15559 | 10877 | 224779581
| Eastern Grid Total |  |  |  | 11721 | 8174 | 174752920
| Western Grid Total |  |  |  | 3838 | 2703 | 50026661
| National Grid Total |  |  |  | 15559 | 10877 | 224779581
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-08-12 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7268 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3295 | MW
i) Dhaka area |  |  | 4148 | MW | i) Khulna area |  |  | 1396 | MW
ii) Chittagong area |  |  | 1010 | MW | ii) Rajshahi area |  |  | 1147 | MW
iii) Comilla area |  |  | 954 | MW | iii) Barisal area |  |  | 260 | MW
iv) Mymensingh area |  |  | 710 | MW | iv) Rangpur area |  |  | 492 | MW
v) Sylhet area |  |  | 446 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10563 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 136 | 1500 | Netrokona | 85 | 1930 | Central s/s | 75 | 1930
Munsiganj | 116 | 2200 | Jamalpur | 111 | 2200 | Noapara | 96 | 2200
Sonargaon | 63 | 1900 | Sherpur | 82 | 200 | Jessore | 148 | 2100
Shyampur | 182 | 1100 | Srimongal | 32 | 2100 | Jhenida | 97 | 2100
Bhulta | 187 | 2100 | Shahjibazar | 100 | 2200 | Bottail | 137 | 2000
Madanganj | 60 | 1930 | Fenchuganj | 48 | 2100 | G.K Project | 56 | 2000
Shitalakhya | 118 | 1700 | Kulawara | 43 | 2100 | Faridpur | 160 | 2100
Rahim steel | 12 | 1700 | Sylhet | 135 | 1900 | Madaripur | 160 | 2100
Matuail | 100 | 900 | Chatak | 26 | 2000 | Gopalganj | 85 | 1930
Ghorasal | 88 | 2300 | Sunamganj | 35 | 2100 | Bagerhat | 91 | 2000
Narsingdi | 128 | 2400 | Biani Bazar | 41 | 1930 | Mongla | 36 | 1900
Haripur (SBU) | 108 | 2100 | Comilla (S) | 147 | 2200 | Satkhira | 100 | 2200
Ullon | 95 | 2000 | Comilla(N) | 105 | 1900 | Gallamari | 50 | 2200
Hasnabad | 217 | 1930 | Chandpur | 96 | 1900 | Magura | 53 | 2000
Magbazar | 134 | 1600 | Feni | 126 | 2200 | Chuadanga | 77 | 1930
Maniknagar | 100 | 1800 | Chowmuhani | 166 | 1900 | Barisal | 122 | 1930
Bangabhaban | 42 | 1300 | Ashuganj | 59 | 2300 | Patuakhali | 83 | 1900
Narinda | 86 | 1300 | Daudkandi | 113 | 1900 | Bhandaria | 42 | 1900
Dhanmondi | 151 | 1300 | B.Baria | 131 | 2000 | Ishurdi | 57 | 2100
Lalbag | 97 | 1900 | Ramganj | 34 | 2300 | Ruppur Paromanobik | 2 | 1000
Madartek | 49 | 1900 | Madunaghat | 54 | 2200 | Natore | 116 | 2000
Mirpur | 107 | 1900 | Hathazari | 92 | 2000 | Bogra | 253 | 2100
Kalyanpur | 126 | 1400 | Khulshi | 192 | 1500 | Noagaon | 88 | 600
Gulshan | 148 | 1900 | Halishahar | 133 | 2000 | Rajshahi | 169 | 2100
Uttara | 92 | 2100 | Baraulia | 135 | 1200 | C.Nawabganj | 77 | 2100
Kamrangirchar | 76 | 1400 | Sikalbaha | 43 | 1900 | Amnura | 43 | 2100
Savar | 125 | 1900 | Dohazari | 82 | 1830 | Pabna | 139 | 2000
Bhasantec | 161 | 1200 | Cox'sbazar | 69 | 1830 | Shahjadpur | 105 | 2100
Agargaon | 48 | 1930 | Chandraghona | 30 | 1830 | Serajganj | 118 | 2100
Satmosjid | 101 | 1600 | Kaptai | 5 | 1900 | Niyamatpur | 37 | 2100
Tongi | 141 | 1900 | A. Khaer Stl. | 12 | 100 | Joypurhat | 32 | 300
Kabirpur | 218 | 2000 | Bakulia | 114 | 1930 | Rangpur | 110 | 200
Basundhara | 130 | 1930 | Julda | 21 | 100 | Lalmonirhat | 78 | 1830
Manikganj | 103 | 1830 | TK chemical | 0.6 | 100 | Saidpur | 99 | 1900
Joydevpur | 234 | 1830 | Modern Steel | 12 | 800 | Purbasadipur | 75 | 700
New Tongi | 108 | 2100 | Shahmirpur | 27 | 900 | Thakurgaon | 58 | 2100
Korda | 255 | 2100 | Abul Khair 230 | 176 | 100 | Palashbari | 96 | 1900
Dhamrai | 52 | 2200 | BSRM | 119 | 1900 | Barapukuria | 45 | 1930
Tangail | 176 | 2100 | Khagrachhari | 18 | 2100 | Panchagar | 32 | 1830
Mymensing | 235 | 2100 | Matarbari | 26 | 1830
Kishorganj | 94 | 2000 | Goalpara | 39 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-08-12
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 391 | 6:00 | 379 | 1:00 | Kaliakoir | 380 | 10:00 | 352 | 12:00
Bheramara | 402 | 7:00 | 389 | 20:00 | Bhulta | 377 | 23:00 | 369 | 11:00
Ashuganj(N) | 378 | 4:00 | 371 | 16:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 228 | 23:00 | Hathazari | 219 | 3:00 | 208 | 13:00
Ishurdi | 231 | 18:30 | 215 | 20:00 | Megnaghat | 227 | 1:00 | 221 | 10:00
Ashuganj | 234 | 18:00 | 230 | 1:00 | Fenchuganj | 237 | 24:00 | 229 | 1:00
Serajganj | 220 | 8:00 | 210 | 19:00 | Siddhirganj | 224 | 23:00 | 219 | 8:00
Baghabari | 220 | 6:00 | 210 | 19:30 | Maniknagar | 222 | 2:00 | 217 | 15:00
Barapukuria | 224 | 9:00 | 205 | 19:30 | Old Airport | 224 | 4:00 | 216 | 10:00
Bogra | 214 | 9:00 | 191 | 19:00 | Barisal | 231 | 9:00 | 215 | 21:00
Khulna South | 239 | 18:00 | 214 | 19:30 | AKSML | 217 | 4:00 | 203 | 12:00
Rampura | 221 | 3:00 | 218 | 11:00 | BSRM | 219 | 14:00 | 209 | 12:00
Haripur | 222 | 21:00 | 218 | 11:00 | Bibiyana | 234 | 18:00 | 227 | 1:00
Hasnabad | 225 | 21:00 | 218 | 8:00 | Bhulta | 223 | 3:00 | 218 | 10:00
Aminbazar | 224 | 4:00 | 217 | 16:00 | Ashuganj (S) | 231 | 17:00 | 227 | 12:00
Tongi | 220 | 7:00 | 211 | 11:00 | Kaliakoir | 227 | 3:00 | 218 | 12:00
Comilla (N) | 230 | 14:00 | 225 | 6:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 130 | 1100 | Ramganj | 121 | 1800 | 115 | 2100
Munsiganj | 136 | 1400 | 131 | 100 | Madanhat | 132 | 300 | 127 | 1600
Megnaghat | 135 | 2100 | 128 | 900 | Hathazari | 130 | 300 | 124 | 1200
Shyampur | 133 | 2100 | 126 | 700 | Khulshi | 127 | 600 | 122 | 1200
Bhulta | 130 | 1800 | 124 | 500 | Halishahar | 130 | 600 | 122 | 1200
Madanganj | 138 | 1300 | 130 | 700 | Baraulia | 126 | 100 | 122 | 1200
Shitalakhya | 139 | 2100 | 133 | 500 | Sikalbaha | 130 | 300 | 123 | 1200
Rahim steal | 135 | 1830 | 130 | 900 | Dohazari | 128 | 500 | 123 | 1200
Matuail | 134 | 2100 | 128 | 1000 | Cox'sbazar | 123 | 600 | 116 | 1930
Ghorasal | 135 | 100 | 132 | 900 | Chandraghona | 131 | 500 | 125 | 1200
Narsinghdi | 130 | 1400 | 125 | 1000 | Kaptai | 132 | 100 | 128 | 800
Haripur (SBU) | 135 | 1900 | 130 | 900 | A. Khaer Stl. | 126 | 500 | 121 | 1200
Ullon | 132 | 500 | 127 | 1100 | Bakulia | 128 | 200 | 121 | 1200
Hasnabad | 134 | 600 | 130 | 700 | Julda | 129 | 600 | 123 | 1200
Magbazar | 132 | 400 | 126 | 1000 | TK Chemical | 132 | 400 | 125 | 1200
Maniknagar | 139 | 600 | 136 | 1000 | Modern Steel | 127 | 400 | 121 | 1200
Bangabhaban | 139 | 600 | 136 | 1000 | Shahmirpur | 128 | 1900 | 121 | 1300
Narinda | 139 | 600 | 136 | 1000 | Khagrachhari | 130 | 300 | 125 | 1100
Dhanmondi | 139 | 600 | 136 | 1000 | Matarbari | 128 | 500 | 122 | 1000
Lalbag | 136 | 2100 | 129 | 900 | Goalpara | 137 | 1830 | 121 | 1930
Madartek | 133 | 600 | 127 | 1500 | Central s/s | 137 | 1830 | 120 | 1930
Mirpur | 134 | 400 | 127 | 1600 | Noapara | 135 | 1800 | 137 | 1930
Kalyanpur | 134 | 600 | 128 | 1500 | Jessore | 129 | 1830 | 112 | 1930
Gulshan | 132 | 500 | 127 | 1500 | Jhenida | 130 | 1830 | 109 | 1930
Uttara | 131 | 300 | 124 | 1200 | Bottail | 135 | 1800 | 122 | 1930
Kamrangirchar | 136 | 100 | 128 | 500 | G.K.Project | 140 | 1800 | 131 | 2000
Savar | 132 | 300 | 126 | 1200 | Faridpur | 136 | 1800 | 121 | 2100
Bhasantec | 132 | 400 | 125 | 1100 | Madaripur | 134 | 1700 | 121 | 2100
Agargaon | 132 | 300 | 126 | 1600 | Gopalganj | 135 | 1800 | 120 | 2000
Satmosjid | 133 | 500 | 126 | 1200 | Bagerhat | 134 | 1400 | 117 | 2100
Tongi | 133 | 800 | 125 | 1100 | Mongla | 132 | 1830 | 115 | 1930
Kabirpur | 137 | 600 | 127 | 700 | Satkhira | 135 | 1800 | 116 | 1930
Basundhara | 133 | 600 | 124 | 1300 | Gallamari | 136 | 1800 | 120 | 1930
Manikganj | 137 | 700 | 126 | 1900 | Magura | 127 | 1830 | 105 | 1930
Joydevpur | 140 | 1800 | 131 | 800 | Chuadanga | 125 | 1800 | 100 | 1930
New Tongi | 136 | 500 | 126 | 1500 | Barisal | 138 | 1800 | 130 | 1930
Kodda | 140 | 1900 | 129 | 800 | Patuakhali | 136 | 1700 | 125 | 2000
Dhamrai | 136 | 600 | 129 | 2100 | Bhandaria | 135 | 1300 | 122 | 1930
Tangail | 135 | 500 | 125 | 2200 | Ishurdi | 138 | 1830 | 128 | 2000
Mymensing | 132 | 600 | 113 | 2100 | Ruppur Paromanobik | 139 | 1830 | 129 | 2000
Kishorganj | 129 | 1800 | 117 | 2000 | Natore | 134 | 1830 | 122 | 2000
Netrokona | 129 | 900 | 114 | 2100 | Bogra | 128 | 900 | 112 | 1900
Jamalpur | 136 | 1800 | 119 | 1900 | Noagaon | 121 | 900 | 107 | 1900
Sherpur | 137 | 1800 | 117 | 2000 | Rajshahi | 131 | 1830 | 118 | 1930
Srimongal | 138 | 700 | 133 | 2100 | C.Nawabganj | 131 | 1800 | 120 | 2000
Shahjibazar | 137 | 900 | 131 | 100 | Amnura | 135 | 1830 | 120 | 1900
Fenchuganj | 137 | 600 | 133 | 100 | Pabna | 132 | 800 | 120 | 2000
Khulawara | 136 | 1800 | 133 | 100 | Shahjadpur | 135 | 1830 | 127 | 1930
Sylhet | 135 | 400 | 132 | 1900 | Serajganj | 128 | 1800 | 120 | 1900
Chatak | 136 | 700 | 131 | 1930 | Niyamatpur | 121 | 1800 | 108 | 1900
Sunamganj | 134 | 500 | 130 | 1900 | Joypurhat | 122 | 900 | 107 | 1900
Biani Bazar | 135 | 700 | 130 | 1930 | Rangpur | 121 | 900 | 98 | 1900
Comilla(s) | 126 | 1000 | 121 | 1830 | Lalmonirhat | 115 | 900 | 90 | 100
Comilla(n) | 135 | 700 | 132 | 1900 | Saidpur | 120 | 900 | 98 | 1900
Chandpur | 126 | 1830 | 120 | 100 | Purbasadipur | 125 | 900 | 100 | 1900
Feni | 120 | 1500 | 116 | 2300 | Thakurgaon | 118 | 900 | 90 | 1900
Chowmuhani | 123 | 1400 | 116 | 1900 | Palashbari | 118 | 900 | 103 | 100
Ashuganj | 136 | 900 | 131 | 100 | Barapukuria | 124 | 900 | 105 | 1930
Daudkandi | 137 | 2100 | 127 | 1600 | Panchagar | 114 | 800 | 86 | 1900
B.Baria | 136 | 700 | 129 | 2100

## L-Curve
Date | 2018-08-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 500 | 7917 | 2756 | 10673 |  |  |  | QF-LDC-12
0:30 | 505 | 7782.5 | 2763 | 10545.5 | Date: | 2018-08-12
1:00 | 510 | 7648 | 2770 | 10418
1:30 | 510 | 7500 | 2771.5 | 10271.5
2:00 | 510 | 7352 | 2773 | 10125
2:30 | 485 | 7272 | 2766.5 | 10038.5 | [5 empty] | Gen. at Eve. Peak | 11097 | 11097 MW (19:30 )
3:00 | 460 | 7192 | 2760 | 9952 | [6 empty] | 19:30
3:30 | 470 | 7158 | 2687.5 | 9845.5 | [5 empty] | Gen. at Day Peak | 9558.9 | 9558.9 MW (12:00 )
4:00 | 480 | 7124 | 2615 | 9739 | [6 empty] | 12:00
4:30 | 470 | 7037.5 | 2596 | 9633.5 | [5 empty] | Highest Generation | 11097
5:00 | 460 | 6951 | 2577 | 9528 | [6 empty] | 19:30
5:30 | 450 | 6721.5 | 2469.5 | 9191
6:00 | 440 | 6492 | 2362 | 8854
6:30 | 430 | 6442.2 | 2326.5 | 8768.7
7:00 | 420 | 6392.4 | 2291 | 8683.4
7:30 | 420 | 6396 | 2231 | 8627
8:00 | 420 | 6399.6 | 2171 | 8570.6
8:30 | 320 | 6540.95 | 2237 | 8777.95
9:00 | 220 | 6682.3 | 2303 | 8985.3
9:30 | 230 | 6764.3 | 2299 | 9063.3
10:00 | 240 | 6846.3 | 2295 | 9141.3
10:30 | 290 | 6991.8 | 2259 | 9250.8
11:00 | 340 | 7137.3 | 2223 | 9360.3
11:30 | 375 | 7193.6 | 2266 | 9459.6
12:00 | 410 | 7249.9 | 2309 | 9558.9
12:30 | 455 | 7248.4 | 2285.5 | 9533.9
13:00 | 500 | 7246.9 | 2262 | 9508.9
13:30 | 495 | 7266.85 | 2210 | 9476.85
14:00 | 490 | 7286.8 | 2158 | 9444.8
14:30 | 515 | 7360.5 | 2178.5 | 9539
15:00 | 540 | 7434.2 | 2199 | 9633.2
15:30 | 515 | 7483.1 | 2203.5 | 9686.6
16:00 | 490 | 7532 | 2208 | 9740
16:30 | 460 | 7416.75 | 2199.5 | 9616.25
17:00 | 430 | 7301.5 | 2191 | 9492.5
17:30 | 395 | 7149.3 | 2160 | 9309.3
18:00 | 360 | 6997.1 | 2129 | 9126.1
18:30 | 450 | 7508.55 | 2449 | 9957.55
19:00 | 540 | 8020 | 2769 | 10789
19:30 | 580 | 8174 | 2923 | 11097
20:00 | 600 | 7967 | 2923 | 10890 |  |  |  | Executive Engineer
20:30 | 575 | 8017.5 | 2919.5 | 10937 |  |  |  | Network Operation Division
21:00 | 550 | 8068 | 2916 | 10984
21:30 | 505 | 7983 | 2830 | 10813
22:00 | 460 | 7898 | 2744 | 10642 |  |  |  |  | Page 6 of 7
22:30 | 440 | 7912.5 | 2733.5 | 10646
23:00 | 420 | 7927 | 2723 | 10650
23:30 | 460 | 7922 | 2739.5 | 10661.5
24:00 | 500 | 7917 | 2756 | 10673
11097 MW (19:30 )
9558.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-08-12 |  | Energy | 234252872
[10 empty] | 2018-08-12 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3862 | 495 | 1670 | 3171 | 0 | 189 | 1122 | 0 | 164
0:30 | 3975 | 495 | 1540 | 3016 | 0 | 188 | 1170.5 | 0 | 161 | Date: | 2018-08-12
1:00 | 4088 | 495 | 1410 | 2861 | 0 | 187 | 1219 | 0 | 158
1:30 | 4077.5 | 495 | 1440 | 2716.5 | 0 | 186 | 1200.5 | 0 | 156 | [7 empty] | Total Energy | 234.2529 | Total Energy Gen 234.253 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 234.253 MKWHr
2:00 | 4067 | 495 | 1470 | 2572 | 0 | 185 | 1182 | 0 | 154 | [7 empty] | Energy not Served | 0
2:30 | 4069 | 495 | 1497.5 | 2478 | 0 | 184 | 1162 | 0 | 153 | [7 empty] | Energy Requirement | 234.2529
3:00 | 4071 | 495 | 1525 | 2384 | 0 | 183 | 1142 | 0 | 152
3:30 | 4065 | 495 | 1579 | 2267 | 0 | 182 | 1107.5 | 0 | 150 | [6 empty] | Shortage
4:00 | 4059 | 495 | 1633 | 2150 | 0 | 181 | 1073 | 0 | 148
4:30 | 4062 | 495 | 1666.5 | 2058 | 0 | 183 | 1024 | 0 | 145
5:00 | 4065 | 495 | 1700 | 1966 | 0 | 185 | 975 | 0 | 142
5:30 | 4024 | 494.5 | 1710 | 1828.5 | 0 | 180 | 818 | 0 | 136
6:00 | 3983 | 494 | 1720 | 1691 | 0 | 175 | 661 | 0 | 130
6:30 | 3923 | 494.5 | 1743.5 | 1663.5 | 0 | 180 | 649 | 0 | 115 |  |  |  |  | Coal
7:00 | 3863 | 495 | 1767 | 1636 | 0 | 185 | 637 | 0 | 100
7:30 | 3850 | 494.5 | 1744 | 1629.5 | 0 | 185 | 625.5 | 0 | 98 |  |  |  | Oil |  |  |  | ,
8:00 | 3837 | 494 | 1721 | 1623 | 0 | 185 | 614 | 0 | 96
8:30 | 3885 | 494 | 1713.5 | 1748.5 | 0 | 187 | 641 | 0 | 108
9:00 | 3933 | 494 | 1706 | 1874 | 0 | 189 | 668 | 0 | 120
9:30 | 3971.5 | 494 | 1685.5 | 1936.5 | 0 | 189 | 665.5 | 0 | 120
10:00 | 4010 | 494 | 1665 | 1999 | 0 | 189 | 663 | 0 | 120
10:30 | 3997 | 494 | 1653.5 | 2094.5 | 0 | 195 | 694.5 | 0 | 121
11:00 | 3984 | 494 | 1642 | 2190 | 0 | 201 | 726 | 0 | 122
11:30 | 4005.5 | 494 | 1594 | 2408 | 0 | 195 | 637.5 | 0 | 124
12:00 | 4027 | 494 | 1546 | 2626 | 0 | 189 | 549 | 0 | 126
12:30 | 3958 | 494 | 1554 | 2663 | 0 | 188 | 545 | 0 | 130
13:00 | 3889 | 494 | 1562 | 2700 | 0 | 187 | 541 | 0 | 134
13:30 | 3889 | 494 | 1562 | 2700 | 0 | 187 | 541 | 0 | 134
14:00 | 3889 | 494 | 1562 | 2700 | 0 | 187 | 541 | 0 | 134
14:30 | 3943 | 494 | 1629 | 2644 | 0 | 184.5 | 537 | 0 | 138
15:00 | 3997 | 494 | 1696 | 2588 | 0 | 182 | 533 | 0 | 142
15:30 | 3996 | 494 | 1745 | 2590 | 0 | 181 | 538.5 | 0 | 141
16:00 | 3995 | 494 | 1794 | 2592 | 0 | 180 | 544 | 0 | 140
16:30 | 3901.5 | 494.5 | 1788.5 | 2536 | 0 | 185 | 569 | 0 | 141
17:00 | 3808 | 495 | 1783 | 2480 | 0 | 190 | 594 | 0 | 142
17:30 | 3671.5 | 495 | 1710.5 | 2505 | 0 | 193 | 597 | 0 | 137
18:00 | 3535 | 495 | 1638 | 2530 | 0 | 196 | 600 | 0 | 132
18:30 | 3769 | 495 | 1695.5 | 2847.5 | 0 | 198 | 800.5 | 0 | 152
19:00 | 4003 | 495 | 1753 | 3165 | 0 | 200 | 1001 | 0 | 172
19:30 | 4080 | 496 | 1751 | 3268 | 0 | 200 | 1130 | 0 | 172
20:00 | 3975 | 496 | 1646 | 3263 | 0 | 200 | 1138 | 0 | 172
20:30 | 3984 | 496 | 1670 | 3277.5 | 0 | 200 | 1137.5 | 0 | 172
21:00 | 3993 | 496 | 1694 | 3292 | 0 | 200 | 1137 | 0 | 172
21:30 | 3929 | 496 | 1650.5 | 3231 | 0 | 200 | 1133.5 | 0 | 173
22:00 | 3865 | 496 | 1607 | 3170 | 0 | 200 | 1130 | 0 | 174
22:30 | 3866 | 496 | 1618 | 3169 | 0 | 194.5 | 1131.5 | 0 | 171
23:00 | 3867 | 496 | 1629 | 3168 | 0 | 189 | 1133 | 0 | 168
23:30 | 3864.5 | 495.5 | 1649.5 | 3169.5 | 0 | 189 | 1127.5 | 0 | 166 | Max Temp. in Dhaka |  | 33.8° C
24:00 | 3862 | 495 | 1670 | 3171 | 0 | 189 | 1122 | 0 | 164
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 234.253 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 234.253 MKWHr
Note on W13: Author:

## Generation
2018-08-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 107 | 105 | 103 | 101 | 105 | 95 | 105 | 105 | 109 | 109 | 121 | 109 | 107 | 107 | 102 | 100 | 110 | 116 |  | 120 | 120 | 120 | 120 | 120 | 109 | 109 | 2541749
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1910600
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 333540
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 227 | 227 | 227 | 228 | 227 | 227 | 228 | 228 | 228 | 203 | 203 | 0 | 0 | [13 empty] | 2490945
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 135 | 100 | 70 | 50 | 50 | 50 | 50 | 50 | 80 | 80 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 80 |  | 135 | 135 | 135 | 135 | 135 | 136 | 130 | 2530339
| Dohazari Peaking | 47 | 46 | 46 | 46 | 46 | 4 | 0 | 0 |  |  | 12 | 16 | 28 | 32 | 34 | 33 | 33 | 33 |  | 33 | 45 | 45 | 42 | 45 | 46 | 46 | 732570
12 | Hathazari peaking | 81 | 81 | 81 | 82 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 60 | 80 | 80 | 80 | 79 | 80 |  | 80 | 80 | 82 | 82 | 80 | 80 | 80 | 1401872
| Daudkandi bangla trak | 140 | 50 | 0 | [8 empty] | 83 | 100 | 50 | 20 | 20 | 0 | 0 |  | 152 | 200 | 200 | 200 | 200 | 200 | 200 | 1578240
14 | Daudkandi Peaking 52MW | 41 | 41 | 41 | 0 | [13 empty] | 0 |  | 50 | 49 | 49 | 49 | 49 | 49 | 49 | 390240
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 218 | 218 | 216 | 222 | 221 | 224 | 219 | 214 | 216 | 214 | 212 | 212 | 209 | 170 | 208 | 208 | 209 | 120 |  | 180 | 214 | 210 | 210 | 216 | 216 | 216 | 5055402
18 | Summit Gazipur | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 178 | 190 | 195 | 190 | 183 | 178 | 175 | 175 | 178 |  | 204 | 210 | 210 | 214 | 215 | 205 | 163 | 4423500
19 | Ashuganj 195MW Modular | 109 | 109 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 157 | 197 | 195 | 194 | 195 | 199 |  | 160 | 110 | 68 | 68 | 68 | 68 | 68 | 2960727
20 | Ghorasal ST: Unit-1,2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1556000
21 | Ghorasal ST: Unit-3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2508660
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2520000
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 300 | 250 | 300 | 365 | 365 | 365 | 365 | 330 | 330 | 330 | 330 | 280 | 250 |  | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 8219999
26
28 | Ashuganj ST: Unit- 3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 80 | 80 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 100 | 100 | 80 | 80 | 80 | 80 | 120 | 2609904
29 | Ashuganj ST: Unit- 4 | [21 empty] | 0 | 10 | 26 | 65 | 70 | 128635
30 | Ashuganj ST: Unit- 5 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 125 | 125 | 60 | 0 |  | 2855130
32 | Ashuganj Engines TSK | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 10 | 10 | 10 | 10 | 31 | 812088
33 | Ashuganj CCPP 225 MW | 220 | 220 | 220 | 222 | 222 | 222 | 222 | 229 | 182 | 199 | 188 | 205 | 184 | 182 | 206 | 199 | 182 | 194 |  | 200 | 178 | 164 | 186 | 220 | 222 | 212 | 4945000
34 | Ashuganj CCPP(South) | 312 | 301 | 305 | 300 | 300 | 300 | 301 | 342 | 300 | 338 | 305 | 334 | 300 | 300 | 338 | 334 | 300 | 301 |  | 360 | 334 | 276 | 276 | 276 | 250 | 250 | 7348000
| Ashuganj CCPP(North) | [20 empty] | 0 | 20 | 20 | 20 | 75 | 18 | 187600
35 | Ashuganj (Precision) 55MW | [14 empty] | 0 | 3 | 3 | 6 |  | 6 | 4 | 4 | 8 | 8 | 8 | 8 | 42720
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2407480
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 390 | 393 | 400 | 405 | 410 | 415 | 370 | 300 | 375 | 375 | 370 | 370 | 360 | 320 | 370 | 380 | 376 | 300 |  | 330 | 374 | 376 | 370 | 365 | 360 | 360 | 8965120
40 | Meghnaghat CCPP 450MW | 370 | 380 | 400 | 400 | 400 | 400 | 400 | 400 | 360 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 340 | 360 |  | 360 | 340 | 340 | 340 | 340 | 340 | 340 | 7860938
41 | Haripur Power CCPP 360MW | 273 | 292 | 292 | 292 | 292 | 290 | 292 | 271 | 252 | 232 | 221 | 211 | 201 | 210 | 212 | 211 | 211 | 212 |  | 221 | 221 | 210 | 191 | 180 | 170 | 196 | 5652000
42 | Mymensingh RPCL 210MW | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 48 | 48 | 48 | 47 | 47 | 47 | 48 |  | 47 | 47 | 47 | 47 | 47 | 48 | 47 | 1150000
43 | Haripur NEPC 110MW | 96 | 96 | 96 | 29 | 13 | 0 |  |  |  |  | 26 | 75 | 96 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1538200
44 | Fenchugonj CCPP-1 | 70 | 70 | 67 | 65 | 65 | 70 | 65 | 65 | 65 | 65 | 67 | 65 | 66 | 66 | 67 | 66 | 70 | 70 |  | 62 | 68 | 65 | 65 | 70 | 70 | 70 | 1593000
45 | Fenchugonj CCPP-2 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1474120
46 | Shajibazar 330 MW | 300 | 302 | 300 | 300 | 300 | 302 | 300 | 321 | 301 | 317 | 328 | 314 | 298 | 300 | 330 | 318 | 302 | 313 |  | 337 | 339 | 338 | 330 | 331 | 330 | 330 | 7178403
47 | Shahjibazar GT: Unit- 8, 9 | 32 | 32 | 32 | 32 | 32 | 20 | 30 | 32 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 710000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 83 | 83 | 84 | 86 | 86 | 86 | 50 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 2043840
49 | Shahjibazar (EPL) 50MW | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 46 | 45 | 44 | 44 | 44 | 45 | 45 | 45 | 46 | 20 |  | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 1057680
50 | Sylhet GT 150 MW | 117 | 98 | 98 | 98 | 98 | 98 | 99 | 98 | 98 | 115 | 117 | 127 | 114 | 114 | 118 | 128 | 80 | 78 |  | 116 | 130 | 134 | 133 | 112 | 112 | 115 | 2655710
51 | Sylhet GT 20 MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 |  |  |  |  | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 350000
52 | Sylhet (EPL) 50MW | 46 | 46 | 46 | 46 | 47 | 46 | 48 | 46 | 47 | 46 | 43 | 43 | 45 | 45 | 42 | 45 | 43 | 43 |  | 43 | 43 | 43 | 43 | 46 | 45 | 45 | 1071480
53 | Sylhet (Desh) 10MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 5 | 5 | 5 | 5 | 5 | 172260
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 3 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252336
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 44 | 44 | 44 | 44 | 47 | 53 | 53 |  | 52 | 53 | 52 | 52 | 52 | 52 | 50 | 1189200
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 15 | 15 | 22 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 21 | 526224
57 | Summit Bibiana- 2 | 7 | 35 | 75 | 180 | 250 | 260 | 280 | 280 | 290 | 300 | 310 | 310 | 300 | 290 | 310 | 310 | 290 | 280 |  | 290 | 325 | 270 | 320 | 270 | 270 | 290 | 6508900
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 36 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1238273
59 | Sikalbaha (Energis) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1088160
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439872
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 500076
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 518292
63 | Tripura | 158 | 154 | 152 | 148 | 142 | 130 | 100 | 96 | 120 | 120 | 122 | 126 | 134 | 134 | 142 | 140 | 142 | 132 |  | 172 | 172 | 172 | 172 | 174 | 168 | 164 | 3381120
64 | Malancha, Ctg. EPZ (United) | 34 | 35 | 34 | 38 | 38 | 38 | 24 | 6 | 2 | 2 | 2 | 2 | 8 | 2 | 2 | 2 | 5 | 2 |  | 4 | 8 | 13 | 23 | 28 | 28 | 27 | 435840
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 451728
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249301
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823400
68 | Summit Comilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 15 | 15 | 15 |  | 21 | 21 | 21 | 21 | 21 | 16 | 15 | 322840
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 22 | 22 | 22 | 30 | 30 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 714600
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 17 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 741800
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 837000
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh) | 52 | 50 | 0 | [8 empty] | 15 | 70 | 100 | 100 | 100 | 50 | 50 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 1248000
77 | Siddhirganj (Dutch Bangla) | 100 | 100 | 100 | 50 | 7 | 7 | 7 | 7 | 7 | 40 | 80 | 85 | 99 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1929600
78 | Gazipur (RPCL) | 51 | 51 | 51 | 51 | 51 | 25 | 25 | 25 | 34 | 34 | 34 | 37 | 43 | 42 | 42 | 44 | 51 | 51 |  | 51 | 51 | 51 | 51 | 52 | 51 | 51 | 1071864
79 | Kodda 149 MW | 132 | 132 | 132 | 132 | 98 | 16 | 16 | 32 | 82 | 82 | 116 | 133 | 133 | 133 | 133 | 133 | 145 | 140 |  | 134 | 132 | 132 | 132 | 137 | 149 | 149 | 2773920
80 | Jamalpur 95MW | 91 | 91 | 91 | 91 | 91 | 64 | 64 | 64 | 80 | 82 | 83 | 83 | 82 | 82 | 82 | 82 | 90 | 90 |  | 90 | 90 | 90 | 90 | 91 | 90 | 91 | 2041920
81 | Lakdhanvi 52 MW | [9 empty] | 0 | 7 | 8 | 0 | [6 empty] | 0 | 8 | 10 | 30 | 0 |  |  | 70080
82 | Madanganj 102MW | 64 | 64 | 64 | 64 | 64 | 16 | 16 | 15 | 15 | 52 | 64 | 48 | 52 | 65 | 60 | 48 | 48 | 60 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1306560
83 | Pagla (DPA ) | 10 | 10 | 0 | [5 empty] | 30 | 31 | 30 | 51 | 46 | 49 | 30 | 31 | 20 | 20 |  | 50 | 51 | 50 | 50 | 50 | 50 | 50 | 652000
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 51 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1306560
85 | Keraniganj (Powerpac) 100MW | 60 | 60 | 60 | 60 | 30 | 10 | 10 | 10 | 50 | 70 | 75 | 75 | 86 | 86 | 86 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1756870
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 305 | 200 | 200 | 200 | 200 | 200 | 200 |  | 305 | 305 | 305 | 305 | 240 | 270 | 270 | 5673329
87 | Meghnaghat (IEL) | 100 | 100 | 100 | 100 | 57 | 15 | 7 | 7 | 7 | 8 | 68 | 90 | 100 | 100 | 99 | 100 | 100 | 100 |  | 100 | 100 | 99 | 99 | 100 | 100 | 100 | 1879680
88 | Ghorashal 78MW (MAX) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | [12 empty] | 363776
90 | Ashuganj (United) 53MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 53 | 53 | 53 | 53 | 10 |  | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 392000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2099760
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1137000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 1007791
94 | Gagnagar (Orion) | 102 | 102 | 102 | 102 | 70 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2418336
95 | Patenga 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 40 | 38 | 45 | 38 | 40 | 44 | 40 | 43 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 34 | 44 | 45 | 44 | 1060320
96 | Chittagong ECPV 108 MW | 88 | 94 | 99 | 98 | 88 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 85 | 85 | 86 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 2113960
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 39 | 6 | 6 | 6 | 9 | 37 | 40 | 35 | 35 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 39 | 40 | 40 | 840048
98 | Bosila 108MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 171840
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 23 | 40 | 40 | 40 | 40 | 40 | 44 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1121363
100 | Northern 55 MW | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 55 | 56 | 55 | 56 | 55 | 56 | 55 | 37 | 37 | 37 | 55 |  | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 1242078
101 | Kushiara 163 MW CCPP GT | 10 | 15 | 10 | 10 | 10 | 30 | 70 | 70 | 109 | 109 | 90 | 10 | 10 | 30 | 40 | 130 | 130 | 130 |  | 130 | 163 | 163 | 163 | 130 | 163 | 163 | 1953327
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.4 | 0.6 | 1.3 | 1.3 | 1.3 | 1.9 | 1.9 | 0.8 | 1.2 | 1 | 0.5 | 0.1 |  | 0 | 0 | 0 |  |  |  |  | 11950
103 | Banco Energy 54MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 |  | 54 | 54 | 54 | 54 | 54 | 18 | 18 | 595800
104 | APR Energy , Keranigonj | 166 | 57 | 0 | [14 empty] | 0 |  | 50 | 54 | 58 | 87 | 107 | 124 | 125 | 833304
105 | Bramhangoan 100 MW (Aggreko) | 50 | 10 | 0 | [5 empty] | 10 | 20 | 50 | 96 | 92 | 93 | 98 | 98 | 70 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 99 | 1294690
106 | United Mymensingh PPL | 130 | 122 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 122 | 122 | 131 | 127 | 127 | 127 | 129 |  | 129 | 129 | 129 | 129 | 129 | 137 | 136 | 3105600
112 | Aggreko Aurahati 100MW | 51 | 21 | 0 | [5 empty] | 10 | 21 | 50 | 97 | 99 | 98 | 99 | 98 | 72 | 51 |  | 99 | 99 | 99 | 99 | 100 | 100 | 100 | 1354861
114 | Summit Gazipur-1 150MW | 125 | 106 | 106 | 106 | 107 | 107 | 107 | 122 | 123 | 118 | 118 | 115 | 144 | 144 | 144 | 144 | 144 | 149 |  | 149 | 149 | 149 | 148 | 148 | 148 | 150 | 3142080
115
116
117
118
120 | Eastern Zone Total | 7648 | 7352 | 7192 | 7124 | 6951 | 6492 | 6392.4 | 6399.6 | 6682.3 | 6846.3 | 7137.3 | 7249.9 | 7246.9 | 7286.8 | 7434.2 | 7532 | 7301.5 | 6997.1 |  | 8020 | 8174 | 7967 | 8068 | 7898 | 7927 | 7917 | 174752920
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 92 | 92 | 92 | 92 | 92 | 69 | 69 | 33 | 85 | 75 | 74 | 73 | 80 | 85 | 83 | 84 | 89 | 95 |  | 101 | 97 | 95 | 96 | 71 | 70 | 70 | 1935840
125 | Khulna (KPCL-2) | 112 | 113 | 112 | 101 | 97 | 97 | 85 | 97 | 97 | 97 | 81 | 80 | 80 | 96 | 95 | 92 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2405760
126
127 | Khulna (Aggreko) 55MW
128 | Faridpur Peaking | 34 | 34 | 34 | 34 | 34 | 34 | 29 | [8 empty] | 4 | 12 | 13 |  | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 512640
129 | Khulna CCPP 225MW
130
131
132
133
| Summit Barisal 110 MW | 96 | 98 | 96 | 87 | 81 | 75 | 64 | 64 | 90 | 80 | 80 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 110 | 110 | 110 | 110 | 113 | 113 | 110 | 2013120
136 | Barisal GT: Unit-1, 2 | [20 empty] | 0 | 12 | 12 | 0 |  | 10 | 30076
137 | Bhola Aggreko 95MW | 98 | 97 | 98 | 98 | 96 | 96 | 94 | 90 | 95 | 95 | 96 | 97 | 94 | 96 | 96 | 98 | 98 | 71 |  | 98 | 98 | 97 | 98 | 97 | 98 | 98 | 2283859
| Bhola CCPP 194MW | 187 | 187 | 190 | 162 | 165 | 141 | 189 | 189 | 187 | 188 | 180 | 187 | 173 | 173 | 183 | 184 | 184 | 184 |  | 173 | 185 | 187 | 188 | 91 | 88 | 84 | 4231058
140 | Bhola (Venture) 33MW | 33 | 31 | 32 | 31 | 32 | 25 | 25 | 24 | 22 | 23 | 24 | 23 | 11 | 24 | 26 | 25 | 18 | 24 |  | 34 | 36 | 37 | 39 | 39 | 38 | 36 | 653486
141 | Bangla Trak Noapara | 98 | 98 | 96 | [7 empty] | 20 | 94 | 94 | 45 | 20 | 20 |  |  |  | 90 | 100 | 93 | 79 | 40 | 30 | 76 | 995520
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 24 | 24 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 813000
143 | Gopalganj Peaking | 65 | 65 | 55 | 45 | 45 | [10 empty] | 8 | 25 | 40 |  | 62 | 91 | 70 | 70 | 70 | 62 | 62 | 744960
144 | Bheramara GT-1,2,3 | [19 empty] | 48 | 48 | 48 | 48 | 48 | 48 | 32 | 248300
145
146 | Bheramara HVDC | 495 | 495 | 495 | 495 | 495 | 494 | 495 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 494 | 495 | 495 |  | 495 | 496 | 496 | 496 | 496 | 496 | 495 | 11812364
147 | Bheramara 360 MW | 410 | 412 | 412 | 417 | 415 | 419 | 350 | 300 | 411 | 410 | 410 | 410 | 410 | 350 | 410 | 410 | 350 | 250 |  | 410 | 410 | 410 | 410 | 411 | 414 | 416 | 9464832
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 43 | 43 | 43 | 43 | 43 | 0 | [13 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 457352
157 | Sirajgonj Unit-1 225MW (Gas) | 217 | 218 | 216 | 217 | 218 | 219 | 218 | 219 | 192 | 186 | 188 | 205 | 214 | 214 | 214 | 214 | 216 | 197 |  | 207 | 220 | 219 | 218 | 219 | 219 | 218 | 5313164
158 | Sirajgonj Unit-1 225MW (Oil)
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 173 | 172 | 172 | 172 | 172 | 172 | 167 | 156 | 147 | 167 | 168 | 173 | 152 | 118 | 118 | 118 | 120 | 120 |  | 155 | 220 | 220 | 220 | 220 | 220 | 220 | 4160127
159 | Sirajgonj Unit-3 225 MW(Gas) | 152 | 153 | 152 | 156 | 156 | 155 | 152 | 150 | 153 | 150 | 149 | 148 | 149 | 151 | 148 | 152 | 152 | 151 |  | 151 | 151 | 153 | 154 | 152 | 154 | 154 | 3619363
160 | Sirajgonj Unit-3 225 MW(Oil) | [17 empty] | 0 |  |  |  |  | 0
161 | Bera Peaking | 31 | 31 | 31 | 31 | 31 | 10 | 0 | 0 | [9 empty] | 10 |  | 36 | 36 | 36 | 38 | 38 | 37 | 37 | 390499
162 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 428160
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236160
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 184820
165 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1097910
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 992000
167 | Katakhali Peaking | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 0 |  |  | 12 | 43 |  | 45 | 46 | 47 | 45 | 45 | 44 | 45 | 799921
168 | Santahar Peaking | 38 | 38 | 38 | 38 | 38 | 39 | 38 | 39 | 39 | 39 | 0 | 0 | [5 empty] | 8 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 627345
169 | Rajlanka 52 MW | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 51 | 50 | 51 | 50 | 51 | 51 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 51 | 52 | 1228320
170 | Chapainawabganj-100 MW | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 75 | 100 | 100 | 100 | 100 | 100 | 100 | 1516996
171
172
173 | Rangpur GT | 15 | 15 | 15 | 15 | 0 | [12 empty] | 0 |  | 17 | 17 | 16 | 17 | 16 | 16 | 16 | 164000
175 | Saidpur GT | 14 | 14 | 14 | 14 | 0 | [12 empty] | 0 |  | 0 | 0 | 16 | 17 | 17 | 16 | 16 | 139000
176
177
178
178 | Western Zone Total | 2770 | 2773 | 2760 | 2615 | 2577 | 2362 | 2291 | 2171 | 2303 | 2295 | 2223 | 2309 | 2262 | 2158 | 2199 | 2208 | 2191 | 2129 | 0 | 2769 | 2923 | 2923 | 2916 | 2744 | 2723 | 2756 | 59499952
176
177