## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-07-03 | Tuesday
|  | Date (day): | 2018-07-03 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10763 | MW |  |  | (b) At Evening Peak Hour : |  | 11495 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-07-02 | 2018-07-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 57 | 62 | 72 | 72 |  | 13
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 270 | 250 | 200 | 250 | 115 |  | Gas shortage
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 0 | 0 | 0
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 0 | 0 | 0
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 345 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 84 | 98 | 98 |  | 12 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 271 | 287 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 410 | 410 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 92 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 130 | 305 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 100 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 88 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 70 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 93 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 115 | 110 | 112 | 112
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 70 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 32 | 32 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 54 | 54 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 88 | 88 | 88 | 88
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 46 | 50 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 301 | 303 | 303 | 303
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 52 | 0 | 0 |  |  | On test
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 63 | 0 | 0
| Dhaka area Total |  |  |  |  | 5635 | 5399 | 3130 | 3686 | 3771 | 3821 | 530 | 540
37 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16
39 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 26 | 26 | 26
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 40 | 208 | 208 | 208 |  | 22 | # 2 under maint
41 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
42 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 200 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 70 | 135 | 70 | 135
44 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 49 | 51 | 51
45 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 48 | 72 | 72
46 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 76 | 76 | 76
47 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 80 | 80 |  | 20 | Engine problem
48 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 16 | 12 | 16
49 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 99 | 98 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 565 | 971 | 953 | 1022 | 360 | 95
50 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 100 | 100 | 100 | 35 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 0 | 0 | 0 | 129 |  | Under shut down
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 110 | 110 | 110 | 24 |  | Gas shortage
51 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 199 | 225 | 225 |  |  | FGMO
52 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 300 | 360 | 360 |  |  | FGMO
53 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 279 | 360 | 360 |  |  | FGMO
54 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 39 | 39 | 39 | 6 |  | Gas shortage
55 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
56 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 5 | 10 | 10 | 43 |  | Gas shortage
57 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 78 | 78 | 117 |  | Gas shortage
58 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
59 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
60 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 42
61 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST under maint.
62 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
63 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 124 | 158 | 119 | 164
64 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
65 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 41 | 52 | 52
66 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 22 | 22 | 22
67 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1643 | 1872 | 1774 | 2061 | 354 | 118
68 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 45 | 48 | 78 | 78 | 124 |  | Gas shortage
69 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
70 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
71 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.3 | 0 | 2 | 0
72 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 150 | 196 | 150 | 196
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 248.3 | 359 | 347 | 391 | 124 | 0
73 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 59 | 55 | 59 | 59
74 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 75 | 75 | 75 | 75
75 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
76 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
77 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 53 | 51 | 51
78 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 50 | 50
79 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
80 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 51 | 60 | 60
81 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
82 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 47 | 50 | 50
83 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint.
84 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
85 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 46 | 47 | 47 | 47
86 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 23 | 23
87 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 290 | 341 | 341 |  |  | FGMO
88 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 993 | 961 | 1026 | 1026 | 0 | 492
89 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 49 | 0 | 49
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 466 | 459 | 479 | 479
90 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 36 | 81 | 51 | 90
91 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 99 | 99 | 99
92 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 47 | 36 | 47
93 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 170 | 225 | 225 |  |  | FGMO
94 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 66 | 70 | 70
95 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 219 | 214 | 350 | 350 | 60 |  | Gas shortage
96 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
97 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 33 | 0 | 54
98 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 95 | 95 | 95
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 947 | 1353 | 1445 | 1598 | 60 | 0
99 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 110 | 110 | 110
100 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
101 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 36 | 35 | 35
102 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 182 | 194 | 194
103 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 356 | 425 | 434 | 464 | 0 | 0
104 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
105 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
106 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 38 | 0 | 38
107 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 40 | 40 |  | 10 | Engine problem
108 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
109 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 43 | 43
110 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 194 | 175 | 214 | 214
111 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 183 | 173 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
112 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 42 | 42
113 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
114 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 12 | 12
115 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
116 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 52 | 52 |  | 0
117 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 101 | 100 | 101
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 558 | 783 | 799 | 881 | 71 | 117
118 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
119 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 147 | 195 | 195 | 195
120 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
121 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 19 | 19
| Rangpur Area Total |  |  |  |  | 564 | 484 | 147 | 229 | 214 | 231 | 0 | 170
| Total |  |  |  |  | 15953 | 15410 | 8587.3 | 10639 | 10763 | 11495 | 1499 | 1532
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8122.3799 | 10063 | 10180.2866 | 10872.6558
A. |  | 2018-07-02 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10639 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7345.04 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10639 | MW
3 | Day peak Generation : |  |  | 8587.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10063 | MW
4 | Evening peak Generation : |  |  | 10639 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 212.1826 | MKWHr | By Solar | 0.0115 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 116.1173 | MKWHr |  | By Oil: | 74.2755 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6861 | MKWHr |  | By Hydro: | 3.6664 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1499 | MW | Dhaka | 3810 | 3810 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1532 | MW | Chittagong | 1041 | 1041 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3031 | MW | Khulna | 1302 | 1302 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 934.37 | MMCFD |  |  | Rajshahi | 977 | 977 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 89018209.92 | ii) Oil : | Taka | 549539584.79 | Comilla | 1005 | 1005 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 0 | Total | Taka | 638557794.71 | Mymensingh | 621 | 621 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 8.7275 | MKWHr. | Sylhet | 427 | 427 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -620 | MW at | 21:00 | hrs | Barisal | 280 | 280 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -620 | MW at | 21:00 | hrs | Rangpur | 600 | 600 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.6° C |  |  | Total | 10063 | 10063 |  | 0
B. |  | 2018-07-03 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11495 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
4 | Reserve(Generation end) |  |  |  | 695 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 215.3935 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6777 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.1244 | MKWHr. | ii) HVDC Flow at Peak Time |  | 459 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3014 | MKWHr. | iii) Maximum HVDC Flow : |  | 466 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 101.96 |  | (b) Today: | 102.19 |  | (c) Rule Curve: |  | 84.16
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-07-02
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 72 | 120 | 0 | 0 | 270 | 14 | 40 | 395 | 272 | 13 | 0 | 390 | 100 | 100 | 98 | 40 | 116 | 0 | 0 | 0 | 93 | 60 | 115 | 80 | 90 | 10 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 70 | 0 | 40 | 57 | 64 | 80 | 99 | 25 | 19 | 29 | 0 | 100 | 100 | 250 | 250 | 182 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 10 | 33 | 18 | 154 | 47 | 95 | 20 | 0 | 58 | 75 | 48 | 50 | 100 | 190 | 51 | 86 | 48 | 78 | 0 | 46 | 10 | 260 | 23 | 11 | 0 | 301 | 0 | 0 | 100 | 0 |  | 464 | 0 | 180 | 51 | 83 | 185 | 0 | 0 | 0 | 62 | 40 | 189 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 102 | 40 | 43 | 45 | 43 | 42 | 18 | 11 | 8 | 0 | 0 | 139 | 15 | 0 | 0 | 168 | 0 | 168 | 97 | 0 | 0 | 0 |  | 6912 | 2335 | 9247 | 3162 | 464 | 1769 | 2103 | 139 | 168 | 1288 | 154 | 0 | 0 | 101.98
2:00 | 72 | 120 | 0 | 0 | 270 | 14 | 40 | 410 | 288 | 13 | 0 | 400 | 100 | 55 | 94 | 30 | 115 | 0 | 0 | 0 | 60 | 30 | 82 | 30 | 90 | 0 | 39 | 54 | 36 | 36 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 70 | 0 | 40 | 57 | 64 | 80 | 99 | 26 | 19 | 32 | 0 | 100 | 100 | 250 | 250 | 182 | 78 | 100 | 33 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 10 | 33 | 18 | 148 | 47 | 95 | 20 | 0 | 58 | 75 | 48 | 50 | 100 | 190 | 51 | 86 | 48 | 78 | 0 | 46 | 10 | 280 | 16 | 11 | 0 | 301 | 0 | 0 | 100 | 0 |  | 464 | 0 | 176 | 51 | 83 | 165 | 0 | 0 | 0 | 54 | 40 | 189 | 26 | 80 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 43 | 45 | 43 | 41 | 18 | 11 | 8 | 0 | 0 | 141 | 15 | 0 | 0 | 170 | 0 | 168 | 97 | 0 | 0 | 0 |  | 6707 | 2253 | 8960 | 3162 | 464 | 1812 | 1854 | 141 | 168 | 1211 | 148 | 0 | 0 | 101.98
3:00 | 72 | 120 | 0 | 0 | 270 | 14 | 60 | 420 | 325 | 13 | 0 | 430 | 100 | 7 | 65 | 30 | 115 | 0 | 0 | 0 | 30 | 7 | 65 | 10 | 90 | 0 | 39 | 36 | 36 | 36 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 88 | 80 | 0 | 0 | 8 | 0 | 195 | 0 | 70 | 0 | 40 | 57 | 64 | 80 | 99 | 26 | 19 | 32 | 0 | 100 | 100 | 250 | 250 | 182 | 78 | 100 | 33 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 10 | 33 | 18 | 148 | 47 | 95 | 20 | 0 | 58 | 75 | 48 | 50 | 100 | 0 | 60 | 86 | 48 | 78 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 301 | 0 | 0 | 100 | 0 |  | 466 | 0 | 190 | 51 | 83 | 130 | 0 | 0 | 0 | 30 | 40 | 189 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 85 | 40 | 43 | 45 | 43 | 42 | 18 | 11 | 8 | 0 | 0 | 140 | 15 | 0 | 0 | 174 | 0 | 171 | 97 | 0 | 0 | 0 |  | 6386 | 2183 | 8569 | 3005 | 466 | 1861 | 1638 | 140 | 168 | 1143 | 148 | 0 | 0 | 101.97
4:00 | 72 | 120 | 0 | 0 | 270 | 14 | 79 | 420 | 326 | 0 | 0 | 430 | 100 | 7 | 65 | 30 | 115 | 0 | 0 | 0 | 30 | 7 | 65 | 10 | 90 | 0 | 39 | 36 | 36 | 36 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 86 | 80 | 0 | 0 | 0 | 0 | 195 | 0 | 70 | 0 | 40 | 57 | 32 | 80 | 45 | 26 | 19 | 34 | 0 | 100 | 100 | 250 | 257 | 188 | 78 | 100 | 33 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 10 | 33 | 22 | 142 | 47 | 48 | 20 | 0 | 58 | 75 | 48 | 50 | 100 | 0 | 61 | 86 | 48 | 78 | 0 | 45 | 10 | 310 | 23 | 10 | 0 | 301 | 0 | 0 | 100 | 0 |  | 465 | 0 | 190 | 51 | 83 | 120 | 0 | 0 | 0 | 10 | 40 | 188 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 43 | 45 | 35 | 0 | 18 | 11 | 8 | 0 | 0 | 137 | 15 | 0 | 0 | 182 | 0 | 180 | 98 | 0 | 0 | 0 |  | 6326 | 2073 | 8399 | 3028 | 465 | 1951 | 1499 | 137 | 166 | 1011 | 142 | 0 | 0 | 101.97
5:00 | 72 | 120 | 0 | 0 | 270 | 14 | 79 | 420 | 327 | 0 | 0 | 450 | 100 | 7 | 65 | 30 | 115 | 0 | 0 | 0 | 30 | 7 | 65 | 10 | 90 | 10 | 39 | 36 | 36 | 36 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 83 | 80 | 0 | 0 | 0 | 0 | 195 | 0 | 70 | 0 | 24 | 0 | 0 | 80 | 46 | 26 | 19 | 35 | 0 | 100 | 100 | 258 | 257 | 194 | 78 | 100 | 33 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 10 | 33 | 22 | 132 | 47 | 48 | 20 | 0 | 58 | 75 | 48 | 50 | 130 | 0 | 61 | 86 | 48 | 0 | 0 | 46 | 10 | 310 | 6 | 5 | 0 | 301 | 0 | 0 | 100 | 0 |  | 466 | 0 | 189 | 51 | 83 | 120 | 0 | 0 | 0 | 10 | 8 | 187 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 0 | 142 | 0 | 0 | 0 | 178 | 0 | 178 | 97 | 0 | 0 | 0 |  | 6186 | 1952 | 8138 | 2940 | 466 | 2004 | 1435 | 142 | 163 | 856 | 132 | 0 | 0 | 101.96
6:00 | 72 | 120 | 0 | 0 | 270 | 14 | 40 | 380 | 326 | 0 | 0 | 380 | 100 | 7 | 14 | 15 | 115 | 0 | 0 | 0 | 7 | 7 | 40 | 10 | 90 | 10 | 39 | 36 | 17 | 17 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 83 | 80 | 0 | 0 | 0 | 0 | 195 | 0 | 50 | 0 | 24 | 0 | 0 | 80 | 45 | 26 | 19 | 35 | 0 | 100 | 100 | 250 | 250 | 182 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 0 | 0 | 33 | 22 | 122 | 48 | 8 | 20 | 0 | 58 | 74 | 48 | 50 | 130 | 0 | 60 | 86 | 48 | 0 | 0 | 47 | 10 | 270 | 6 | 11 | 0 | 301 | 0 | 0 | 100 | 0 |  | 466 | 0 | 190 | 10 | 26 | 120 | 0 | 0 | 0 | 10 | 8 | 187 | 27 | 24 | 0 | 0 | 0 | 0 | 0 | 40 | 35 | 16 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 0 | 141 | 0 | 0 | 0 | 169 | 0 | 169 | 97 | 0 | 0 | 0 |  | 5726 | 1780 | 7506 | 2853 | 466 | 1855 | 1113 | 141 | 163 | 793 | 122 | 0 | 0 | 101.96
7:00 | 72 | 120 | 0 | 0 | 270 | 14 | 40 | 380 | 326 | 0 | 0 | 380 | 100 | 7 | 14 | 15 | 115 | 0 | 0 | 0 | 7 | 7 | 32 | 10 | 70 | 10 | 39 | 18 | 17 | 17 | 19 | 25 | 0 | 33 | 33 | 33 | 0 | 82 | 80 | 0 | 0 | 0 | 0 | 195 | 0 | 70 | 0 | 24 | 0 | 0 | 68 | 46 | 25 | 19 | 17 | 0 | 100 | 100 | 250 | 250 | 183 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 13 | 0 | 33 | 22 | 112 | 47 | 8 | 20 | 0.04 | 58 | 74 | 48 | 50 | 130 | 0 | 50 | 86 | 48 | 0 | 0 | 47 | 10 | 290 | 6 | 11 | 0 | 204 | 0 | 0 | 100 | 0 |  | 466 | 0 | 245 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 188 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 16 | 0 | 8 | 0 | 18 | 11 | 5 | 0 | 0 | 138 | 0 | 0 | 0 | 171 | 0 | 171 | 95 | 0 | 0 | 0 |  | 5553.04 | 1792 | 7345.04 | 2877 | 466 | 1853 | 953 | 138 | 162 | 784 | 112 | 0.04 | 0 | 101.95
8:00 | 72 | 120 | 0 | 0 | 300 | 15 | 60 | 380 | 310 | 0 | 0 | 430 | 100 | 7 | 14 | 15 | 115 | 0 | 0 | 0 | 7 | 7 | 36 | 10 | 70 | 10 | 39 | 18 | 17 | 17 | 19 | 25 | 0 | 33 | 25 | 33 | 0 | 83 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 70 | 0 | 24 | 0 | 0 | 68 | 40 | 25 | 19 | 2 | 0 | 100 | 100 | 305 | 275 | 197 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 16 | 0 | 33 | 22 | 112 | 47 | 8 | 20 | 0.1 | 58 | 74 | 48 | 50 | 130 | 0 | 60 | 86 | 47 | 0 | 0 | 47 | 10 | 305 | 6 | 11 | 0 | 205 | 0 | 0 | 103 | 0 |  | 466 | 0 | 245 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 189 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 16 | 0 | 8 | 0 | 18 | 11 | 5 | 0 | 0 | 138 | 0 | 0 | 0 | 175 | 0 | 175 | 97 | 0 | 0 | 0 |  | 5760.1 | 1801 | 7561.1 | 3007 | 466 | 1907 | 967 | 138 | 163 | 801 | 112 | 0.1 | 0 | 101.95
9:00 | 72 | 120 | 0 | 0 | 300 | 15 | 77 | 410 | 280 | 0 | 0 | 430 | 100 | 7 | 15 | 23 | 115 | 0 | 0 | 0 | 7 | 7 | 70 | 40 | 90 | 10 | 39 | 54 | 35 | 55 | 19 | 25 | 0 | 33 | 33 | 43 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 70 | 0 | 30 | 0 | 0 | 68 | 85 | 26 | 19 | 2 | 0 | 100 | 100 | 325 | 300 | 199 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 18 | 0 | 33 | 22 | 118 | 46 | 8 | 20 | 0.9 | 58 | 74 | 48 | 50 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 46 | 9 | 320 | 15 | 11 | 0 | 227 | 0 | 0 | 103 | 0 |  | 466 | 0 | 246 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 23 | 26 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 16 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 0 | 148 | 0 | 0 | 0 | 187 | 0 | 186 | 95 | 0 | 0 | 0 |  | 6163.9 | 1848 | 8011.9 | 3108 | 466 | 1937 | 1212 | 148 | 164 | 858 | 118 | 0.9 | 0 | 101.94
10:00 | 55 | 120 | 0 | 0 | 280 | 45 | 76 | 345 | 281 | 0 | 0 | 430 | 145 | 35 | 44 | 42 | 115 | 0 | 0 | 0 | 32 | 16 | 82 | 75 | 90 | 21 | 37 | 54 | 55 | 55 | 19 | 25 | 0 | 33 | 33 | 50 | 0 | 60 | 40 | 0 | 0 | 16 | 0 | 197 | 0 | 100 | 0 | 24 | 0 | 0 | 80 | 98 | 26 | 18 | 2 | 0 | 100 | 100 | 315 | 315 | 192 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 8 | 33 | 22 | 120 | 46 | 8 | 20 | 1.8 | 58 | 74 | 48 | 47 | 163 | 0 | 60 | 86 | 45 | 0 | 0 | 46 | 9 | 320 | 15 | 11 | 0 | 298 | 0 | 0 | 142 | 0 |  | 465 | 0 | 240 | 10 | 44 | 120 | 0 | 0 | 0 | 0 | 40 | 191 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 35 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 0 | 154 | 0 | 0 | 0 | 187 | 0 | 186 | 93 | 0 | 0 | 0 |  | 6426.8 | 1945 | 8371.8 | 3006 | 465 | 1960 | 1668 | 154 | 100 | 897 | 120 | 1.8 | 0 | 101.94
11:00 | 55 | 120 | 0 | 0 | 270 | 22 | 40 | 353 | 281 | 0 | 0 | 410 | 100 | 91 | 70 | 42 | 115 | 0 | 0 | 0 | 85 | 40 | 82 | 88 | 90 | 21 | 32 | 54 | 54 | 55 | 19 | 25 | 24 | 33 | 33 | 50 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 200 | 0 | 70 | 0 | 24 | 0 | 0 | 80 | 99 | 26 | 19 | 3 | 0 | 100 | 100 | 325 | 327 | 201 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 0 | 19 | 8 | 33 | 22 | 128 | 46 | 20 | 20 | 1.1 | 58 | 74 | 48 | 47 | 163 | 0 | 59 | 86 | 45 | 0 | 0 | 46 | 10 | 315 | 23 | 11 | 0 | 301 | 0 | 0 | 150 | 0 |  | 466 | 0 | 221 | 10 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 192 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 185 | 0 | 182 | 96 | 0 | 0 | 0 |  | 6471.1 | 1951 | 8422.1 | 3049 | 466 | 1881 | 1843 | 150 | 40 | 864 | 128 | 1.1 | 0 | 101.94
12:00 | 57 | 120 | 0 | 0 | 270 | 22 | 40 | 360 | 271 | 0 | 0 | 410 | 130 | 92 | 80 | 42 | 115 | 0 | 0 | 0 | 90 | 70 | 82 | 88 | 88 | 21 | 32 | 54 | 54 | 55 | 19 | 25 | 30 | 33 | 33 | 46 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 209 | 0 | 70 | 0 | 32 | 0 | 0 | 80 | 99 | 0 | 16 | 3 | 0 | 100 | 100 | 335 | 335 | 207 | 78 | 100 | 36 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 8 | 33 | 22 | 124 | 45 | 32 | 20 | 1.3 | 59 | 75 | 48 | 47 | 163 | 0 | 60 | 86 | 45 | 0 | 0 | 46 | 10 | 320 | 23 | 11 | 0 | 301 | 0 | 0 | 150 | 0 |  | 466 | 0 | 219 | 36 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 147 | 0 | 0 | 0 | 194 | 0 | 183 | 95 | 0 | 0 | 0 |  | 6579.3 | 2008 | 8587.3 | 3085 | 466 | 1883 | 1933 | 147 | 40 | 908 | 124 | 1.3 | 0 | 101.93
13:00 | 60 | 120 | 0 | 0 | 270 | 12 | 20 | 370 | 262 | 0 | 0 | 390 | 200 | 100 | 82 | 55 | 120 | 0 | 0 | 0 | 90 | 102 | 98 | 100 | 79 | 21 | 32 | 18 | 54 | 55 | 19 | 25 | 30 | 33 | 33 | 50 | 0 | 40 | 80 | 0 | 0 | 16 | 0 | 196 | 0 | 70 | 0 | 32 | 0 | 0 | 80 | 92 | 3 | 17 | 2 | 0 | 100 | 100 | 320 | 323 | 195 | 78 | 100 | 36 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 5 | 33 | 22 | 132 | 45 | 92 | 20 | 0.7 | 59 | 75 | 48 | 50 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 47 | 10 | 325 | 23 | 11 | 0 | 303 | 0 | 0 | 150 | 0 |  | 466 | 0 | 213 | 39 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 188 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 146 | 0 | 0 | 0 | 194 | 0 | 187 | 96 | 0 | 0 | 0 |  | 6750.7 | 2019 | 8769.7 | 3055 | 466 | 1827 | 2090 | 146 | 120 | 933 | 132 | 0.7 | 0 | 101.92
14:00 | 62 | 120 | 0 | 0 | 270 | 12 | 20 | 345 | 261 | 0 | 0 | 390 | 200 | 100 | 98 | 55 | 140 | 0 | 0 | 0 | 90 | 98 | 98 | 100 | 80 | 20 | 32 | 54 | 54 | 55 | 19 | 25 | 30 | 33 | 33 | 50 | 0 | 40 | 80 | 0 | 0 | 16 | 0 | 194 | 0 | 50 | 0 | 34 | 0 | 0 | 80 | 92 | 25 | 17 | 2 | 30 | 100 | 100 | 310 | 312 | 191 | 78 | 100 | 36 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 130 | 48 | 95 | 20 | 1.5 | 59 | 75 | 48 | 50 | 100 | 0 | 60 | 86 | 45 | 0 | 0 | 46 | 10 | 300 | 23 | 11 | 0 | 303 | 0 | 0 | 150 | 0 |  | 466 | 0 | 214 | 39 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 183 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 178 | 0 | 175 | 97 | 0 | 0 | 0 |  | 6722.5 | 1996 | 8718.5 | 3062 | 466 | 1743 | 2165 | 148 | 120 | 883 | 130 | 1.5 | 0 | 101.91
15:00 | 62 | 120 | 0 | 0 | 270 | 14 | 20 | 360 | 260 | 13 | 0 | 390 | 240 | 100 | 98 | 55 | 120 | 0 | 0 | 2 | 90 | 102 | 98 | 100 | 80 | 20 | 32 | 54 | 54 | 55 | 19 | 25 | 22 | 33 | 33 | 50 | 0 | 38 | 80 | 0 | 0 | 16 | 0 | 208 | 0 | 80 | 0 | 40 | 0 | 0 | 80 | 98 | 26 | 17 | 2 | 70 | 70 | 100 | 327 | 327 | 147 | 78 | 100 | 36 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 0 | 33 | 22 | 124 | 46 | 95 | 20 | 1.6 | 54 | 75 | 48 | 50 | 100 | 0 | 60 | 86 | 45 | 0 | 0 | 46 | 10 | 320 | 23 | 11 | 0 | 303 | 0 | 0 | 150 | 0 |  | 466 | 0 | 213 | 39 | 66 | 120 | 0 | 0 | 0 | 4 | 40 | 191 | 19 | 50 | 0 | 0 | 0 | 0 | 0 | 68 | 40 | 43 | 0 | 8 | 0 | 17 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 184 | 0 | 184 | 95 | 0 | 0 | 0 |  | 6818.6 | 2019 | 8837.6 | 3036 | 466 | 1757 | 2239 | 150 | 118 | 946 | 124 | 1.6 | 0 | 0
16:00 | 62 | 120 | 0 | 0 | 250 | 0 | 20 | 365 | 271 | 40 | 0 | 390 | 240 | 100 | 98 | 55 | 110 | 0 | 0 | 17 | 90 | 102 | 98 | 100 | 80 | 20 | 32 | 54 | 54 | 55 | 19 | 25 | 31 | 33 | 8 | 46 | 0 | 86 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 80 | 0 | 40 | 0 | 0 | 80 | 98 | 26 | 17 | 2 | 55 | 110 | 80 | 300 | 283 | 139 | 78 | 100 | 36 | 0 | 10 | 45 | 85 | 0 | 11 | 19 | 0 | 33 | 20 | 124 | 45 | 72 | 17 | 1 | 54 | 75 | 49 | 50 | 163 | 0 | 60 | 86 | 44 | 0 | 0 | 46 | 10 | 320 | 23 | 11 | 0 | 303 | 0 | 0 | 150 | 0 |  | 465 | 0 | 213 | 45 | 89 | 120 | 0 | 0 | 0 | 7 | 40 | 193 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 146 | 0 | 0 | 0 | 185 | 0 | 184 | 97 | 0 | 0 | 0 |  | 6819 | 2033 | 8852 | 2917 | 465 | 1815 | 2292 | 146 | 166 | 926 | 124 | 1 | 0 | 0
17:00 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 345 | 272 | 55 | 0 | 390 | 240 | 75 | 70 | 55 | 110 | 0 | 0 | 17 | 50 | 51 | 98 | 60 | 80 | 10 | 32 | 54 | 54 | 55 | 19 | 25 | 31 | 33 | 33 | 50 | 0 | 86 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 80 | 0 | 40 | 0 | 0 | 80 | 98 | 26 | 16 | 2 | 100 | 0 | 110 | 300 | 283 | 183 | 78 | 100 | 36 | 0 | 5 | 45 | 52 | 0 | 25 | 19 | 0 | 33 | 19 | 122 | 46 | 56 | 20 | 0.6 | 50 | 75 | 50 | 50 | 163 | 0 | 52 | 50 | 20 | 0 | 0 | 46 | 10 | 290 | 23 | 11 | 0 | 303 | 0 | 0 | 150 | 0 |  | 466 | 0 | 213 | 45 | 99 | 120 | 0 | 0 | 0 | 15 | 40 | 188 | 24 | 48 | 0 | 0 | 0 | 0 | 10 | 50 | 25 | 8 | 0 | 8 | 0 | 11 | 11 | 11 | 0 | 0 | 148 | 0 | 0 | 0 | 172 | 0 | 172 | 98 | 0 | 0 | 0 |  | 6497.6 | 1982 | 8479.6 | 2916 | 466 | 1667 | 2075 | 148 | 166 | 919 | 122 | 0.6 | 0 | 0
18:00 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 343 | 276 | 55 | 0 | 390 | 200 | 55 | 70 | 55 | 110 | 0 | 0 | 17 | 50 | 24 | 98 | 30 | 85 | 10 | 33 | 54 | 54 | 55 | 19 | 25 | 31 | 33 | 33 | 50 | 0 | 85 | 60 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 40 | 0 | 17 | 80 | 98 | 26 | 19 | 2 | 100 | 0 | 110 | 300 | 253 | 184 | 78 | 100 | 36 | 0 | 5 | 45 | 51 | 0 | 25 | 19 | 0 | 33 | 19 | 128 | 46 | 56 | 20 | 0 | 30 | 75 | 13 | 47 | 120 | 0 | 60 | 30 | 20 | 0 | 0 | 47 | 10 | 300 | 23 | 11 | 0 | 303 | 0 | 0 | 140 | 0 |  | 459 | 0 | 213 | 45 | 99 | 120 | 0 | 0 | 0 | 25 | 24 | 191 | 24 | 48 | 0 | 0 | 0 | 0 | 27 | 50 | 12 | 8 | 0 | 8 | 0 | 5 | 11 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 172 | 0 | 171 | 64 | 0 | 0 | 0 |  | 6219 | 1937 | 8156 | 2879 | 459 | 1538 | 1925 | 150 | 145 | 932 | 128 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 358 | 286 | 55 | 0 | 390 | 260 | 62 | 70 | 55 | 110 | 0 | 0 | 17 | 60 | 40 | 130 | 95 | 88 | 10 | 32 | 54 | 54 | 55 | 19 | 25 | 22 | 33 | 33 | 50 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 209 | 0 | 120 | 0 | 40 | 56 | 47 | 80 | 98 | 26 | 19 | 2 | 120 | 0 | 110 | 330 | 320 | 184 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 27 | 25 | 19 | 0 | 33 | 19 | 150 | 46 | 50 | 20 | 0 | 60 | 75 | 32 | 47 | 163 | 0 | 60 | 86 | 45 | 0 | 0 | 47 | 10 | 300 | 23 | 11 | 20 | 303 | 0 | 0 | 0 | 0 |  | 458 | 0 | 213 | 87 | 99 | 130 | 0 | 12 | 50 | 50 | 32 | 190 | 32 | 80 | 0 | 0 | 0 | 43 | 37 | 66 | 16 | 8 | 39 | 8 | 22 | 16 | 11 | 0 | 0 | 0 | 147 | 17 | 18 | 0 | 178 | 0 | 178 | 98 | 20 | 0 | 0 |  | 6909 | 2355 | 9264 | 3023 | 458 | 1784 | 2077 | 147 | 208 | 1417 | 150 | 0 | 0 | 0
19:30 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 393 | 286 | 84 | 0 | 410 | 305 | 100 | 101 | 55 | 110 | 0 | 0 | 60 | 90 | 80 | 149 | 100 | 88 | 50 | 32 | 54 | 54 | 55 | 19 | 25 | 22 | 33 | 33 | 50 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 215 | 0 | 135 | 0 | 42 | 56 | 70 | 80 | 98 | 26 | 19 | 2 | 100 | 0 | 110 | 335 | 316 | 165 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 41 | 25 | 19 | 11 | 33 | 22 | 158 | 46 | 95 | 20 | 0 | 55 | 75 | 53 | 47 | 163 | 0 | 60 | 86 | 45 | 0 | 0 | 47 | 10 | 330 | 23 | 11 | 60 | 303 | 0 | 18 | 4 | 30 |  | 458 | 16 | 214 | 84 | 99 | 170 | 0 | 12 | 49 | 50 | 40 | 190 | 36 | 110 | 0 | 0 | 0 | 43 | 37 | 100 | 40 | 25 | 45 | 8 | 42 | 18 | 11 | 11 | 0 | 0 | 160 | 17 | 18 | 0 | 190 | 0 | 189 | 96 | 53 | 0 | 0 |  | 7511 | 2631 | 10142 | 3041 | 458 | 1859 | 2626 | 160 | 208 | 1632 | 158 | 0 | 0 | 0
20:00 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 375 | 286 | 84 | 0 | 410 | 305 | 100 | 100 | 55 | 110 | 0 | 0 | 54 | 91 | 102 | 149 | 100 | 88 | 50 | 32 | 54 | 54 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 135 | 0 | 42 | 56 | 76 | 80 | 98 | 26 | 19 | 8 | 100 | 0 | 110 | 310 | 290 | 174 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 41 | 33 | 19 | 0 | 33 | 22 | 162 | 47 | 95 | 20 | 0 | 55 | 75 | 53 | 47 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 46 | 10 | 320 | 23 | 11 | 170 | 303 | 0 | 51 | 120 | 63 |  | 458 | 32 | 213 | 79 | 99 | 170 | 0 | 33 | 49 | 60 | 40 | 191 | 37 | 110 | 0 | 0 | 0 | 43 | 38 | 101 | 40 | 43 | 47 | 43 | 42 | 18 | 11 | 11 | 0 | 0 | 158 | 17 | 18 | 0 | 187 | 0 | 186 | 97 | 95 | 0 | 0 |  | 7760 | 2766 | 10526 | 2981 | 458 | 1857 | 3053 | 158 | 208 | 1649 | 162 | 0 | 0 | 0
21:00 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 345 | 287 | 84 | 0 | 410 | 305 | 100 | 100 | 55 | 110 | 0 | 0 | 70 | 93 | 102 | 149 | 100 | 88 | 51 | 32 | 54 | 54 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 135 | 0 | 49 | 48 | 76 | 80 | 98 | 26 | 19 | 16 | 100 | 0 | 110 | 300 | 279 | 199 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 42 | 41 | 19 | 11 | 33 | 22 | 158 | 48 | 95 | 20 | 0 | 55 | 75 | 53 | 50 | 163 | 0 | 51 | 86 | 47 | 0 | 0 | 47 | 10 | 290 | 23 | 11 | 200 | 303 | 0 | 52 | 196 | 63 |  | 459 | 49 | 214 | 81 | 99 | 170 | 0 | 33 | 47 | 66 | 40 | 182 | 36 | 110 | 0 | 0 | 0 | 43 | 38 | 101 | 40 | 43 | 45 | 43 | 42 | 18 | 11 | 11 | 0 | 0 | 195 | 17 | 17 | 0 | 175 | 0 | 173 | 97 | 95 | 0 | 0 |  | 7849 | 2790 | 10639 | 2950 | 459 | 1840 | 3196 | 195 | 208 | 1633 | 158 | 0 | 0 | 0
22:00 | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 344 | 292 | 70 | 0 | 410 | 240 | 100 | 97 | 55 | 110 | 0 | 0 | 100 | 93 | 64 | 149 | 100 | 88 | 10 | 33 | 54 | 54 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 100 | 0 | 51 | 48 | 76 | 80 | 98 | 26 | 19 | 21 | 100 | 0 | 110 | 300 | 279 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 42 | 25 | 19 | 11 | 33 | 22 | 158 | 49 | 95 | 20 | 0 | 58 | 75 | 53 | 50 | 130 | 0 | 51 | 86 | 47 | 0 | 0 | 47 | 10 | 280 | 23 | 11 | 50 | 303 | 0 | 0 | 192 | 0 |  | 458 | 33 | 213 | 45 | 96 | 170 | 0 | 33 | 47 | 63 | 40 | 184 | 37 | 110 | 0 | 0 | 0 | 43 | 37 | 102 | 40 | 43 | 45 | 43 | 41 | 18 | 11 | 11 | 0 | 0 | 200 | 17 | 17 | 0 | 167 | 0 | 167 | 98 | 97 | 0 | 0 |  | 7357 | 2726 | 10083 | 2938 | 458 | 1809 | 2747 | 200 | 208 | 1565 | 158 | 0 | 0 | 0
23:00 | 62 | 120 | 0 | 0 | 200 | 0 | 0 | 300 | 292 | 26 | 0 | 340 | 240 | 100 | 97 | 55 | 110 | 0 | 0 | 0 | 93 | 64 | 149 | 100 | 90 | 10 | 32 | 54 | 54 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 130 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 100 | 0 | 51 | 48 | 75 | 80 | 98 | 26 | 19 | 21 | 100 | 0 | 110 | 305 | 287 | 188 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 42 | 25 | 19 | 11 | 33 | 22 | 160 | 48 | 48 | 20 | 0 | 58 | 75 | 53 | 50 | 100 | 0 | 62 | 86 | 47 | 0 | 0 | 47 | 10 | 290 | 23 | 11 | 0 | 301 | 0 | 0 | 194 | 0 |  | 458 | 33 | 215 | 51 | 96 | 170 | 0 | 33 | 42 | 60 | 40 | 191 | 28 | 110 | 0 | 0 | 0 | 43 | 37 | 102 | 40 | 43 | 45 | 43 | 42 | 18 | 11 | 11 | 0 | 0 | 157 | 15 | 18 | 0 | 168 | 0 | 168 | 98 | 97 | 0 | 0 |  | 6964 | 2683 | 9647 | 2881 | 458 | 1710 | 2513 | 157 | 210 | 1558 | 160 | 0 | 0 | 0
24:00 | 62 | 120 | 0 | 0 | 200 | 0 | 0 | 300 | 337 | 13 | 0 | 300 | 200 | 60 | 97 | 55 | 103 | 0 | 0 | 0 | 60 | 32 | 149 | 20 | 90 | 10 | 32 | 54 | 54 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 130 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 51 | 48 | 76 | 80 | 98 | 26 | 19 | 22 | 100 | 0 | 110 | 300 | 279 | 182 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 42 | 25 | 19 | 11 | 33 | 22 | 156 | 47 | 24 | 20 | 0 | 58 | 74 | 53 | 50 | 100 | 0 | 48 | 86 | 47 | 0 | 0 | 46 | 10 | 280 | 23 | 11 | 0 | 301 | 0 | 0 | 194 | 0 |  | 458 | 33 | 214 | 51 | 96 | 170 | 0 | 33 | 42 | 60 | 40 | 186 | 36 | 112 | 0 | 0 | 0 | 43 | 36 | 102 | 40 | 43 | 45 | 43 | 36 | 18 | 11 | 11 | 0 | 0 | 145 | 15 | 18 | 0 | 169 | 0 | 169 | 95 | 97 | 0 | 0 |  | 6602 | 2667 | 9269 | 2833 | 458 | 1710 | 2253 | 145 | 210 | 1504 | 156 | 0 | 0 | 0
KWH | 1386000 | 2730735 | 0 | 0 | 6578327 | 285409 | 959616 | 9000960 | 6932000 | 568400 | 0 | 9176001 | 4272145 | 1525440 | 1803864 | 1043022 | 2829001 | 0 | 0 | 374400 | 1571414 | 1294027 | 2307360 | 1541013 | 2037120 | 383790 | 855312 | 1121760 | 1082077 | 1143000 | 430200 | 600000 | 579960 | 729600 | 805100 | 1109484 | 0 | 1879844 | 1786600 | 0 | 0 | 316620 | 0 | 4737419 | 0 | 1843118 | 0 | 892800 | 521928 | 653149 | 1809840 | 2054400 | 592800 | 436120 | 311040 | 929284 | 1583200 | 2444392 | 7429200 | 6920250 | 4515000 | 1890181 | 2377000 | 826776 | 0 | 195000 | 954592 | 1803864 | 210472 | 253426 | 417456 | 154800 | 816700 | 535810 | 3301440 | 1138360 | 1378820 | 459828 | 11500 | 1295000 | 1780280 | 1110600 | 1182000 | 3246163 | 487203 | 1364000 | 1989120 | 1040040 | 355570 | 0 | 1062640 | 251280 | 7521000 | 451368 | 256032 | 466560 | 7060579 | 0 | 100734 | 3064800 | 126410 |  | 11124364 | 167600 | 5202144 | 965280 | 1704000 | 3428160 | 0 | 164650 | 278880 | 560896 | 765000 | 4593017 | 614240 | 1536000 | 0 | 0 | 0 | 248048 | 225686 | 1478452 | 927440 | 819056 | 441100 | 499200 | 334745 | 408000 | 267372 | 209260 | 0 | 0 | 3686100 | 156000 | 96000 | 0 | 4481300 | 0 | 4408145 | 2269189 | 472320 | 0 | 0 |  | 159650945 | 52531644 | 212182589 | 72647933 | 11124364 | 43469347 | 47697003 | 3686100 | 3666444 | 26578458 | 3301440 | 11500 | 0
Fuel Cost | 1191960 | 2348432.1 | 0 | 0 | 5657361.22 | 231181.29 | 902039.04 | 5490585.6 | 4228520 | 5462324 | 0 | 6147920.67 | 64893882.55 | 9579763.2 | 12049811.52 | 6372864.42 | 1838850.65 | 0 | 0 | 5825664 | 9821337.5 | 8527637.93 | 22312171.2 | 9816252.81 | 12202348.8 | 6136802.1 | 5704931.04 | 7998148.8 | 6762981.25 | 7166610 | 322650 | 450000 | 0 | 0 | 0 | 10495718.64 | 0 | 0 | 0 | 0 | 0 | 2998391.4 | 0 | 64665769.35 | 0 | 40382715.38 | 0 | 7847712 | 5621164.56 | 6355139.77 | 11202909.6 | 13271424 | 3876912 | 370702 | 0 | 845648.44 | 1440712 | 2224396.72 | 6760572 | 4774972.5 | 3160500 | 1304224.89 | 2281920 | 553939.92 | 0 | 179400 | 782765.44 | 1695632.16 | 2281516.48 | 1880420.92 | 321441.12 | 116100 | 628859 | 401857.5 | 22581849.6 | 853770 | 12671355.8 | 354067.56 | 0 | 1346800 | 1851491.2 | 1066176 | 1063800 | 4187550.27 | 341042.1 | 1554960 | 2128358.4 | 1144044 | 405349.8 | 0 | 988255.2 | 233690.4 | 4813440 | 338526 | 194584.32 | 8085484.8 | 0 | 0 | 0 | 0 | 0 |  | 56734256.4 | 4885540 | 3485436.48 | 6370848 | 11416800 | 55124812.8 | 0 | 2627814 | 3140188.8 | 6607354.88 | 4873050 | 4547086.83 | 608097.6 | 9492480 | 0 | 0 | 0 | 2840149.6 | 2419353.92 | 13246929.92 | 8022356 | 7289598.4 | 4697715 | 4952064 | 3605203.65 | 448800 | 251329.68 | 158409.82 | 0 | 0 | 0 | 3598920 | 2058240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 494371064.93 | 223502835.78 | 717873900.71 | 56612984.88 | 56734256.4 | 32405225.04 | 305696699.48 | 0 | 0 | 243842885.31 | 22581849.6 | 0 | 0
Yesterday Day Peak | 57 | 120 | 0 | 0 | 270 | 22 | 40 | 360 | 271 | 0 | 0 | 410 | 130 | 92 | 80 | 42 | 115 | 0 | 0 | 0 | 90 | 70 | 82 | 88 | 88 | 21 | 32 | 54 | 54 | 55 | 19 | 25 | 30 | 33 | 33 | 46 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 209 | 0 | 70 | 0 | 32 | 0 | 0 | 80 | 99 | 0 | 16 | 3 | 0 | 100 | 100 | 335 | 335 | 207 | 78 | 100 | 36 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 8 | 33 | 22 | 124 | 45 | 32 | 20 | 1.3 | 59 | 75 | 48 | 47 | 163 | 0 | 60 | 86 | 45 | 0 | 0 | 46 | 10 | 320 | 23 | 11 | 0 | 301 | 0 | 0 | 150 | 0 |  | 466 | 0 | 219 | 36 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 11 | 0 | 0 | 147 | 0 | 0 | 0 | 194 | 0 | 183 | 95 | 0 | 0 | 0 |  | 8587.3 | DayPeak
Yesterday Evening Peak | 62 | 120 | 0 | 0 | 250 | 0 | 0 | 345 | 287 | 84 | 0 | 410 | 305 | 100 | 100 | 55 | 110 | 0 | 0 | 70 | 93 | 102 | 149 | 100 | 88 | 51 | 32 | 54 | 54 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 135 | 0 | 49 | 48 | 76 | 80 | 98 | 26 | 19 | 16 | 100 | 0 | 110 | 300 | 279 | 199 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 42 | 41 | 19 | 11 | 33 | 22 | 158 | 48 | 95 | 20 | 0 | 55 | 75 | 53 | 50 | 163 | 0 | 51 | 86 | 47 | 0 | 0 | 47 | 10 | 290 | 23 | 11 | 200 | 303 | 0 | 52 | 196 | 63 |  | 459 | 49 | 214 | 81 | 99 | 170 | 0 | 33 | 47 | 66 | 40 | 182 | 36 | 110 | 0 | 0 | 0 | 43 | 38 | 101 | 40 | 43 | 45 | 43 | 42 | 18 | 11 | 11 | 0 | 0 | 195 | 17 | 17 | 0 | 175 | 0 | 173 | 97 | 95 | 0 | 0 |  | 10639 | EvPeak
Forecast for Evening | 72 | 120 | 0 | 0 | 250 | 0 | 0 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 100 | 55 | 112 | 0 | 0 | 100 | 93 | 102 | 149 | 100 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 135 | 0 | 51 | 72 | 76 | 80 | 98 | 26 | 19 | 16 | 100 | 0 | 110 | 360 | 360 | 225 | 78 | 100 | 39 | 0 | 10 | 51 | 85 | 42 | 52 | 19 | 11 | 33 | 22 | 164 | 78 | 95 | 22 | 0 | 59 | 75 | 51 | 50 | 163 | 0 | 60 | 86 | 50 | 0 | 0 | 47 | 10 | 341 | 23 | 11 | 200 | 303 | 0 | 0 | 196 | 0 |  | 479 | 49 | 350 | 90 | 99 | 225 | 0 | 54 | 47 | 70 | 40 | 194 | 35 | 110 | 30 | 0 | 0 | 43 | 38 | 101 | 40 | 43 | 43 | 52 | 42 | 22 | 12 | 11 | 0 | 0 | 195 | 17 | 19 | 0 | 214 | 0 | 220 | 95 | 95
Forecast for Day | 72 | 120 | 0 | 0 | 200 | 0 | 0 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 100 | 55 | 112 | 0 | 0 | 100 | 93 | 102 | 149 | 100 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 128 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 70 | 0 | 51 | 72 | 76 | 80 | 98 | 26 | 19 | 12 | 100 | 0 | 110 | 360 | 360 | 225 | 78 | 100 | 39 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 11 | 33 | 22 | 119 | 78 | 95 | 22 | 2 | 59 | 75 | 51 | 50 | 163 | 0 | 60 | 86 | 50 | 0 | 0 | 47 | 10 | 341 | 23 | 11 | 0 | 303 | 0 | 0 | 150 | 0 |  | 479 | 0 | 350 | 51 | 99 | 225 | 0 | 0 | 36 | 70 | 40 | 194 | 35 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 43 | 43 | 52 | 42 | 22 | 12 | 11 | 0 | 0 | 195 |  | 19 | 0 | 214 | 0 | 220 | 95 | 95
Generation at 08:00(Today) | 62 | 120 | 0 | 0 | 200 | 0 | 0 | 290 | 353 | 0 | 0 | 300 | 200 | 7 | 15 | 15 | 112 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 17 | 17 | 19 | 25 | 32 | 33 | 28 | 25 | 0 | 123 | 80 | 0 | 0 | 0 | 0 | 204 | 0 | 50 | 0 | 8 | 0 | 0 | 80 | 12 | 6 | 19 | 12 | 100 | 0 | 110 | 335 | 334 | 205 | 78 | 100 | 10 | 0 | 5 | 6 | 50 | 0 | 0 | 19 | 11 | 8 | 18 | 104 | 78 | 8 | 20 | 0 | 59 | 74 | 5 | 5 | 100 | 0 | 60 | 50 | 5 | 0 | 0 | 5 | 10 | 320 | 23 | 8 | 0 | 50 | 0 | 0 | 54 | 0 | 0 | 466 | 0 | 300 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 193 | 21 | 49 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 43 | 0 | 8 | 0 | 13 | 11 | 5 | 0 | 0 | 146 | 0 | 0 | 0 | 186 | 0 | 134 | 97 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7345.04 | 7:00
| Highest Generation |  | 10639 | 21:00
| Day Peak Generation |  | 8587.3 | 12:00
| Evening Peak Generation |  | 10639 | 21:00
| HVDC Max Flow |  | 466 | 3:00
| HVDC EvPeak Flow |  | 459 | 21:00
| Load factor L.F |  | 83.1%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-07-03
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-07-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8587.3 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6777 | MW
Evening Peak Generation : |  | 10639 | MW Hour : | 21:00 | Available Max Generation : |  | 11495 | MW
E.P. Demand (at gen end) : |  | 10639 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10800 | MW
Maximum Generation : |  | 10639 | MW Hour : | 21:00 | Reserve(Generation end) |  | 695 | MW
Total Gen. (MKWH) : |  | 212.1826 | System Load Factor : | 83.1% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -620 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-07-03
Actual : | 102.19 | Ft.(MSL) , | Rule curve : | 84.16 | Ft.( MSL )
Gas Consumed : | Total = | 934.37 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 89018209.92
|  | Coal : | 0 | Oil : | 549539584.79 | Total : | 638557794.71
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3806.2179 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1293.2972 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1158.5684 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1046.7992 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 946.0132 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 763.3966 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 428.176 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 196.5891 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 588.763 |  |  | 0 | 0%
Total | 0 |  | 10227.8206 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
3) Ghorasal Unit-2,4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Siddhirganj 132/33 kV T1 transformer tripped at 10:15 showing lock out relay and was switched on at 10:37. |  |  |  | About 95 MW Power interruption occurred under Siddhirganj S/S
area from 10:15 to 10:37.
b) Sirajganj-Bagherhat 230 kV Ckt-1 was under shut down from 11:03 to 13:54 for red hot maintenance at Sirajganj end.
c) Meghnaghat Summit GT-1 was synchronized at 11:28.
d) Ishurdi 230/132 kV T03 transformer tripped at 12:50 showing without any relay and is still under maintenance.
e) Ashuganj Unit-3 was synchronized at 13:05.
f) Faridpur 132/33 T2 transformer was under shut down from 13:50 to 14:38 for red hot maintenance at B-Phase
33 kV CT clamp.
g) Tongi 132/33 kV T3 transformer was under shut down from 10:40 to 15:27 for red hot maintenance at 33 kV Bus-2. |  |  |  | About 10 MW Power interruption occurred under Tongi S/S
area from 10:40 to 15:57.
h) Ashuganj Unit-4 was shut down at 16:15 due to gas shortage.
i) Tongi-Bashundhara 132 kV Ckt-1 tripped at 18:11 showing O/C relay at Tongi end & E/F relay at Bashundhara end
and was switched on at 18:50.
j) Jamalpur-Sherpur 132 kV Ckt-1 & 2 tripped at 18:40 due to 33 kV Sharisabari feeder fault and were switched on at
18:46.
k) Jamalpur 132/33 kV T1 & T2 transformers tripped at 18:40 showing lock-out relay and were switched on at 18:44.
l) Rampura-Bhulta 230 kV Ckt was switched on at 21:17.
m) Palashbari 132/33 kV T2 transformer was under shut down from 17:26 to 18:40 for red hot maintenance.
n) Barisal 132/33 kV T1 & T2 transformers tripped at 01:05 (03/07/2018) showing instantaneous relay and was
switched on at 01:08 (03/07/2018).
o) Jhenaidah 132/33 kV T1 and its associated 33 kV bus was under shut down from 07:30 to 08:10 (03/07/2018) for |  |  |  | About 30 MW Power interruption occurred under Jhenaidah S/S
red hot maintenance at 33 kV Kaliganj feeder. |  |  |  | area from 07:30 to 08:10.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-07-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 62 | 1386000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2730735 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 250 | 6578327 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 959616 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 285409 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 345 | 9000960 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 84 | 568400 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 287 | 6932000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 410 | 9176001 | Frequency control
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1525440
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 4272145
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 100 | 1803864
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1043022
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1541013
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 430200
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 70 | 374400 | Engine problem
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 93 | 1571414 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 110 | 2829001 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 383790
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1294027
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 32 | 855312 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1121760
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2307360
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 54 | 1082077
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1143000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 88 | 2037120 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1179960 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 729600
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 805100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 1109484
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 303 | 7060579
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 52 | 100734
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 63 | 126410
| Dhaka area Total |  |  |  | 5399 | 3686 | 74344260
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 316620 | Engine problem
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 26 | 592800
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 208 | 3666444 | # 5 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 200 | 4737419 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 1843118
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 49 | 892800
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 48 | 521928
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 76 | 653149
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1809840 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436120
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 16 | 311040
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 2054400 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 971 | 17835678
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 929284 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 1583200 | S/D due to gas shortage.
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 110 | 2444392
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 199 | 4515000 | FGMO
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7429200 | FGMO
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 279 | 6920250 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 39 | 826776 | Engine problem
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 195000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 78 | 1890181 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 954592
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1803864
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 42 | 210472
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2377000 | ST S/D
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 417456
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 154800
** | Tripura |  | Imported power | 0 | 160 | 158 | 3301440
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816700
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 41 | 253426 | Line over load
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 535810 | Engine problem
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 200 | 466560
| Comilla Area Total |  |  |  | 2541 | 1872 | 38025403
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 48 | 1138360 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 459828
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1378820
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 11500
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 196 | 3064800
| Mymensingh Area Total |  |  |  | 522 | 359 | 6053308
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 55 | 1295000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 75 | 1780280
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3246163
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 487203 | Under maint.
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1110600
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1182000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 256032
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 51 | 1364000 | FGMO
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1989120
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 1040040
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 355570
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 1062640 | Engine problem
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 451368
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 290 | 7521000 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 251280
| Sylhet Area Total |  |  |  | 1549 | 961 | 23392296
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 49 | 167600
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 459 | 11124364
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 81 | 965280 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1704000 | Engine problem
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 47 | 278880
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 170 | 3428160 | Low demand
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 66 | 560896
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 214 | 5202144 | Gas shortage
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 765000
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 33 | 164650 | Low demand
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 95 | 472320
| Khulna Area Total |  |  |  | 1769 | 1353 | 24833294
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1536000
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 36 | 614240
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 182 | 4593017
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 2269189
| Barisal Area Total |  |  |  | 462 | 425 | 9012446
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 248048
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 38 | 225686
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 927440 | Engine problem
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 819056 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 441100
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 175 | 0 | FGMO
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 173 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 42 | 334745
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 408000
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 267372 | Engine problem
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 209260
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 499200 | Engine problem
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 101 | 1478452
| Rajshahi Area Total |  |  |  | 1123 | 783 | 5858359
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 195 | 3686100
120 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 156000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 96000
| Rangpur Area Total |  |  |  | 484 | 229 | 3938100
| Total |  |  |  | 15410 | 10639 | 203293144
| Eastern Grid Total |  |  |  | 11572 | 7849 | 159650945
| Western Grid Total |  |  |  | 3838 | 2790 | 43642199
| National Grid Total |  |  |  | 15410 | 10639 | 203293144
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-07-02 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6904 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3159 | MW
i) Dhaka area |  |  | 3810 | MW | i) Khulna area |  |  | 1302 | MW
ii) Chittagong area |  |  | 1041 | MW | ii) Rajshahi area |  |  | 977 | MW
iii) Comilla area |  |  | 1005 | MW | iii) Barisal area |  |  | 280 | MW
iv) Mymensingh area |  |  | 621 | MW | iv) Rangpur area |  |  | 600 | MW
v) Sylhet area |  |  | 427 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10063 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 900 | Kishorganj | 95 | 2100 | Goalpara | 43 | 2000
Munsiganj | 114 | 2100 | Netrokona | 75 | 1930 | Central s/s | 72 | 1930
Sonargaon | 45 | 1900 | Jamalpur | 96 | 100 | Noapara | 93 | 1930
Shyampur | 158 | 100 | Sherpur | 76 | 2100 | Jessore | 146 | 2100
Bhulta | 175 | 2000 | Srimongal | 32 | 1930 | Jhenida | 81 | 2200
Madanganj | 52 | 2100 | Shahjibazar | 101 | 2200 | Bottail | 112 | 2100
Shitalakhya | 108 | 1200 | Fenchuganj | 44 | 1930 | G.K Project | 45 | 2200
Rahim steel | 6 | 1500 | Kulawara | 39 | 1930 | Faridpur | 148 | 2000
Matuail | 89 | 1200 | Sylhet | 129 | 2100 | Madaripur | 146 | 2100
Ghorasal | 80 | 2100 | Chatak | 24 | 2100 | Gopalganj | 81 | 2000
Narsingdi | 119 | 2100 | Sunamganj | 30 | 2000 | Bagerhat | 78 | 2000
Haripur (SBU) | 82 | 100 | Biani Bazar | 36 | 2000 | Mongla | 34 | 1300
Ullon | 96 | 1900 | Comilla (S) | 162 | 2000 | Satkhira | 92 | 2200
Hasnabad | 205 | 2100 | Comilla(N) | 107 | 2100 | Gallamari | 48 | 2000
Magbazar | 133 | 1300 | Chandpur | 117 | 2100 | Magura | 52 | 1930
Maniknagar | 98 | 1300 | Feni | 122 | 2000 | Chuadanga | 64 | 100
Bangabhaban | 40 | 1500 | Chowmuhani | 180 | 2100 | Barisal | 114 | 2000
Narinda | 80 | 1600 | Ashuganj | 56 | 2100 | Patuakhali | 90 | 2100
Dhanmondi | 129 | 1200 | Daudkandi | 104 | 2100 | Bhandaria | 48 | 2100
Lalbag | 87 | 2100 | B.Baria | 129 | 2000 | Ishurdi | 56 | 2000
Madartek | 51 | 1900 | Ramganj | 32 | 2100 | Ruppur Paromanobik | 1 | 100
Mirpur | 106 | 2100 | Madunaghat | 52 | 2000 | Natore | 104 | 2100
Kalyanpur | 126 | 1400 | Hathazari | 94 | 2100 | Bogra | 210 | 2100
Gulshan | 148 | 1500 | Khulshi | 196 | 1500 | Noagaon | 97 | 2000
Uttara | 89 | 1900 | Halishahar | 138 | 1400 | Rajshahi | 126 | 2100
Kamrangirchar | 72 | 1930 | Baraulia | 152 | 300 | C.Nawabganj | 58 | 2100
Savar | 137 | 1400 | Sikalbaha | 37 | 1930 | Amnura | 35 | 2100
Bhasantec | 162 | 1300 | Dohazari | 88 | 1930 | Pabna | 95 | 2100
Agargaon | 46 | 1930 | Cox'sbazar | 96 | 2000 | Shahjadpur | 64 | 1500
Satmosjid | 97 | 1830 | Chandraghona | 33 | 1930 | Serajganj | 72 | 2000
Tongi | 130 | 1200 | Kaptai | 4 | 2000 | Niyamatpur | 39 | 100
Kabirpur | 206 | 1300 | A. Khaer Stl. | 16 | 1300 | Joypurhat | 40 | 2000
Basundhara | 131 | 2000 | Bakulia | 108 | 1900 | Rangpur | 120 | 2000
Manikganj | 100 | 2000 | Julda | 20 | 1000 | Lalmonirhat | 85 | 2000
Joydevpur | 234 | 1500 | TK chemical | 6 | 1200 | Saidpur | 101 | 1900
New Tongi | 115 | 1700 | Modern Steel | 11 | 400 | Purbasadipur | 85 | 1930
Korda | 230 | 2100 | Shahmirpur | 26 | 2000 | Thakurgaon | 66 | 2100
Dhamrai | 19 | 2200 | Abul Khair 230 | 6 | 1700 | Palashbari | 86 | 2100
Tangail | 133 | 2000 | BSRM | 107 | 1930 | Barapukuria | 41 | 1930
Mymensing | 200 | 2000 | Khagrachhari | 17 | 2000 | Panchagar | 36 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-07-02
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 392 | 7:00 | 383 | 15:00 | Kaliakoir | 375 | 7:00 | 364 | 19:00
Bheramara | 405 | 7:00 | 399 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 225 | 23:00 | 217 | 11:00
Ishurdi | 235 | 2:00 | 225 | 15:00 | Comilla (N) | 232 | 5:00 | 225 | 12:00
Ashuganj | 235 | 1:00 | 231 | 21:00 | Hathazari | 217 | 24:00 | 210 | 11:00
Serajganj | 225 | 10:00 | 219 | 23:00 | Megnaghat | 226 | 5:00 | 221 | 12:00
Baghabari | 228 | 18:00 | 218 | 20:00 | Fenchuganj | 237 | 6:00 | 231 | 16:00
Barapukuria | 234 | 6:00 | 221 | 21:00 | Siddhirganj | 225 | 4:00 | 219 | 11:00
Bogra | 223 | 6:00 | 206 | 21:00 | Maniknagar | 223 | 22:00 | 216 | 12:00
Khulna South | 239 | 18:00 | 229 | 21:00 | Old Airport | 225 | 2:00 | 216 | 12:00
Rampura | 222 | 24:00 | 218 | 11:00 | Barisal | 232 | 12:00 | 226 | 15:00
Haripur | 222 | 3:00 | 218 | 11:00 | AKSML | 217 | 7:00 | 209 | 15:00
Hasnabad | 225 | 1:00 | 219 | 11:00 | BSRM | 220 | 24:00 | 213 | 10:00
Aminbazar | 225 | 4:00 | 219 | 9:00 | Bibiyana | 233 | 6:00 | 227 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 2200 | 131 | 900 | B.Baria | 139 | 700 | 132 | 1930
Munsiganj | 136 | 1900 | 131 | 800 | Ramganj | 124 | 1930 | 113 | 2200
Megnaghat | 134 | 2100 | 130 | 1100 | Madanhat | 132 | 2400 | 127 | 1200
Shyampur | 132 | 2000 | 125 | 900 | Hathazari | 130 | 2400 | 125 | 900
Bhulta | 126 | 100 | 122 | 1000 | Khulshi | 127 | 2400 | 121 | 1200
Madanganj | 136 | 2100 | 130 | 900 | Halishahar | 130 | 2400 | 125 | 1100
Shitalakhya | 139 | 2100 | 131 | 1000 | Baraulia | 128 | 600 | 124 | 1100
Rahim steal | 135 | 2300 | 131 | 900 | Sikalbaha | 131 | 1830 | 125 | 1200
Matuail | 135 | 2100 | 129 | 1000 | Dohazari | 126 | 2400 | 124 | 1200
Ghorasal | 140 | 2300 | 135 | 100 | Cox'sbazar | 121 | 1700 | 112 | 1930
Narsinghdi | 131 | 100 | 127 | 1000 | Chandraghona | 133 | 2100 | 125 | 1200
Haripur (SBU) | 135 | 100 | 131 | 1000 | Kaptai | 130 | 100 | 125 | 1200
Ullon | 135 | 600 | 128 | 1300 | A. Khaer Stl. | 127 | 700 | 123 | 1600
Hasnabad | 135 | 600 | 130 | 1000 | Bakulia | 128 | 2400 | 123 | 1200
Magbazar | 135 | 600 | 127 | 1600 | Julda | 129 | 2400 | 124 | 1200
Maniknagar | 135 | 600 | 130 | 1300 | TK Chemical | 133 | 2400 | 127 | 1200
Bangabhaban | 135 | 600 | 130 | 1300 | Modern Steel | 128 | 2400 | 123 | 1200
Narinda | 135 | 600 | 130 | 1300 | Shahmirpur | 129 | 1200 | 124 | 1100
Dhanmondi | 135 | 600 | 128 | 1300 | Khagrachhari | 130 | 2400 | 125 | 1200
Lalbag | 132 | 600 | 126 | 1100 | Goalpara | 136 | 1700 | 132 | 700
Madartek | 135 | 600 | 128 | 1400 | Central s/s | 138 | 1900 | 132 | 800
Mirpur | 135 | 700 | 130 | 1200 | Noapara | 135 | 1800 | 129 | 900
Kalyanpur | 136 | 700 | 132 | 1830 | Jessore | 130 | 1800 | 124 | 200
Gulshan | 134 | 600 | 126 | 1200 | Jhenida | 132 | 1800 | 121 | 2100
Uttara | 133 | 600 | 125 | 1200 | Bottail | 137 | 1800 | 130 | 2100
Kamrangirchar | 135 | 200 | 131 | 1200 | G.K.Project | 141 | 1800 | 135 | 2100
Savar | 133 | 300 | 118 | 1400 | Faridpur | 132 | 1200 | 126 | 1500
Bhasantec | 133 | 600 | 126 | 1200 | Madaripur | 130 | 500 | 125 | 1500
Agargaon | 133 | 200 | 127 | 1200 | Gopalganj | 133 | 1830 | 122 | 1500
Satmosjid | 133 | 600 | 126 | 1100 | Bagerhat | 134 | 300 | 130 | 700
Tongi | 134 | 700 | 128 | 1100 | Mongla | 132 | 1800 | 127 | 800
Kabirpur | 134 | 600 | 122 | 1100 | Satkhira | 135 | 1700 | 129 | 100
Basundhara | 131 | 200 | 126 | 1600 | Gallamari | 136 | 1700 | 132 | 100
Manikganj | 137 | 400 | 131 | 1200 | Magura | 130 | 1800 | 118 | 2100
Joydevpur | 140 | 2100 | 132 | 800 | Chuadanga | 131 | 1900 | 115 | 100
New Tongi | 135 | 100 | 129 | 1930 | Barisal | 136 | 500 | 133 | 1500
Kodda | 136 | 2000 | 131 | 2200 | Patuakhali | 135 | 1200 | 125 | 1930
Dhamrai | 134 | 1800 | 128 | 1200 | Bhandaria | 138 | 1700 | 129 | 1930
Tangail | 135 | 500 | 126 | 1900 | Ishurdi | 140 | 500 | 135 | 200
Mymensing | 132 | 1500 | 119 | 1830 | Ruppur Paromanobik | 139 | 1700 | 133 | 1500
Kishorganj | 132 | 1000 | 121 | 1930 | Natore | 139 | 1800 | 128 | 1700
Netrokona | 132 | 1000 | 122 | 1900 | Bogra | 137 | 1800 | 122 | 2100
Jamalpur | 136 | 1300 | 127 | 1930 | Noagaon | 131 | 1700 | 117 | 2100
Sherpur | 136 | 1300 | 130 | 300 | Rajshahi | 135 | 1800 | 127 | 2100
Srimongal | 140 | 600 | 135 | 100 | C.Nawabganj | 135 | 1700 | 128 | 900
Shahjibazar | 138 | 600 | 133 | 1930 | Amnura | 139 | 1700 | 131 | 900
Fenchuganj | 136 | 600 | 131 | 1930 | Pabna | 134 | 1800 | 126 | 2100
Khulawara | 135 | 300 | 131 | 1930 | Shahjadpur | 140 | 500 | 136 | 200
Sylhet | 135 | 500 | 129 | 1900 | Serajganj | 135 | 600 | 126 | 2000
Chatak | 135 | 400 | 127 | 1930 | Niyamatpur | 132 | 1700 | 112 | 2100
Sunamganj | 133 | 700 | 128 | 100 | Joypurhat | 132 | 1700 | 114 | 2100
Biani Bazar | 135 | 600 | 128 | 1900 | Rangpur | 124 | 600 | 103 | 2100
Comilla(s) | 129 | 600 | 122 | 2000 | Lalmonirhat | 120 | 600 | 95 | 2000
Comilla(n) | 136 | 700 | 134 | 1100 | Saidpur | 126 | 500 | 100 | 2100
Chandpur | 127 | 1400 | 123 | 2200 | Purbasadipur | 132 | 600 | 116 | 2000
Feni | 120 | 1400 | 115 | 1900 | Thakurgaon | 125 | 600 | 104 | 2100
Chowmuhani | 124 | 700 | 114 | 2000 | Palashbari | 125 | 600 | 106 | 2100
Ashuganj | 140 | 700 | 135 | 100 | Barapukuria | 134 | 600 | 121 | 2100
Daudkandi | 137 | 2100 | 129 | 1500 | Panchagar | 123 | 600 | 99 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-07-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 380 | 6602 | 2667 | 9269 |  |  |  | QF-LDC-12
0:30 | 490 | 6757 | 2501 | 9258 | Date: | 2018-07-02
1:00 | 600 | 6912 | 2335 | 9247
1:30 | 600 | 6809.5 | 2294 | 9103.5
2:00 | 600 | 6707 | 2253 | 8960
2:30 | 580 | 6546.5 | 2218 | 8764.5 | [5 empty] | Gen. at Eve. Peak | 10639 | 10639 MW (21:00 )
3:00 | 560 | 6386 | 2183 | 8569 | [6 empty] | 21:00
3:30 | 560 | 6356 | 2128 | 8484 | [5 empty] | Gen. at Day Peak | 8587.3 | 8587.3 MW (12:00 )
4:00 | 560 | 6326 | 2073 | 8399 | [6 empty] | 12:00
4:30 | 560 | 6256 | 2012.5 | 8268.5 | [5 empty] | Highest Generation | 10639
5:00 | 560 | 6186 | 1952 | 8138 | [6 empty] | 21:00
5:30 | 540 | 5956 | 1866 | 7822
6:00 | 520 | 5726 | 1780 | 7506
6:30 | 520 | 5639.52 | 1786 | 7425.52
7:00 | 520 | 5553.04 | 1792 | 7345.04
7:30 | 505 | 5656.57 | 1796.5 | 7453.07
8:00 | 490 | 5760.1 | 1801 | 7561.1
8:30 | 435 | 5962 | 1824.5 | 7786.5
9:00 | 380 | 6163.9 | 1848 | 8011.9
9:30 | 355 | 6295.35 | 1896.5 | 8191.85
10:00 | 330 | 6426.8 | 1945 | 8371.8
10:30 | 335 | 6448.95 | 1948 | 8396.95
11:00 | 340 | 6471.1 | 1951 | 8422.1
11:30 | 345 | 6525.2 | 1979.5 | 8504.7
12:00 | 350 | 6579.3 | 2008 | 8587.3
12:30 | 395 | 6665 | 2013.5 | 8678.5
13:00 | 440 | 6750.7 | 2019 | 8769.7
13:30 | 450 | 6736.6 | 2007.5 | 8744.1
14:00 | 460 | 6722.5 | 1996 | 8718.5
14:30 | 480 | 6770.55 | 2007.5 | 8778.05
15:00 | 500 | 6818.6 | 2019 | 8837.6
15:30 | 450 | 6818.8 | 2026 | 8844.8
16:00 | 400 | 6819 | 2033 | 8852
16:30 | 300 | 6658.3 | 2007.5 | 8665.8
17:00 | 200 | 6497.6 | 1982 | 8479.6
17:30 | 175 | 6358.3 | 1959.5 | 8317.8
18:00 | 150 | 6219 | 1937 | 8156
18:30 | 175 | 6564 | 2146 | 8710
19:00 | 200 | 6909 | 2355 | 9264
19:30 | 400 | 7511 | 2631 | 10142
20:00 | 540 | 7760 | 2766 | 10526 |  |  |  | Executive Engineer
20:30 | 580 | 7804.5 | 2778 | 10582.5 |  |  |  | Network Operation Division
21:00 | 620 | 7849 | 2790 | 10639
21:30 | 590 | 7603 | 2758 | 10361
22:00 | 560 | 7357 | 2726 | 10083 |  |  |  |  | Page 6 of 7
22:30 | 510 | 7160.5 | 2704.5 | 9865
23:00 | 460 | 6964 | 2683 | 9647
23:30 | 420 | 6783 | 2675 | 9458
24:00 | 380 | 6602 | 2667 | 9269
10639 MW (21:00 )
8587.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-07-02 |  | Energy | 212182589
[10 empty] | 2018-07-02 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 2833 | 458 | 1710 | 2253 | 145 | 210 | 1504 | 0 | 156
0:30 | 2997.5 | 461 | 1739.5 | 2178 | 142 | 189 | 1396 | 0 | 155 | Date: | 2018-07-02
1:00 | 3162 | 464 | 1769 | 2103 | 139 | 168 | 1288 | 0 | 154
1:30 | 3162 | 464 | 1790.5 | 1978.5 | 140 | 168 | 1249.5 | 0 | 151 | [7 empty] | Total Energy | 212.1826 | Total Energy Gen 212.183 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 212.183 MKWHr
2:00 | 3162 | 464 | 1812 | 1854 | 141 | 168 | 1211 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 3083.5 | 465 | 1836.5 | 1746 | 140.5 | 168 | 1177 | 0 | 148 | [7 empty] | Energy Requirement | 212.1826
3:00 | 3005 | 466 | 1861 | 1638 | 140 | 168 | 1143 | 0 | 148
3:30 | 3016.5 | 465.5 | 1906 | 1568.5 | 138.5 | 167 | 1077 | 0 | 145 | [6 empty] | Shortage
4:00 | 3028 | 465 | 1951 | 1499 | 137 | 166 | 1011 | 0 | 142
4:30 | 2984 | 465.5 | 1977.5 | 1467 | 139.5 | 164.5 | 933.5 | 0 | 137
5:00 | 2940 | 466 | 2004 | 1435 | 142 | 163 | 856 | 0 | 132
5:30 | 2896.5 | 466 | 1929.5 | 1274 | 141.5 | 163 | 824.5 | 0 | 127
6:00 | 2853 | 466 | 1855 | 1113 | 141 | 163 | 793 | 0 | 122
6:30 | 2865 | 466 | 1854 | 1033 | 139.5 | 162.5 | 788.5 | 0 | 117 |  |  |  |  | Coal
7:00 | 2877 | 466 | 1853 | 953 | 138 | 162 | 784 | 0 | 112
7:30 | 2942 | 466 | 1880 | 960 | 138 | 162.5 | 792.5 | 0 | 112 |  |  |  | Oil |  |  |  | ,
8:00 | 3007 | 466 | 1907 | 967 | 138 | 163 | 801 | 0 | 112
8:30 | 3057.5 | 466 | 1922 | 1089.5 | 143 | 163.5 | 829.5 | 0 | 115
9:00 | 3108 | 466 | 1937 | 1212 | 148 | 164 | 858 | 0 | 118
9:30 | 3057 | 465.5 | 1948.5 | 1440 | 151 | 132 | 877.5 | 0 | 119
10:00 | 3006 | 465 | 1960 | 1668 | 154 | 100 | 897 | 0 | 120
10:30 | 3027.5 | 465.5 | 1920.5 | 1755.5 | 152 | 70 | 880.5 | 0 | 124
11:00 | 3049 | 466 | 1881 | 1843 | 150 | 40 | 864 | 0 | 128
11:30 | 3067 | 466 | 1882 | 1888 | 148.5 | 40 | 886 | 0 | 126
12:00 | 3085 | 466 | 1883 | 1933 | 147 | 40 | 908 | 0 | 124
12:30 | 3070 | 466 | 1855 | 2011.5 | 146.5 | 80 | 920.5 | 0 | 128
13:00 | 3055 | 466 | 1827 | 2090 | 146 | 120 | 933 | 0 | 132
13:30 | 3055 | 466 | 1827 | 2090 | 146 | 120 | 933 | 0 | 132
14:00 | 3055 | 466 | 1827 | 2090 | 146 | 120 | 933 | 0 | 132
14:30 | 3045.5 | 466 | 1792 | 2164.5 | 148 | 119 | 939.5 | 0 | 128
15:00 | 3036 | 466 | 1757 | 2239 | 150 | 118 | 946 | 0 | 124
15:30 | 2976.5 | 465.5 | 1786 | 2265.5 | 148 | 142 | 936 | 0 | 124
16:00 | 2917 | 465 | 1815 | 2292 | 146 | 166 | 926 | 0 | 124
16:30 | 2916.5 | 465.5 | 1741 | 2183.5 | 147 | 166 | 922.5 | 0 | 123
17:00 | 2916 | 466 | 1667 | 2075 | 148 | 166 | 919 | 0 | 122
17:30 | 2897.5 | 462.5 | 1602.5 | 2000 | 149 | 155.5 | 925.5 | 0 | 125
18:00 | 2879 | 459 | 1538 | 1925 | 150 | 145 | 932 | 0 | 128
18:30 | 2951 | 458.5 | 1661 | 2001 | 148.5 | 176.5 | 1174.5 | 0 | 139
19:00 | 3023 | 458 | 1784 | 2077 | 147 | 208 | 1417 | 0 | 150
19:30 | 3041 | 458 | 1859 | 2626 | 160 | 208 | 1632 | 0 | 158
20:00 | 2981 | 458 | 1857 | 3053 | 158 | 208 | 1649 | 0 | 162
20:30 | 2965.5 | 458.5 | 1848.5 | 3124.5 | 176.5 | 208 | 1641 | 0 | 160
21:00 | 2950 | 459 | 1840 | 3196 | 195 | 208 | 1633 | 0 | 158
21:30 | 2944 | 458.5 | 1824.5 | 2971.5 | 197.5 | 208 | 1599 | 0 | 158
22:00 | 2938 | 458 | 1809 | 2747 | 200 | 208 | 1565 | 0 | 158
22:30 | 2909.5 | 458 | 1759.5 | 2630 | 178.5 | 209 | 1561.5 | 0 | 159
23:00 | 2881 | 458 | 1710 | 2513 | 157 | 210 | 1558 | 0 | 160
23:30 | 2857 | 458 | 1710 | 2383 | 151 | 210 | 1531 | 0 | 158 | Max Temp. in Dhaka |  | 33.6° C
24:00 | 2833 | 458 | 1710 | 2253 | 145 | 210 | 1504 | 0 | 156
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 212.183 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 212.183 MKWHr
Note on W13: Author:

## Generation
,. | 2018-07-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 88 | 88 | 88 | 86 | 83 | 83 | 82 | 83 | 84 | 60 | 0 | 0 | 40 | 40 | 38 | 86 | 86 | 85 |  | 128 | 128 | 128 | 128 | 128 | 130 | 130 | 1879844
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 40 | 40 | 40 | 80 | 80 | 80 | 80 | 80 | 60 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1786600
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 8 | 0 |  |  | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 316620
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 200 | 200 | 197 | 200 | 209 | 196 | 194 | 208 | 202 | 202 | 202 |  | 209 | 215 | 202 | 200 | 201 | 201 | 201 | 4737419
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 70 | 70 | 70 | 70 | 70 | 50 | 70 | 70 | 70 | 100 | 70 | 70 | 70 | 50 | 80 | 80 | 80 | 50 |  | 120 | 135 | 135 | 135 | 100 | 100 | 50 | 1843118
| Dohazari Peaking | 64 | 64 | 64 | 32 | 0 | [12 empty] | 17 |  | 47 | 70 | 76 | 76 | 76 | 75 | 76 | 653149
12 | Hathazari peaking | 57 | 57 | 57 | 57 | 0 | [14 empty] | 56 | 56 | 56 | 48 | 48 | 48 | 48 | 521928
| Daudkandi bangla trak | [17 empty] | 0 |  | 20 | 60 | 170 | 200 | 50 | 0 |  | 466560
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 27 | 41 | 41 | 42 | 42 | 42 | 42 | 210472
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 116 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 120 | 140 | 120 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 103 | 2829001
18 | Summit Gazipur | 301 | 301 | 301 | 301 | 301 | 301 | 204 | 205 | 227 | 298 | 301 | 301 | 303 | 303 | 303 | 303 | 303 | 303 |  | 303 | 303 | 303 | 303 | 303 | 301 | 301 | 7060579
19 | Ashuganj 195MW Modular | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1890181
20 | Ghorasal ST: Unit-1,2 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 55 | 55 | 57 | 60 | 62 | 62 | 62 | 62 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1386000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2730735
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 300 | 280 | 270 | 270 | 270 | 270 | 270 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 200 | 200 | 6578327
26
28 | Ashuganj ST: Unit- 3 | [13 empty] | 30 | 70 | 55 | 100 | 100 |  | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 929284
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 110 | 0 | [9 empty] | 1583200
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2444392
32 | Ashuganj Engines TSK | 36 | 33 | 33 | 33 | 33 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 826776
33 | Ashuganj CCPP 225 MW | 182 | 182 | 182 | 188 | 194 | 182 | 183 | 197 | 199 | 192 | 201 | 207 | 195 | 191 | 147 | 139 | 183 | 184 |  | 184 | 165 | 174 | 199 | 183 | 188 | 182 | 4515000
34 | Ashuganj CCPP(South) | 250 | 250 | 250 | 257 | 257 | 250 | 250 | 275 | 300 | 315 | 327 | 335 | 323 | 312 | 327 | 283 | 283 | 253 |  | 320 | 316 | 290 | 279 | 279 | 287 | 279 | 6920250
| Ashuganj CCPP(North) | 250 | 250 | 250 | 250 | 258 | 250 | 250 | 305 | 325 | 315 | 325 | 335 | 320 | 310 | 327 | 300 | 300 | 300 |  | 330 | 335 | 310 | 300 | 300 | 305 | 300 | 7429200
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2377000
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 395 | 410 | 420 | 420 | 420 | 380 | 380 | 380 | 410 | 345 | 353 | 360 | 370 | 345 | 360 | 365 | 345 | 343 |  | 358 | 393 | 375 | 345 | 344 | 300 | 300 | 9000960
40 | Meghnaghat CCPP 450MW | 390 | 400 | 430 | 430 | 450 | 380 | 380 | 430 | 430 | 430 | 410 | 410 | 390 | 390 | 390 | 390 | 390 | 390 |  | 390 | 410 | 410 | 410 | 410 | 340 | 300 | 9176001
41 | Haripur Power CCPP 360MW | 272 | 288 | 325 | 326 | 327 | 326 | 326 | 310 | 280 | 281 | 281 | 271 | 262 | 261 | 260 | 271 | 272 | 276 |  | 286 | 286 | 286 | 287 | 292 | 292 | 337 | 6932000
42 | Mymensingh RPCL 210MW | 47 | 47 | 47 | 47 | 47 | 48 | 47 | 47 | 46 | 46 | 46 | 45 | 45 | 48 | 46 | 45 | 46 | 46 |  | 46 | 46 | 47 | 48 | 49 | 48 | 47 | 1138360
43 | Haripur NEPC 110MW | 13 | 13 | 13 | 0 | [10 empty] | 13 | 40 | 55 | 55 |  | 55 | 84 | 84 | 84 | 70 | 26 | 13 | 568400
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 59 | 59 | 59 | 54 | 54 | 50 | 30 |  | 60 | 55 | 55 | 55 | 58 | 58 | 58 | 1295000
45 | Fenchugonj CCPP-2 | 75 | 75 | 75 | 75 | 75 | 74 | 74 | 74 | 74 | 74 | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 1780280
46 | Shajibazar 330 MW | 190 | 190 | 0 | [23 empty] | 487203
47 | Shahjibazar GT: Unit- 8, 9 | 51 | 51 | 60 | 61 | 61 | 60 | 50 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 60 | 60 | 52 | 60 |  | 60 | 60 | 60 | 51 | 51 | 62 | 48 | 1364000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 50 | 30 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1989120
49 | Shahjibazar (EPL) 50MW | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 46 | 45 | 45 | 45 | 46 | 45 | 45 | 44 | 20 | 20 |  | 45 | 45 | 46 | 47 | 47 | 47 | 47 | 1040040
50 | Sylhet GT 150 MW | 78 | 78 | 78 | 78 | 0 | [21 empty] | 355570
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 46 | 46 | 0 | 45 | 46 | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 47 | 46 | 46 | 46 | 46 | 47 |  | 47 | 47 | 46 | 47 | 47 | 47 | 46 | 1062640
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 251280
54 | Hobiganj 11MW | 11 | 11 | 11 | 10 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 256032
55 | Fenchugonj (Barakatullah) 51MW | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 50 | 13 |  | 32 | 53 | 53 | 53 | 53 | 53 | 53 | 1110600
56 | Shahjahanulla 25 MW | 23 | 16 | 16 | 23 | 6 | 6 | 6 | 6 | 15 | 15 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 451368
57 | Summit Bibiana- 2 | 260 | 280 | 290 | 310 | 310 | 270 | 290 | 305 | 320 | 320 | 315 | 320 | 325 | 300 | 320 | 320 | 290 | 300 |  | 300 | 330 | 320 | 290 | 280 | 290 | 280 | 7521000
58 | Southern 55MW | 55 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1143000
59 | Sikalbaha (Energis) | 40 | 40 | 40 | 40 | 24 | 24 | 24 | 24 | 30 | 24 | 24 | 32 | 32 | 34 | 40 | 40 | 40 | 40 |  | 40 | 42 | 42 | 49 | 51 | 51 | 51 | 892800
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 19 | 16 | 17 | 17 | 17 | 17 | 16 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 436120
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 430200
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 459828
63 | Tripura | 154 | 148 | 148 | 142 | 132 | 122 | 112 | 112 | 118 | 120 | 128 | 124 | 132 | 130 | 124 | 124 | 122 | 128 |  | 150 | 158 | 162 | 158 | 158 | 160 | 156 | 3301440
64 | Malancha, Ctg. EPZ (United) | 29 | 32 | 32 | 34 | 35 | 35 | 17 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 2 | 8 | 16 | 21 | 21 | 22 | 311040
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 0 | 13 | 16 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 417456
66 | Feni, Mohipal (Doreen) | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 8 | 8 | 8 | 5 | 11 | 0 | 0 |  | 0 |  | 0 | 11 | 0 | 11 | 11 | 11 | 11 | 154800
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816700
68 | Summit Comilla 25MW | 18 | 18 | 18 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 535810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 0 | 0 | 0 |  | 24 | 30 | 30 | 30 | 22 | 31 | 31 | 31 |  | 22 | 22 | 32 | 32 | 32 | 32 | 32 | 579960
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 729600
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805100
73 | Ghorashal (Regent) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 45 | 22 | 22 | 12 | 12 | 14 | 0 | 0 | 0 | [8 empty] | 285409
76 | Siddhirganj (Desh) | [14 empty] | 2 | 17 | 17 | 17 |  | 17 | 60 | 54 | 70 | 100 | 0 |  | 374400
77 | Siddhirganj (Dutch Bangla) | 93 | 60 | 30 | 30 | 30 | 7 | 7 | 7 | 7 | 32 | 85 | 90 | 90 | 90 | 90 | 90 | 50 | 50 |  | 60 | 90 | 91 | 93 | 93 | 93 | 60 | 1571414
78 | Gazipur (RPCL) | 50 | 50 | 42 | 33 | 33 | 33 | 33 | 33 | 43 | 50 | 50 | 46 | 50 | 50 | 50 | 46 | 50 | 50 |  | 50 | 50 | 50 | 50 | 51 | 51 | 51 | 1109484
79 | Kodda 150MW | 115 | 82 | 65 | 65 | 65 | 40 | 32 | 36 | 70 | 82 | 82 | 82 | 98 | 98 | 98 | 98 | 98 | 98 |  | 130 | 149 | 149 | 149 | 149 | 149 | 149 | 2307360
80 | Jamalpur 95MW | 95 | 95 | 95 | 48 | 48 | 8 | 8 | 8 | 8 | 8 | 20 | 32 | 92 | 95 | 95 | 72 | 56 | 56 |  | 50 | 95 | 95 | 95 | 95 | 48 | 24 | 1378820
81 | Lakdhanvi 52 MW | [15 empty] | 11 | 25 | 25 |  | 25 | 25 | 33 | 41 | 25 | 25 | 25 | 253426
82 | Madanganj 102MW | 98 | 94 | 65 | 65 | 65 | 14 | 14 | 14 | 15 | 44 | 70 | 80 | 82 | 98 | 98 | 98 | 70 | 70 |  | 70 | 101 | 100 | 100 | 97 | 97 | 97 | 1803864
83 | Pagla (DPA ) | 10 | 0 |  | 0 | 10 | 10 | 10 | 10 | 10 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 10 | 10 |  | 10 | 50 | 50 | 51 | 10 | 10 | 10 | 383790
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 52 | 51 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1803864
85 | Keraniganj (Powerpac) 100MW | 80 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 75 | 88 | 88 | 100 | 100 | 100 | 100 | 60 | 30 |  | 95 | 100 | 100 | 100 | 100 | 100 | 20 | 1541013
86 | Meghnaghat CCPP(Summit) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 145 | 100 | 130 | 200 | 200 | 240 | 240 | 240 | 200 |  | 260 | 305 | 305 | 305 | 240 | 240 | 200 | 4272145
87 | Meghnaghat (IEL) | 100 | 55 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 35 | 91 | 92 | 100 | 100 | 100 | 100 | 75 | 55 |  | 62 | 100 | 100 | 100 | 100 | 100 | 60 | 1525440
88 | Ghorashal 78MW (MAX) | 40 | 40 | 60 | 79 | 79 | 40 | 40 | 60 | 77 | 76 | 40 | 40 | 20 | 20 | 20 | 20 | 0 | 0 | [8 empty] | 959616
90 | Ashuganj (United) 53MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 195000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 68 | 68 | 68 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1809840
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 47 |  | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 1182000
93 | Ashuganj (Midland) 51MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 51 | 51 | 51 | 51 | 45 | 45 | 45 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 954592
94 | Gagnagar (Orion) | 60 | 30 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 40 | 70 | 102 | 98 | 102 | 102 | 51 | 24 |  | 40 | 80 | 102 | 102 | 64 | 64 | 32 | 1294027
95 | Patenga 50MW | 25 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 26 | 26 | 26 | 0 | 3 | 25 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 592800
96 | Chittagong ECPV 108 MW | 99 | 99 | 99 | 45 | 46 | 45 | 46 | 40 | 85 | 98 | 99 | 99 | 92 | 92 | 98 | 98 | 98 | 98 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 2054400
97 | Katpotti 51 MW | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 37 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 33 |  | 32 | 32 | 32 | 32 | 33 | 32 | 32 | 855312
98 | Bosila 108MW | 90 | 90 | 90 | 90 | 90 | 90 | 70 | 70 | 90 | 90 | 90 | 88 | 79 | 80 | 80 | 80 | 80 | 85 |  | 88 | 88 | 88 | 88 | 88 | 90 | 90 | 2037120
99 | Madanganj-55 MW | 40 | 30 | 30 | 30 | 30 | 15 | 15 | 15 | 23 | 42 | 42 | 42 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1043022
100 | Northern 55 MW | 55 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 35 | 55 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1082077
101 | Kushiara 163 MW CCPP GT | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 163 | 163 | 120 |  | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 3246163
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.04 | 0.1 | 0.9 | 1.8 | 1.1 | 1.3 | 0.7 | 1.5 | 1.6 | 1 | 0.6 | 0 |  | 0 | [6 empty] | 11500
103 | Banco Energy 54MW | 54 | 54 | 36 | 36 | 36 | 36 | 18 | 18 | 54 | 54 | 54 | 54 | 18 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1121760
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [20 empty] | 18 | 51 | 52 | 0 |  |  | 100734
106 | United Mymensingh PPL | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 103 | 103 | 142 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 140 |  | 0 | 4 | 120 | 196 | 192 | 194 | 194 | 3064800
112 | Aggreko Aurahati 100MW | [20 empty] | 30 | 63 | 63 | 0 |  |  | 126410
113
114
115
116
117
118 | Eastern Zone Total | 6912 | 6707 | 6386 | 6326 | 6186 | 5726 | 5553.04 | 5760.1 | 6163.9 | 6426.8 | 6471.1 | 6579.3 | 6750.7 | 6722.5 | 6818.6 | 6819 | 6497.6 | 6219 | 0 | 6909 | 7511 | 7760 | 7849 | 7357 | 6964 | 6602 | 159650945
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 36 | 39 | 39 | 39 | 45 | 45 | 45 |  | 87 | 84 | 79 | 81 | 45 | 51 | 51 | 965280
124 | Khulna (KPCL-2) | 83 | 83 | 83 | 83 | 83 | 26 | 16 | 16 | 16 | 44 | 66 | 66 | 66 | 66 | 66 | 89 | 99 | 99 |  | 99 | 99 | 99 | 99 | 96 | 96 | 96 | 1704000
125
126 | Khulna (Aggreko) 55MW | [19 empty] | 12 | 12 | 33 | 33 | 33 | 33 | 33 | 164650
127 | Faridpur Peaking | [19 empty] | 50 | 49 | 49 | 47 | 47 | 42 | 42 | 278880
128 | Khulna CCPP 225MW | 185 | 165 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 130 | 170 | 170 | 170 | 170 | 170 | 170 | 3428160
129
130
131
132
133
| Summit Barisal 110 MW | 110 | 80 | 48 | 48 | 48 | 24 | 16 | 16 | 26 | 48 | 48 | 48 | 48 | 48 | 50 | 48 | 48 | 48 |  | 80 | 110 | 110 | 110 | 110 | 110 | 112 | 1536000
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 97 | 97 | 97 | 98 | 97 | 97 | 95 | 97 | 95 | 93 | 96 | 95 | 96 | 97 | 95 | 97 | 98 | 64 |  | 98 | 96 | 97 | 97 | 98 | 98 | 95 | 2269189
137 | Bhola CCPP 194MW | 189 | 189 | 189 | 188 | 187 | 187 | 188 | 189 | 191 | 191 | 192 | 189 | 188 | 183 | 191 | 193 | 188 | 191 |  | 190 | 190 | 191 | 182 | 184 | 191 | 186 | 4593017
| Bhola (Venture) 33MW | 32 | 26 | 24 | 26 | 27 | 27 | 25 | 23 | 23 | 22 | 22 | 24 | 17 | 23 | 19 | 20 | 24 | 24 |  | 32 | 36 | 37 | 36 | 37 | 28 | 36 | 614240
140 | Bangla Trak Noapara | [19 empty] | 20 | 53 | 95 | 95 | 97 | 97 | 97 | 472320
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 8 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 24 |  | 32 | 40 | 40 | 40 | 40 | 40 | 40 | 765000
142 | Gopalganj Peaking | 62 | 54 | 30 | 10 | 10 | 10 | 0 | [7 empty] | 4 | 7 | 15 | 25 |  | 50 | 50 | 60 | 66 | 63 | 60 | 60 | 560896
143 | Bheramara GT-1,2,3 | [20 empty] | 16 | 32 | 49 | 33 | 33 | 33 | 167600
144
145 | Bheramara HVDC | 464 | 464 | 466 | 465 | 466 | 466 | 466 | 466 | 466 | 465 | 466 | 466 | 466 | 466 | 466 | 465 | 466 | 459 |  | 458 | 458 | 458 | 459 | 458 | 458 | 458 | 11124364
146 | Bheramara 360 MW | 180 | 176 | 190 | 190 | 189 | 190 | 245 | 245 | 246 | 240 | 221 | 219 | 213 | 214 | 213 | 213 | 213 | 213 |  | 213 | 214 | 213 | 214 | 213 | 215 | 214 | 5202144
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2
151 | Barapukuria Unit-3 | 139 | 141 | 140 | 137 | 142 | 141 | 138 | 138 | 148 | 154 | 150 | 147 | 146 | 148 | 150 | 146 | 148 | 150 |  | 147 | 160 | 158 | 195 | 200 | 157 | 145 | 3686100
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | [17 empty] | 0 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 248048
Sirajgonj Unit-1 225MW (Gas)
157 | Sirajgonj Unit-1 225MW (Oil) | 168 | 170 | 174 | 182 | 178 | 169 | 171 | 175 | 187 | 187 | 185 | 194 | 194 | 178 | 184 | 185 | 172 | 172 |  | 178 | 190 | 187 | 175 | 167 | 168 | 169 | 4481300
158 | Sirajgonj Unit-2 225MW (Gas) | [25 empty] | 0 | 0
| Sirajgonj Unit-2 225MW (Oil) | 168 | 168 | 171 | 180 | 178 | 169 | 171 | 175 | 186 | 186 | 182 | 183 | 187 | 175 | 184 | 184 | 172 | 171 |  | 178 | 189 | 186 | 173 | 167 | 168 | 169 | 4408145
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | [16 empty] | 10 | 27 |  | 37 | 37 | 38 | 38 | 37 | 37 | 36 | 225686
161 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 11 | 5 |  | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 408000
162 | Bogra (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 267372
163 | Ullapara (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 209260
164 | Amnura 50MW | 40 | 40 | 40 | 40 | 40 | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 25 | 12 |  | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 927440
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 16 | 16 | 16 | 16 | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 8 |  | 8 | 25 | 43 | 43 | 43 | 43 | 43 | 819056
166 | Katakhali Peaking | 45 | 45 | 45 | 45 | 0 | [12 empty] | 0 |  | 39 | 45 | 47 | 45 | 45 | 45 | 45 | 441100
167 | Santahar Peaking | 42 | 41 | 42 | 0 | [13 empty] | 0 |  | 22 | 42 | 42 | 42 | 41 | 42 | 36 | 334745
168 | Rajlanka 52 MW | 43 | 43 | 43 | 35 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 43 | 43 | 43 | 43 | 43 | 499200
169 | Chapainawabganj-100 MW | 102 | 85 | 85 | 40 | 40 | 40 | 25 | 25 | 25 | 25 | 25 | 50 | 68 | 68 | 68 | 50 | 50 | 50 |  | 66 | 100 | 101 | 101 | 102 | 102 | 102 | 1478452
170
171
172 | Rangpur GT | 15 | 15 | 15 | 15 | 0 | [12 empty] | 0 |  | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 156000
173 | Saidpur GT | [17 empty] | 0 |  | 18 | 18 | 18 | 17 | 17 | 18 | 18 | 96000
175
176
177
178 | Western Zone Total | 2335 | 2253 | 2183 | 2073 | 1952 | 1780 | 1792 | 1801 | 1848 | 1945 | 1951 | 2008 | 2019 | 1996 | 2019 | 2033 | 1982 | 1937 | 0 | 2355 | 2631 | 2766 | 2790 | 2726 | 2683 | 2667 | 52531644
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953