## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-02-14 | Tuesday
|  | Date (day): | 2023-02-14 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9684.6 | MW |  |  | (b) At Evening Peak Hour : |  | 11157 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-02-13 | 2023-02-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 160 | 130 | 130 | 130
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 70 | 110 | 110
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 81 | 52 | 20 | 20 | 88 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 246 | 252 | 230 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 30 | 50 | 17 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 150 | 150 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 34 | 34 | 34 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 25 | 30 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 27 | 50 | 50 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 |  |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 50 | 16 | 50 | 52 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 64 | 64 | 82 | 67 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 17 | 55 |  |  | fuel shortage.
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 47 | 49 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 21 | 21 | 22 | 22 |  | 11 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 42 | 25 | 42 | 10 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 65 | 99 | 32 | 95 | 205 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 72 | 35 | 72 | 77 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 90 | 88 | 17 |  | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 54 | 17 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 127 | 17 | 126
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1431 | 1886 | 1464 | 1939 | 2466 | 954
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17 | 8 |  | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 19 | 19 | 31 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 60 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 151 | 151 | 150 | 151 |  | 74 | ST Under maint
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 85 | 17 | 85 | 20 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 40 | 65 | 40 | 64 | 34 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 81 | 68 | 85 |  | 17 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 33 | 67 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 116 | 285 | 100 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 92 | 55 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 28 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 688 | 1051 | 708 | 1050 | 1055 | 250
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 188 | 195 | 220 | 200 | 21 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 325 | 310 | 310 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 270 | 280 | 320 | 320 | 80 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 |  |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 45 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 33 | 132 | 75 | 150 | 0 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 31 | 38 | 10 | 30 |  | 22 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 34 | 34 | 34 | 166 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21 |  |  | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 118 | 124 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 13 | 16 | 21 | 21 |  | 12 | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 73 | 17 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1147 | 1482 | 1401 | 1571 | 898 | 609
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 31 | 70 | 55 | 70 | 132 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 11 | 11 |  |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 74 | 65 | 75 | 125 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 115 | 78 | 50 | 76 | 39 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 284 | 241 | 238.6 | 238 | 132 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 112 | 112 | 112 |  | 51 | ST Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 51 | 31 | 51 |  |  | Engine problem
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 50 | 49 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 62 | 61 | 61
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 40 | 86 | 84 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 214 | 218 | 220 | 220
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 400 | 406 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 6 | 8 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 380 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1722 | 1793 | 1769 | 1811 | 0 | 575
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 679 | 469 | 784 | 784
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 33 | 0 | 32 | 83 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 45 |  | 9 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 30 | 0 | 75 |  | 34 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 16 | 0 | 24 | 16 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 55 | 17 | 55 | 50 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 15 | 50 | 67 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 95 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 789 | 691 | 968 | 1115 | 905 | 43
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 16 | 21 | 16 | 21 |  | 19 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 188 | 190 | 190 | 190
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1022 | 1202 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 108 | 107 | 110 | 110 |  | 110 | GT-1 under maint.
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 150 | 35 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 238 | 208 | 300 | 300
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1623 | 1894 | 1911 | 2031 | 94 | 129
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 33 | 0 | 37 |  | 34 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 50 | 42 | 42 |  |  | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 43 | 41 | 40 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 186 | 170 | 179 | 182 | 28 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 284 | 262 | 300 | 300 | 114 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 12 | 23 | 0 | 30 |  | 20 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 18 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0 | 52 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 98 | 42 | 96
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 70 | 50 | 70 | 43 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 75 | 35 | 75 | 38 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 741 | 888 | 723 | 939 | 1086 | 82
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 251 | 250 | 250 |  | 24
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 42 | 93 | 49 | 100 | 13 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 113 | 35 | 113
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 162 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 528 | 457 | 502 | 463 | 138 | 109
| Total |  |  |  |  | 23482 | 22700 | 8953 | 10383 | 9684.6 | 11157 | 6774 | 2751
A. |  | 2023-02-13 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 10383 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 7371 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10432 | MW
3 | Day peak Generation : |  |  | 8953 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10019.29 | MW
4 | Evening peak Generation : |  |  | 10383 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 45 | MW
5 | Total Energy Generation : |  | 212.4908 | MKWHr | By Solar | 2.7086 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 110.0237 | MKWHr |  | By Oil: | 40.5669 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 38.8752 | MKWHr |  | By Hydro: | 1.1085 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6774 | MW | Dhaka | 3585.69 | 3585.69 |  | 0 |  | 18:00 |  | 567
|  |  | For Plants S/D or M/C prob = |  |  | 2751 | MW | Chittagong | 1016.2 | 1016.2 |  | 0 |  | 19:00 |  | 432.2187
|  |  | Total = |  |  | 9525 | MW | Khulna | 1144.8 | 1144.8 |  | 0 |  | 19:30 |  | 196.2955
7 | Total Gas Supplied : |  |  | 864.63 | MMCFD |  |  | Rajshahi | 1100.6 | 1100.6 |  | 0 |  | 20:00 |  | 45.1572
8 | Fuel Cost : | i) Gas : | Taka | 114830334.452 | ii) Oil : | Taka | 539671981.2 | Comilla | 867 | 867 |  | 0 |  | 21:00 |  | 24.8825
|  | iii) Coal : | Taka | 279183874 | Total | Taka | 933686189.652 | Mymensingh | 944 | 909 |  | 35 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 347 | 347 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 216 | MW (E to W) at | 20:00 | hrs | Barisal | 278 | 278 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 216 | MW at | 20:00 | hrs | Rangpur | 736 | 726 |  | 10
10 | Maximum Temperature in Dhaka was |  |  |  | 28.0° C |  |  | Total | 10019.29 | 9974.29 |  | 45
B. |  | 2023-02-14 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 27.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11157 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10050 | MW
4 | Reserve(Generation end) |  |  |  | 457 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 218.9783 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7071 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.4393 | MKWHr. | ii) HVDC Flow at Peak Time |  | 469 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7686 | MKWHr. | iii) Maximum HVDC Flow : |  | 902 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.3 |  | (b) Today: | 82.23 |  | (c) Rule Curve: |  | 95.18
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-02-13 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 200 | 0 | 0 | 81 | 0 | 0 | 152 |  | 0 | 225 | 120 | 17 | 34 | 15 | 60 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 107 | 0 | 0 | 0 |  | 6 | 68 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 211 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 8 | 21 | 8 | 33 | 21 | 104 | 103 | 0 | 16 | 0 | 43 | 43 | 31 | 50 | 112 | 0 | 62 | 86 | 0 | 213 | 19 | 0 | 10 | 290 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 406 | 49 | 52 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 250 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 17 | 17 | 273 | 0 | 0 |  | 902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1122 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 |  | 4816 | 3364 | 8180 | 2912 | 902 | 1651 | 0 | 811 | 1570 | 30 | 0 | 200 | 104 | 0 | 0 | 82.32
2:00 | 0 | 0 | 200 | 0 | 0 | 81 | 0 | 0 | 149 |  | 0 | 225 | 112 | 17 | 34 | 15 | 61 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 85 | 0 | 0 | 0 |  | 6 | 12 | 60 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 212 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 106 | 104 | 0 | 16 | 0 | 43 | 43 | 22 | 50 | 112 | 0 | 62 | 86 | 0 | 213 | 19 | 0 | 10 | 270 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 5 | 405 | 49 | 52 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 235 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 288 | 0 | 0 |  | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 1092 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 0 | 0 |  | 4638 | 3195 | 7833 | 2890 | 751 | 1622 | 0 | 803 | 1543 | 30 | 0 | 88 | 106 | 0 | 0 | 82.31
3:00 | 0 | 0 | 200 | 0 | 0 | 81 | 0 | 0 | 153 |  | 0 | 225 | 112 | 18 | 34 | 15 | 61 | 0 | 0 | 18 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 75 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 216 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 102 | 104 | 0 | 16 | 0 | 43 | 43 | 11 | 40 | 112 | 0 | 62 | 10 | 0 | 213 | 19 | 0 | 10 | 295 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 406 | 49 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 275 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 288 | 0 | 0 |  | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1010 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 |  | 4535 | 3069 | 7604 | 2931 | 751 | 1562 | 0 | 753 | 1459 | 30 | 0 | 16 | 102 | 0 | 0 | 82.31
4:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 0 | 142 |  | 0 | 225 | 112 | 17 | 34 | 15 | 61 | 0 | 0 | 18 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 40 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 102 | 104 | 0 | 16 | 0 | 43 | 43 | 11 | 40 | 112 | 0 | 63 | 10 | 0 | 215 | 19 | 0 | 10 | 290 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 405 | 49 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 290 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 18 | 17 | 280 | 0 | 0 |  | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 0 | 0 |  | 4387 | 3027 | 7414 | 2822 | 751 | 1517 | 0 | 718 | 1458 | 30 | 0 | 16 | 102 | 0 | 0 | 82.31
5:00 | 0 | 0 | 150 | 0 | 0 | 42 | 0 | 0 | 145 |  | 0 | 225 | 111 | 18 | 34 | 15 | 61 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 20 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 224 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 98 | 104 | 0 | 16 | 0 | 43 | 43 | 11 | 40 | 112 | 0 | 63 | 10 | 0 | 213 | 19 | 0 | 10 | 280 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 405 | 49 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 320 | 17 | 0 | 17 | 107 | 0 | 0 | 0 | 17 | 17 | 281 | 0 | 0 |  | 751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1010 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 0 | 0 |  | 4387 | 2984 | 7371 | 2810 | 751 | 1490 | 0 | 717 | 1459 | 30 | 0 | 16 | 98 | 0 | 0 | 82.31
6:00 | 0 | 0 | 200 | 0 | 0 | 78 | 0 | 0 | 145 |  | 0 | 225 | 112 | 17 | 22 | 15 | 62 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 20 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 305 | 0 | 222 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 21 | 8 | 33 | 21 | 104 | 110 | 0 | 17 | 0 | 43 | 43 | 11 | 50 | 112 | 0 | 63 | 40 | 0 | 213 | 19 | 0 | 10 | 290 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 5 | 405 | 49 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 330 | 17 | 0 | 17 | 95 | 0 | 0 | 0 | 18 | 17 | 330 | 0 | 0 |  | 617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 250 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 8 | 0 | 30 | 0 | 0 | 0 | 0 | 35 | 1050 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 0 | 0 |  | 4597 | 3057 | 7654 | 2940 | 617 | 1605 | 0 | 790 | 1552 | 30 | 0 | 16 | 104 | 0 | 0 | 82.3
7:00 | 0 | 0 | 200 | 0 | 0 | 81 | 0 | 0 | 143 |  | 0 | 225 | 112 | 17 | 34 | 15 | 61 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 21 | 0 | 0 | 0 |  | 6 | 4 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 215 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 21 | 8 | 18 | 21 | 110 | 48 | 0 | 17 | 0 | 43 | 43 | 22 | 50 | 112 | 0 | 62 | 86 | 0 | 213 | 19 | 0 | 10 | 310 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 405 | 49 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 2 | 17 | 107 | 0 | 0 | 1 | 18 | 17 | 300 | 0 | 0 |  | 588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 35 | 1092 | 109 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 1 | 269 | 0 | 6 |  | 4634 | 3271 | 7905 | 2912 | 588 | 1709 | 0 | 912 | 1611 | 30 | 0 | 20 | 110 | 13 | 548.3371 | 82.3
8:00 | 0 | 0 | 200 | 0 | 0 | 81 | 0 | 0 | 198 |  | 0 | 225 | 142 | 17 | 34 | 15 | 0 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 25 | 33 | 24 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 85 | 0 | 0 | 0 |  | 6 | 40 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 206 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 18 | 0 | 21 | 8 | 14 | 21 | 116 | 47 | 0 | 16 | 1 | 43 | 43 | 22 | 50 | 112 | 0 | 62 | 60 | 0 | 213 | 19 | 0 | 10 | 290 | 8 | 8 | 0 | 30 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 6 | 405 | 49 | 35 | 17 | 0 | 16 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 16 | 17 | 107 | 0 | 12 | 11 | 18 | 17 | 300 | 0 | 0 |  | 544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 7 | 0 | 0 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 338 | 0 | 0 | 50 | 15 | 40 | 0 | 1 | 35 | 1092 | 109 | 0 | 11 | 1 | 25 | 0 | 0 | 0 | 0 | 8 | 268 | 0 | 46 |  | 4753 | 3315 | 8068 | 2924 | 544 | 1725 | 0 | 929 | 1610 | 30 | 0 | 81 | 116 | 109 | 951.0654 | 82.3
9:00 | 0 | 0 | 200 | 0 | 0 | 78 | 0 | 0 | 215 |  | 0 | 225 | 142 | 15 | 34 | 15 | 0 | 0 | 0 | 17 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24 | 33 | 22 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 136 | 0 | 0 | 0 |  | 6 | 40 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 195 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 21 | 8 | 13 | 21 | 118 | 44 | 0 | 16 | 2 | 43 | 43 | 22 | 50 | 112 | 0 | 61 | 40 | 0 | 213 | 19 | 0 | 8 | 310 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 11 | 25 | 34 | 6 | 405 | 49 | 35 | 17 | 1 | 100 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 30 | 17 | 107 | 0 | 17 | 10 | 18 | 17 | 269 | 0 | 0 |  | 544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 16 | 0 | 0 | 20 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 0 | 0 | 50 | 15 | 42 | 0 | 2 | 35 | 1022 | 108 | 0 | 17 | 3 | 51 | 0 | 0 | 0 | 0 | 19 | 255 | 0 | 91 |  | 4903 | 3329 | 8232 | 2925 | 544 | 1716 | 0 | 1033 | 1527 | 30 | 0 | 119 | 118 | 220 | 984.2421 | 82.3
10:00 | 0 | 0 | 160 | 0 | 0 | 78 | 0 | 0 | 222 |  | 0 | 225 | 142 | 17 | 34 | 15 | 0 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24 | 33 | 22 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 6 | 40 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 197 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 21 | 8 | 13 | 21 | 116 | 32 | 0 | 13 | 2 | 43 | 43 | 22 | 47 | 112 | 0 | 61 | 40 | 0 | 215 | 18 | 0 | 8 | 290 | 8 | 5 | 0 | 32 | 0 | 0 | 18 | 0 | 17 | 16 | 25 | 34 | 6 | 377 | 49 | 52 | 17 | 3 | 100 | 17 | 54 | 17 | 9 | 25 | 360 | 17 | 42 | 17 | 107 | 0 | 17 | 20 | 18 | 17 | 281 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 42 | 24 | 0 | 0 | 3 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 304 | 0 | 0 | 50 | 15 | 35 | 0 | 4 | 35 | 1022 | 106 | 0 | 17 | 4 | 75 | 35 | 0 | 0 | 0 | 28 | 238 | 0 | 125 |  | 4900 | 3449 | 8349 | 2860 | 608 | 1665 | 0 | 1089 | 1510 | 30 | 0 | 152 | 116 | 319 | 1014.6541 | 82.29
11:00 | 0 | 0 | 160 | 0 | 0 | 78 | 0 | 0 | 217 |  | 0 | 225 | 142 | 18 | 34 | 15 | 0 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 33 | 22 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 46 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 190 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 19 | 8 | 13 | 21 | 124 | 32 | 0 | 13 | 2 | 43 | 43 | 22 | 47 | 112 | 0 | 60 | 40 | 0 | 215 | 18 | 0 | 0 | 310 | 8 | 5 | 0 | 37 | 0 | 0 | 37 | 0 | 34 | 18 | 25 | 34 | 6 | 375 | 115 | 52 | 17 | 4 | 116 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 49 | 35 | 107 | 0 | 17 | 31 | 17 | 17 | 280 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 15 | 16 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 42 | 28 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 0 | 0 | 50 | 15 | 42 | 0 | 5 | 35 | 1022 | 108 | 0 | 35 | 5 | 88 | 35 | 0 | 0 | 0 | 33 | 238 | 0 | 153 |  | 5068 | 3576 | 8644 | 2843 | 608 | 1679 | 0 | 1255 | 1510 | 30 | 0 | 207 | 124 | 388 | 973.1832 | 82.29
12:00 | 0 | 0 | 160 | 0 | 0 | 81 | 0 | 0 | 246 |  | 0 | 225 | 150 | 30 | 34 | 15 | 0 | 0 | 0 | 27 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 40 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 188 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 19 | 8 | 13 | 21 | 118 | 31 | 0 | 13 | 3 | 43 | 43 | 22 | 50 | 112 | 0 | 61 | 40 | 0 | 214 | 18 | 0 | 6 | 300 | 8 | 5 | 0 | 65 | 0 | 0 | 65 | 0 | 35 | 20 | 25 | 34 | 33 | 400 | 115 | 52 | 17 | 4 | 116 | 17 | 54 | 17 | 9 | 28 | 400 | 17 | 51 | 35 | 107 | 0 | 17 | 33 | 18 | 17 | 270 | 0 | 0 |  | 679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 16 | 16 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 42 | 43 | 0 | 12 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 50 | 15 | 42 | 0 | 5 | 35 | 1022 | 108 | 0 | 35 | 5 | 95 | 35 | 0 | 0 | 0 | 34 | 238 | 0 | 162 |  | 5272 | 3681 | 8953 | 2871 | 679 | 1709 | 0 | 1365 | 1510 | 60 | 0 | 229 | 118 | 412 | 918.8103 | 82.29
13:00 | 0 | 0 | 160 | 0 | 0 | 81 | 0 | 0 | 250 |  | 0 | 225 | 150 | 45 | 24 | 15 | 0 | 0 | 0 | 50 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 40 | 51 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 186 | 8 | 0 | 10 | 0 | 0 | 35 | 0 | 31 | 0 | 21 | 8 | 7 | 21 | 126 | 32 | 0 | 13 | 2 | 43 | 43 | 22 | 46 | 112 | 0 | 61 | 40 | 0 | 213 | 18 | 0 | 6 | 300 | 8 | 5 | 0 | 65 | 0 | 0 | 115 | 0 | 36 | 19 | 25 | 34 | 75 | 400 | 115 | 35 | 17 | 4 | 100 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 50 | 35 | 107 | 0 | 17 | 32 | 18 | 17 | 270 | 0 | 0 |  | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 18 | 16 | 0 | 0 | 0 | 34 | 6 | 50 | 0 | 42 | 40 | 0 | 23 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 17 | 0 | 50 | 15 | 50 | 0 | 5 | 35 | 1022 | 106 | 0 | 35 | 5 | 92 | 35 | 0 | 0 | 0 | 33 | 238 | 0 | 155 |  | 5415 | 3822 | 9237 | 2861 | 772 | 1696 | 0 | 1492 | 1510 | 60 | 0 | 323 | 126 | 397 | 700.397 | 82.29
14:00 | 0 | 0 | 160 | 0 | 0 | 81 | 0 | 0 | 248 |  | 0 | 225 | 150 | 50 | 2 | 15 | 0 | 0 | 0 | 50 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 40 | 51 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 160 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 21 | 8 | 8 | 21 | 130 | 32 | 0 | 13 | 2 | 43 | 43 | 22 | 46 | 80 | 0 | 40 | 40 | 0 | 212 | 18 | 0 | 8 | 270 | 8 | 5 | 0 | 32 | 0 | 0 | 121 | 0 | 35 | 18 | 25 | 34 | 103 | 374 | 115 | 35 | 17 | 3 | 100 | 17 | 54 | 17 | 8 | 25 | 400 | 17 | 45 | 35 | 107 | 0 | 17 | 29 | 18 | 17 | 270 | 0 | 0 |  | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 16 | 16 | 0 | 0 | 0 | 34 | 15 | 50 | 0 | 8 | 40 | 0 | 23 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 26 | 0 | 50 | 15 | 49 | 0 | 5 | 35 | 1022 | 107 | 0 | 35 | 5 | 82 | 36 | 0 | 0 | 0 | 29 | 211 | 0 | 141 |  | 5260 | 3737 | 8997 | 2787 | 772 | 1633 | 0 | 1457 | 1483 | 60 | 0 | 316 | 130 | 359 | 434.9834 | 82.29
15:00 | 0 | 0 | 160 | 0 | 0 | 81 | 0 | 0 | 256 |  | 0 | 225 | 150 | 50 | 26 | 15 | 0 | 0 | 0 | 50 | 32 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 22 | 25 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 37 | 56 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 203 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 19 | 8 | 8 | 21 | 126 | 32 | 0 | 13 | 2 | 43 | 43 | 22 | 46 | 112 | 0 | 61 | 40 | 0 | 212 | 18 | 0 | 8 | 305 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 35 | 13 | 25 | 34 | 112 | 407 | 115 | 35 | 17 | 3 | 100 | 17 | 54 | 17 | 9 | 25 | 400 | 17 | 34 | 35 | 87 | 0 | 17 | 22 | 18 | 17 | 220 | 0 | 0 |  | 773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 14 | 16 | 0 | 0 | 0 | 34 | 18 | 50 | 0 | 8 | 40 | 0 | 24 | 18 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254 | 37 | 0 | 50 | 15 | 49 | 0 | 4 | 35 | 1022 | 107 | 0 | 35 | 4 | 62 | 36 | 0 | 0 | 0 | 23 | 208 | 0 | 108 |  | 5269 | 3666 | 8935 | 2831 | 773 | 1689 | 0 | 1378 | 1481 | 60 | 0 | 322 | 126 | 275 | 719.7501 | 82.28
16:00 | 0 | 0 | 161 | 0 | 0 | 81 | 0 | 0 | 256 |  | 0 | 225 | 150 | 49 | 34 | 15 | 0 | 0 | 0 | 50 | 32 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 22 | 25 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 37 | 84 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 214 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 21 | 8 | 12 | 21 | 122 | 34 | 0 | 13 | 1 | 43 | 43 | 22 | 46 | 112 | 0 | 61 | 40 | 0 | 212 | 18 | 0 | 8 | 280 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 35 | 8 | 25 | 34 | 113 | 407 | 48 | 35 | 17 | 1 | 100 | 17 | 63 | 17 | 9 | 25 | 400 | 19 | 20 | 35 | 100 | 0 | 17 | 13 | 25 | 17 | 250 | 0 | 0 |  | 771 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 185 | 12 | 16 | 0 | 0 | 0 | 34 | 26 | 50 | 0 | 42 | 40 | 0 | 30 | 18 | 0 | 8 | 0 | 0 | 251 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 256 | 37 | 0 | 50 | 15 | 68 | 0 | 3 | 35 | 1022 | 107 | 0 | 17 | 2 | 36 | 36 | 0 | 0 | 0 | 13 | 208 | 0 | 65 |  | 5293 | 3642 | 8935 | 2876 | 771 | 1664 | 0 | 1435 | 1481 | 60 | 0 | 364 | 122 | 162 | 529.9056 | 82.28
17:00 | 0 | 0 | 160 | 0 | 0 | 81 | 0 | 0 | 253 |  | 0 | 225 | 150 | 46 | 34 | 15 | 0 | 0 | 0 | 50 | 32 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 22 | 24 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 36 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 205 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 33 | 0 | 21 | 8 | 12 | 21 | 120 | 34 | 0 | 13 | 0 | 43 | 43 | 22 | 46 | 112 | 0 | 61 | 40 | 0 | 214 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 48 | 0 | 0 | 9 | 0 | 35 | 2 | 25 | 34 | 115 | 407 | 48 | 35 | 50 | 0 | 100 | 17 | 74 | 114 | 9 | 25 | 400 | 25 | 5 | 35 | 107 | 0 | 17 | 4 | 39 | 17 | 250 | 0 | 0 |  | 608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 188 | 14 | 16 | 0 | 0 | 0 | 34 | 32 | 50 | 0 | 42 | 39 | 0 | 23 | 20 | 0 | 8 | 0 | 0 | 251 | 0 | 0 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 46 | 0 | 50 | 15 | 85 | 0 | 1 | 50 | 1032 | 107 | 0 | 17 | 0 | 11 | 36 | 0 | 0 | 0 | 4 | 209 | 0 | 19 |  | 5479 | 3451 | 8930 | 2868 | 608 | 1686 | 0 | 1686 | 1492 | 60 | 0 | 364 | 120 | 46 | 570.4549 | 82.28
18:00 | 0 | 0 | 160 | 25 | 0 | 81 | 0 | 0 | 255 |  | 0 | 225 | 155 | 45 | 34 | 15 | 0 | 0 | 0 | 50 | 42 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 24 | 33 | 21 | 41 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 54 | 80 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 211 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 7 | 21 | 8 | 12 | 21 | 132 | 34 | 0 | 13 | 0 | 43 | 43 | 22 | 49 | 80 | 0 | 63 | 86 | 0 | 210 | 18 | 0 | 8 | 270 | 8 | 8 | 0 | 99 | 0 | 0 | 28 | 0 | 36 | 0 | 25 | 34 | 127 | 385 | 48 | 70 | 85 | 0 | 285 | 17 | 88 | 114 | 9 | 25 | 360 | 36 | 0 | 35 | 107 | 0 | 15 | 0 | 61 | 17 | 260 | 0 | 0 |  | 608 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 38 | 30 | 16 | 189 | 18 | 16 | 0 | 0 | 0 | 34 | 32 | 84 | 0 | 42 | 40 | 0 | 22 | 20 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 55 | 0 | 50 | 32 | 92 | 0 | 0 | 55 | 1020 | 107 | 0 | 100 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 208 | 0 | 0 |  | 5918 | 3717 | 9635 | 2850 | 608 | 1676 | 0 | 2330 | 1479 | 60 | 0 | 500 | 132 | 0 | 567 | 82.27
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 153 | 35 | 0 | 52 | 0 | 0 | 256 |  | 0 | 225 | 155 | 50 | 34 | 25 | 0 | 0 | 0 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 25 | 33 | 21 | 41 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 65 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 207 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 9 | 21 | 8 | 16 | 21 | 134 | 55 | 0 | 13 | 0 | 40 | 43 | 51 | 49 | 112 | 0 | 63 | 86 | 0 | 210 | 18 | 0 | 8 | 270 | 8 | 8 | 0 | 99 | 0 | 0 | 74 | 0 | 70 | 0 | 25 | 34 | 133 | 405 | 77 | 70 | 85 | 0 | 285 | 17 | 92 | 114 | 9 | 25 | 380 | 55 | 0 | 92 | 107 | 0 | 17 | 0 | 71 | 17 | 280 | 0 | 0 |  | 469 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 44 | 30 | 16 | 171 | 21 | 16 | 0 | 0 | 0 | 34 | 32 | 97 | 0 | 50 | 40 | 0 | 22 | 20 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 55 | 0 | 50 | 50 | 92 | 0 | 0 | 75 | 1120 | 107 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 208 | 0 | 0 |  | 6337 | 3794 | 10131 | 2910 | 469 | 1712 | 0 | 2716 | 1579 | 60 | 0 | 551 | 134 | 0 | 432.2187 | 82.26
19:30 | 0 | 0 | 160 | 40 | 0 | 52 | 0 | 0 | 256 |  | 0 | 225 | 155 | 50 | 34 | 11 | 0 | 0 | 0 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 25 | 33 | 21 | 41 | 0 | 30 | 30 | 0 | 0 | 17 | 150 | 0 | 0 | 0 |  | 6 | 65 | 70 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 295 | 0 | 205 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 16 | 22 | 8 | 16 | 21 | 126 | 64 | 0 | 13 | 0 | 43 | 43 | 51 | 49 | 112 | 0 | 63 | 86 | 0 | 210 | 19 | 0 | 8 | 260 | 8 | 8 | 0 | 98 | 0 | 0 | 74 | 0 | 72 | 0 | 25 | 34 | 135 | 405 | 78 | 88 | 85 | 0 | 285 | 17 | 92 | 114 | 9 | 25 | 380 | 55 | 0 | 126 | 107 | 0 | 17 | 0 | 72 | 17 | 290 | 0 | 0 |  | 469 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 38 | 30 | 16 | 190 | 21 | 16 | 0 | 0 | 0 | 34 | 33 | 97 | 0 | 50 | 40 | 0 | 23 | 20 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255 | 55 | 0 | 50 | 50 | 93 | 0 | 0 | 75 | 1202 | 107 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 209 | 0 | 0 |  | 6387 | 3900 | 10287 | 2963 | 469 | 1708 | 0 | 2767 | 1662 | 60 | 0 | 532 | 126 | 0 | 196.2955 | 0
20:00 | 0 | 0 | 130 | 70 | 0 | 52 | 0 | 0 | 252 |  | 0 | 225 | 150 | 50 | 34 | 15 | 0 | 0 | 0 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 25 | 33 | 21 | 42 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 65 | 81 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 195 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 16 | 19 | 8 | 16 | 21 | 124 | 70 | 0 | 13 | 0 | 43 | 43 | 51 | 49 | 112 | 0 | 62 | 86 | 0 | 218 | 19 | 0 | 8 | 280 | 8 | 8 | 0 | 99 | 0 | 0 | 74 | 0 | 72 | 0 | 25 | 34 | 132 | 406 | 78 | 88 | 85 | 0 | 285 | 17 | 92 | 114 | 9 | 25 | 400 | 54 | 0 | 127 | 107 | 0 | 17 | 0 | 73 | 17 | 280 | 0 | 0 |  | 469 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 38 | 30 | 16 | 190 | 21 | 16 | 0 | 0 | 0 | 34 | 33 | 98 | 0 | 50 | 41 | 0 | 23 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 55 | 0 | 70 | 50 | 93 | 0 | 0 | 75 | 1202 | 107 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 208 | 0 | 0 |  | 6453 | 3930 | 10383 | 3006 | 469 | 1727 | 0 | 2791 | 1661 | 60 | 0 | 545 | 124 | 0 | 45.1572 | 82.27
21:00 | 0 | 0 | 130 | 80 | 0 | 52 | 0 | 0 | 251 |  | 0 | 225 | 150 | 50 | 34 | 15 | 0 | 0 | 0 | 50 | 50 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 25 | 33 | 21 | 43 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 70 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 208 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 8 | 22 | 8 | 19 | 21 | 122 | 104 | 0 | 14 | 0 | 43 | 43 | 51 | 50 | 112 | 0 | 63 | 86 | 0 | 218 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 98 | 0 | 0 | 74 | 0 | 72 | 0 | 25 | 34 | 135 | 405 | 79 | 88 | 85 | 0 | 285 | 17 | 92 | 17 | 9 | 25 | 400 | 54 | 0 | 86 | 107 | 0 | 17 | 0 | 72 | 17 | 280 | 0 | 0 |  | 608 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 38 | 0 | 16 | 191 | 22 | 16 | 0 | 0 | 0 | 34 | 33 | 97 | 0 | 42 | 40 | 0 | 23 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 55 | 0 | 70 | 32 | 92 | 0 | 0 | 75 | 1222 | 107 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 208 | 0 | 0 |  | 6286 | 4035 | 10321 | 3040 | 608 | 1737 | 0 | 2583 | 1681 | 60 | 0 | 490 | 122 | 0 | 24.8825 | 82.26
22:00 | 0 | 0 | 130 | 110 | 0 | 52 | 0 | 0 | 256 |  | 0 | 225 | 150 | 24 | 22 | 15 | 0 | 0 | 0 | 28 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 26 | 33 | 21 | 43 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 6 | 70 | 85 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 215 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 8 | 22 | 8 | 23 | 21 | 116 | 102 | 0 | 14 | 0 | 43 | 43 | 31 | 50 | 80 | 0 | 40 | 40 | 0 | 217 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 98 | 0 | 0 | 74 | 0 | 72 | 0 | 25 | 34 | 135 | 355 | 79 | 88 | 85 | 0 | 268 | 17 | 92 | 17 | 9 | 25 | 330 | 55 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 290 | 0 | 0 |  | 694 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 38 | 0 | 16 | 182 | 21 | 16 | 0 | 0 | 0 | 34 | 33 | 97 | 0 | 42 | 40 | 0 | 23 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227 | 55 | 0 | 70 | 15 | 71 | 0 | 0 | 75 | 1120 | 107 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 189 | 0 | 0 |  | 5873 | 3914 | 9787 | 2928 | 694 | 1589 | 0 | 2366 | 1560 | 60 | 0 | 474 | 116 | 0 | 0 | 82.32
23:00 | 0 | 0 | 130 | 110 | 0 | 52 | 0 | 0 | 256 |  | 0 | 225 | 150 | 17 | 0 | 15 | 0 | 0 | 0 | 17 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 22 | 26 | 25 | 22 | 25 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 |  | 5 | 70 | 74 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 219 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 8 | 22 | 8 | 24 | 21 | 113 | 104 | 0 | 14 | 0 | 43 | 43 | 31 | 50 | 80 | 0 | 40 | 40 | 0 | 216 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 67 | 0 | 0 | 9 | 0 | 36 | 0 | 25 | 34 | 85 | 403 | 49 | 35 | 85 | 0 | 16 | 17 | 92 | 17 | 9 | 25 | 400 | 33 | 0 | 17 | 107 | 0 | 17 | 0 | 72 | 17 | 300 | 0 | 0 |  | 772 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 20 | 16 | 0 | 0 | 0 | 34 | 32 | 98 | 0 | 42 | 40 | 0 | 23 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 55 | 0 | 70 | 15 | 34 | 0 | 0 | 35 | 1120 | 108 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 189 | 0 | 0 |  | 5355 | 3846 | 9201 | 3045 | 772 | 1672 | 0 | 1605 | 1509 | 60 | 0 | 425 | 113 | 0 | 0 | 82.32
24:00 | 0 | 0 | 130 | 110 | 0 | 52 | 0 | 0 | 250 |  | 0 | 225 | 150 | 17 | 0 | 15 | 0 | 0 | 0 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 26 | 25 | 24 | 0 | 0 | 30 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 4 | 0 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 219 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 104 | 103 | 0 | 14 | 0 | 43 | 43 | 31 | 30 | 112 | 0 | 40 | 40 | 0 | 216 | 19 | 0 | 10 | 290 | 8 | 8 | 0 | 37 | 0 | 0 | 9 | 0 | 17 | 0 | 25 | 34 | 73 | 405 | 49 | 35 | 85 | 0 | 16 | 17 | 66 | 17 | 9 | 25 | 400 | 18 | 0 | 17 | 107 | 0 | 17 | 0 | 67 | 17 | 310 | 0 | 0 |  | 772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 200 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 55 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 1120 | 107 | 0 | 88 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 190 | 0 | 0 |  | 5019 | 3505 | 8524 | 3079 | 772 | 1679 | 0 | 1237 | 1510 | 60 | 0 | 83 | 104 | 0 | 0 | 82.32
KWH | 0 | 0 | 3998844 | 472500 | 0 | 1647636 | 0 | 0 | 5104000 |  | 0 | 4717900 | 3259142 | 699840 | 625954 | 392910 | 444109 | 0 | 0 | 705600 | 507744 | 760320 | 0 | 0 | 0 | 0 | 161640 | 306153 | 299136 | 355644 | 528000 | 588960 | 815100 | 545100 | 710400 | 0 | 724500 | 384000 | 0 | 0 | 263433 | 2714690 | 0 | 0 | 0 |  | 145920 | 923376 | 969996 | 530160 | 0 | 469920 | 0 | 5760 | 0 | 0 | 0 | 7641300 | 0 | 4980000 | 217454 | 0 | 277776 | 0 | 0 | 1013121 | 0 | 579248 | 128966 | 494964 | 179280 | 478100 | 496650 | 2768640 | 1545600 | 0 | 344232 | 15800 | 1019000 | 985920 | 626400 | 1129320 | 2674063 | 0 | 1406400 | 1326720 | 0 | 5290350 | 444000 | 0 | 202320 | 7149500 | 190992 | 177504 | 0 | 1196836 | 0 | 0 | 828000 | 0 | 813744 | 119340 | 605760 | 840960 | 1446909 | 9573000 | 1660800 | 1183200 | 961814 | 24000 | 2438836 | 452552 | 1597448 | 839040 | 221760 | 596160 | 8688200 | 617280 | 345080 | 771840 | 2541709 | 0 | 314640 | 207890 | 826560 | 433080 | 6704300 | 0 | 0 |  | 16439272 | 0 | 0 | 0 | 184320 | 0 | 0 | 0 | 194400 | 100608 | 104625 | 4490642 | 409500 | 246624 | 0 | 0 | 0 | 379902 | 259748 | 982592 | 0 | 655526 | 506944 | 0 | 241837 | 444480 | 0 | 223236 | 0 | 0 | 5685500 | 0 | 0 | 4431709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6982800 | 578400 | 0 | 1126368 | 390960 | 1129392 | 0 | 34837 | 916032 | 27647900 | 2587500 | 0 | 1160400 | 39540 | 626400 | 1038528 | 0 | 0 | 0 | 223040 | 5541800 | 0 | 1072720 |  | 125412745 | 87078082 | 212490827 | 70526102 | 16439272 | 39497616 | 0 | 34667879 | 38875200 | 1108500 | 0 | 5898971 | 2768640 | 2708647 | 0
Fuel Cost | 0 | 0 | 5838312.24 | 704025 | 0 | 2191355.88 | 0 | 0 | 5512320 |  | 0 | 5142511 | 3617647.62 | 7824211.2 | 8293890.5 | 5206057.5 | 497402.08 | 0 | 0 | 10315872 | 7143958.08 | 12324787.2 | 0 | 0 | 0 | 0 | 2056060.8 | 4133065.5 | 4011413.76 | 266733 | 396000 | 0 | 0 | 0 | 12083904 | 0 | 195615 | 103680 | 0 | 0 | 4307129.55 | 2823277.6 | 0 | 0 | 0 |  | 1904256 | 15401911.68 | 16509331.92 | 7162461.6 | 0 | 5436974.4 | 0 | 19180.8 | 0 | 0 | 0 | 8481843 | 0 | 5776800 | 280515.66 | 0 | 313886.88 | 0 | 0 | 1691912.07 | 0 | 10003612.96 | 1734592.7 | 678100.68 | 134460 | 836675 | 372487.5 | 19878835.2 | 1684704 | 0 | 468155.52 | 251852 | 1396030 | 1301414.4 | 1089936 | 1953723.6 | 3075172.45 | 0 | 2728416 | 3024921.6 | 0 | 5343253.5 | 954600 | 0 | 400593.6 | 7149500 | 143244 | 134903.04 | 0 | 16336811.4 | 0 | 0 | 11161440 | 0 | 11270354.4 | 1395084.6 | 6251443.2 | 11487513.6 | 19200482.43 | 8807160 | 20195328 | 17109072 | 12166947.1 | 0 | 28631934.64 | 4928291.28 | 16980872.24 | 11385772.8 | 2858486.4 | 7022764.8 | 7993144 | 7993776 | 4986406 | 9794649.6 | 28924648.42 | 0 | 4109198.4 | 2484285.5 | 12373603.2 | 5703663.6 | 0 | 0 | 0 |  | 49317816 | 0 | 0 | 0 | 1918771.2 | 0 | 0 | 0 | 3501144 | 1810944 | 1503461.25 | 5029519.04 | 794430 | 2688201.6 | 0 | 0 | 0 | 6370956.54 | 4542992.52 | 15367738.88 | 0 | 10855510.56 | 8572423.04 | 0 | 4079790.19 | 920073.6 | 0 | 168989.652 | 0 | 0 | 30076295 | 0 | 0 | 5140782.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6912972 | 7773696 | 0 | 13324933.44 | 5649372 | 14343278.4 | 0 | 384948.85 | 11120628.48 | 249107579 | 2639250 | 0 | 8586960 | 447197.4 | 7347672 | 15920634.24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 524260620.88 | 496218961.322 | 1020479582.202 | 68414318.572 | 49317816 | 46416015.88 | 0 | 441186348.27 | 279183874 | 299295 | 0 | 98485632.93 | 19878835.2 | 17297446.35 | 0
Yesterday Day Peak | 0 | 0 | 160 | 0 | 0 | 81 | 0 | 0 | 246 |  | 0 | 225 | 150 | 30 | 34 | 15 | 0 | 0 | 0 | 27 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 25 | 33 | 21 | 25 | 0 | 30 | 30 | 0 | 0 | 8 | 151 | 0 | 0 | 0 |  | 6 | 40 | 0 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 188 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 31 | 0 | 19 | 8 | 13 | 21 | 118 | 31 | 0 | 13 | 3 | 43 | 43 | 22 | 50 | 112 | 0 | 61 | 40 | 0 | 214 | 18 | 0 | 6 | 300 | 8 | 5 | 0 | 65 | 0 | 0 | 65 | 0 | 35 | 20 | 25 | 34 | 33 | 400 | 115 | 52 | 17 | 4 | 116 | 17 | 54 | 17 | 9 | 28 | 400 | 17 | 51 | 35 | 107 | 0 | 17 | 33 | 18 | 17 | 270 | 0 | 0 |  | 679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 16 | 16 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 42 | 43 | 0 | 12 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 284 | 0 | 0 | 50 | 15 | 42 | 0 | 5 | 35 | 1022 | 108 | 0 | 35 | 5 | 95 | 35 | 0 | 0 | 0 | 34 | 238 | 0 | 162 |  | 8953 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 70 | 0 | 52 | 0 | 0 | 252 | 0 | 0 | 225 | 150 | 50 | 34 | 15 | 0 | 0 | 0 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 25 | 33 | 21 | 42 | 0 | 30 | 30 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 6 | 65 | 81 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 325 | 0 | 195 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 38 | 16 | 19 | 8 | 16 | 21 | 124 | 70 | 0 | 13 | 0 | 43 | 43 | 51 | 49 | 112 | 0 | 62 | 86 | 0 | 218 | 19 | 0 | 8 | 280 | 8 | 8 | 0 | 99 | 0 | 0 | 74 | 0 | 72 | 0 | 25 | 34 | 132 | 406 | 78 | 88 | 85 | 0 | 285 | 17 | 92 | 114 | 9 | 25 | 400 | 54 | 0 | 127 | 107 | 0 | 17 | 0 | 73 | 17 | 280 | 0 | 0 |  | 469 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 38 | 30 | 16 | 190 | 21 | 16 | 0 | 0 | 0 | 34 | 33 | 98 | 0 | 50 | 41 | 0 | 23 | 21 | 0 | 11 | 0 | 0 | 251 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262 | 55 | 0 | 70 | 50 | 93 | 0 | 0 | 75 | 1202 | 107 | 0 | 150 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 208 | 0 | 0 |  | 10383 | EvPeak
Forecast for Evening | 0 | 0 | 130 | 110 | 0 | 20 | 0 | 0 | 250 | 0 | 0 | 225 | 150 | 50 | 34 | 25 | 0 | 0 |  | 50 | 50 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 22 | 27 | 33 | 22 | 42 | 0 | 30 | 0 | 0 | 0 | 17 | 151 | 0 | 0 | 0 | 0 | 6 | 64 | 85 | 33 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 200 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 30 | 8 | 21 | 8 | 21 | 21 | 153 | 70 | 0 | 11 | 0 | 43 | 43 | 51 | 50 | 112 | 0 | 61 | 86 | 0 | 220 | 19 | 0 | 10 | 300 | 8 | 8 |  | 95 | 0 | 0 | 75 | 0 | 72 | 0 | 25 | 34 | 150 | 400 | 76 | 88 | 85 | 0 | 300 | 17 | 92 | 114 | 9 | 25 | 400 | 55 | 0 | 126 | 107 | 0 | 17 |  | 94 | 17 | 320 |  |  |  | 784 | 0 | 0 |  | 32 | 0 | 0 | 0 | 45 | 75 | 24 | 190 | 21 | 16 | 0 | 0 | 0 | 34 | 37 | 96 | 0 | 42 | 40 | 0 | 30 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 182 |  | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 55 | 0 | 70 | 100 | 100 | 0 | 0 | 75 | 1244 | 110 |  | 150 |  |  | 113 | 0 |  | 0 |  | 300 | 0
Forecast for Day | 0 | 0 | 130 | 110 | 0 | 20 | 0 | 0 | 230 | 0 | 0 | 225 | 150 | 17 | 34 | 15 | 0 | 0 | 0 | 50 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 27 | 33 | 22 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 6 | 40 | 68 | 22 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 10 | 8 | 21 | 8 | 21 | 21 | 135 | 55 | 0 | 11 | 1.6 | 43 | 43 | 31 | 50 | 112 | 0 | 61 | 84 | 0 | 220 | 19 | 0 | 10 | 300 | 8 | 8 | 0 | 32 | 0 | 0 | 65 | 0 | 35 | 20 | 25 | 34 | 75 | 400 | 50 | 90 | 17 | 5 | 100 | 17 | 55 | 114 | 9 | 25 | 380 | 17 | 50 | 17 | 107 | 0 | 17 | 30 | 17 | 17 | 320 |  |  |  | 784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 42 | 40 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 50 | 67 | 49 | 0 | 8 | 35 | 1244 | 110 |  | 35 | 6 | 100 | 35 | 0 |  | 0 | 30 | 300 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 110 | 0 | 23 | 0 | 0 | 280 | 0 | 0 | 225 | 132 | 17 | 1 | 15 | 0 | 0 | 0 | 17 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 27 | 33 | 22 | 25 | 0 | 30 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 22 | 0 | 18 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 220 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 13 | 15 | 106 | 44 | 0 | 18 | 1 | 42 | 43 | 22 | 20 | 112 | 0 | 64 | 84 | 0 | 216 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 32 | 0 | 0 | 9 | 0 | 17 | 8 | 25 | 0 | 75 | 397 | 49 | 35 | 17 | 1 | 16 | 17 | 54 | 114 | 9 | 25 | 400 | 17 | 14 | 17 | 107 | 0 | 12 | 9 | 18 | 17 | 320 | 0 | 0 | 0 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 15 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 35 | 15 | 37 | 0 | 1 | 35 | 1244 | 0 | 0 | 4 | 1 | 24 | 0 | 0 | 0 | 0 | 7 | 219 | 0 | 36 | 0 |  |  |  | 110.0237 | 16.4393 | 40.5669 | 38.8752 | 1.1085 | 2.7686 | 2.7086
212.4908
| Minimum Generation |  | 7371 | 5:00
| Highest Generation |  | 10383 | 20:00
| Day Peak Generation |  | 8953 | 12:00
| Evening Peak Generation |  | 10383 | 20:00
| HVDC Max Flow |  | 902 | 1:00
| HVDC EvPeak Flow |  | 469 | 20:00
| Load factor L.F |  | 85.27% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-02-14
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-02-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8953 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7071
Evening Peak Generation : |  |  | 10383 | MW Hour : | 20:00 | Available Max Generation : |  | 11157
E.P. Demand (at gen end) : |  |  | 10432 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10700
Maximum Generation : |  |  | 10383 | MW Hour : | 20:00 | Reserve(Generation end) |  | 457
Total Gen. (MKWH) : |  |  | 212.4908 | System Load Factor : | 85.27% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 216 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-02-14
Actual : |  | 82.23 | Ft.(MSL) , | Rule curve : | 95.18 | Ft.( MSL )
Gas Consumed : |  | Total = | 864.63 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 114830334.452
: |  |  | Coal : | 279183874 | Oil : | 539671981.2 | Total : | 933686189.652
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3442.0938 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 975.0853 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1287.0316 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1141.9176 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 972.0825 |  |  | 0 | 0%
Mymensingh Area |  | 35 | 840:00 | 803.0854 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 358.9443 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 292.6024 |  |  | 0 | 0%
Rangpur Area |  | 10 | 240:00 | 634.0883 |  |  | 0 | 0%
Total |  | 45 |  | 9906.9312 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,5,7
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:31 | 14:50 | Sunamganj 132/33kV S/S Tr-2 LT Scheduled S/D Due to Annual Maintenance works.
08:37 | 16:48 | Cumilla(N)-Shahjibazar 230 kV Ckt-2 Scheduled S/D Due to Annual Maintenance.
08:37 | 13:01 | Khulshi 132/33kV S/S Khulshi-Baraulia Circuit-2 Scheduled S/D Due to annual maintenance.
08:41 | 18:40 | Candpur (Desh)- Chandpur 132kV Ckt-2 Scheduled S/D from Chandpur 132/33kV end Due to Annual maintenance .
08:45 | 14:14 | Hathazari 230/132/33kV S/S T-02 HT Scheduled S/D Due to Annual maintenance.
08:50 | 18:23 | Aminbazar-Mirpur 132kV Ckt-2 Scheduled S/D Due to Amin Bazer Ckt-2 Line DS Change Work.
08:51 | 17:18 | Chandraghona-Madunaghat 132 kV Ckt-2 Scheduled S/D Due to Annual maintenance .
08:59 | 17:37 | Goalpara 132/33kV S/S Bus A Scheduled S/D Due to Gantry Tower and Structure Painting Works .
| 09:16 | Ashuganj-Kishoreganj 132kV Ckt-2 is restored.
09:25 | 17:46 | Jamalpur 132/33kV S/S T-2 HT Scheduled S/D Due to T-2 Transformer painting work .
09:31 | 14:50 | Sunamganj 132/33kV S/S Tr-2 HT Scheduled S/D Due to Annual Maintenance Works .
09:34 | 13:25 | Faridpur 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Oil Leakage Maintenance .
10:15 | 11:47 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D Due to Work done by Kaliakoir Grid.
10:26 | 11:47 | Dhamrai-Kaliakoir 132 kV Ckt-1 Scheduled S/D from Kaliakoir 400/230/132kV end Due to Relay Test
10:52 |  | Ashugonj north-south xfr-2 was S/D
11:01 | 14:02 | Barishal 230/132kV S/S T-4 HT Project Work S/D Due to SAS Commissioning.
11:11 | 14:52 | Kalurghat 132/33kV S/S TRFO-01(506T) LT Forced S/D Due to Maintenance by BPDB work.
11:12 |  | Joydebpur 132/33kV S/S GT-2 LT Scheduled S/D Due to S/D
12:04 | 12:46 | Dhamrai-Kaliakoir 132 kV Ckt-2 Scheduled S/D Due to Work done by Kaliakoir Grid .
| 14:00 | Madanganj 132/33kV S/S GT-2 HT is restored.
14:12 | 17:19 | Barishal 230/132kV S/S T-5 LT Project Work S/D Due to SAS commisioning.
| 17:16 | Aminbazar-Kaliakoir 230kV Ckt-2 is restored.
17:20 |  | Ghorasal ST:Unit-5 was sync.
| 17:30 | Kaliakoir-Kodda(300MW) 230kV Ckt-1 is restored.
| 18:23 | Mirpur 132/33kV S/S Reserve Bus is restored.
| 19:39 | Gopalganj 400/132kV S/S 400kV Rampal Ckt-2 is restored.
04:45 |  | Bhola Natun Biddut BD LTD (GAS) tripped.
07:50 |  | Lalbag SS 132/33kV GT-1 was shutdown.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-02-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3998844
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 70 | 472500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 52 | 1647636 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 252 | 5104000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4717900 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 50 | 699840 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 150 | 3259142 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 625954 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 392910 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 355644
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 50 | 705600 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 444109 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 50 | 507744 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 161640 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 760320 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 306153
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 299136 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1116960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 815100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 21 | 545100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 42 | 710400 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 99 | 1196836 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 72 | 813744 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1183200 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 54 | 617280 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 127 | 771840 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 207890
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 433080 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1886 | 32870502
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 263433 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 119340
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 469920 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 60 | 1108500 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 151 | 2714690
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 961814 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 65 | 923376 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 81 | 969996 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 530160 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 605760 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 5760
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24000
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 285 | 2438836 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 452552 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1597448 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 596160 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2541709 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1051 | 16323454
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 195 | 4980000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7641300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 280 | 6704300 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 277776 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1013121 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 132 | 1446909 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 38 | 579248 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 34 | 840960 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 494964
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 179280 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2768640
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 16 | 478100 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 128966 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 496650 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 839040
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 221760 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 314640 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 73 | 826560 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1482 | 30449668
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 70 | 1545600 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 344232 | Gas shortage
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15800
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 74 | 828000 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 1660800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 345080
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 145920 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 241 | 4885432
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1019000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 985920 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 2674063 | ST under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 626400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 1129320
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 177504 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1406400
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1326720
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 5290350
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 444000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 190992 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7149500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 406 | 9573000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 202320
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8688200
| Sylhet Area Total |  |  |  | 2427 | 1793 | 40883689
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 469 | 16439272
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 33 | 184320 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 194400 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 30 | 100608 | High voltage
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 16 | 104625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 55 | 578400 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 50 | 390960 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 626400
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Khulna Area Total |  |  |  | 3001 | 691 | 18618985
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 246624 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 21 | 409500 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 190 | 4490642
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1202 | 27647900
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 107 | 2587500 | GT-1 Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1160400
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 208 | 5541800 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1894 | 42084366
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 379902 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 33 | 259748 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 655526
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 41 | 506944 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 170 | 4431709 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 262 | 6982800 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 23 | 241837 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 444480
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 223236
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 982592
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1126368 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 916032 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 39540
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 888 | 17190714
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 251 | 5685500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 93 | 1129392 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34837
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 1038528
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 223040
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1072720
| Rangpur Area Total |  |  |  | 750 | 457 | 9184017
| Total |  |  |  | 22700 | 10383 | 212490827
| Eastern Grid Total |  |  |  | 14555 | 6453 | 125412745
| Western Grid Total |  |  |  | 8145 | 3930 | 87078082
| National Grid Total |  |  |  | 22700 | 10383 | 212490827
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-02-13
| (a) ENTIRE EASTERN GRID : |  | 6724.89 | MW | (b) ENTIRE WESTERN GRID : |  | 3249.4 | MW
| i) Dhaka area |  | 3585.69 | MW | i) Khulna area |  | 1144.8 | MW
| ii) Chittagong area |  | 1016.2 | MW | ii) Rajshahi area |  | 1100.6 | MW
| iii) Comilla area |  | 867 | MW | iii) Barisal area |  | 278 | MW
| iv) Mymensingh area |  | 909 | MW | iv) Rangpur area |  | 726 | MW
| v) Sylhet area |  | 347 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9974.29 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 18:30 | Kamrangirchar | 48 | 12:00 | Natore | 104 | 20:00 | Shitalakhya | 100 | 16:00
2 | AKSML | 12.5 | 13:00 | Chowmuhani | 128 | 19:00 | Kaptai | 4 | 18:00 | Nawabganj | 27.6 | 21:00 | Sholosohor | 25 | 14:00
3 | Aftabnagar | 24 | 13:00 | Chuadanga | 73 | 19:00 | Kazla | 85 | 13:00 | Netrakona | 112 | 20:00 | Shyampur | 120 | 00:00
4 | Agargaon | 56 | 13:00 | Coxsbazar | 100 | 20:00 | Keranigonj | 58 | 19:30 | New | 60.8 | 12:00 | Siddhirganj | 96 | 12:00
5 | Agrabad | 50 | 14:00 | Cumilla(N) | 102 | 20:00 | Khagrachori | 28 | 19:30 | Niamatpur | 98 | 21:00 | Sirajganj | 83 | 20:00
6 | Amnura | 43 | 20:00 | Cumilla(S) | 136 | 18:30 | Khulna | 85 | 19:00 | Noapara | 34 | 19:00 | Sonargaon | 83 | 22:00
7 | Ashuganj | 43 | 12:00 | Daudkandi | 97 | 19:30 | Khulshi | 145 | 19:30 | PHP | 9 | 00:00 | Sreemongol | 37 | 18:00
8 | BIPTC | N/A | N/A | Dhaka | 60 | 13:00 | Kishoreganj | 110 | 21:00 | Pabna | 71 | 20:00 | Srinagar | 28.59 | 20:00
9 | BSRM | 112 | 00:00 | Dhamrai | 80 | 13:00 | Kodda | 215 | 19:30 | Palashbari | 102 | 20:00 | Sunamganj | 35 | 19:00
10 | Bagerhat | 73 | 18:30 | Dhanmondi | 96 | 13:00 | Kulaura | 28 | 18:30 | Panchagarh | 44 | 20:00 | Sylhet | 95 | 18:30
11 | Bakulia | 88 | 18:30 | Dohazari | 60 | 19:00 | Kurigram | 53 | 20:00 | Patuakhali | 68 | 21:00 | TK | 20.4 | 19:30
12 | Banani | 28 | 12:00 | Faridpur | 100 | 19:00 | Kushtia | 100 | 18:30 | Payra | 10 | 18:00 | Tangail | 176 | 20:00
13 | Bangabhaban | 14 | 11:00 | Fatullah | 54 | 11:00 | Lalbag | 69 | 13:00 | Postogola | 30 | 13:00 | Thakurgaon | 74 | 19:00
14 | Barapukuria | 52 | 21:00 | Fenchuganj | 26 | 18:30 | Lalmonirhat | 33 | 19:30 | Purbachal | 14 | 15:00 | Tongi | 101 | 17:00
15 | Barguna | 12 | 18:30 | Feni | 87 | 20:00 | Madanganj | 32 | 19:30 | Purbasadipur | 109 | 21:00 | Ullon | 30 | 18:00
16 | Barishal | 72 | 18:30 | GPH | 82 | 10:00 | Madaripur | 63 | 19:00 | Rahanpur_I | 5.3 | 18:00 | Uttara | 50 | 13:00
17 | Barishal-230 | 60 | 21:00 | Ghorashal | 58 | 22:00 | Madartek | 50 | 13:00 | Rahim | 34 | 11:00 | UttaraNew | 13 | 09:00
18 | Baroaulia | 57 | 11:00 | Goalpara | 17 | 08:00 | Madunaghat | 39 | 19:30 | Rajbari | 49 | 18:30 | Zigatola | 55 | 13:00
19 | Baroirhat | 33 | 19:30 | Gollamari | 28 | 08:00 | Magura | 50 | 18:30 | Rajendrapur | 106 | 19:30
20 | Bashundhara | 113 | 13:00 | Gopalganj | 77 | 19:00 | Mahasthangarh | 48 | 20:00 | Rajshahi | 102 | 18:30
21 | BashundharaCement | 6 | 14:00 | Gulshan | 76 | 13:00 | Manikganj | 80 | 19:00 | Rajshahi-230 | 27 | 20:00
22 | Beanibazar | 42 | 18:00 | Halishahar | 93 | 15:00 | Maniknagar | 49 | 14:00 | Ramganj | 72 | 18:30
23 | Benapole | 40 | 13:00 | HaripurSBU | 143 | 23:00 | Matarbari | 33 | 19:30 | Rampur | 18 | 00:00
24 | Bhaluka | 102 | 21:00 | Hasnabad | 61 | 00:00 | Matuail | 64 | 10:00 | Rangamati | 12 | 19:30
25 | Bhandaria | 30 | 18:30 | Hathazari | 43 | 20:00 | Millgate | 60 | 16:00 | Rangpur | 110 | 19:30
26 | Bhangura | 22 | 22:00 | Ishurdi | 49 | 19:00 | Mirpur | 89 | 13:00 | Ruppur | 4 | 11:00
27 | Bheramara(GK) | 44 | 18:30 | Jaldhaka | 50 | 20:00 | Mirsorai | 2 | 10:00 | SSM | 8 | 02:00
28 | Bhulta | 219 | 23:00 | Jamalpur | 123 | 21:00 | Mithapukur | 25 | 19:30 | Saidpur | 93 | 20:00
29 | Bog-Sherpur | 62 | 20:00 | Jashore | 107 | 18:30 | Modern | 0 | 00:00 | Satkhira | 98 | 18:30
30 | Bogura | 112 | 20:00 | Jhenaidah | 94 | 19:00 | Mogbazar | 90 | 15:00 | Satmasjid | 66 | 13:00
31 | Borhanuddin | 33 | 22:00 | Joydebpur | 100 | 00:00 | Mongla | 28 | 04:00 | Savar | 132 | 18:00
32 | Brahmanbaria | 108 | 19:00 | Joypurhat | 51 | 18:00 | Motijheel | 27 | 13:00 | Shahjadpur | 67 | 20:00
33 | Cantonment | 94 | 13:00 | Juldah | 27 | 08:00 | Munshiganj | 61 | 21:00 | Shahjibazar | 83 | 21:00
34 | Chandpur | 41 | 19:30 | KSRM | 30 | 03:00 | Mymensingh | 193 | 19:00 | Shahmirpur | 39.4 | 02:00
35 | Chandraghona | 24 | 18:30 | Kabirpur | 235 | 18:00 | Naogaon | 106 | 20:00 | Shariatpur | 46 | 20:00
36 | Chapai | 51 | 21:00 | Kachua | 50 | 19:30 | Narail | 41 | 19:00 | Sherpur | 140 | 13:00
37 | Charsaidpur | 46 | 11:00 | Kallyanpur | 60 | 18:30 | Narinda | 43 | 12:00 | Shikalbaha | 19 | 13:00
38 | Chauddagram | 32 | 18:30 | Kalurghat | 8 | 18:00 | Narshingdi | 138 | 20:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-02-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 407 | 05:00 | 394 | 12:00 | Gopalganj | 418 | 04:00 | 398 | 10:00
| Bhulta | 395 | 04:00 | 382 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bibiana | 403 | 05:00 | 395 | 13:00 | Payra | 415 | 03:00 | 410 | 11:00
| BIPTC | 407 | 06:00 | 394 | 13:00 | Rahanpur_I | 419 | 19:00 | 395 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 236 | 05:00 | 227 | 12:00 | Hasnabad | 236 | 19:30 | 226 | 12:00
| AKSML | 244 | 22:00 | 219 | 14:00 | Hathazari | 243 | 19:00 | 233 | 08:00
| Aminbazar | 237 | 18:30 | 229 | 11:00 | Ishurdi | 239 | 19:30 | 227 | 12:00
| Ashuganj | 242 | 22:00 | 232 | 09:00 | Jhenaidah | 238 | 05:00 | 224 | 12:00
| Baghabari | 235 | 19:00 | 226 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Barapukuria | 231 | 19:00 | 221 | 07:00 | Keranigonj | 235 | 03:00 | 226 | 11:00
| Barishal | 246 | 19:00 | 241 | 08:00 | Khulna(S) | 241 | 04:00 | 225 | 12:00
| Bheramara | 237 | 19:30 | 224 | 12:00 | Maniknagar | 235 | 05:00 | 224 | 14:00
| Bhulta | 237 | 05:00 | 227 | 12:00 | Meghnaghat | 241 | 18:30 | 232 | 10:00
| Bibiana | 239 | 19:30 | 233 | 08:00 | Mirsorai | 240 | 18:30 | 229 | 14:00
| BIPTC | 239 | 22:00 | 225 | 12:00 | Rajshahi | 241 | 22:00 | 228 | 12:00
| Bogura | 234 | 19:00 | 226 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 04:00 | 245 | 00:00 | Rampura | 234 | 20:00 | 225 | 12:00
| BSRM | 241 | 19:00 | 230 | 14:00 | Shikalbaha | 243 | 18:00 | 231 | 15:00
| Cumilla(N) | 238 | 22:00 | 228 | 12:00 | Shyampur | 235 | 19:00 | 226 | 12:00
| Fenchuganj | 241 | 19:00 | 237 | 10:00 | Siddhirganj | 237 | 02:00 | 228 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 234 | 19:00 | 228 | 12:00
| GPH | 241 | 22:00 | 230 | 14:00 | Tongi | 230 | 18:30 | 220 | 15:00
| Haripur | 234 | 22:00 | 226 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 04:00 | 129 | 12:00 | Kushtia | 138 | 22:00 | 129 | 12:00
| Agargaon | 138 | 05:00 | 131 | 11:00 | Lalbag | 137 | 05:00 | 131 | 10:00
| Agrabad | 140 | 00:00 | 131 | 14:00 | Lalmonirhat | 132 | 18:30 | 125 | 00:00
| AKS | 138 | 00:00 | 132 | 05:00 | Madanganj | 136 | 18:30 | 128 | 13:00
| Aminbazar | 139 | 18:30 | 132 | 09:00 | Madaripur | 137 | 18:00 | 133 | 11:00
| Amnura | 137 | 19:00 | 129 | 04:00 | Madartek | 137 | 05:00 | 129 | 13:00
| Ashuganj | 139 | 19:00 | 135 | 15:00 | Madunaghat | 141 | 00:00 | 136 | 08:00
| Bagerhat | 138 | 19:30 | 125 | 12:00 | Magura | 137 | 03:00 | 126 | 12:00
| Bakulia | 141 | 00:00 | 135 | 11:00 | Mahasthangarh | 137 | 19:00 | 130 | 12:00
| Banani | 135 | 01:00 | 128 | 16:00 | Manikganj | 133 | 05:00 | 123 | 16:00
| Bangabhaban | 136 | 05:00 | 129 | 12:00 | Maniknagar | 135 | 03:00 | 129 | 11:00
| Barapukuria | 137 | 19:00 | 128 | 07:00 | Matarbari | 136 | 00:00 | 123 | 14:00
| Barguna | 138 | 22:00 | 129 | 00:00 | Matuail | 139 | 19:00 | 130 | 12:00
| Barishal | 138 | 02:00 | 136 | 00:00 | Millgate | 137 | 04:00 | 128 | 16:00
| Barishal-230 | 139 | 05:00 | 136 | 00:00 | Mirpur | 138 | 20:00 | 131 | 10:00
| Baroaulia | 142 | 18:30 | 132 | 14:00 | Mithapukur | 136 | 19:00 | 126 | 07:00
| Baroirhat | 142 | 19:00 | 133 | 15:00 | Modern | 140 | 00:00 | 135 | 08:00
| Bashundhara | 137 | 04:00 | 128 | 10:00 | Mogbazar | 137 | 04:00 | 130 | 12:00
| BashundharaCement | 136 | 16:00 | 129 | 11:00 | Mongla | 138 | 19:00 | 124 | 12:00
| Beanibazar | 134 | 02:00 | 132 | 10:00 | Motijheel | 136 | 05:00 | 129 | 12:00
| Benapole | 135 | 02:00 | 124 | 13:00 | Munshiganj | 137 | 19:00 | 130 | 11:00
| Bhaluka | 127 | 00:00 | 116 | 06:00 | Mymensingh | 135 | 12:00 | 116 | 08:00
| Bhandaria | 138 | 04:00 | 136 | 00:00 | Naogaon | 132 | 18:00 | 126 | 12:00
| Bhangura | 141 | 19:00 | 134 | 12:00 | Narail | 136 | 04:00 | 125 | 13:00
| Bheramara | 139 | 22:00 | 129 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 137 | 03:00 | 131 | 12:00 | Narshingdi | 135 | 05:00 | 126 | 10:00
| Bhulta | 130 | 18:00 | 123 | 10:00 | Natore | 137 | 19:30 | 130 | 12:00
| Bog-Sherpur | 138 | 19:00 | 132 | 11:00 | Nawabganj | 137 | 05:00 | 130 | 11:00
| Bogura | 138 | 19:00 | 131 | 14:00 | Netrakona | 128 | 00:00 | 116 | 21:00
| Bogura-230 | 138 | 19:00 | 132 | 01:00 | New | 138 | 05:00 | 129 | 16:00
| Brahmanbaria | 134 | 00:00 | 131 | 10:00 | Niamatpur | 130 | 18:00 | 123 | 06:00
| Cantonment | 138 | 05:00 | 131 | 11:00 | Noapara | 137 | 02:00 | 126 | 12:00
| Chandpur | 141 | 18:30 | 132 | 14:00 | Pabna | 139 | 22:00 | 131 | 12:00
| Chandraghona | 142 | 18:30 | 136 | 14:00 | Palashbari | 134 | 19:00 | 124 | 06:00
| Chapai | 137 | 22:00 | 129 | 12:00 | Panchagarh | 137 | 19:00 | 121 | 00:00
| Charsaidpur | 137 | 05:00 | 129 | 13:00 | Patuakhali | 136 | 21:00 | 126 | 05:00
| Chauddagram | 140 | 18:00 | 134 | 08:00 | Payra | 133 | 19:30 | 128 | 12:00
| Chhatak | 133 | 01:00 | 131 | 10:00 | PHP | 141 | 19:00 | 133 | 14:00
| Chowmuhani | 139 | 18:30 | 132 | 08:00 | Postogola | 137 | 19:30 | 130 | 10:00
| Chuadanga | 139 | 03:00 | 124 | 12:00 | Purbachal | 137 | 04:00 | 128 | 16:00
| Coxsbazar | 135 | 00:00 | 122 | 14:00 | Purbasadipur | 136 | 19:00 | 121 | 00:00
| Cumilla(N) | 141 | 18:00 | 135 | 11:00 | Rahim | 137 | 23:00 | 124 | 17:00
| Cumilla(S) | 140 | 19:00 | 126 | 18:00 | Rajbari | 136 | 04:00 | 130 | 12:00
| Daudkandi | 138 | 18:30 | 130 | 13:00 | Rajendrapur | 136 | 19:00 | 128 | 17:00
| Dhaka | 137 | 04:00 | 130 | 11:00 | Rajshahi | 136 | 22:00 | 129 | 12:00
| Dhamrai | 137 | 05:00 | 130 | 11:00 | Rajshahi-230 | 134 | 23:00 | 128 | 12:00
| Dhanmondi | 138 | 05:00 | 130 | 10:00 | Ramganj | 138 | 17:00 | 130 | 13:00
| Dohazari | 139 | 18:30 | 131 | 23:00 | Rampur | 140 | 19:00 | 131 | 15:00
| Faridpur | 136 | 19:00 | 131 | 12:00 | Rampura | 135 | 03:00 | 129 | 12:00
| Fatullah | 137 | 19:00 | 130 | 11:00 | Rangamati | 141 | 00:00 | 134 | 14:00
| Fenchuganj | 137 | 00:00 | 135 | 03:00 | Rangpur | 133 | 18:30 | 123 | 07:00
| Feni | 142 | 19:00 | 134 | 12:00 | Ruppur | 137 | 04:00 | 132 | 12:00
| Ghorashal | 140 | 00:00 | 135 | 19:30 | Saidpur | 136 | 19:00 | 124 | 00:00
| Goalpara | 139 | 02:00 | 128 | 12:00 | Satkhira | 139 | 05:00 | 126 | 12:00
| Gollamari | 139 | 19:00 | 132 | 00:00 | Satmasjid | 137 | 05:00 | 131 | 13:00
| Gopalganj | 139 | 19:00 | 132 | 11:00 | Savar | 140 | 19:30 | 130 | 10:00
| Gopalganj-400 | 136 | 03:00 | 132 | 10:00 | Shahjadpur | 145 | 19:30 | 138 | 12:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 135 | 00:00 | 133 | 10:00
| Gulshan | 136 | 05:00 | 130 | 10:00 | Shahmirpur | 140 | 18:30 | 133 | 14:00
| Halishahar | 140 | 00:00 | 131 | 14:00 | Shariatpur | 137 | 19:00 | 132 | 01:00
| Haripur | 136 | 01:00 | 131 | 10:00 | Sherpur | 138 | 12:00 | 128 | 17:00
| HaripurSBU | 138 | 22:00 | 132 | 13:00 | Shikalbaha | 140 | 00:00 | 127 | 09:00
| Hasnabad | 136 | 00:00 | 130 | 11:00 | Shikalbaha-230 | 140 | 18:00 | 102 | 02:00
| Hathazari | 142 | 00:00 | 137 | 06:00 | Shitalakhya | 136 | 01:00 | 129 | 13:00
| Ishurdi | 139 | 19:30 | 132 | 12:00 | Sholosohor | 141 | 18:00 | 134 | 14:00
| Jaldhaka | 135 | 19:00 | 121 | 07:00 | Shyampur | 136 | 22:00 | 131 | 11:00
| Jamalpur | 139 | 12:00 | 114 | 23:00 | Shyampur-230 | 136 | 02:00 | 130 | 12:00
| Jashore | 137 | 14:00 | 125 | 12:00 | Siddhirganj | 136 | 16:00 | 130 | 12:00
| Jhenaidah | 138 | 04:00 | 128 | 12:00 | Sirajganj | 138 | 19:30 | 132 | 07:00
| Jhenaidah-230 | 139 | 05:00 | 129 | 12:00 | Sonargaon | 136 | 19:00 | 129 | 12:00
| Joydebpur | 142 | 18:30 | 136 | 15:00 | Sreemongol | 134 | 00:00 | 132 | 11:00
| Joypurhat | 132 | 19:00 | 125 | 17:00 | Srinagar | 137 | 05:00 | 130 | 11:00
| Juldah | 140 | 18:30 | 129 | 14:00 | SSM | 142 | 19:00 | 130 | 14:00
| Kabirpur | 139 | 22:00 | 127 | 16:00 | Sunamganj | 132 | 05:00 | 129 | 12:00
| Kachua | 139 | 17:00 | 131 | 14:00 | Sylhet | 133 | 00:00 | 132 | 09:00
| Kaliakoir | N/A | N/A | N/A | N/A | Tangail | 135 | 12:00 | 125 | 16:00
| Kallyanpur | 138 | 22:00 | 132 | 10:00 | Thakurgaon | 138 | 19:00 | 119 | 00:00
| Kalurghat | 141 | 00:00 | 134 | 14:00 | TK | 141 | 18:00 | 133 | 14:00
| Kamrangirchar | 136 | 22:00 | 130 | 11:00 | Tongi | 135 | 04:00 | 131 | 09:00
| Kaptai | 140 | 00:00 | 136 | 07:00 | Ullon | 136 | 01:00 | 130 | 13:00
| Kazla | 135 | 02:00 | 128 | 13:00 | Uttara | 136 | 03:00 | 128 | 11:00
| Keranigonj | 136 | 05:00 | 130 | 13:00 | UttaraNew | 137 | 04:00 | 129 | 10:00
| Khagrachori | 140 | 00:00 | 135 | 07:00 | Zigatola | 136 | 06:00 | 130 | 11:00
| Khulna | 139 | 04:00 | 128 | 12:00
| Khulna(S) | 140 | 04:00 | 129 | 12:00
| Khulshi | 139 | 00:00 | 132 | 14:00
| Kishoreganj | 132 | 00:00 | 121 | 08:00
| Kodda | 141 | 02:00 | 129 | 17:00
| KSRM | 142 | 18:00 | 135 | 14:00
| Kulaura | 136 | 00:00 | 135 | 08:00
| Kurigram | 132 | 19:00 | 121 | 06:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-02-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 820 | 5019 | 3505 | 8524 |  |  |  | QF-LDC-11
0:30 | 930 | 4917.5 | 3434.5 | 8352 | Date: | 2023-02-13
1:00 | 1040 | 4816 | 3364 | 8180
1:30 | 972 | 4727 | 3279.5 | 8006.5
2:00 | 904 | 4638 | 3195 | 7833
2:30 | 902 | 4586.5 | 3132 | 7718.5 | [5 empty] | Gen. at Eve. Peak | 10383 | 10383 MW (20:00 )
3:00 | 900 | 4535 | 3069 | 7604 | [6 empty] | 20:00
3:30 | 881 | 4461 | 3048 | 7509 | [5 empty] | Gen. at Day Peak | 8953 | 8953 MW (12:00 )
4:00 | 862 | 4387 | 3027 | 7414 | [6 empty] | 12:00
4:30 | 841 | 4387 | 3005.5 | 7392.5 | [5 empty] | Highest Generation | 10383
5:00 | 820 | 4387 | 2984 | 7371 | [6 empty] | 20:00
5:30 | 810 | 4492 | 3020.5 | 7512.5
6:00 | 800 | 4597 | 3057 | 7654
6:30 | 793 | 4615.5 | 3164 | 7779.5
7:00 | 786 | 4634 | 3271 | 7905
7:30 | 843 | 4693.5 | 3293 | 7986.5
8:00 | 900 | 4753 | 3315 | 8068
8:30 | 1008 | 4828 | 3322 | 8150
9:00 | 1116 | 4903 | 3329 | 8232
9:30 | 1085 | 4901.5 | 3389 | 8290.5
10:00 | 1054 | 4900 | 3449 | 8349
10:30 | 1070 | 4984 | 3512.5 | 8496.5
11:00 | 1086 | 5068 | 3576 | 8644
11:30 | 1076 | 5170 | 3628.5 | 8798.5
12:00 | 1066 | 5272 | 3681 | 8953
12:30 | 1099 | 5343.5 | 3751.5 | 9095
13:00 | 1132 | 5415 | 3822 | 9237
13:30 | 1201 | 5337.5 | 3779.5 | 9117
14:00 | 1270 | 5260 | 3737 | 8997
14:30 | 1252 | 5264.5 | 3701.5 | 8966
15:00 | 1234 | 5269 | 3666 | 8935
15:30 | 1102 | 5281 | 3654 | 8935
16:00 | 970 | 5293 | 3642 | 8935
16:30 | 900 | 5386 | 3546.5 | 8932.5
17:00 | 830 | 5479 | 3451 | 8930
17:30 | 810 | 5698.5 | 3584 | 9282.5
18:00 | 790 | 5918 | 3717 | 9635
18:30 | 702 | 6127.5 | 3755.5 | 9883
19:00 | 614 | 6337 | 3794 | 10131
19:30 | 398 | 6387 | 3900 | 10287
20:00 | 216 | 6453 | 3930 | 10383 |  |  |  | Executive Engineer
20:30 | 286 | 6369.5 | 3982.5 | 10352 |  |  |  | Network Operation Division
21:00 | 356 | 6286 | 4035 | 10321
21:30 | 470 | 6079.5 | 3974.5 | 10054
22:00 | 584 | 5873 | 3914 | 9787 |  |  |  |  | Page 6 of 7
22:30 | 744 | 5614 | 3880 | 9494
23:00 | 904 | 5355 | 3846 | 9201
23:30 | 862 | 5187 | 3675.5 | 8862.5
24:00 | 820 | 5019 | 3505 | 8524
10383 MW (20:00 )
8953 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-02-13 |  | Energy |  | 212490827
[13 empty] | 2023-02-13 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3079 | 772 | 1679 | 0 | 1237 | 1510 | 60 | 0 | 83 | 104 | 0 | 0
0:30 | 2995.5 | 837 | 1665 | 0 | 1024 | 1540 | 45 | 0 | 141.5 | 104 | 0 | 0 | Date: | 2023-02-13
1:00 | 2912 | 902 | 1651 | 0 | 811 | 1570 | 30 | 0 | 200 | 104 | 0 | 0
1:30 | 2901 | 826.5 | 1636.5 | 0 | 807 | 1556.5 | 30 | 0 | 144 | 105 | 0 | 0 | [7 empty] | Total Energy | 212.4908 | Total Energy Gen 212.491 MKWHr Energy Not Served 8.784 MKWHr Energy Requirement 221.274 MKWHr
2:00 | 2890 | 751 | 1622 | 0 | 803 | 1543 | 30 | 0 | 88 | 106 | 0 | 0 | [7 empty] | Energy not Served | 8.7836
2:30 | 2910.5 | 751 | 1592 | 0 | 778 | 1501 | 30 | 0 | 52 | 104 | 0 | 0 | [7 empty] | Energy Requirement | 221.2745
3:00 | 2931 | 751 | 1562 | 0 | 753 | 1459 | 30 | 0 | 16 | 102 | 0 | 0
3:30 | 2876.5 | 751 | 1539.5 | 0 | 735.5 | 1458.5 | 30 | 0 | 16 | 102 | 0 | 0 | [5 empty] | Shortage
4:00 | 2822 | 751 | 1517 | 0 | 718 | 1458 | 30 | 0 | 16 | 102 | 0 | 0
4:30 | 2816 | 751 | 1503.5 | 0 | 717.5 | 1458.5 | 30 | 0 | 16 | 100 | 0 | 0
5:00 | 2810 | 751 | 1490 | 0 | 717 | 1459 | 30 | 0 | 16 | 98 | 0 | 0
5:30 | 2875 | 684 | 1547.5 | 0 | 753.5 | 1505.5 | 30 | 0 | 16 | 101 | 0 | 0
6:00 | 2940 | 617 | 1605 | 0 | 790 | 1552 | 30 | 0 | 16 | 104 | 0 | 0
6:30 | 2926 | 602.5 | 1657 | 0 | 851 | 1581.5 | 30 | 0 | 18 | 107 | 6.5 | 274.1686 |  |  |  | Coal
7:00 | 2912 | 588 | 1709 | 0 | 912 | 1611 | 30 | 0 | 20 | 110 | 13 | 548.3371
7:30 | 2918 | 566 | 1717 | 0 | 920.5 | 1610.5 | 30 | 0 | 50.5 | 113 | 61 | 749.7013 |  |  | Oil |  |  |  | ,
8:00 | 2924 | 544 | 1725 | 0 | 929 | 1610 | 30 | 0 | 81 | 116 | 109 | 951.0654
8:30 | 2924.5 | 544 | 1720.5 | 0 | 981 | 1568.5 | 30 | 0 | 100 | 117 | 164.5 | 967.6537
9:00 | 2925 | 544 | 1716 | 0 | 1033 | 1527 | 30 | 0 | 119 | 118 | 220 | 984.2421
9:30 | 2892.5 | 576 | 1690.5 | 0 | 1061 | 1518.5 | 30 | 0 | 135.5 | 117 | 269.5 | 999.4481
10:00 | 2860 | 608 | 1665 | 0 | 1089 | 1510 | 30 | 0 | 152 | 116 | 319 | 1014.6541
10:30 | 2851.5 | 608 | 1672 | 0 | 1172 | 1510 | 30 | 0 | 179.5 | 120 | 353.5 | 993.9186
11:00 | 2843 | 608 | 1679 | 0 | 1255 | 1510 | 30 | 0 | 207 | 124 | 388 | 973.1832
11:30 | 2857 | 643.5 | 1694 | 0 | 1310 | 1510 | 45 | 0 | 218 | 121 | 400 | 945.9967
12:00 | 2871 | 679 | 1709 | 0 | 1365 | 1510 | 60 | 0 | 229 | 118 | 412 | 918.8103
12:30 | 2866 | 725.5 | 1702.5 | 0 | 1428.5 | 1510 | 60 | 0 | 276 | 122 | 404.5 | 676.8968
13:00 | 2861 | 772 | 1696 | 0 | 1492 | 1510 | 60 | 0 | 323 | 126 | 397 | 434.9834
13:30 | 2861 | 772 | 1696 | 0 | 1492 | 1510 | 60 | 0 | 323 | 126 | 397 | 434.9834
14:00 | 2861 | 772 | 1696 | 0 | 1492 | 1510 | 60 | 0 | 323 | 126 | 397 | 434.9834
14:30 | 2846 | 772.5 | 1692.5 | 0 | 1435 | 1495.5 | 60 | 0 | 322.5 | 126 | 336 | 577.3667
15:00 | 2831 | 773 | 1689 | 0 | 1378 | 1481 | 60 | 0 | 322 | 126 | 275 | 719.7501
15:30 | 2853.5 | 772 | 1676.5 | 0 | 1406.5 | 1481 | 60 | 0 | 343 | 124 | 218.5 | 624.8278
16:00 | 2876 | 771 | 1664 | 0 | 1435 | 1481 | 60 | 0 | 364 | 122 | 162 | 529.9056
16:30 | 2872 | 689.5 | 1675 | 0 | 1560.5 | 1486.5 | 60 | 0 | 364 | 121 | 104 | 550.1803
17:00 | 2868 | 608 | 1686 | 0 | 1686 | 1492 | 60 | 0 | 364 | 120 | 46 | 570.4549
17:30 | 2859 | 608 | 1681 | 0 | 2008 | 1485.5 | 60 | 0 | 432 | 126 | 23 | 568.7275
18:00 | 2850 | 608 | 1676 | 0 | 2330 | 1479 | 60 | 0 | 500 | 132 | 0 | 567
18:30 | 2880 | 538.5 | 1694 | 0 | 2523 | 1529 | 60 | 0 | 525.5 | 133 | 0 | 499.6093
19:00 | 2910 | 469 | 1712 | 0 | 2716 | 1579 | 60 | 0 | 551 | 134 | 0 | 432.2187
19:30 | 2963 | 469 | 1708 | 0 | 2767 | 1662 | 60 | 0 | 532 | 126 | 0 | 238.6879
20:00 | 3006 | 469 | 1727 | 0 | 2791 | 1661 | 60 | 0 | 545 | 124 | 0 | 45.1572
20:30 | 3023 | 538.5 | 1732 | 0 | 2687 | 1671 | 60 | 0 | 517.5 | 123 | 0 | 35.0198
21:00 | 3040 | 608 | 1737 | 0 | 2583 | 1681 | 60 | 0 | 490 | 122 | 0 | 24.8825
21:30 | 2984 | 651 | 1663 | 0 | 2474.5 | 1620.5 | 60 | 0 | 482 | 119 | 0 | 12.4413
22:00 | 2928 | 694 | 1589 | 0 | 2366 | 1560 | 60 | 0 | 474 | 116 | 0 | 0
22:30 | 2986.5 | 733 | 1630.5 | 0 | 1985.5 | 1534.5 | 60 | 0 | 449.5 | 114.5 | 0 | 0
23:00 | 3045 | 772 | 1672 | 0 | 1605 | 1509 | 60 | 0 | 425 | 113 | 0 | 0
23:30 | 3062 | 772 | 1675.5 | 0 | 1421 | 1509.5 | 60 | 0 | 254 | 108.5 | 0 | 0 | Max Temp. in Dhaka |  | 28.0° C
24:00 | 3079 | 772 | 1679 | 0 | 1237 | 1510 | 60 | 0 | 83 | 104 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 212.491 MKWHr Energy Not Served 8.784 MKWHr Energy Requirement 221.274 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-02-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 724500
2 | Karnaphuli Hydro PP Unit-4 & 5 | [11 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 384000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 263433
| Teknaf 20MW PP (Solartech) | [8 empty] | 11 | 16 | 18 | 20 | 19 | 18 | 13 | 8 | 2 | [9 empty] | 119340
6 | Sikalbaha 225MW CCPP (Gas) | 107 | 85 | 75 | 40 | 20 | 20 | 21 | 85 | 136 | 154 | 151 | 151 | 151 | 150 | 151 | 151 | 151 | 151 |  | 151 | 150 | 151 | 151 | 151 | 151 | 151 | 2714690
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 60 | 0 | [9 empty] | 51 | 51 | 56 | 84 | 85 | 80 |  | 85 | 70 | 81 | 85 | 85 | 74 | 0 | 969996
12 | Hathazari 100 MW peaking PP | 68 | 12 | 0 |  |  |  | 4 | 40 | 40 | 40 | 46 | 40 | 40 | 40 | 37 | 37 | 36 | 54 |  | 65 | 65 | 65 | 70 | 70 | 70 |  | 923376
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 50 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 961814
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 31 | 0 | [5 empty] | 18 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 |  | 579248
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 60 | 61 | 61 | 61 | 61 | 62 | 61 | [19 empty] | 444109
18 | Kodda 300 MW PP Unit-2 (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 32 | 32 | 37 | 65 | 65 | 32 | 32 | 32 | 48 | 99 |  | 99 | 98 | 99 | 98 | 98 | 67 | 37 | 1196836
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 150 | 150 | 200 | 200 | 200 | 200 | 160 | 160 | 160 | 160 | 160 | 160 | 161 | 160 | 160 |  | 153 | 160 | 130 | 130 | 130 | 130 | 130 | 3998844
23 | Ghorasal TPP Unit-5 | [17 empty] | 25 |  | 35 | 40 | 70 | 80 | 110 | 110 | 110 | 472500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 277776
33 | Ashuganj 225 MW CCPP | 211 | 212 | 216 | 220 | 224 | 222 | 215 | 206 | 195 | 197 | 190 | 188 | 186 | 160 | 203 | 214 | 205 | 211 |  | 207 | 205 | 195 | 208 | 215 | 219 | 219 | 4980000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 295 | 295 | 315 | 295 | 295 | 305 | 290 | 295 | 295 | 330 | 290 | 290 | 290 | 295 | 295 | 295 | 295 | 295 |  | 295 | 295 | 325 | 290 | 285 | 285 | 285 | 7641300
| Ashuganj 420 MW CCPP(East) | 273 | 288 | 288 | 280 | 281 | 330 | 300 | 300 | 269 | 281 | 280 | 270 | 270 | 270 | 220 | 250 | 250 | 260 |  | 280 | 290 | 280 | 280 | 290 | 300 | 310 | 6704300
35 | Ashuganj 55 MW PP (Precision) | [26 empty] | 0
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4717900
41 | Haripur 360MW CCPP(HPL) | 152 | 149 | 153 | 142 | 145 | 145 | 143 | 198 | 215 | 222 | 217 | 246 | 250 | 248 | 256 | 256 | 253 | 255 |  | 256 | 256 | 252 | 251 | 256 | 256 | 250 | 5104000
42 | RPCL 210MW CCPP | 103 | 104 | 104 | 104 | 104 | 110 | 48 | 47 | 44 | 32 | 32 | 31 | 32 | 32 | 32 | 34 | 34 | 34 |  | 55 | 64 | 70 | 104 | 102 | 104 | 103 | 1545600
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 16 | 30 | 42 | 49 | 51 | 50 | 45 | 34 | 20 | 5 | 0 | [8 empty] | 345080
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 1019000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 985920
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 63 | 63 | 63 | 62 | 62 | 61 | 61 | 60 | 61 | 61 | 40 | 61 | 61 | 61 | 63 |  | 63 | 63 | 62 | 63 | 40 | 40 | 40 | 1406400
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 10 | 10 | 10 | 40 | 86 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 86 |  | 86 | 86 | 86 | 86 | 40 | 40 | 40 | 1326720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 213 | 213 | 213 | 215 | 213 | 213 | 213 | 213 | 213 | 215 | 215 | 214 | 213 | 212 | 212 | 212 | 214 | 210 |  | 210 | 210 | 218 | 218 | 217 | 216 | 216 | 5290350
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 444000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 0 | 6 | 6 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 202320
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 177504
55 | Fenchugonj 51 MW PP (Barakatullah) | 31 | 22 | 11 | 11 | 11 | 11 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 51 | 51 | 51 | 51 | 31 | 31 | 31 | 626400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190992
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 295 | 290 | 280 | 290 | 310 | 290 | 310 | 290 | 310 | 300 | 300 | 270 | 305 | 280 | 300 | 270 |  | 270 | 260 | 280 | 290 | 270 | 290 | 290 | 7149500
| Bibiyana South 400 MW | 250 | 235 | 275 | 290 | 320 | 330 | 400 | 400 | 400 | 360 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 360 |  | 380 | 380 | 400 | 400 | 330 | 400 | 400 | 8688200
58 | Nababganj 55 MW PP (Southern power ) |  |  |  |  | 0 | 17 | 17 | 17 | [7 empty] | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 299136
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 5 | 4 | 145920
60 | Barabkunda 22 MW PP (Regent) | [19 empty] | 0 | 0 | 0
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 355644
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 16 | 16 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 14 | 14 | 14 | 14 | 344232
63 | Impoprt (Tripura) | 104 | 106 | 102 | 102 | 98 | 104 | 110 | 116 | 118 | 116 | 124 | 118 | 126 | 130 | 126 | 122 | 120 | 132 |  | 134 | 126 | 124 | 122 | 116 | 113 | 104 | 2768640
64 | Malancha, Ctg. EPZ (United) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5760
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 21 | 21 | 19 | 21 | 21 | 21 |  | 21 | 22 | 19 | 22 | 22 | 22 | 22 | 494964
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 179280
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 18 | 14 | 13 | 13 | 13 | 13 | 7 | 8 | 8 | 12 | 12 | 12 |  | 16 | 16 | 16 | 19 | 23 | 24 | 33 | 478100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 496650
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 |  | 25 | 25 | 25 | 25 | 26 | 26 | 26 | 588960
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 815100
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 24 | 545100
73 | Ghorashal 108MW PP (Regent) | 81 | 81 | 81 | 42 | 42 | 78 | 81 | 81 | 78 | 78 | 78 | 81 | 81 | 81 | 81 | 81 | 81 | 81 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1647636
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 114 | 114 |  | 114 | 114 | 114 | 17 | 17 | 17 | 17 | 839040
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 221760
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 92 | 126 | 127 | 86 | 17 | 17 | 17 | 771840
77 | Siddhirganj 100 PP(Dutch Bangla) | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 28 | 17 | 17 | 705600
78 | Gazipur 52 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 41 |  | 41 | 41 | 42 | 43 | 43 | 25 |  | 710400
79 | Kodda 150MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 32 | 32 | 32 | 32 | 48 |  | 64 | 64 | 64 | 32 | 16 | 16 |  | 760320
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [10 empty] | 7 |  | 9 | 16 | 16 | 8 | 8 | 8 | 8 | 128966
| Gazipur 100 MW PP | 52 | 52 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 52 | 52 | 52 | 35 | 35 | 35 | 35 | 35 | 70 |  | 70 | 88 | 88 | 88 | 88 | 35 | 35 | 1183200
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 0 | 1 | 3 | 4 | 4 | 4 | 3 | 3 | 1 | 0 | [9 empty] | 24000
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 452552
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 63 | 74 | 88 |  | 92 | 92 | 92 | 92 | 92 | 92 | 66 | 1597448
82 | Madanganj 102 PP(Summit) | 34 | 34 | 34 | 34 | 34 | 22 | 34 | 34 | 34 | 34 | 34 | 34 | 24 | 2 | 26 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 22 |  |  | 625954
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 120 | 112 | 112 | 112 | 111 | 112 | 112 | 142 | 142 | 142 | 142 | 150 | 150 | 150 | 150 | 150 | 150 | 155 |  | 155 | 155 | 150 | 150 | 150 | 150 | 150 | 3259142
87 | Meghnaghat 100 MW(IEL) | 17 | 17 | 18 | 17 | 18 | 17 | 17 | 17 | 15 | 17 | 18 | 30 | 45 | 50 | 50 | 49 | 46 | 45 |  | 50 | 50 | 50 | 50 | 24 | 17 | 17 | 699840
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 25 | 36 |  | 55 | 55 | 54 | 54 | 55 | 33 | 18 | 617280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 530160
92 | Fenchuganj 44MW (Energyprima) | 50 | 50 | 40 | 40 | 40 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 46 | 46 | 46 | 46 | 46 | 49 |  | 49 | 49 | 49 | 50 | 50 | 50 | 30 | 1129320
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1013121
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 24 | 32 | 32 | 32 | 42 |  | 50 | 50 | 50 | 50 | 16 | 16 | 16 | 507744
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 469920
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 25 | 11 | 15 | 15 | 15 | 15 | 15 | 392910
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 35 |  | 55 | 55 | 55 | 35 | 35 | 17 |  | 306153
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 | 112 | 112 | 112 | 80 |  | 112 | 112 | 112 | 112 | 80 | 80 | 112 | 2674063
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15800
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 17 |  | 35 | 35 | 35 | 17 | 17 |  |  | 161640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 18 | 37 | 65 | 115 | 121 | 9 | 9 | 9 | 28 |  | 74 | 74 | 74 | 74 | 74 | 9 | 9 | 828000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 35 | 36 | 35 | 35 | 35 | 35 | 36 |  | 70 | 72 | 72 | 72 | 72 | 36 | 17 | 813744
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 605760
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 840960
117 | Ashuganj 150MW PP (Midland) | 6 | 5 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 33 | 75 | 103 | 112 | 113 | 115 | 127 |  | 133 | 135 | 132 | 135 | 135 | 85 | 73 | 1446909
118 | Bibiyana-III 400 MW CCPP | 406 | 405 | 406 | 405 | 405 | 405 | 405 | 405 | 405 | 377 | 375 | 400 | 400 | 374 | 407 | 407 | 407 | 385 |  | 405 | 405 | 406 | 405 | 355 | 403 | 405 | 9573000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 115 | 115 | 115 | 115 | 115 | 48 | 48 | 48 |  | 77 | 78 | 78 | 79 | 79 | 49 | 49 | 1660800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 100 | 116 | 116 | 100 | 100 | 100 | 100 | 100 | 285 |  | 285 | 285 | 285 | 285 | 268 | 16 | 16 | 2438836
| Juldah unit-2 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 596160
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 95 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 87 | 100 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2541709
| Bhairob 54.5 MW | [7 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 314640
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 11 | 10 | 20 | 31 | 33 | 32 | 29 | 22 | 13 | 4 | [9 empty] | 207890
| Chandpur 115(Doreen) | 17 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 25 | 39 | 61 |  | 71 | 72 | 73 | 72 | 72 | 72 | 67 | 826560
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 433080
| Mirsharai 150 MW (Oil) | [26 empty] | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4816 | 4638 | 4535 | 4387 | 4387 | 4597 | 4634 | 4753 | 4903 | 4900 | 5068 | 5272 | 5415 | 5260 | 5269 | 5293 | 5479 | 5918 |  | 6337 | 6387 | 6453 | 6286 | 5873 | 5355 | 5019 | 125412745
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [17 empty] | 16 |  | 33 | 33 | 33 | 33 | 33 | 16 |  | 184320
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 38 |  | 44 | 38 | 38 | 38 | 38 |  |  | 194400
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) |  |  |  |  | 0 | 8 | 17 | [5 empty] | 17 | 26 | 37 | 37 | 46 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 578400
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 3 | 25 | 51 | 75 | 88 | 95 | 92 | 82 | 62 | 36 | 11 | [9 empty] | 626400
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [7 empty] | 11 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 100 |  | 150 | 150 | 150 | 150 | 150 | 150 | 88 | 1160400
133 | Bhola Nutan Biddut BD LTD (GAS) | 107 | 107 | 107 | 107 | 108 | 107 | 109 | 109 | 108 | 106 | 108 | 108 | 106 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 108 | 107 | 2587500
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 246624
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 248 | 251 | 249 | 248 | 249 | 252 | 269 | 268 | 255 | 238 | 238 | 238 | 238 | 211 | 208 | 208 | 209 | 208 |  | 208 | 209 | 208 | 208 | 189 | 189 | 190 | 5541800
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 188 | 187 | 173 | 173 | 173 | 173 | 175 | 193 | 193 | 186 | 188 | 188 | 188 | 188 | 184 | 185 | 188 | 189 |  | 171 | 190 | 190 | 191 | 182 | 190 | 183 | 4490642
140 | Bhola 33 MW PP (Venture) | 19 | 18 | 15 | 15 | 15 | 17 | 17 | 16 | 16 | 15 | 15 | 16 | 18 | 16 | 14 | 12 | 14 | 18 |  | 21 | 21 | 21 | 22 | 21 | 20 | 19 | 409500
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [15 empty] | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 |  |  | 104625
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 30 |  | 30 | 30 | 30 |  |  |  |  | 100608
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [7 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 |  | 50 | 50 | 50 | 32 | 15 | 15 |  | 390960
146 | Bheramara HVDC | 902 | 751 | 751 | 751 | 751 | 617 | 588 | 544 | 544 | 608 | 608 | 679 | 772 | 772 | 773 | 771 | 608 | 608 |  | 469 | 469 | 469 | 608 | 694 | 772 | 772 | 16439272
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1122 | 1092 | 1010 | 1010 | 1010 | 1050 | 1092 | 1092 | 1022 | 1022 | 1022 | 1022 | 1022 | 1022 | 1022 | 1022 | 1032 | 1020 |  | 1120 | 1202 | 1202 | 1222 | 1120 | 1120 | 1120 | 27647900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 251 | 251 | 251 |  | 251 | 251 | 251 | 251 | 251 | 200 | 200 | 5685500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 |  | 379902
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 2 | 0 | [9 empty] | 39540
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 183 | 182 | 182 | 165 | 140 | 145 | 191 | 192 | 192 | 192 | 188 | 186 | 182 | 177 | 176 | 173 | 171 | 172 |  | 168 | 169 | 170 | 174 | 170 | 152 | 174 | 4431709
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 296 | 308 | 319 | 329 | 309 | 336 | 360 | 338 | 319 | 304 | 294 | 284 | 279 | 271 | 254 | 256 | 257 | 249 |  | 249 | 255 | 262 | 261 | 227 | 289 | 290 | 6982800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [10 empty] | 4 | 5 | 6 | 15 | 18 | 26 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 32 |  | 259748
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 3 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 |  | 20 | 20 | 21 | 21 | 21 | 22 | 22 | 444480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 223236
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) |  |  |  |  | 0 | 8 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 8 | 8 | 42 | 42 | 42 |  | 50 | 50 | 50 | 42 | 42 | 42 |  | 655526
167 | Katakhali 50 MW Peaking PP | [7 empty] | 7 | 16 | 24 | 28 | 43 | 40 | 40 | 40 | 40 | 39 | 40 |  | 40 | 40 | 41 | 40 | 40 | 40 |  | 506944
168 | Santahar 50 MW Peaking PP | [11 empty] | 12 | 23 | 23 | 24 | 30 | 23 | 22 |  | 22 | 23 | 23 | 23 | 23 | 23 |  | 241837
169 | Natore 52 MW PP (Rajlanka) | [26 empty] | 0
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 84 |  | 97 | 97 | 98 | 97 | 97 | 98 | 83 | 982592
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 |  |  |  |  | 0 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 70 | 70 | 70 | 70 | 35 | 1126368
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 0 |  | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 55 |  | 75 | 75 | 75 | 75 | 75 | 35 | 35 | 916032
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 35 | 35 | 34 | 0 |  |  | 34 | 40 | 42 | 35 | 42 | 42 | 50 | 49 | 49 | 68 | 85 | 92 |  | 92 | 93 | 93 | 92 | 71 | 34 | 34 | 1129392
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 1 | [9 empty] | 34837
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 110 |  | 113 | 113 | 113 | 113 | 113 | 113 | 90 | 1038528
| Intraco Solar 30 MW | [6 empty] | 1 | 8 | 19 | 28 | 33 | 34 | 33 | 29 | 23 | 13 | 4 | 0 | [8 empty] | 223040
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 6 | 46 | 91 | 125 | 153 | 162 | 155 | 141 | 108 | 65 | 19 | [9 empty] | 1072720