## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-04-01 | Saturday
|  | Date (day): | 2023-04-01 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12648.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14026 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-03-31 | 2023-04-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 35 | 78 | 75 | 81 | 27 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 301 | 394 | 370 | 390 |  |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 338 | 342 | 300 | 300 | 40 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 400 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 75 | 90 |  | 10 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 270 | 250 | 280 | 280 | 55 |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 34 | 90 | 90 |  | 12 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 10 | 22 | 19 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 9 | 92 | 92 |  | 10 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 218 | 212 | 150 | 220 |  | 118 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 102 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 35 | 35
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 64 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 0 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 42 | 45 | 51 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 15 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 8 | 25 | 51
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 280 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 88 | 17 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 70 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 34 | 72 | 72 | 32 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 4 | 108 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 34 | 17 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1955 | 2517 | 3129 | 3617 | 1501 | 679
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 15 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 6 | 20 | 20 | 30 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 219 | 227 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 48 |  | 50 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 0 | 65 |  | 37 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 66 | 55 | 66 |  | 34 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 70 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 5 | 8 | 5 | 5 | 17 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 24 | 40 | 2 | 10
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 5 | 12 | 96 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 15 | 50 | 300 | 300 | 0
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 17 | 54 | 0
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 52 | 36 | 51 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 60 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 107 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 621 | 847 | 1049 | 1233 | 852 | 280
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 174 | 210 | 210 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 290 | 310 | 310 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 401 | 240 | 320 | 320 |  | 400
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 15 | 49 | 50 | 50
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 10 | 45 | 30 | 45
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 135 | 25 | 135 |  | 15
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 180 | 160 | 180 |  | 20 | Engine problem
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 18 | 18 | 18
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 132 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 21 | 18 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 9 | 9 | 9 | 104 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 1 | 17 | 17 | 17 |  | 18 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 75 | 94 | 115 | 21
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1169 | 1480 | 1605 | 1879 | 646 | 1005
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 46 | 106 | 51 | 106 | 96 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 16 | 16 | 16 | 6 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 2 | 75 | 100 | 180 |  | 20 | Engine problem
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 25 | 113 | 95 | 110 |  | 5 | Engine problem
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 36 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 18 | 12 | 18 |  | 4 | Engine problem
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 124 | 328 | 325.6 | 430 | 102 | 29
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 41 | 41 | 41 |  | 29 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 31 | 31 | 31 | 31 |  | 59 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 112 | 112 | 112 |  | 51 | ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 50 | 20 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 20 | 47 | 20 | 47
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 64 | 65 | 65
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 89 | 89 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 108 | 151 | 162 | 162 |  | 69
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 | 9 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 265 | 280 | 280 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 366 | 367 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1419 | 1669 | 1669 | 1727 | 9 | 641
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 905 | 796 | 922 | 922
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 0 | 66 | 83 |  | 32 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 40 | 50 |  | 4 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 40 | 65 |  | 44 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 260 | 240 | 260 | 150 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 8 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 53 | 53 | 52 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 100
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 18 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Under maintenance
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1163 | 1056 | 1469 | 1573 | 548 | 80
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 48 | 48 | 62 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 8 | 19 | 19 | 19 |  | 21 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 144 | 171 | 170 | 170 | 24 |  | Gas shortage
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 720 | 860 | 900 | 900 |  |  | Line O/L
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 150 | 249 | 250 | 250 |  |  | Line O/L
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1022 | 1299 | 1387 | 1387 | 86 | 241
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 32 |  | 20 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 18 | 40 |  | 31 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 42 | 42
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 32 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 176 | 150 | 170 | 40 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 308 | 387 | 330 | 330 | 84 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 36 | 0 | 26 | 36 |  | 14 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 34 | 18 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 50 | 100 |  | 4 | Enging problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 50 | 70 | 18 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 95 | 113
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 761 | 764 | 760 | 760 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1276 | 1392 | 1592 | 1800 | 971 | 79
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 | 104 |  | Coal Shortage.
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 49 | 0 | 35 | 95 | 18 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 36 | 50 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 11 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 158 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 427 | 206 | 423 | 380 | 247 | 85
| Total |  |  |  |  | 23482 | 22700 | 9176 | 10794 | 12648.6 | 14026 | 4962 | 3119
A. |  | 2023-03-31 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 10798 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6307 | MW at | 2:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10794 | MW
3 | Day peak Generation : |  |  | 9176 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10391.29 | MW
4 | Evening peak Generation : |  |  | 10794 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 211.8828 | MKWHr | By Solar | 1.9327 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 121.5866 | MKWHr |  | By Oil: | 20.9238 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 43.9854 | MKWHr |  | By Hydro: | 0.60426 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4962 | MW | Dhaka | 3685.29 | 3685.29 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3119 | MW | Chittagong | 1141.8 | 1141.8 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 8081 | MW | Khulna | 1293.8 | 1293.8 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 942.5 | MMCFD |  |  | Rajshahi | 1005 | 1005 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 129156356.92 | ii) Oil : | Taka | 266737088.99 | Comilla | 1048 | 1048 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 192345763 | Total | Taka | 588239208.91 | Mymensingh | 801 | 801 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.066 | MKWHr. | Sylhet | 410 | 410 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 440 | MW (E to W) at | 21:00 | hrs | Barisal | 331.4 | 331.4 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 80 | MW at | 3:00 | hrs | Rangpur | 675 | 675 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6° C |  |  | Total | 10391.29 | 10391.29 |  | 0
B. |  | 2023-04-01 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 30.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14026 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9500 | MW
4 | Reserve(Generation end) |  |  |  | 2126 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 233.5067 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5602 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.4356 | MKWHr. | ii) HVDC Flow at Peak Time |  | 796 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4144 | MKWHr. | iii) Maximum HVDC Flow : |  | 906 | MW at | 24:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.02 |  | (b) Today: | 75.93 |  | (c) Rule Curve: |  | 88
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-03-31 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 352 | 265 |  | 0 | 320 | 229 | 0 | 1 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 23 | 25 | 0 | 26 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 68 | 55 | 0 | 6 | 5 | 35 | 0 | 0 | 0 | 280 | 0 | 150 | 8 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 116 | 87 | 0 | 0 | 0 | 41 | 31 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 19 | 18 | 0 | 0 | 250 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 51 | 0 | 317 | 0 | 0 | 17 | 0 | 30 | 17 | 54 | 0 | 0 | 30 | 315 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 10 | 17 | 250 | 0 | 0 |  | 805 | 0 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 750 | 0 | 0 |  | 4514 | 3206 | 7720 | 3007 | 805 | 1516 | 0 | 512 | 1671 | 25 | 0 | 68 | 116 | 0 | 0 | 76.04
2:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 240 |  | 0 | 270 | 255 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 51 | 22 | 0 | 6 | 5 | 35 | 0 | 0 | 0 | 270 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 21 | 114 | 77 | 0 | 0 | 0 | 41 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 19 | 18 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 319 | 0 | 0 | 17 | 0 | 30 | 17 | 54 | 0 | 0 | 30 | 370 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 17 | 0 | 220 | 0 | 0 |  | 501 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 555 | 0 | 0 |  | 3717 | 2590 | 6307 | 2497 | 501 | 1316 | 0 | 387 | 1416 | 25 | 0 | 51 | 114 | 0 | 0 | 76.04
3:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 255 |  | 0 | 330 | 267 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 51 | 22 | 0 | 6 | 5 | 35 | 0 | 0 | 0 | 270 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 0 | 0 | 20 | 77 | 0 | 0 | 0 | 41 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 65 | 19 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 367 | 5 | 0 | 17 | 0 | 30 | 17 | 54 | 0 | 0 | 30 | 370 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 17 | 0 | 260 | 0 | 0 |  | 840 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 550 | 0 | 0 |  | 3855 | 3108 | 6963 | 2632 | 840 | 1551 | 0 | 392 | 1452 | 25 | 0 | 51 | 20 | 0 | 0 | 76.03
4:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 353 |  | 0 | 360 | 270 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 0 | 0 | 51 | 22 | 0 | 6 | 5 | 40 | 0 | 0 | 0 | 300 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 48 | 76 | 0 | 0 | 0 | 41 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 66 | 19 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 17 | 0 | 365 | 24 | 0 | 17 | 0 | 30 | 17 | 54 | 0 | 0 | 30 | 370 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 |  | 904 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 570 | 0 | 0 |  | 4191 | 3332 | 7523 | 2802 | 904 | 1693 | 0 | 428 | 1572 | 25 | 0 | 51 | 48 | 0 | 0 | 76.03
5:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 285 |  | 0 | 300 | 236 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 0 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 11 | 22 | 0 | 6 | 5 | 42 | 0 | 0 | 0 | 300 | 0 | 159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 11 | 72 | 89 | 0 | 0 | 0 | 41 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 66 | 19 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 365 | 24 | 0 | 17 | 0 | 15 | 17 | 54 | 0 | 0 | 30 | 340 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 17 | 0 | 300 | 0 | 0 |  | 905 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 570 | 0 | 0 |  | 3960 | 3205 | 7165 | 2780 | 905 | 1425 | 0 | 376 | 1571 | 25 | 0 | 11 | 72 | 0 | 0 | 76.02
6:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 266 |  | 0 | 300 | 230 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 8 | 16 | 8 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 185 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 42 | 0 | 0 | 0 | 300 | 0 | 131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 12 | 78 | 88 | 0 | 0 | 0 | 41 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 67 | 19 | 0 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 366 | 8 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 |  | 833 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 568 | 0 | 0 |  | 3622 | 2975 | 6597 | 2707 | 833 | 1351 | 0 | 144 | 1459 | 25 | 0 | 0 | 78 | 0 | 0 | 76.02
7:00 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 29 | 280 |  | 0 | 300 | 230 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 8 | 16 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 186 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33 | 0 | 0 | 0 | 300 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 33 | 12 | 62 | 48 | 0 | 0 | 0 | 43 | 22 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 82 | 18 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 6 | 0 | 17 | 0 | 0 | 3 | 0 | 0 | 300 | 0 | 0 |  | 833 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 4 | 152 | 568 | 23 | 0 |  | 3613 | 3048 | 6661 | 2837 | 833 | 1355 | 0 | 29 | 1470 | 25 | 0 | 0 | 62 | 50 | 0 | 76.02
8:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 33 | 305 |  | 0 | 330 | 278 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 10 | 16 | 24 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37 | 0 | 0 | 0 | 280 | 0 | 184 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 33 | 12 | 62 | 47 | 0 | 0 | 1 | 41 | 22 | 0 | 5 | 0 | 0 | 40 | 10 | 0 | 90 | 19 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 19 | 0 | 17 | 0 | 0 | 10 | 0 | 0 | 300 | 0 | 0 |  | 834 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 640 | 0 | 0 | 0 | 1 | 38 | 0 | 0 | 0 | 0 | 12 | 152 | 568 | 53 | 0 |  | 3851 | 3278 | 7129 | 2942 | 834 | 1572 | 0 | 29 | 1530 | 25 | 0 | 0 | 62 | 135 | 23.9609 | 76.01
9:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 49 | 308 |  | 0 | 330 | 303 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 27 | 16 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 202 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35 | 0 | 0 | 0 | 315 | 0 | 200 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 12 | 74 | 47 | 0 | 0 | 1 | 41 | 22 | 5 | 5 | 0 | 0 | 40 | 10 | 0 | 90 | 18 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 398 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 33 | 0 | 17 | 0 | 0 | 8 | 0 | 0 | 300 | 0 | 0 |  | 856 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 720 | 0 | 0 | 0 | 1 | 27 | 0 | 0 | 0 | 0 | 21 | 151 | 612 | 110 | 0 |  | 4043 | 3495 | 7538 | 3082 | 856 | 1595 | 0 | 46 | 1653 | 25 | 0 | 0 | 74 | 207 | 24.8825 | 76.01
10:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 158 | 354 |  | 0 | 330 | 260 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 24 | 16 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 5 | 26 | 0 | 0 | 0 | 290 | 0 | 184 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 33 | 12 | 86 | 47 | 0 | 14 | 2 | 41 | 22 | 5 | 5 | 0 | 0 | 40 | 10 | 0 | 106 | 18 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 0 | 0 | 365 | 2 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 4 | 0 | 400 | 0 | 50 | 0 | 25 | 0 | 0 | 32 | 2 | 0 | 300 | 0 | 0 |  | 904 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 720 | 0 | 0 | 0 | 4 | 26 | 5 | 0 | 0 | 0 | 22 | 151 | 750 | 147 | 0 |  | 4266 | 3749 | 8015 | 3202 | 904 | 1604 | 0 | 94 | 1791 | 25 | 0 | 0 | 86 | 309 | 18.4315 | 76.01
11:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 268 | 353 |  | 0 | 330 | 282 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 19 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 3 | 5 | 24 | 0 | 0 | 0 | 290 | 0 | 186 | 0 | 0 | 5 | 2 | 0 | 5 | 0 | 0 | 0 | 18 | 5 | 33 | 12 | 96 | 46 | 0 | 14 | 2 | 41 | 22 | 5 | 5 | 0 | 0 | 40 | 10 | 0 | 106 | 18 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 52 | 17 | 0 | 364 | 16 | 0 | 16 | 4 | 15 | 0 | 49 | 0 | 9 | 7 | 400 | 0 | 37 | 0 | 72 | 0 | 0 | 34 | 34 | 0 | 300 | 0 | 0 |  | 904 | 0 | 238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 49 | 0 | 5 | 0 | 720 | 0 | 0 | 0 | 3 | 47 | 35 | 0 | 0 | 0 | 19 | 151 | 762 | 163 | 0 |  | 4652 | 3889 | 8541 | 3328 | 904 | 1616 | 0 | 401 | 1803 | 25 | 0 | 36 | 96 | 332 | 11.9805 | 76
12:00 | 0 | 0 | 0 | 180 | 0 | 35 | 0 | 301 | 338 |  | 0 | 450 | 270 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 23 | 19 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 6 | 5 | 24 | 0 | 0 | 0 | 305 | 0 | 184 | 0 | 0 | 15 | 10 | 0 | 20 | 0 | 0 | 0 | 0 | 5 | 33 | 12 | 104 | 46 | 0 | 14 | 1 | 41 | 31 | 5 | 20 | 0 | 0 | 61 | 89 | 0 | 108 | 18 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 15 | 88 | 17 | 0 | 366 | 25 | 0 | 17 | 3 | 15 | 0 | 52 | 0 | 9 | 12 | 400 | 0 | 36 | 4 | 107 | 0 | 1 | 32 | 53 | 0 | 401 | 0 | 0 |  | 905 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 49 | 0 | 4 | 0 | 720 | 0 | 0 | 0 | 4 | 18 | 35 | 0 | 0 | 0 | 11 | 150 | 761 | 158 | 0 |  | 5288 | 3888 | 9176 | 3602 | 905 | 1879 | 0 | 542 | 1801 | 25 | 0 | 36 | 104 | 282 | 11.0589 | 76
13:00 | 0 | 0 | 0 | 180 | 0 | 68 | 0 | 349 | 338 |  | 0 | 400 | 256 | 0 | 0 | 1 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 12 | 7 | 23 | 14 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 3 | 0 | 0 | 44 | 0 | 6 | 5 | 35 | 0 | 0 | 0 | 280 | 0 | 183 | 0 | 0 | 40 | 35 | 0 | 43 | 0 | 0 | 0 | 12 | 5 | 33 | 12 | 124 | 45 | 0 | 16 | 1 | 41 | 31 | 53 | 40 | 80 | 0 | 40 | 89 | 0 | 109 | 18 | 0 | 10 | 275 | 8 | 0 | 0 | 10 | 0 | 0 | 8 | 0 | 37 | 17 | 88 | 59 | 0 | 368 | 95 | 0 | 17 | 2 | 45 | 0 | 52 | 0 | 12 | 19 | 380 | 15 | 41 | 35 | 107 | 0 | 17 | 18 | 54 | 17 | 300 | 0 | 0 |  | 905 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 257 | 0 | 0 | 0 | 0 | 49 | 0 | 5 | 0 | 710 | 0 | 0 | 0 | 3 | 69 | 35 | 0 | 0 | 0 | 22 | 149 | 755 | 51 | 0 |  | 5752 | 3808 | 9560 | 3526 | 905 | 2010 | 0 | 921 | 1784 | 25 | 0 | 36 | 124 | 229 | 10 | 76
14:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 282 | 255 |  | 0 | 300 | 303 | 0 | 0 | 15 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 7 | 23 | 8 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 16 | 0 | 0 | 44 | 0 | 6 | 5 | 31 | 0 | 0 | 0 | 290 | 0 | 189 | 0 | 0 | 47 | 47 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 20 | 114 | 45 | 0 | 16 | 1 | 41 | 31 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 109 | 18 | 0 | 10 | 270 | 16 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 52 | 17 | 88 | 85 | 0 | 344 | 94 | 0 | 17 | 3 | 45 | 0 | 52 | 0 | 9 | 50 | 340 | 17 | 23 | 35 | 107 | 0 | 17 | 18 | 53 | 17 | 250 | 0 | 0 |  | 904 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 49 | 0 | 5 | 0 | 660 | 0 | 0 | 0 | 0 | 87 | 35 | 0 | 0 | 0 | 14 | 151 | 763 | 79 | 0 |  | 5259 | 3794 | 9053 | 3303 | 904 | 1653 | 0 | 1027 | 1744 | 25 | 0 | 36 | 114 | 247 | 0 | 76
15:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 348 | 303 |  | 0 | 340 | 291 | 0 | 0 | 15 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 23 | 6 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 216 | 0 | 0 | 0 |  | 18 | 0 | 0 | 44 | 0 | 6 | 5 | 31 | 0 | 0 | 0 | 290 | 0 | 187 | 0 | 0 | 45 | 47 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 20 | 104 | 45 | 0 | 16 | 1 | 41 | 31 | 11 | 10 | 112 | 0 | 62 | 88 | 0 | 109 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 52 | 13 | 88 | 85 | 0 | 369 | 94 | 0 | 17 | 1 | 45 | 0 | 54 | 0 | 9 | 50 | 394 | 17 | 9 | 35 | 107 | 0 | 17 | 6 | 53 | 17 | 250 | 0 | 0 |  | 904 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 235 | 0 | 0 | 0 | 0 | 49 | 0 | 4 | 0 | 660 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 0 | 17 | 151 | 767 | 110 | 0 |  | 5586 | 3741 | 9327 | 3409 | 904 | 1844 | 0 | 1049 | 1748 | 25 | 0 | 36 | 104 | 208 | 0 | 75.99
16:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 358 | 303 |  | 0 | 340 | 301 | 0 | 0 | 15 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 23 | 6 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 |  | 18 | 0 | 0 | 44 | 2 | 6 | 5 | 35 | 0 | 0 | 0 | 315 | 0 | 201 | 0 | 0 | 45 | 48 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 102 | 45 | 0 | 16 | 0 | 41 | 31 | 11 | 10 | 112 | 0 | 62 | 88 | 0 | 109 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 52 | 6 | 88 | 85 | 0 | 394 | 94 | 0 | 17 | 1 | 45 | 9 | 54 | 0 | 9 | 50 | 394 | 17 | 7 | 35 | 107 | 0 | 17 | 2 | 51 | 17 | 250 | 0 | 0 |  | 904 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 | 0 | 49 | 0 | 3 | 0 | 660 | 0 | 0 | 0 | 0 | 40 | 36 | 0 | 0 | 0 | 4 | 151 | 764 | 38 | 0 |  | 5670 | 3654 | 9324 | 3496 | 904 | 1856 | 0 | 1059 | 1745 | 25 | 0 | 36 | 102 | 101 | 0 | 75.99
17:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 358 | 303 |  | 0 | 340 | 306 | 1 | 0 | 15 | 130 | 0 | 0 | 3 | 8 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 23 | 14 | 25 | 30 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 218 | 0 | 0 | 0 |  | 18 | 0 | 0 | 44 | 6 | 0 | 7 | 20 | 0 | 0 | 0 | 350 | 0 | 202 | 0 | 0 | 46 | 51 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 33 | 21 | 110 | 45 | 0 | 16 | 0 | 41 | 31 | 11 | 10 | 112 | 0 | 62 | 88 | 0 | 143 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 15 | 0 | 0 | 8 | 0 | 52 | 3 | 100 | 85 | 0 | 408 | 104 | 0 | 17 | 1 | 65 | 17 | 54 | 0 | 9 | 50 | 390 | 17 | 1 | 35 | 107 | 0 | 17 | 2 | 70 | 17 | 250 | 0 | 0 |  | 904 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 | 0 | 49 | 0 | 2 | 0 | 660 | 0 | 0 | 0 | 0 | 8 | 36 | 0 | 0 | 0 | 3 | 152 | 771 | 9 | 0 |  | 5832 | 3667 | 9499 | 3648 | 904 | 1856 | 0 | 1138 | 1753 | 25 | 0 | 36 | 110 | 29 | 0 | 75.98
18:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 371 | 303 |  | 0 | 380 | 250 | 14 | 17 | 18 | 130 | 0 | 0 | 9 | 24 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 23 | 14 | 25 | 21 | 8 | 0 | 25 | 0 | 0 | 0 | 1 | 228 | 0 | 0 | 0 |  | 18 | 12 | 0 | 55 | 6 | 4 | 7 | 40 | 0 | 0 | 0 | 290 | 0 | 190 | 0 | 0 | 48 | 53 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 124 | 44 | 0 | 16 | 0 | 41 | 31 | 11 | 10 | 112 | 0 | 63 | 88 | 0 | 145 | 18 | 0 | 10 | 275 | 16 | 0 | 0 | 15 | 0 | 0 | 26 | 0 | 72 | 0 | 100 | 85 | 6 | 368 | 104 | 17 | 17 | 0 | 65 | 35 | 51 | 17 | 9 | 50 | 400 | 50 | 0 | 57 | 107 | 0 | 17 | 0 | 75 | 22 | 250 | 0 | 0 |  | 905 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 2 | 0 | 15 | 15 | 49 | 0 | 1 | 35 | 660 | 0 | 0 | 0 | 0 | 1 | 46 | 0 | 0 | 0 | 0 | 181 | 763 | 0 | 0 |  | 6047 | 3778 | 9825 | 3567 | 905 | 1889 | 0 | 1443 | 1774 | 25 | 0 | 96 | 124 | 2 | 0 | 75.98
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 50 | 0 | 360 | 242 |  | 0 | 400 | 283 | 24 | 34 | 30 | 225 | 0 | 0 | 9 | 24 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 23 | 14 | 25 | 24 | 34 | 0 | 25 | 0 | 0 | 0 | 8 | 225 | 0 | 0 | 0 |  | 18 | 40 | 51 | 55 | 6 | 6 | 8 | 38 | 0 | 0 | 0 | 290 | 0 | 192 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 134 | 45 | 0 | 16 | 0 | 41 | 31 | 40 | 20 | 80 | 0 | 63 | 88 | 0 | 145 | 18 | 0 | 10 | 250 | 16 | 0 | 0 | 45 | 0 | 0 | 90 | 0 | 100 | 0 | 100 | 85 | 75 | 304 | 104 | 50 | 17 | 0 | 75 | 54 | 17 | 17 | 9 | 51 | 400 | 50 | 0 | 108 | 107 | 0 | 17 | 0 | 89 | 34 | 240 | 0 | 0 |  | 894 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 16 | 159 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 17 | 0 | 35 | 15 | 49 | 0 | 0 | 35 | 610 | 0 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 205 | 763 | 0 | 0 |  | 6524 | 3837 | 10361 | 3541 | 894 | 1937 | 0 | 1907 | 1748 | 25 | 0 | 175 | 134 | 0 | 0 | 75.97
19:30 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 341 | 243 |  | 0 | 400 | 249 | 24 | 34 | 40 | 225 | 0 | 0 | 9 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 23 | 22 | 25 | 24 | 8 | 0 | 25 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 18 | 18 | 51 | 55 | 6 | 6 | 8 | 40 | 0 | 0 | 0 | 290 | 0 | 190 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 124 | 57 | 0 | 16 | 0 | 41 | 31 | 53 | 42 | 80 | 0 | 40 | 88 | 0 | 145 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 80 | 0 | 0 | 120 | 0 | 100 | 0 | 100 | 120 | 128 | 311 | 113 | 50 | 17 | 0 | 135 | 54 | 17 | 17 | 9 | 60 | 400 | 52 | 0 | 108 | 107 | 0 | 17 | 0 | 75 | 34 | 240 | 0 | 0 |  | 796 | 0 | 220 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 309 | 17 | 0 | 35 | 0 | 90 | 0 | 0 | 2 | 740 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 210 | 762 | 0 | 0 |  | 6676 | 3809 | 10485 | 3525 | 796 | 1977 | 0 | 2035 | 1882 | 25 | 0 | 121 | 124 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 344 | 273 |  | 0 | 450 | 293 | 24 | 34 | 45 | 220 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 22 | 22 | 23 | 27 | 25 | 31 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 224 | 0 | 0 | 0 |  | 18 | 0 | 51 | 55 | 6 | 6 | 8 | 37 | 0 | 0 | 0 | 305 | 0 | 187 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 130 | 57 | 0 | 16 | 0 | 41 | 31 | 51 | 47 | 80 | 0 | 40 | 89 | 0 | 145 | 18 | 0 | 10 | 260 | 16 | 8 | 0 | 15 | 0 | 0 | 100 | 0 | 99 | 0 | 100 | 152 | 115 | 327 | 113 | 52 | 17 | 0 | 135 | 54 | 17 | 17 | 9 | 60 | 400 | 34 | 0 | 108 | 107 | 0 | 17 | 0 | 75 | 34 | 240 | 0 | 0 |  | 796 | 0 | 250 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0 | 35 | 0 | 10 | 0 | 0 | 0 | 740 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 211 | 760 | 0 | 0 |  | 6753 | 3715 | 10468 | 3636 | 796 | 2112 | 0 | 1821 | 1881 | 25 | 0 | 67 | 130 | 0 | 0 | 75.97
21:00 | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 394 | 342 |  | 0 | 450 | 250 | 8 | 34 | 55 | 212 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 23 | 22 | 25 | 15 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 0 | 6 | 8 | 40 | 0 | 0 | 0 | 290 | 0 | 174 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 132 | 106 | 0 | 16 | 0 | 41 | 31 | 50 | 47 | 112 | 0 | 64 | 89 | 0 | 151 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 15 | 0 | 0 | 75 | 0 | 88 | 0 | 100 | 180 | 135 | 367 | 113 | 17 | 17 | 0 | 50 | 54 | 36 | 0 | 9 | 60 | 400 | 34 | 0 | 108 | 107 | 0 | 17 | 0 | 75 | 34 | 240 | 0 | 0 |  | 796 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 249 | 764 | 0 | 0 |  | 6841 | 3953 | 10794 | 3797 | 796 | 2249 | 0 | 1685 | 2043 | 25 | 0 | 67 | 132 | 0 | 0 | 75.97
22:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 395 | 347 |  | 0 | 450 | 259 | 0 | 4 | 15 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 23 | 27 | 25 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 0 | 6 | 8 | 38 | 0 | 0 | 0 | 290 | 0 | 172 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 132 | 100 | 0 | 16 | 0 | 41 | 31 | 51 | 47 | 112 | 0 | 64 | 89 | 0 | 163 | 18 | 0 | 10 | 260 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 65 | 0 | 100 | 180 | 138 | 367 | 113 | 17 | 17 | 0 | 50 | 54 | 51 | 0 | 9 | 14 | 400 | 17 | 0 | 108 | 107 | 0 | 17 | 0 | 76 | 34 | 240 | 0 | 0 |  | 848 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 980 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 250 | 754 | 0 | 0 |  | 6678 | 4120 | 10798 | 3810 | 848 | 2258 | 0 | 1520 | 2154 | 25 | 0 | 51 | 132 | 0 | 0 | 75.97
23:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 397 | 347 |  | 0 | 450 | 279 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 23 | 27 | 25 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 0 |  | 18 | 0 | 51 | 66 | 0 | 6 | 8 | 38 | 0 | 0 | 0 | 290 | 0 | 171 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 128 | 96 | 0 | 16 | 0 | 41 | 31 | 51 | 47 | 80 | 0 | 63 | 89 | 0 | 162 | 18 | 0 | 10 | 250 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 52 | 0 | 100 | 155 | 10 | 367 | 113 | 0 | 17 | 0 | 15 | 35 | 54 | 0 | 9 | 12 | 400 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 74 | 23 | 240 | 0 | 0 |  | 905 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 249 | 772 | 0 | 0 |  | 6147 | 4072 | 10219 | 3789 | 905 | 2212 | 0 | 948 | 2161 | 25 | 0 | 51 | 128 | 0 | 0 | 75.96
24:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 398 | 345 |  | 0 | 400 | 294 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 25 | 16 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 12 | 0 | 51 | 66 | 0 | 6 | 7 | 38 | 0 | 0 | 0 | 320 | 0 | 182 | 0 | 0 | 46 | 35 | 0 | 10 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 122 | 94 | 0 | 16 | 0 | 41 | 31 | 11 | 10 | 80 | 0 | 40 | 89 | 0 | 160 | 18 | 0 | 10 | 270 | 16 | 8 | 0 | 0 | 0 | 0 | 46 | 0 | 41 | 0 | 88 | 120 | 0 | 380 | 47 | 0 | 17 | 0 | 15 | 35 | 54 | 0 | 9 | 12 | 400 | 0 | 0 | 0 | 107 | 0 | 17 | 0 | 75 | 0 | 240 | 0 | 0 |  | 906 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 759 | 0 | 0 |  | 5752 | 3957 | 9709 | 3743 | 906 | 2034 | 0 | 775 | 2053 | 25 | 0 | 51 | 122 | 0 | 0 | 75.96
KWH | 0 | 0 | 0 | 4221000 | 0 | 656545 | 0 | 5787650 | 7226000 |  | 0 | 8372500 | 6555084 | 72960 | 113174 | 263308 | 3752765 | 0 | 0 | 31680 | 77904 | 121440 | 0 | 0 | 0 | 0 | 426960 | 375872 | 222261 | 134136 | 552000 | 320580 | 452700 | 489400 | 80861 | 0 | 604260 | 0 | 0 | 0 | 20998 | 4865102 | 0 | 0 | 0 |  | 200880 | 61776 | 520151 | 799920 | 30720 | 119040 | 128064 | 871680 | 0 | 0 | 0 | 7379500 | 0 | 4289000 | 0 | 0 | 586512 | 575520 | 0 | 611534 | 0 | 0 | 60312 | 401652 | 156960 | 751600 | 391510 | 2414400 | 1485120 | 0 | 229572 | 9150 | 971000 | 597720 | 407400 | 385992 | 1208127 | 0 | 1142016 | 1047360 | 0 | 2443480 | 421000 | 0 | 141120 | 6568000 | 175296 | 47300 | 0 | 198218 | 0 | 0 | 532800 | 0 | 796032 | 98550 | 1732800 | 1573440 | 557018 | 8686000 | 1305600 | 200640 | 348763 | 21719 | 950945 | 464244 | 990250 | 51300 | 173880 | 702720 | 8993300 | 264960 | 246420 | 717120 | 2201727 | 0 | 233280 | 0 | 1022400 | 300960 | 6551300 | 0 | 0 |  | 20435636 | 0 | 5689152 | 0 | 245760 | 0 | 0 | 0 | 0 | 0 | 18750 | 3225808 | 349300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7663 | 0 | 8957 | 322793 | 306960 | 0 | 92160 | 0 | 0 | 4137500 | 0 | 0 | 3873555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7019600 | 30240 | 0 | 204672 | 27936 | 523363 | 0 | 35527 | 75840 | 18918800 | 0 | 0 | 0 | 18960 | 375120 | 538560 | 0 | 0 | 0 | 152496 | 4123600 | 16805455 | 974770 | 0 |  | 123343910 | 88538933 | 211882843 | 79283910 | 20435636 | 42302722 | 0 | 19897688 | 43985355 | 604260 | 0 | 1026160 | 2414400 | 1932712 | 0
Fuel Cost | 0 | 0 | 0 | 6289290 | 0 | 873204.85 | 0 | 6077032.5 | 7804080 |  | 0 | 9126025 | 7276143.24 | 815692.8 | 1499555.5 | 3488831 | 4203096.8 | 0 | 0 | 463161.6 | 1096109.28 | 1968542.4 | 0 | 0 | 0 | 0 | 5430931.2 | 5074272 | 2980520.01 | 100602 | 414000 | 0 | 0 | 0 | 1375445.61 | 0 | 163150.2 | 0 | 0 | 0 | 343317.3 | 5059706.08 | 0 | 0 | 0 |  | 2621484 | 1030423.68 | 8852970.02 | 10806919.2 | 389529.6 | 1377292.8 | 162641.28 | 2902694.4 | 0 | 0 | 0 | 8191245 | 0 | 4975240 | 0 | 0 | 662758.56 | 857524.8 | 0 | 1021261.78 | 0 | 0 | 811196.4 | 550263.24 | 117720 | 1315300 | 293632.5 | 17335392 | 1618780.8 | 0 | 312217.92 | 145851 | 1330270 | 788990.4 | 708876 | 667766.16 | 1389346.05 | 0 | 2215511.04 | 2387980.8 | 0 | 2467914.8 | 905150 | 0 | 279417.6 | 6568000 | 131472 | 35948 | 0 | 2705675.7 | 0 | 0 | 7182144 | 0 | 11025043.2 | 1152049.5 | 17882496 | 21493190.4 | 7391628.86 | 7991120 | 15876096 | 2901254.4 | 4411851.95 | 0 | 11164094.3 | 5055617.16 | 10526357.5 | 696141 | 2241313.2 | 8278041.6 | 8273836 | 3431232 | 3560769 | 9100252.8 | 25055653.26 | 0 | 3046636.8 | 0 | 15305328 | 3963643.2 | 0 | 0 | 0 |  | 61306908 | 0 | 6371850.24 | 0 | 2558361.6 | 0 | 0 | 0 | 0 | 0 | 269437.5 | 3612904.96 | 677642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126899.28 | 0 | 122083.91 | 5445517.91 | 635407.2 | 0 | 69765.12 | 0 | 0 | 21887375 | 0 | 0 | 4493323.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6949404 | 406425.6 | 0 | 2421269.76 | 403675.2 | 6646710.1 | 0 | 392573.35 | 920697.6 | 170458388 | 0 | 0 | 0 | 214437.6 | 4400157.6 | 8256124.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 367863157.03 | 309047340.13 | 676910497.16 | 79031583.04 | 61306908 | 50124773.88 | 0 | 249439634.98 | 192345763 | 163150.2 | 0 | 17297454.01 | 17335392 | 9865838.05 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 35 | 0 | 301 | 338 |  | 0 | 450 | 270 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 23 | 19 | 25 | 33 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 219 | 0 | 0 | 0 |  | 0 | 0 | 0 | 33 | 0 | 6 | 5 | 24 | 0 | 0 | 0 | 305 | 0 | 184 | 0 | 0 | 15 | 10 | 0 | 20 | 0 | 0 | 0 | 0 | 5 | 33 | 12 | 104 | 46 | 0 | 14 | 1 | 41 | 31 | 5 | 20 | 0 | 0 | 61 | 89 | 0 | 108 | 18 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 15 | 88 | 17 | 0 | 366 | 25 | 0 | 17 | 3 | 15 | 0 | 52 | 0 | 9 | 12 | 400 | 0 | 36 | 4 | 107 | 0 | 1 | 32 | 53 | 0 | 401 | 0 | 0 |  | 905 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 0 | 5 | 0 | 0 | 170 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 0 | 0 | 0 | 0 | 49 | 0 | 4 | 0 | 720 | 0 | 0 | 0 | 4 | 18 | 35 | 0 | 0 | 0 | 11 | 150 | 761 | 158 | 0 |  | 9176 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 78 | 0 | 394 | 342 | 0 | 0 | 450 | 250 | 8 | 34 | 55 | 212 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 23 | 22 | 25 | 15 | 8 | 0 | 25 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 | 0 | 18 | 0 | 51 | 66 | 0 | 6 | 8 | 40 | 0 | 0 | 0 | 290 | 0 | 174 | 0 | 0 | 49 | 45 | 0 | 43 | 0 | 0 | 8 | 18 | 11 | 33 | 21 | 132 | 106 | 0 | 16 | 0 | 41 | 31 | 50 | 47 | 112 | 0 | 64 | 89 | 0 | 151 | 18 | 0 | 10 | 265 | 16 | 8 | 0 | 15 | 0 | 0 | 75 | 0 | 88 | 0 | 100 | 180 | 135 | 367 | 113 | 17 | 17 | 0 | 50 | 54 | 36 | 0 | 9 | 60 | 400 | 34 | 0 | 108 | 107 | 0 | 17 | 0 | 75 | 34 | 240 | 0 | 0 |  | 796 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 860 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 249 | 764 | 0 | 0 |  | 10794 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 390 | 300 | 0 | 0 | 450 | 280 | 90 | 90 | 55 | 220 | 0 | 0 | 92 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 23 | 28 | 33 | 33 | 51 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 18 | 48 | 65 | 66 | 12 | 20 | 5 | 10 | 0 | 0 | 0 | 310 | 0 | 210 | 8 | 0 | 50 | 45 | 0 | 43 | 0 | 35 | 52 | 18 | 11 | 33 | 21 | 153 | 106 | 0 | 16 | 0 | 41 | 31 | 51 | 47 | 112 | 0 | 65 | 86 | 0 | 162 | 18 | 0 | 10 | 280 | 16 | 8 |  | 300 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 180 | 135 | 400 | 110 | 105 | 17 | 0 | 300 | 54 | 54 | 114 | 9 | 100 | 400 | 72 | 0 | 162 | 107 | 0 | 17 |  | 115 | 34 | 320 |  |  |  | 922 | 0 | 260 |  | 83 | 0 | 0 | 0 | 50 | 65 | 40 | 170 | 19 | 48 | 0 | 0 | 0 | 32 | 40 | 100 | 0 | 42 | 40 | 34 | 36 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 170 |  | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 53 | 0 | 70 | 100 | 95 | 0 | 0 | 113 | 900 | 0 |  | 0 |  |  | 115 | 0 |  | 0 |  | 250 | 760 |  | 0
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 370 | 300 | 0 | 0 | 400 | 280 | 75 | 90 | 55 | 150 | 0 | 0 | 92 | 102 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 23 | 28 | 33 | 33 | 25 | 0 | 25 | 0 | 0 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 55 | 5 | 20 | 5 | 2 | 0 | 0 | 0 | 310 | 0 | 210 | 8 | 0 | 50 | 30 | 0 | 43 | 0 | 0 | 0 | 18 | 11 | 33 | 18 | 135 | 51 | 0 | 16 | 1.6 | 41 | 31 | 20 | 20 | 112 | 0 | 65 | 86 | 0 | 162 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 280 | 0 | 0 | 100 | 0 | 17 | 20 | 70 | 160 | 25 | 400 | 95 | 70 | 17 | 5 | 300 | 17 | 51 | 114 | 9 | 100 | 400 | 72 | 50 | 162 | 107 | 0 | 17 | 30 | 94 | 17 | 320 |  |  |  | 922 | 0 | 240 | 0 | 66 | 0 | 0 | 0 | 40 | 40 | 8 | 170 | 19 | 48 | 0 | 0 | 0 | 0 | 18 | 50 | 0 | 42 | 32 | 0 | 26 | 22 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 53 | 0 | 50 | 0 | 35 | 0 | 8 | 95 | 900 | 0 |  | 0 | 6 | 100 | 50 | 0 |  | 0 | 30 | 250 | 760 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 6 | 0 | 307 | 270 | 0 | 0 | 250 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 28 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310 | 0 | 201 | 0 | 0 | 5 | 3 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 8 | 6 | 94 | 34 | 0 | 16 | 1 | 41 | 31 | 11 | 10 | 0 | 0 | 32 | 10 | 0 | 162 | 18 | 0 | 7 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 70 | 0 | 0 | 324 | 0 | 0 | 17 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 220 | 0 | 26 | 0 | 68 | 0 | 0 | 8 | 0 | 0 | 280 | 0 | 0 | 0 | 292 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 152 | 556 | 38 | 0 | 0 |  |  |  | 121.5866 | 20.4356 | 20.9238 | 43.9854 | 0.60426 | 2.4144 | 1.9327
211.8828
| Minimum Generation |  | 6307 | 2:00
| Highest Generation |  | 10798 | 22:00
| Day Peak Generation |  | 9176 | 12:00
| Evening Peak Generation |  | 10794 | 21:00
| HVDC Max Flow |  | 906 | 24:00
| HVDC EvPeak Flow |  | 796 | 21:00
| Load factor L.F |  | 81.76% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-04-01
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-03-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9176 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5602
Evening Peak Generation : |  |  | 10794 | MW Hour : | 21:00 | Available Max Generation : |  | 14026
E.P. Demand (at gen end) : |  |  | 10794 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11900
Maximum Generation : |  |  | 10798 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2126
Total Gen. (MKWH) : |  |  | 211.8828 | System Load Factor : | 81.76% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 80 | MW at | 3:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-04-01
Actual : |  | 75.93 | Ft.(MSL) , | Rule curve : | 88 | Ft.( MSL )
Gas Consumed : |  | Total = | 942.5 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 129156356.92
: |  |  | Coal : | 192345763 | Oil : | 266737088.99 | Total : | 588239208.91
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 3948.8334 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1090.4778 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1432.9418 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1263.6312 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1079.1812 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 886.6511 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 401.0597 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 323.2277 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 700.1211 |  |  | 0 | 0%
Total |  | 0 |  | 11126.125 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
[5 empty] | 1) Barapukuria ST: Unit- 1,2 | 10) Bhula Nuton Biddut
2) Ghorasal-3,7
3) Ashuganj-5
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-2 & 3
9) Kushiara 163 MW ST
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:26 | 10:29 | Kushtia 132/33kV S/S T-1 LT Forced S/D Due to Red hot maintenance | [5 empty] | 26.0MW load interrup.
08:27 | 10:28 | Kushtia 132/33kV S/S T-1 HT Forced S/D Due to Red hot maintenance | [5 empty] | 26.0MW load interrup.
08:27 | 08:43 | Rampur 230/132/33 S/S ATR-02 (716T) LT Forced S/D Due to maintenance work .
08:27 | 08:43 | Rampur 230/132/33 S/S ATR-02 (716T) HT Forced S/D Due to maintenance work .
08:40 | 10:04 | Sonargaon 132/33kV S/S Tr-2 LT Forced S/D Due to Emergency maintenance work of PBS. | [5 empty] | 25.0MW load interrup.
08:40 | 18:35 | Chowmuhani-Feni 132 kV Ckt-1 Forced S/D from Feni 132/33kV end Due to Line maintenance by chowmohani SS.
08:41 | 10:02 | Sonargaon 132/33kV S/S Tr-2 HT Forced S/D Due to Emergency maintenance work of PBS. | [5 empty] | 25.0MW load interrup.
08:52 | 18:36 | Chowmuhani-Feni 132 kV Ckt-2 Forced S/D from Chowmuhani 132/33kV end Due to Clear Scaffolding and from Feni
132/33kV end Due to Line maintenance by chowmohani SS
09:08 |  | Haripur 412MW CCPP ST was sync.
| 09:09 | Coxsbazar 132/33kV S/S 405T-T1 HT is restored.
09:43 | 11:26 | Chandraghona 132/33kV S/S TR-01(406T) HT Project Work S/D Due to Avr relay cheak
09:50 | 12:22 | Joydebpur-Kodda B 132 kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to Wire restore to tower.
09:52 | 14:02 | Maniknagar 132/33kV S/S Transformer GT-1 HT Scheduled S/D Due to 33KV breaker maintenance work by DPDC. Shut down
taken by Md. Rokonul Islam, SDE, DPDC. Instructed by Md. Abdul Awal. SDE, NLDC.
| 10:21 | Jashore 132/33kV S/S T-1 HT is restored.
10:23 | 21:35 | BIPTC S/S Baharampur-3 Scheduled S/D Due to Shutdown taken from Baharampur s/s end
| 10:24 | Jashore 132/33kV S/S T-1 LT is restored.
| 10:52 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 is restored.
11:02 | 13:17 | Jashore 132/33kV S/S T-2 LT Forced S/D Due to T1A red hot maintainence
11:03 | 13:16 | Jashore 132/33kV S/S T-2 HT Forced S/D Due to T2A red hot maintainence
11:18 | 12:38 | Bogura 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Red hot at talora 33kv bus side isolator | [5 empty] | 32.0MW load interrup.
11:18 | 12:38 | Bogura 132/33kV S/S Transformer-2 LT Scheduled S/D Due to Red hot at talora 33kv isolato bus side | [5 empty] | 32.0MW load interrup.
11:33 |  | Siddhirganj 132/33kV S/S 132kV MTR 1 Forced S/D Due to Trip 230 Kv Side
| 11:38 | Chandraghona 132/33kV S/S TR-01(406T) LT is restored.
12:28 | 14:31 | Joydebpur-Kodda B 132 kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Wire restore at Tower.
| 12:48 | Ashuganj (South)-Ghorashal 230kV ckt-2 is restored
12:53 |  | Ashuganj (South)-Ghorashal 230kV ckt-1 was S/D due to OPGW conductor joining work
13:17 | 21:23 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-1 Scheduled S/D Due to Corrective maintenance work.
13:20 | 14:09 | Aminbazar 400/230/132kV S/S Bus-1 Scheduled S/D Due to 400 kV New ATR Shifting ( 400 kV BUS-1)
13:20 | 14:10 | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to 400 kV New ATR Shifting
13:30 | 14:10 | Gopalganj 400/132kV S/S 400kV Aminbazar Ckt-1 Project Work S/D Due to Aminbazar 400kv ss side project Work
| 14:06 | Siddhirganj 230/132kV S/S MTR 1 HT is restored.
14:15 |  | Aminbazar 400/230/132kV S/S Bus-2 Scheduled S/D Due to New ATR installation
14:32 | 15:20 | Chowmuhani 132/33kV S/S TR3-435T LT Forced S/D Due to LPBS Feeder-1 | [5 empty] | 20.0MW load interrup.
14:33 | 15:18 | Chowmuhani 132/33kV S/S TR3-435T HT Forced S/D Due to LPBS Feeder-1 | [5 empty] | 20.0MW
| 14:35 | Maniknagar-Matuail 132kV Ckt-1 is restored.
14:54 | 15:59 | Jashore 132/33kV S/S T-1 LT Forced S/D Due to red hot maintainence
14:55 | 15:58 | Jashore 132/33kV S/S T-1 HT Forced S/D Due to red hot maintainence
| 17:58 | Bogura(New)-Naogaon 132 kV Ckt-2 is restored.
| 17:58 | Bogura(New)-Naogaon 132 kV Ckt-2 is restored.
19:09 | 20:35 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to OPGW work between tower no 51-50 | [5 empty] | 104.0MW load interrup.
21:00 |  | Evening Peak Generation =10,794MW
23:40 | 00:05 | Madanganj-Munsiganj 132 kV Ckt-1 Tripped from Madanganj 132/33kV end showing Over current and earth fault relay.
86 A/B OPTD relays.
23:50 | 00:10 | Madanganj-Munsiganj 132 kV Ckt-1 Tripped from Munshiganj 132/33kV end showing Line Diff. Relay. relays.
04:00 |  | Extreme bad weather ( heavy rain and thunderstorm ) occurred all over the country that started from 04:00 hr.
Several machines were shut down to control the system frequency. The HVDC schedule is revised and Adani power was
also reduced load as per our Demand.
04:42 | 05:57 | Jaldhaka 132/33kV S/S 416T LT Tripped showing P142 relays Due to Dabigonj-3, 33 KV feeder Fault for Bad Weather with | [5 empty] | 18.0MW load interrup.
Running and Tendering.
04:42 | 05:55 | Jaldhaka 132/33kV S/S 406T LT Tripped showing P142 relays Due to Dabigonj-3, 33 KV feeder Fault for Bad Weather with | [5 empty] | 18.0MW load interrup.
Running and Tendering.
06:00 |  | Minimum Load: 5602 MW
06:46 |  | Bogura(New)-Naogaon 132 kV Ckt-2 Project Work S/D from Bogura 230/132kV end Due to Tower Height Extension. and
from Naogaon 132/33kV end Due to Shutdown for Bogura side
07:26 |  | Hathazari 230/132/33kV S/S Shikolbaha-02 Tripped showing Main relays.
07:26 |  | Shikalbaha 230/132kV S/S Hathazari-02 Tripped showing Main-1 Protection Relay, Main-2 protection relay relays.
07:44 |  | Bheramara 230/132kV S/S Transformer-2 LT Scheduled S/D Due to Aircell change
07:44 |  | Bheramara 230/132kV S/S Transformer-2 HT Scheduled S/D Due to Aircell change
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-03-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4221000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 78 | 656545 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 394 | 5787650 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 342 | 7226000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 8372500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 72960 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 250 | 6555084 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 113174 | Low demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 263308
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 134136
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 31680 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 212 | 3752765 | ST U/M.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 77904 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 426960 | Engine problem
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 121440 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 375872 | Line S/D
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 222261 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 872580 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 452700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 15 | 489400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 80861 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 198218 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 88 | 796032 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 200640 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 34 | 264960 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 717120 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 300960 | Engine problem
| Dhaka area Total |  |  |  | 5847 | 2517 | 42784710
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 0 | 20998 | Reserve.
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 98550
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 119040 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 604260 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 227 | 4865102
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 348763 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 61776 | Reserve.
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 520151 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 66 | 799920 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1732800
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 128064 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 871680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 30720 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21719
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 50 | 950945 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 464244
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 36 | 990250 | Low demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 60 | 702720 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 107 | 2201727 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 847 | 15533429
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 174 | 4289000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7379500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Gas shortage & ST Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 240 | 6551300 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 49 | 586512
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 45 | 575520 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 611534 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 557018 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 180 | 1573440 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 401652 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 156960
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 132 | 2414400
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 751600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 60312 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 391510 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 51300 | Reserve.
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 9 | 173880 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 233280 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 75 | 1022400 | Low demand
| Cumilla Area Total |  |  |  | 3285 | 1480 | 27781118
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 106 | 1485120 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 229572 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9150
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 75 | 532800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 113 | 1305600
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 246420
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 200880 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 328 | 4009542
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 971000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 31 | 597720 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 1208127 | ST U/M.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 407400
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 47 | 385992
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 47300 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1142016
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 1047360
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 151 | 2443480 | ST U/M.
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 175296 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 265 | 6568000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8686000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 141120
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8993300
| Sylhet Area Total |  |  |  | 2427 | 1669 | 33235111
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 796 | 20435636
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 0 | 245760 | Reserve.
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 5689152 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 18750 | Reserve.
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 30240 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 27936 | Transformer O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 375120
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1056 | 26822594
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 19 | 349300 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 171 | 3225808 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 860 | 18918800 | Line O/L
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 249 | 4123600 | On test.
| Barisal Area Total |  |  |  | 2265 | 1299 | 26617508
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 7663 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 176 | 3873555 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 387 | 7019600 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 322793 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 306960
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 92160
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 8957 | Reserve.
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve.
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 204672 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 75840 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 18960
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 764 | 16805455 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1392 | 28736615
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4137500 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 0 | 523363 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35527
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 36 | 538560 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 152496
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 974770
| Rangpur Area Total |  |  |  | 750 | 206 | 6362216
| Total |  |  |  | 22700 | 10794 | 211882843
| Eastern Grid Total |  |  |  | 14555 | 6841 | 123343910
| Western Grid Total |  |  |  | 8145 | 3953 | 88538933
| National Grid Total |  |  |  | 22700 | 10794 | 211882843
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-03-31
| (a) ENTIRE EASTERN GRID : |  | 7086.09 | MW | (b) ENTIRE WESTERN GRID : |  | 3305.2 | MW
| i) Dhaka area |  | 3685.29 | MW | i) Khulna area |  | 1293.8 | MW
| ii) Chittagong area |  | 1141.8 | MW | ii) Rajshahi area |  | 1005 | MW
| iii) Comilla area |  | 1048 | MW | iii) Barisal area |  | 331.4 | MW
| iv) Mymensingh area |  | 801 | MW | iv) Rangpur area |  | 675 | MW
| v) Sylhet area |  | 410 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10391.29 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 8 | 09:00 | Chhatak | 23 | 21:00 | Kamrangirchar | 47 | 00:00 | Natore | 118 | 03:00 | Shitalakhya | 93 | 15:00
2 | AKSML | 77 | 00:00 | Chowmuhani | 154 | 21:00 | Kaptai | 4 | 18:30 | Nawabganj | 37.8 | 19:30 | Sholosohor | 26 | 19:00
3 | Aftabnagar | 28 | 19:00 | Chuadanga | 82 | 21:00 | Kazla | 79 | 00:00 | Netrakona | 98 | 18:00 | Shyampur | 168 | 00:00
4 | Agargaon | 59 | 21:00 | Coxsbazar | 123 | 21:00 | Keranigonj | 62 | 19:30 | New | 56 | 00:00 | Siddhirganj | 112 | 22:00
5 | Agrabad | 50 | 19:00 | Cumilla(N) | 131 | 21:00 | Khagrachori | 26 | 18:30 | Niamatpur | 71 | 12:00 | Sirajganj | 68 | 20:00
6 | Amnura | 59 | 21:00 | Cumilla(S) | 134 | 19:00 | Khulna | 91 | 21:00 | Noapara | 38 | 19:30 | Sonargaon | 93 | 00:00
7 | Ashuganj | 60 | 00:00 | Daudkandi | 106 | 19:30 | Khulshi | 154 | 00:00 | PHP | 4 | 13:00 | Sreemongol | 40 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 20 | 12:00 | Kishoreganj | 106 | 19:30 | Pabna | 90 | 03:00 | Srinagar | 35.55 | 20:00
9 | BSRM | 109 | 07:00 | Dhamrai | 98 | 19:30 | Kodda | 222 | 00:00 | Palashbari | 96 | 19:30 | Sunamganj | 38 | 21:00
10 | Bagerhat | 70 | 20:00 | Dhanmondi | 90 | 19:30 | Kulaura | 32 | 18:30 | Panchagarh | 43 | 17:00 | Sylhet | 107 | 21:00
11 | Bakulia | 82 | 19:30 | Dohazari | 88 | 19:00 | Kurigram | 58 | 10:00 | Patuakhali | 75 | 00:00 | TK | 24.6 | 19:00
12 | Banani | 28 | 19:30 | Faridpur | 110 | 19:30 | Kushtia | 98 | 19:30 | Payra | 12.6 | 00:00 | Tangail | 154 | 19:00
13 | Bangabhaban | 4 | 00:00 | Fatullah | 55 | 00:00 | Lalbag | 66 | 00:00 | Postogola | 31 | 20:00 | Thakurgaon | 70 | 19:00
14 | Barapukuria | 48 | 09:00 | Fenchuganj | 36 | 21:00 | Lalmonirhat | 40 | 18:00 | Purbachal | 15 | 13:00 | Tongi | 103 | 00:00
15 | Barguna | 14 | 00:00 | Feni | 106 | 21:00 | Madanganj | 36 | 16:00 | Purbasadipur | 109 | 12:00 | Ullon | 38 | 21:00
16 | Barishal | 86 | 20:00 | GPH | 84 | 15:00 | Madaripur | 78 | 21:00 | Rahanpur_I | 0 | 00:00 | Uttara | 63 | 19:30
17 | Barishal-230 | 66 | 19:00 | Ghorashal | 59 | 00:00 | Madartek | 66 | 22:00 | Rahim | 35 | 00:00 | UttaraNew | 17 | 12:00
18 | Baroaulia | 65 | 00:00 | Goalpara | 30 | 18:30 | Madunaghat | 48 | 19:30 | Rajbari | 50 | 03:00 | Zigatola | 48 | 21:00
19 | Baroirhat | 38 | 20:00 | Gollamari | 31 | 00:00 | Magura | 44 | 00:00 | Rajendrapur | 90 | 19:30
20 | Bashundhara | 122 | 19:30 | Gopalganj | 76.8 | 21:00 | Mahasthangarh | 62 | 19:30 | Rajshahi | 120 | 03:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 68 | 19:00 | Manikganj | 72 | 22:00 | Rajshahi-230 | 28 | 04:00
22 | Beanibazar | 48 | 18:30 | Halishahar | 68 | 19:30 | Maniknagar | 49 | 22:00 | Ramganj | 88 | 19:30
23 | Benapole | 56 | 20:00 | HaripurSBU | 146 | 00:00 | Matarbari | 40 | 00:00 | Rampur | 32 | 19:30
24 | Bhaluka | 94 | 21:00 | Hasnabad | 52 | 20:00 | Matuail | 58 | 00:00 | Rangamati | 14 | 19:00
25 | Bhandaria | 38 | 21:00 | Hathazari | 53 | 19:00 | Millgate | 58 | 00:00 | Rangpur | 118 | 17:00
26 | Bhangura | 25 | 03:00 | Ishurdi | 50 | 03:00 | Mirpur | 103 | 20:00 | Ruppur | 4.4 | 12:00
27 | Bheramara(GK) | 43 | 19:00 | Jaldhaka | 59 | 17:00 | Mirsorai | 3 | 19:30 | SSM | 0 | 00:00
28 | Bhulta | 222 | 00:00 | Jamalpur | 110 | 19:30 | Mithapukur | 36 | 03:00 | Saidpur | 89 | 13:00
29 | Bog-Sherpur | 44 | 09:00 | Jashore | 97 | 19:00 | Modern | 0 | 00:00 | Satkhira | 103 | 21:00
30 | Bogura | 116 | 22:00 | Jhenaidah | 96 | 19:00 | Mogbazar | 91 | 20:00 | Satmasjid | 91 | 19:00
31 | Borhanuddin | 45 | 21:00 | Joydebpur | 137 | 00:00 | Mongla | 23 | 00:00 | Savar | 130 | 00:00
32 | Brahmanbaria | 140 | 20:00 | Joypurhat | 49 | 03:00 | Motijheel | 26 | 19:30 | Shahjadpur | 66 | 19:30
33 | Cantonment | 107 | 21:00 | Juldah | 24 | 15:00 | Munshiganj | 81 | 21:00 | Shahjibazar | 91 | 00:00
34 | Chandpur | 44 | 19:30 | KSRM | 30 | 03:00 | Mymensingh | 165 | 18:00 | Shahmirpur | 32.1 | 01:00
35 | Chandraghona | 26 | 19:00 | Kabirpur | 220 | 00:00 | Naogaon | 93 | 08:00 | Shariatpur | 54 | 18:30
36 | Chapai | 61 | 04:00 | Kachua | 61 | 21:00 | Narail | 43 | 19:00 | Sherpur | 106 | 19:30
37 | Charsaidpur | 51 | 09:00 | Kallyanpur | 78 | 19:30 | Narinda | 48 | 13:00 | Shikalbaha | 31 | 00:00
38 | Chauddagram | 40 | 21:00 | Kalurghat | 24 | 00:00 | Narshingdi | 150 | 22:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-03-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 419 | 02:00 | 394 | 22:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 403 | 02:00 | 383 | 12:00 | Madunaghat_I | 402 | 19:30 | 375 | 09:00
| Bibiana | 408 | 19:30 | 397 | 11:00 | Payra | 422 | 02:00 | 413 | 00:00
| BIPTC | 406 | 02:00 | 387 | 12:00 | Rahanpur_I | 418 | 18:30 | 405 | 10:00
| Gopalganj | 423 | 01:00 | 392 | 23:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 243 | 02:00 | 225 | 23:00 | Hasnabad | 238 | 02:00 | 230 | 12:00
| AKSML | 238 | 04:00 | 204 | 08:00 | Hathazari | 232 | 20:00 | 217 | 09:00
| Aminbazar | 246 | 02:00 | 233 | 07:00 | Ishurdi | 237 | 01:00 | 228 | 12:00
| Ashuganj | 242 | 02:00 | 230 | 11:00 | Jhenaidah | 234 | 06:00 | 221 | 20:00
| Baghabari | 233 | 01:00 | 227 | 09:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Barapukuria | 223 | 06:00 | 215 | 09:00 | Keranigonj | 243 | 02:00 | 226 | 12:00
| Barishal | 240 | 05:00 | 230 | 23:00 | Khulna(S) | 243 | 01:00 | 223 | 21:00
| Bheramara | 235 | 01:00 | 225 | 12:00 | Madunaghat_I | 235 | 19:30 | 218 | 09:00
| Bhulta | 244 | 02:00 | 229 | 12:00 | Maniknagar | 237 | 04:00 | 227 | 23:00
| Bibiana | 241 | 19:00 | 233 | 11:00 | Meghnaghat | 240 | 02:00 | 235 | 10:00
| BIPTC | 237 | 01:00 | 226 | 12:00 | Mirsorai | 235 | 19:30 | 218 | 10:00
| Bogura | 228 | 19:30 | 219 | 10:00 | Rajshahi | 233 | 02:00 | 225 | 17:00
| Borhanuddin | 241 | 06:00 | 232 | 00:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 235 | 04:00 | 222 | 12:00 | Rampura | 242 | 02:00 | 227 | 12:00
| Cumilla(N) | 240 | 02:00 | 225 | 12:00 | Shikalbaha | 236 | 19:00 | 217 | 10:00
| Fenchuganj | 246 | 18:00 | 238 | 11:00 | Shyampur | 241 | 02:00 | 227 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 244 | 01:00 | 230 | 11:00
| GPH | 234 | 06:00 | 219 | 09:00 | Sirajgonj | 232 | 19:00 | 226 | 17:00
| Haripur | 242 | 02:00 | 227 | 12:00 | Tongi | 236 | 01:00 | 222 | 11:00
| 132 kV | KV |  | KV
| Aftabnagar | 140 | 02:00 | 129 | 12:00 | Lalbag | 139 | 02:00 | 129 | 23:00
| Agargaon | 141 | 02:00 | 130 | 12:00 | Lalmonirhat | 130 | 14:00 | 121 | 09:00
| Agrabad | 134 | 05:00 | 124 | 09:00 | Madanganj | 142 | 02:00 | 130 | 11:00
| AKS | 133 | 18:30 | 125 | 09:00 | Madaripur | 136 | 05:00 | 129 | 23:00
| Aminbazar | 142 | 02:00 | 132 | 11:00 | Madartek | 141 | 02:00 | 130 | 12:00
| Amnura | 134 | 05:00 | 129 | 10:00 | Madunaghat | 135 | 06:00 | 125 | 09:00
| Ashuganj | 142 | 02:00 | 135 | 11:00 | Magura | 137 | 05:00 | 129 | 21:00
| Bagerhat | 136 | 01:00 | 124 | 21:00 | Mahasthangarh | 135 | 18:30 | 126 | 09:00
| Bakulia | 134 | 04:00 | 124 | 23:00 | Manikganj | 145 | 01:00 | 130 | 17:00
| Banani | 141 | 02:00 | 131 | 11:00 | Maniknagar | 141 | 02:00 | 130 | 23:00
| Bangabhaban | 141 | 02:00 | 129 | 23:00 | Matarbari | 127 | 06:00 | 111 | 21:00
| Barapukuria | 136 | 18:30 | 129 | 09:00 | Matuail | 133 | 00:00 | 129 | 23:00
| Barguna | 130 | 06:00 | 125 | 21:00 | Millgate | 144 | 01:00 | 129 | 12:00
| Barishal | 135 | 04:00 | 129 | 21:00 | Mirpur | 137 | 01:00 | 128 | 23:00
| Barishal-230 | 137 | 05:00 | 130 | 20:00 | Mithapukur | 133 | 19:00 | 123 | 08:00
| Baroaulia | 135 | 19:00 | 126 | 11:00 | Modern | 135 | 19:00 | 126 | 10:00
| Baroirhat | 136 | 04:00 | 127 | 10:00 | Mogbazar | 142 | 02:00 | 131 | 12:00
| Bashundhara | 143 | 01:00 | 130 | 12:00 | Mongla | 135 | 06:00 | 122 | 21:00
| BashundharaCement | 142 | 02:00 | 130 | 11:00 | Motijheel | 141 | 02:00 | 129 | 23:00
| Beanibazar | 137 | 02:00 | 132 | 00:00 | Munshiganj | 138 | 02:00 | 131 | 12:00
| Benapole | 134 | 05:00 | 123 | 21:00 | Mymensingh | 138 | 01:00 | 120 | 17:00
| Bhaluka | 135 | 01:00 | 118 | 17:00 | Naogaon | 132 | 18:00 | 119 | 09:00
| Bhandaria | 135 | 07:00 | 126 | 20:00 | Narail | 138 | 06:00 | 127 | 21:00
| Bhangura | 139 | 01:00 | 134 | 09:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 136 | 01:00 | 132 | 11:00 | Narshingdi | 144 | 02:00 | 128 | 00:00
| Bheramara(GK) | 138 | 00:00 | 133 | 20:00 | Natore | 135 | 06:00 | 130 | 03:00
| Bhulta | 140 | 02:00 | 123 | 23:00 | Nawabganj | 138 | 02:00 | 129 | 23:00
| Bog-Sherpur | 136 | 18:30 | 129 | 09:00 | Netrakona | 136 | 01:00 | 115 | 17:00
| Bogura | 135 | 06:00 | 130 | 04:00 | New | 143 | 02:00 | 130 | 12:00
| Bogura-230 | 137 | 18:30 | 128 | 10:00 | Niamatpur | 128 | 18:30 | 121 | 03:00
| Brahmanbaria | 140 | 02:00 | 131 | 11:00 | Noapara | 136 | 01:00 | 125 | 21:00
| Cantonment | 141 | 02:00 | 129 | 23:00 | Pabna | 137 | 01:00 | 132 | 11:00
| Chandpur | 140 | 19:30 | 125 | 09:00 | Palashbari | 132 | 18:30 | 123 | 09:00
| Chandraghona | 137 | 05:00 | 127 | 09:00 | Panchagarh | 135 | 18:30 | 118 | 08:00
| Chapai | 135 | 06:00 | 129 | 21:00 | Patuakhali | 129 | 15:00 | 125 | 21:00
| Charsaidpur | 141 | 02:00 | 130 | 12:00 | Payra | 131 | 06:00 | 126 | 21:00
| Chauddagram | 139 | 03:00 | 127 | 10:00 | PHP | 137 | 04:00 | 125 | 12:00
| Chhatak | 135 | 04:00 | 132 | 00:00 | Postogola | 142 | 02:00 | 129 | 23:00
| Chowmuhani | 132 | 05:00 | 118 | 18:00 | Purbachal | 141 | 01:00 | 131 | 11:00
| Chuadanga | 137 | 06:00 | 125 | 21:00 | Purbasadipur | 133 | 18:30 | 117 | 09:00
| Coxsbazar | 129 | 07:00 | 110 | 22:00 | Rahim | 145 | 02:00 | 133 | 00:00
| Cumilla(N) | 140 | 02:00 | 130 | 12:00 | Rajbari | 136 | 06:00 | 129 | 12:00
| Cumilla(S) | 139 | 03:00 | 126 | 19:00 | Rajendrapur | 146 | 02:00 | 127 | 12:00
| Daudkandi | 142 | 02:00 | 130 | 00:00 | Rajshahi | 134 | 06:00 | 128 | 12:00
| Dhaka | 141 | 01:00 | 130 | 12:00 | Rajshahi-230 | 135 | 06:00 | 128 | 21:00
| Dhamrai | 141 | 02:00 | 128 | 12:00 | Ramganj | 136 | 04:00 | 120 | 09:00
| Dhanmondi | 144 | 02:00 | 132 | 23:00 | Rampur | 134 | 19:30 | 127 | 09:00
| Dohazari | 133 | 06:00 | 123 | 22:00 | Rampura | 141 | 02:00 | 131 | 11:00
| Faridpur | 136 | 01:00 | 129 | 23:00 | Rangamati | 136 | 06:00 | 126 | 23:00
| Fatullah | 142 | 02:00 | 131 | 11:00 | Rangpur | 132 | 18:30 | 122 | 09:00
| Fenchuganj | 140 | 01:00 | 136 | 00:00 | Ruppur | 138 | 06:00 | 133 | 11:00
| Feni | 136 | 05:00 | 127 | 12:00 | Saidpur | 131 | 19:00 | 122 | 13:00
| Ghorashal | 148 | 02:00 | 129 | 00:00 | Satkhira | 138 | 01:00 | 122 | 21:00
| Goalpara | 138 | 01:00 | 130 | 17:00 | Satmasjid | 140 | 02:00 | 130 | 12:00
| Gollamari | 136 | 02:00 | 128 | 21:00 | Savar | 142 | 02:00 | 128 | 14:00
| Gopalganj | 136 | 06:00 | 128 | 21:00 | Shahjadpur | 144 | 04:00 | 137 | 10:00
| Gopalganj-400 | 138 | 02:00 | 130 | 23:00 | Shahjibazar | 140 | 02:00 | 132 | 12:00
| Gulshan | 139 | 02:00 | 130 | 12:00 | Shahmirpur | 134 | 19:00 | 124 | 09:00
| Halishahar | 135 | 06:00 | 125 | 09:00 | Shariatpur | 137 | 02:00 | 129 | 22:00
| Haripur | 145 | 02:00 | 133 | 00:00 | Sherpur | 137 | 18:30 | 118 | 09:00
| HaripurSBU | 145 | 02:00 | 133 | 12:00 | Shikalbaha | 135 | 06:00 | 127 | 10:00
| Hasnabad | 137 | 06:00 | 131 | 10:00 | Shikalbaha-230 | 135 | 19:00 | 125 | 10:00
| Hathazari | 135 | 00:00 | 129 | 10:00 | Shitalakhya | 142 | 02:00 | 130 | 12:00
| Ishurdi | 138 | 06:00 | 133 | 12:00 | Sholosohor | 135 | 06:00 | 126 | 12:00
| Jaldhaka | 133 | 18:30 | 122 | 09:00 | Shyampur | 137 | 02:00 | 132 | 00:00
| Jamalpur | 140 | 18:30 | 126 | 08:00 | Shyampur-230 | 140 | 02:00 | 130 | 12:00
| Jashore | 135 | 06:00 | 124 | 21:00 | Siddhirganj | 139 | 05:00 | 132 | 12:00
| Jhenaidah | 140 | 06:00 | 132 | 21:00 | Sirajganj | 137 | 18:30 | 133 | 10:00
| Jhenaidah-230 | 140 | 06:00 | 133 | 03:00 | Sonargaon | 143 | 02:00 | 129 | 12:00
| Joydebpur | 146 | 01:00 | 131 | 12:00 | Sreemongol | 139 | 02:00 | 132 | 11:00
| Joypurhat | 131 | 18:00 | 118 | 09:00 | Srinagar | 141 | 02:00 | 129 | 10:00
| Juldah | 134 | 06:00 | 125 | 10:00 | SSM | 138 | 04:00 | 132 | 07:00
| Kabirpur | 145 | 01:00 | 128 | 12:00 | Sunamganj | 133 | 03:00 | 130 | 18:30
| Kachua | 139 | 03:00 | 125 | 09:00 | Sylhet | 136 | 02:00 | 133 | 15:00
| Kaliakoir | N/A | N/A | N/A | N/A | Tangail | 143 | 01:00 | 130 | 09:00
| Kallyanpur | 142 | 02:00 | 130 | 23:00 | Thakurgaon | 136 | 18:30 | 114 | 09:00
| Kalurghat | 135 | 18:00 | 125 | 10:00 | TK | 135 | 19:00 | 124 | 08:00
| Kamrangirchar | 137 | 02:00 | 130 | 10:00 | Tongi | 144 | 02:00 | 131 | 13:00
| Kaptai | 138 | 18:00 | 132 | 07:00 | Ullon | 141 | 02:00 | 131 | 12:00
| Kazla | 140 | 03:00 | 131 | 12:00 | Uttara | 141 | 02:00 | 129 | 12:00
| Keranigonj | 138 | 02:00 | 130 | 10:00 | UttaraNew | 143 | 01:00 | 130 | 12:00
| Khagrachori | 137 | 06:00 | 127 | 10:00 | Zigatola | 138 | 02:00 | 129 | 10:00
| Khulna | 137 | 18:00 | 125 | 21:00
| Khulna(S) | 138 | 01:00 | 126 | 21:00
| Khulshi | 133 | 06:00 | 125 | 09:00
| Kishoreganj | 138 | 01:00 | 126 | 12:00
| Kodda | 145 | 01:00 | 128 | 12:00
| KSRM | 134 | 18:00 | 127 | 12:00
| Kulaura | 138 | 01:00 | 135 | 13:00
| Kurigram | 132 | 19:00 | 122 | 09:00
| Kushtia | 138 | 06:00 | 132 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-03-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1000 | 5752 | 3957 | 9709 |  |  |  | QF-LDC-11
0:30 | 905 | 5133 | 3581.5 | 8714.5 | Date: | 2023-03-31
1:00 | 810 | 4514 | 3206 | 7720
1:30 | 590 | 4115.5 | 2898 | 7013.5
2:00 | 370 | 3717 | 2590 | 6307
2:30 | 225 | 3786 | 2849 | 6635 | [5 empty] | Gen. at Eve. Peak | 10794 | 10794 MW (21:00 )
3:00 | 80 | 3855 | 3108 | 6963 | [6 empty] | 21:00
3:30 | 294 | 4023 | 3220 | 7243 | [5 empty] | Gen. at Day Peak | 9176 | 9176 MW (12:00 )
4:00 | 508 | 4191 | 3332 | 7523 | [6 empty] | 12:00
4:30 | 559 | 4075.5 | 3268.5 | 7344 | [5 empty] | Highest Generation | 10798
5:00 | 610 | 3960 | 3205 | 7165 | [6 empty] | 22:00
5:30 | 630 | 3791 | 3090 | 6881
6:00 | 650 | 3622 | 2975 | 6597
6:30 | 640 | 3617.5 | 3011.5 | 6629
7:00 | 630 | 3613 | 3048 | 6661
7:30 | 827 | 3732 | 3163 | 6895
8:00 | 1024 | 3851 | 3278 | 7129
8:30 | 1042 | 3947 | 3386.5 | 7333.5
9:00 | 1060 | 4043 | 3495 | 7538
9:30 | 1090 | 4154.5 | 3622 | 7776.5
10:00 | 1120 | 4266 | 3749 | 8015
10:30 | 1195 | 4459 | 3819 | 8278
11:00 | 1270 | 4652 | 3889 | 8541
11:30 | 1171 | 4970 | 3888.5 | 8858.5
12:00 | 1072 | 5288 | 3888 | 9176
12:30 | 1026 | 5520 | 3848 | 9368
13:00 | 980 | 5752 | 3808 | 9560
13:30 | 1040 | 5505.5 | 3801 | 9306.5
14:00 | 1100 | 5259 | 3794 | 9053
14:30 | 1086 | 5422.5 | 3767.5 | 9190
15:00 | 1072 | 5586 | 3741 | 9327
15:30 | 996 | 5628 | 3697.5 | 9325.5
16:00 | 920 | 5670 | 3654 | 9324
16:30 | 841 | 5751 | 3660.5 | 9411.5
17:00 | 762 | 5832 | 3667 | 9499
17:30 | 701 | 5939.5 | 3722.5 | 9662
18:00 | 640 | 6047 | 3778 | 9825
18:30 | 545 | 6285.5 | 3807.5 | 10093
19:00 | 450 | 6524 | 3837 | 10361
19:30 | 310 | 6676 | 3809 | 10485
20:00 | 190 | 6753 | 3715 | 10468 |  |  |  | Executive Engineer
20:30 | 315 | 6797 | 3834 | 10631 |  |  |  | Network Operation Division
21:00 | 440 | 6841 | 3953 | 10794
21:30 | 550 | 6759.5 | 4036.5 | 10796
22:00 | 660 | 6678 | 4120 | 10798 |  |  |  |  | Page 6 of 7
22:30 | 735 | 6412.5 | 4096 | 10508.5
23:00 | 810 | 6147 | 4072 | 10219
23:30 | 905 | 5949.5 | 4014.5 | 9964
24:00 | 1000 | 5752 | 3957 | 9709
10794 MW (21:00 )
9176 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-03-31 |  | Energy |  | 211882843
[13 empty] | 2023-03-31 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3743 | 906 | 2034 | 0 | 775 | 2053 | 25 | 0 | 51 | 122 | 0 | 0
0:30 | 3375 | 855.5 | 1775 | 0 | 643.5 | 1862 | 25 | 0 | 59.5 | 119 | 0 | 0 |  | Date: | 43554
1:00 | 3007 | 805 | 1516 | 0 | 512 | 1671 | 25 | 0 | 68 | 116 | 0 | 0
1:30 | 2752 | 653 | 1416 | 0 | 449.5 | 1543.5 | 25 | 0 | 59.5 | 115 | 0 | 0 | [8 empty] | Total Energy | 211.8828 | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 211.883 MKWHr Energy Not Served 0.087 MKWHr Energy Requirement 211.970 MKWHr
2:00 | 2497 | 501 | 1316 | 0 | 387 | 1416 | 25 | 0 | 51 | 114 | 0 | 0 | [8 empty] | Energy not Served | 0.086702
2:30 | 2564.5 | 670.5 | 1433.5 | 0 | 389.5 | 1434 | 25 | 0 | 51 | 67 | 0 | 0 | [8 empty] | Energy Requirement | 211.9695
3:00 | 2632 | 840 | 1551 | 0 | 392 | 1452 | 25 | 0 | 51 | 20 | 0 | 0
3:30 | 2717 | 872 | 1622 | 0 | 410 | 1512 | 25 | 0 | 51 | 34 | 0 | 0 | [7 empty] | Shortage
4:00 | 2802 | 904 | 1693 | 0 | 428 | 1572 | 25 | 0 | 51 | 48 | 0 | 0
4:30 | 2791 | 904.5 | 1559 | 0 | 402 | 1571.5 | 25 | 0 | 31 | 60 | 0 | 0
5:00 | 2780 | 905 | 1425 | 0 | 376 | 1571 | 25 | 0 | 11 | 72 | 0 | 0
5:30 | 2743.5 | 869 | 1388 | 0 | 260 | 1515 | 25 | 0 | 5.5 | 75 | 0 | 0
6:00 | 2707 | 833 | 1351 | 0 | 144 | 1459 | 25 | 0 | 0 | 78 | 0 | 0
6:30 | 2772 | 833 | 1353 | 0 | 86.5 | 1464.5 | 25 | 0 | 0 | 70 | 25 | 0 | [6 empty] | Coal
7:00 | 2837 | 833 | 1355 | 0 | 29 | 1470 | 25 | 0 | 0 | 62 | 50 | 0
7:30 | 2889.5 | 833.5 | 1463.5 | 0 | 29 | 1500 | 25 | 0 | 0 | 62 | 92.5 | 11.9805 | [5 empty] | Oil
8:00 | 2942 | 834 | 1572 | 0 | 29 | 1530 | 25 | 0 | 0 | 62 | 135 | 23.9609
8:30 | 3012 | 845 | 1583.5 | 0 | 37.5 | 1591.5 | 25 | 0 | 0 | 68 | 171 | 24.4217
9:00 | 3082 | 856 | 1595 | 0 | 46 | 1653 | 25 | 0 | 0 | 74 | 207 | 24.8825
9:30 | 3142 | 880 | 1599.5 | 0 | 70 | 1722 | 25 | 0 | 0 | 80 | 258 | 21.657
10:00 | 3202 | 904 | 1604 | 0 | 94 | 1791 | 25 | 0 | 0 | 86 | 309 | 18.4315
10:30 | 3265 | 904 | 1610 | 0 | 247.5 | 1797 | 25 | 0 | 18 | 91 | 320.5 | 15.206
11:00 | 3328 | 904 | 1616 | 0 | 401 | 1803 | 25 | 0 | 36 | 96 | 332 | 11.9805
11:30 | 3465 | 904.5 | 1747.5 | 0 | 471.5 | 1802 | 25 | 0 | 36 | 100 | 307 | 11.5197
12:00 | 3602 | 905 | 1879 | 0 | 542 | 1801 | 25 | 0 | 36 | 104 | 282 | 11.0589
12:30 | 3564 | 905 | 1944.5 | 0 | 731.5 | 1792.5 | 25 | 0 | 36 | 114 | 255.5 | 5.5294
13:00 | 3526 | 905 | 2010 | 0 | 921 | 1784 | 25 | 0 | 36 | 124 | 229 | 0
13:30 | 3526 | 905 | 2010 | 0 | 921 | 1784 | 25 | 0 | 36 | 124 | 229 | 0
14:00 | 3526 | 905 | 2010 | 0 | 921 | 1784 | 25 | 0 | 36 | 124 | 229 | 0
14:30 | 3467.5 | 904.5 | 1927 | 0 | 985 | 1766 | 25 | 0 | 36 | 114 | 218.5 | 0
15:00 | 3409 | 904 | 1844 | 0 | 1049 | 1748 | 25 | 0 | 36 | 104 | 208 | 0
15:30 | 3452.5 | 904 | 1850 | 0 | 1054 | 1746.5 | 25 | 0 | 36 | 103 | 154.5 | 0
16:00 | 3496 | 904 | 1856 | 0 | 1059 | 1745 | 25 | 0 | 36 | 102 | 101 | 0
16:30 | 3572 | 904 | 1856 | 0 | 1098.5 | 1749 | 25 | 0 | 36 | 106 | 65 | 0
17:00 | 3648 | 904 | 1856 | 0 | 1138 | 1753 | 25 | 0 | 36 | 110 | 29 | 0
17:30 | 3607.5 | 904.5 | 1872.5 | 0 | 1290.5 | 1763.5 | 25 | 0 | 66 | 117 | 15.5 | 0
18:00 | 3567 | 905 | 1889 | 0 | 1443 | 1774 | 25 | 0 | 96 | 124 | 2 | 0
18:30 | 3554 | 899.5 | 1913 | 0 | 1675 | 1761 | 25 | 0 | 135.5 | 129 | 1 | 0
19:00 | 3541 | 894 | 1937 | 0 | 1907 | 1748 | 25 | 0 | 175 | 134 | 0 | 0
19:30 | 3525 | 796 | 1977 | 0 | 2035 | 1882 | 25 | 0 | 121 | 124 | 0 | 0
20:00 | 3636 | 796 | 2112 | 0 | 1821 | 1881 | 25 | 0 | 67 | 130 | 0 | 0
20:30 | 3716.5 | 796 | 2180.5 | 0 | 1753 | 1962 | 25 | 0 | 67 | 131 | 0 | 0
21:00 | 3797 | 796 | 2249 | 0 | 1685 | 2043 | 25 | 0 | 67 | 132 | 0 | 0
21:30 | 3803.5 | 822 | 2253.5 | 0 | 1602.5 | 2098.5 | 25 | 0 | 59 | 132 | 0 | 0
22:00 | 3810 | 848 | 2258 | 0 | 1520 | 2154 | 25 | 0 | 51 | 132 | 0 | 0
22:30 | 3799.5 | 876.5 | 2235 | 0 | 1234 | 2157.5 | 25 | 0 | 51 | 130 | 0 | 0
23:00 | 3789 | 905 | 2212 | 0 | 948 | 2161 | 25 | 0 | 51 | 128 | 0 | 0
23:30 | 3766 | 905.5 | 2123 | 0 | 861.5 | 2107 | 25 | 0 | 51 | 125 | 0 | 0 |  | Max Temp. in Dhaka |  | 31.6° C
24:00 | 3743 | 906 | 2034 | 0 | 775 | 2053 | 25 | 0 | 51 | 122 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 211.883 MKWHr Energy Not Served 0.087 MKWHr Energy Requirement 211.970 MKWHr
Note on W13: Author:

## Generation
g | 2023-03-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604260
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [17 empty] | 1 |  | 8 | 8 |  |  |  |  | 0 | 20998
| Teknaf 20MW PP (Solartech) | [8 empty] | 0 | 18 | 18 | 15 | 17 | 17 | 13 | 6 | 3 | 0 | [8 empty] | 98550
6 | Sikalbaha 225MW CCPP (Gas) | 186 | 186 | 186 | 185 | 186 | 185 | 186 | 201 | 202 | 219 | 218 | 219 | 220 | 216 | 216 | 220 | 218 | 228 |  | 225 | 226 | 224 | 227 | 226 | 215 | 201 | 4865102
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 51 | 51 | 51 | 11 | [14 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 520151
12 | Hathazari 100 MW peaking PP | [17 empty] | 12 |  | 40 | 18 | [5 empty] | 61776
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 0 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 348763
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 90 | 90 | 90 | 170 | 140 | 90 | 90 | 140 | 140 | 140 | 140 | 218 | 220 | 130 | 130 | 130 | 130 | 130 |  | 225 | 225 | 220 | 212 | 210 | 222 | 170 | 3752765
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 0 | 10 | 15 | 15 | 15 | 15 | 15 |  | 45 | 80 | 15 | 15 |  |  | 0 | 198218
19 | Ashuganj 195MW PP (APSCL-United) | 8 | [24 empty] | 0 | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4221000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | [6 empty] | 5 | 5 | 5 | 5 | 15 | 40 | 47 | 45 | 45 | 46 | 48 |  | 49 | 49 | 49 | 49 | 49 | 49 | 46 | 586512
33 | Ashuganj 225 MW CCPP | 150 | 132 | 161 | 161 | 159 | 131 | 155 | 184 | 200 | 184 | 186 | 184 | 183 | 189 | 187 | 201 | 202 | 190 |  | 192 | 190 | 187 | 174 | 172 | 171 | 182 | 4289000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 280 | 270 | 270 | 300 | 300 | 300 | 300 | 280 | 315 | 290 | 290 | 305 | 280 | 290 | 290 | 315 | 350 | 290 |  | 290 | 290 | 305 | 290 | 290 | 290 | 320 | 7379500
| Ashuganj 420 MW CCPP(East) | 250 | 220 | 260 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 401 | 300 | 250 | 250 | 250 | 250 | 250 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 6551300
35 | Ashuganj 55 MW PP (Precision) | 0 | [8 empty] | 0 | 2 | 10 | 35 | 47 | 47 | 48 | 51 | 53 |  | 45 | 45 | 45 | 45 | 45 | 45 | 35 | 575520
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 352 | [5 empty] | 29 | 33 | 49 | 158 | 268 | 301 | 349 | 282 | 348 | 358 | 358 | 371 |  | 360 | 341 | 344 | 394 | 395 | 397 | 398 | 5787650
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 270 | 330 | 360 | 300 | 300 | 300 | 330 | 330 | 330 | 330 | 450 | 400 | 300 | 340 | 340 | 340 | 380 |  | 400 | 400 | 450 | 450 | 450 | 450 | 400 | 8372500
41 | Haripur 360MW CCPP(HPL) | 265 | 240 | 255 | 353 | 285 | 266 | 280 | 305 | 308 | 354 | 353 | 338 | 338 | 255 | 303 | 303 | 303 | 303 |  | 242 | 243 | 273 | 342 | 347 | 347 | 345 | 7226000
42 | RPCL 210MW CCPP | 87 | 77 | 77 | 76 | 89 | 88 | 48 | 47 | 47 | 47 | 46 | 46 | 45 | 45 | 45 | 45 | 45 | 44 |  | 45 | 57 | 57 | 106 | 100 | 96 | 94 | 1485120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 6 | 19 | 33 | 50 | 37 | 36 | 41 | 23 | 9 | 7 | 1 | 0 | [8 empty] | 246420
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 41 | 41 | 41 | 41 | 43 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 971000
45 | Fenchugonj CCPP Phase-2 | 31 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 597720
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 61 | 40 | 40 | 62 | 62 | 62 | 63 |  | 63 | 40 | 40 | 64 | 64 | 63 | 40 | 1142016
48 | Shahjibazar 86MW PP (Shahjibazar) | 10 | [6 empty] | 10 | 10 | 10 | 10 | 89 | 89 | 10 | 88 | 88 | 88 | 88 |  | 88 | 88 | 89 | 89 | 89 | 89 | 89 | 1047360
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 19 | 19 | 65 | 66 | 66 | 67 | 82 | 90 | 90 | 106 | 106 | 108 | 109 | 109 | 109 | 109 | 143 | 145 |  | 145 | 145 | 145 | 151 | 163 | 162 | 160 | 2443480
51 | Sylhet 20 MW GTPP | 18 | 18 | 19 | 19 | 19 | 19 | 18 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [10 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 141120
54 | Hobiganj 11MW PP Cofidence-E | 8 | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 47300
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | [7 empty] | 5 | 5 | 5 | 5 | 53 | 11 | 11 | 11 | 11 | 11 |  | 40 | 53 | 51 | 50 | 51 | 51 | 11 | 407400
56 | Shahjahanulla 25 MW PP | 16 | [11 empty] | 8 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 175296
57 | Bibiana-II 341 MW CCPP (Summit) | 250 | 255 | 285 | 285 | 270 | 255 | 260 | 275 | 270 | 270 | 280 | 270 | 275 | 270 | 275 | 275 | 280 | 275 |  | 250 | 265 | 260 | 265 | 260 | 250 | 270 | 6568000
| Bibiyana South 400 MW | 315 | 370 | 370 | 370 | 340 | 340 | 370 | 370 | 370 | 400 | 400 | 400 | 380 | 340 | 394 | 394 | 390 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 8993300
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 12 | 17 | 17 | 17 | 17 |  |  |  | 17 | 22 | 35 | 55 |  | 0 | 222261
59 | Tangail Palli Power Gen 22 MW | [11 empty] | 0 | 3 | 16 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 12 | 200880
60 | Barabkunda 22 MW PP (Regent) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 7 |  | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 128064
61 | Narshingdi 22 MW PP (Doreen) | [11 empty] | 10 | 7 | 7 | [7 empty] | 22 | 22 | 22 | 22 | 22 | 134136
62 | Tangail 22 MW PP (Doreen) | [8 empty] | 0 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 229572
63 | Impoprt (Tripura) | 116 | 114 | 20 | 48 | 72 | 78 | 62 | 62 | 74 | 86 | 96 | 104 | 124 | 114 | 104 | 102 | 110 | 124 |  | 134 | 124 | 130 | 132 | 132 | 128 | 122 | 2414400
64 | Malancha, Ctg. EPZ (United) | 35 | 35 | 35 | 40 | 42 | 42 | 33 | 37 | 35 | 26 | 24 | 24 | 35 | 31 | 31 | 35 | 20 | 40 |  | 38 | 40 | 37 | 40 | 38 | 38 | 38 | 871680
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 12 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 401652
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 |  |  |  | 5 | 5 | 0 | 5 | 5 | 5 | 5 | 8 | 11 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 156960
67 | Jangalia 33MW PP (Summit) | 33 | 33 |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 751600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 |  |  | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 20 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 391510
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 25 | 0 | 0 | 0 | 0 | 8 | 8 | 10 | 27 | 24 | 19 | 19 | 14 | 8 | 6 | 6 | 14 | 14 |  | 14 | 22 | 27 | 22 | 27 | 27 | 27 | 320580
71 | Maona 33 MW PP(Summit) |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 452700
72 | Rupganj 33 MW PP(Summit) | 26 |  |  |  |  | 8 | 16 | 24 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 21 |  | 24 | 24 | 31 | 15 | 16 | 16 | 16 | 489400
73 | Ghorashal 108MW PP (Regent) | 13 | [6 empty] | 12 | 12 | 12 | 12 | 35 | 68 | 13 | 12 | 12 | 12 | 12 |  | 50 | 70 | 78 | 78 | 80 | 80 | 43 | 656545
| Feni Lanka Power | [17 empty] | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 51300
| Chowmuhani 113 MW | [9 empty] | 4 | 9 | 9 | 12 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 173880
| Manikgonj 162MW PP(MPGL) | [11 empty] | 4 | 35 | 35 | 35 | 35 | 35 | 57 |  | 108 | 108 | 108 | 108 | 108 |  | 0 | 717120
77 | Siddhirganj 100 PP(Dutch Bangla) | [16 empty] | 3 | 9 |  | 9 | 9 | 9 | 9 |  |  | 0 | 31680
78 | Gazipur 52 MW PP | [17 empty] | 8 |  | 34 | 8 | 8 | 8 |  |  | 0 | 80861
79 | Kodda 150 MW PP | [17 empty] | 48 |  | 48 | 16 | 16 | 16 |  |  | 0 | 121440
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [16 empty] | 0 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 60312
| Gazipur 100 MW PP | [17 empty] | 17 |  | 50 | 50 | 52 | 17 | 17 |  | 0 | 200640
| Kaptai 7 MW Solar PP | [8 empty] | 4 | 4 | 4 | 3 | 2 | 3 | 1 | 1 | 1 | [9 empty] | 21719
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | [10 empty] | 9 | 17 | 35 |  | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 464244
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 17 |  |  |  | 4 | 49 | 52 | 52 | 52 | 54 | 54 | 54 | 51 |  | 17 | 17 | 17 | 36 | 51 | 54 | 54 | 990250
82 | Madanganj 102 PP(Summit) | 1 | [16 empty] | 17 |  | 34 | 34 | 34 | 34 | 4 |  | 0 | 113174
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 229 | 255 | 267 | 270 | 236 | 230 | 230 | 278 | 303 | 260 | 282 | 270 | 256 | 303 | 291 | 301 | 306 | 250 |  | 283 | 249 | 293 | 250 | 259 | 279 | 294 | 6555084
87 | Meghnaghat 100 MW(IEL) | [16 empty] | 1 | 14 |  | 24 | 24 | 24 | 8 |  |  | 0 | 72960
| Meghnaghat 104 MW PP (OPCL) | [12 empty] | 15 | 17 | 17 | 17 | 17 | 50 |  | 50 | 52 | 34 | 34 | 17 |  | 0 | 264960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 55 | 22 | 22 | 22 | 22 |  |  |  |  | 10 | 10 | 33 | 44 | 44 | 44 | 44 | 44 | 55 |  | 55 | 55 | 55 | 66 | 66 | 66 | 66 | 799920
92 | Fenchuganj 44MW (Energyprima) | 10 | [6 empty] | 5 | 5 | 5 | 5 | 20 | 40 | 10 | 10 | 10 | 10 | 10 |  | 20 | 42 | 47 | 47 | 47 | 47 | 10 | 385992
93 | Ashuganj 51 MW PP (Midland) | [10 empty] | 5 | 20 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 611534
94 | Gagnagar 102 MW PP (Digital Power) | [16 empty] | 8 | 24 |  | 24 | 24 | 8 | 8 |  |  | 0 | 77904
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 5 |  |  |  | 0 | 3 | 6 | 6 | 6 | 6 | 6 |  | 4 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 119040
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 2 | 6 | 6 |  | 6 | 6 | 6 |  |  |  | 0 | 30720
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 1 | 15 | 15 | 15 | 15 | 18 |  | 30 | 40 | 45 | 55 | 15 |  | 0 | 263308
100 | Manikganj 55 MW PP (Northern) |  |  |  | 17 | 17 | 17 |  | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 35 |  |  |  | 35 |  | 0 | 375872
101 | Kushiara 163 MW CCPP (KP) | 80 | [11 empty] | 80 | 80 | 112 | 112 | 112 | 112 |  | 80 | 80 | 80 | 112 | 112 | 80 | 80 | 1208127
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 9150
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | [10 empty] | 0 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 0 | 426960
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [11 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 26 |  | 90 | 120 | 100 | 75 | 40 | 40 | 46 | 532800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [12 empty] | 37 | 52 | 52 | 52 | 52 | 72 |  | 100 | 100 | 99 | 88 | 65 | 52 | 41 | 796032
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 70 | 70 | 70 | 50 | 12 | 12 | 12 | 12 | 25 | 52 | 88 | 88 | 88 | 88 | 88 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 88 | 1732800
116 | Chandpur 200MW (Desh energy) | 51 | 17 | 17 | 17 | [5 empty] | 0 | 17 | 17 | 59 | 85 | 85 | 85 | 85 | 85 |  | 85 | 120 | 152 | 180 | 180 | 155 | 120 | 1573440
117 | Ashuganj 150MW PP (Midland) | [17 empty] | 6 |  | 75 | 128 | 115 | 135 | 138 | 10 | 0 | 557018
118 | Bibiyana-III 400 MW CCPP | 317 | 319 | 367 | 365 | 365 | 366 | 396 | 365 | 398 | 365 | 364 | 366 | 368 | 344 | 369 | 394 | 408 | 368 |  | 304 | 311 | 327 | 367 | 367 | 367 | 380 | 8686000
| Jamalpur 115 MW PP (United) |  |  | 5 | 24 | 24 | 8 |  |  |  | 2 | 16 | 25 | 95 | 94 | 94 | 94 | 104 | 104 |  | 104 | 113 | 113 | 113 | 113 | 113 | 47 | 1305600
| Anwara 300 MW PP (United) | 30 | 30 | 30 | 30 | 15 |  |  |  |  | 0 | 15 | 15 | 45 | 45 | 45 | 45 | 65 | 65 |  | 75 | 135 | 135 | 50 | 50 | 15 | 15 | 950945
| Juldah unit-2 (Acorn) | 30 | 30 | 30 | 30 | 30 |  |  |  |  | 0 | 7 | 12 | 19 | 50 | 50 | 50 | 50 | 50 |  | 51 | 60 | 60 | 60 | 14 | 12 | 12 | 702720
| Anlima Energy Ltd. | 107 | 107 | 107 | 107 | 107 | 68 | 17 | 17 | 17 | 25 | 72 | 107 | 107 | 107 | 107 | 107 | 107 | 107 |  | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 2201727
| Bhairob 54.5 MW | [11 empty] | 1 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 233280
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 10 | 8 | 32 | 34 | 32 | 18 | 18 | 6 | 2 | 2
| Chandpur 115(Doreen) | 10 | 17 | 17 | 17 | 17 |  |  |  |  | 2 | 34 | 53 | 54 | 53 | 53 | 51 | 70 | 75 |  | 89 | 75 | 75 | 75 | 76 | 74 | 75 | 1022400
| Kanchan Purbachal Power Generation Ltd. | 17 | [10 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 22 |  | 34 | 34 | 34 | 34 | 34 | 23 | 0 | 300960
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4514 | 3717 | 3855 | 4191 | 3960 | 3622 | 3613 | 3851 | 4043 | 4266 | 4652 | 5288 | 5752 | 5259 | 5586 | 5670 | 5832 | 6047 |  | 6524 | 6676 | 6753 | 6841 | 6678 | 6147 | 5752 | 123343910
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [11 empty] | 0 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 |  |  |  | 0 | 245760
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 2 |  | 17 | 17 |  |  |  |  | 0 | 30240
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 14 | 38 | 27 | 26 | 47 | 18 | 69 | 87 | 47 | 40 | 8 | 1 | [8 empty] | 375120
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 151 | 151 | 152 | 152 | 151 | 151 | 152 | 152 | 151 | 151 | 151 | 150 | 149 | 151 | 151 | 151 | 152 | 181 |  | 205 | 210 | 211 | 249 | 250 | 249 | 204 | 4123600
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 140 | 107 | 107 | 107 | 102 | 95 | 107 | 107 | 108 | 108 | 144 | 144 | 144 | 144 | 103 | 104 | 170 | 170 |  | 159 | 151 | 171 | 171 | 158 | 170 | 171 | 3225808
140 | Bhola 33 MW PP (Venture) | 22 | 21 | 21 | 11 | 10 | 11 | 10 | 10 | 10 | 10 | 11 | 8 | 9 | 14 | 14 | 14 | 14 | 15 |  | 18 | 18 | 18 | 19 | 18 | 17 | 16 | 349300
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 16 | [5 empty] | 0 | 18750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [17 empty] | 15 |  | 15 | [5 empty] | 0 | 27936
146 | Bheramara HVDC | 805 | 501 | 840 | 904 | 905 | 833 | 833 | 834 | 856 | 904 | 904 | 905 | 905 | 904 | 904 | 904 | 904 | 905 |  | 894 | 796 | 796 | 796 | 848 | 905 | 906 | 20435636
147 | Bheramara 410 MW CCPP | 165 | 175 | 185 | 195 | 195 | 200 | 215 | 240 | 240 | 240 | 238 | 240 | 240 | 250 | 240 | 250 | 250 | 250 |  | 220 | 220 | 250 | 260 | 255 | 255 | 250 | 5689152
148 | Payra 1320 MW | 600 | 540 | 580 | 680 | 680 | 570 | 580 | 640 | 720 | 720 | 720 | 720 | 710 | 660 | 660 | 660 | 660 | 660 |  | 610 | 740 | 740 | 860 | 980 | 970 | 920 | 18918800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4137500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 4 | 3 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 18960
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 130 | 145 | 169 | 140 | 130 | 130 | 142 | 160 | 161 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 176 | 199 | 170 | 170 | 3873555
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 258 | 240 | 358 | 374 | 282 | 247 | 242 | 310 | 307 | 307 | 265 | 308 | 257 | 234 | 235 | 232 | 234 | 265 |  | 308 | 309 | 316 | 387 | 387 | 364 | 362 | 7019600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 306960
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | [9 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 92160
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | [6 empty] | 7663
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [9 empty] | 0 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | [5 empty] | 322793
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 8 | [5 empty] | 0 | 8957
170 | Chapainawabganj 100 MW Peaking PP | [26 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 15 |  | 35 | 35 | 35 | 35 | 35 |  | 0 | 204672
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 35 |  | 35 | 2 |  |  |  |  | 0 | 75840
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [9 empty] | 0 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 90 | 10 |  |  |  | 0 | 523363
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 4 | 5 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [8 empty] | 35527
178 | Energypac Power Venture Thakurgaon Ltd. | [9 empty] | 5 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 46 |  | 72 | 54 | 36 | 36 | 36 |  | 0 | 538560
| Intraco Solar 30 MW | [5 empty] | 0 | 4 | 12 | 21 | 22 | 19 | 11 | 22 | 14 | 17 | 4 | 3 | 0 | [8 empty] | 152496
| Adani Power Jharkhanda Ltd | 750 | 555 | 550 | 570 | 570 | 568 | 568 | 568 | 612 | 750 | 762 | 761 | 755 | 763 | 767 | 764 | 771 | 763 |  | 763 | 762 | 760 | 764 | 754 | 772 | 759 | 16805455
178 | Teesta Solar Limited | [6 empty] | 23 | 53 | 110 | 147 | 163 | 158 | 51 | 79 | 110 | 38 | 9 | [9 empty] | 974770