## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-07-20 | Saturday
|  | Date (day): | 2019-07-20 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11842 | MW |  |  | (b) At Evening Peak Hour : |  | 14010 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-07-19 | 2019-07-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 199 | 199 | 199 | 199
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 67 | 67 | 78 | 78
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 35 | 103 | 106 | 106
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 377 | 340 | 370 | 370 | 42 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 303 | 329 | 340 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 420 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 75 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 296 | 300 | 300 | 335
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 64 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 55 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 |  |  | Test
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 102 | 100 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 48 | 48 | 50
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 111 | 145 | 145
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 45 | 45 | 45 |  | 63 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 29 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 42 | 42 | 42 |  | 10 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 260 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 135 | 100 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 103 | 103 | 100 | 100
| Dhaka area Total |  |  |  |  | 5959 | 5723 | 2233 | 3406 | 3587 | 4295 | 397 | 851
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 46 | 40 | 40 |  | 10 | Engine problem
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 165 | 165 | 165 |  |  | # 01 Under maint.
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 219 | 205 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 143 | 135 | 102 | 130
44 | Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Contract expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 17 | 50 | 100
46 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 77
47 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85
48 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 10 | 100 | 100
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 100 | 100 | 100
50 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 11 | 42 | 5 | 25
51 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 11 | 50 | 100 | 100
52 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.8 | 0 | 4.4 | 0
53 | Anwara 300 MW PP (United) |  | HFO | United Group | 300 MW | 300 | 300 | 202 | 231 | 230 | 260
| Chattogram area Total |  |  |  |  | 2113 | 2053 | 1076.8 | 1345 | 1398.4 | 1664 | 140 | 10
54 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 135 | 135 | 135 | 0 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
55 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 184 | 220 | 220
56 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 240 | 0 | 0
57 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 310 | 340 | 360
58 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 33 | 33 | 33 | 33 |  | 12
59 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 51 | 55 | 55
60 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
61 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 68 | 195 | 195 | 0
62 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 43 | 43 | 43 |  | 8 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 150 | 150 | 150
64 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
65 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
66 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 141 | 142 | 142
67 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 199 | 200 | 200
68 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
69 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 174 | 123 | 182
70 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
71 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
72 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 15 | 15 | 15 |  | 10 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1576 | 1860 | 1769 | 2098 | 263 | 30
74 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 146 | 146 | 150 | 150 |  | 52 | GT-1 Under maint.
75 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
76 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 25 | 95 | 95 | 95
77 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2.3 | 0 | 1.6 | 0
78 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 50 | 190 | 100 | 200
79 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 88 | 106 | 110 | 110
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 333.3 | 559 | 478.6 | 577 | 0 | 52
80 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 56 | 51 | 55 | 55
81 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 63 | 64 | 63 | 63
82 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 100 | 163 | 163
83 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 271 | 263 | 260 | 260 |  | 67
84 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
85 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 46 | 44 | 44
86 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
87 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 63 | 66 | 66 |  |  | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 40 | 80 | 86
89 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 10 | 44 | 43 | 46 |  | 7 | Engine problem
90 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 122 | 116 | 125 | 125
91 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18 |  | 20
92 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 46 | 44 | 44 |  | 6 | Engine problem
93 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
94 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 330 | 280 | 315 | 320
95 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 0 | 0 | 0 |  | 285 | Under maint.
96 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1225 | 1225 | 1372 | 1386 | 0 | 385
97 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 32
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 899 | 908 | 908
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
98 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 1 | 115 | 115
99 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 41 | 10 | 33
100 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 150
101 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 45 | 10 | 80
102 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 |  | 410 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 33 | 33 | 33 |  | 7 | Engine problem
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
105 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 53 | 105 | 105
106 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 87 | 86 | 90 | 90 |  | 15 | Engine problem
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1050 | 1290 | 1271 | 1646 | 0 | 432
107 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 70 | 110
108 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 32
109 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 33 | 30 | 36
110 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 84 | 135 | 195
111 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 219 | 336 | 330 | 468 | 0 | 0
112 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 60 | 60 | 60
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
114 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 13 | 0 | 30
115 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 32 | 40 | 30 | 40 |  | 10 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 34 | 40 | 42 |  | 8 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 15 | 45
118 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 203 | 182 | 215 | 215 |  |  | FGMO
119 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 207 | 186 | 200 | 210 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 206 | 188 | 205 | 215 |  |  | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 36 | 0 | 0 | 0 |  |  | Under shut down.
122 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36
123 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
124 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 14 | 14 | 15 | 15
125 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
126 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52
127 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 86 | 50 | 95
128 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
129 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 36 | 94 | 94 | 94 |  | 23 | Engine problem
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 870 | 1112 | 1209 | 1432 | 0 | 141
130 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 77 | 77 | 77 |  | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 199 | 249 | 250 | 250
132 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  |  | Under maint.
133 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 17
| Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 0 | 0 | 14 | 0 | 100 | 100
| Rangpur Area Total |  |  |  |  | 564 | 484 | 294 | 344 | 427 | 444 | 0 | 170
| Total |  |  |  |  | 18991 | 18468 | 8877.1 | 11477 | 11842 | 14010 | 800 | 2071
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8462.5208 | 10941 | 11288.9537 | 13355.7036
A. |  | 2019-07-19 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11602 | MW at | 24:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8052.11 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11477 | MW
3 | Day peak Generation : |  |  | 8841.1 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10941 | MW
4 | Evening peak Generation : |  |  | 11477 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 235.801 | MKWHr | By Solar | 0.14917 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 141.1368 | MKWHr |  | By Oil: | 58.5697 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 7.0909 | MKWHr |  | By Hydro: | 3.7657 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 800 | MW | Dhaka | 3871 | 3871 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2071 | MW | Chittagong | 1108 | 1108 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2871 | MW | Khulna | 1222 | 1222 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1265.27 | MMCFD |  |  | Rajshahi | 1194 | 1194 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 141853561.458 | ii) Oil : | Taka | 524590970.61 | Comilla | 1108 | 1108 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 33074822.64 | Total | Taka | 699519354.708 | Mymensingh | 943 | 943 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 5.11 | MKWHr. | Sylhet | 478 | 478 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -630 | MW (E to W) at | 21:00 | hrs | Barisal | 320 | 320 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -670 | MW at | 1:00 | hrs | Rangpur | 697 | 697 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.0° C |  |  | Total | 10941 | 10941 |  | 0
B. |  | 2019-07-20 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14010 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
4 | Reserve(Generation end) |  |  |  | 1710 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 249.9872 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8787.72 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.6116 | MKWHr. | ii) HVDC Flow at Peak Time |  | 899 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4771 | MKWHr. | iii) Maximum HVDC Flow : |  | 926 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 107.16 |  | (b) Today: | 107.2 |  | (c) Rule Curve: |  | 87.04
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2019-07-19
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 199 | 200 | 0 | 0 | 107 | 69 | 339 | 320 |  | 0 | 400 | 275 | 100 | 98 | 55 | 0 | 0 | 0 | 0 | 100 | 101 | 120 | 100 | 43 | 0 | 8 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 75 | 90 | 95 | 100 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 51 | 10 | 44 | 47 | 18 | 38 | 135 | 0 | 0 | 300 | 310 | 216 | 73 | 140 | 33 | 52 | 0 | 43 | 0 | 50 | 52 | 21 | 11 | 33 | 14 | 166 | 144 | 91 | 22 | 0 | 55 | 63 | 50 | 49 | 100 | 263 | 63 | 78 | 46 | 113 | 0 | 45 | 9 | 300 | 16 | 8 | 0 | 300 | 0 | 0 | 36 | 0 | 149 | 0 | 90 | 200 | 50 | 0 | 58 | 103 | 34 | 0 | 214 |  | 868 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 39 | 33 | 84 | 37 | 110 | 0 | 0 | 60 | 50 | 13 | 78 | 40 | 42 | 34 | 52 | 0 | 22 | 14 | 11 | 20 | 0 | 199 | 0 | 17 | 181 | 0 | 185 | 0 | 98 | 99 | 191 | 0 | 0 | 54 | 0 | 113 | 86 | 0 | 0 |  | 8313 | 2994 | 11307 | 4107 | 868 | 1950 | 3331 | 219 | 165 | 501 | 166 | 0 | 0 | 107.11
2:00 | 0 | 199 | 200 | 0 | 0 | 107 | 69 | 357 | 353 |  | 0 | 420 | 283 | 100 | 47 | 55 | 0 | 0 | 0 | 0 | 24 | 101 | 120 | 50 | 43 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 75 | 90 | 95 | 100 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 51 | 10 | 44 | 47 | 18 | 39 | 135 | 0 | 0 | 0 | 320 | 216 | 185 | 141 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 14 | 160 | 144 | 91 | 22 | 0 | 55 | 63 | 50 | 49 | 130 | 266 | 63 | 78 | 46 | 112 | 0 | 45 | 9 | 310 | 16 | 9 | 0 | 250 | 0 | 0 | 36 | 0 | 149 | 0 | 90 | 200 | 50 | 0 | 58 | 103 | 34 | 0 | 214 |  | 926 | 16 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 34 | 33 | 84 | 36 | 110 | 0 | 0 | 60 | 50 | 12 | 78 | 40 | 42 | 0 | 52 | 0 | 22 | 14 | 8 | 70 | 0 | 199 | 0 | 17 | 193 | 0 | 195 | 0 | 96 | 99 | 202 | 0 | 0 | 54 | 0 | 113 | 87 | 0 | 0 |  | 7974 | 3090 | 11064 | 3869 | 926 | 2153 | 3111 | 269 | 165 | 411 | 160 | 0 | 0 | 107.12
3:00 | 0 | 199 | 200 | 0 | 0 | 107 | 69 | 343 | 353 |  | 0 | 420 | 263 | 100 | 47 | 55 | 0 | 0 | 0 | 0 | 24 | 101 | 120 | 50 | 43 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 41 | 0 | 75 | 90 | 95 | 100 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 51 | 10 | 44 | 47 | 18 | 39 | 135 | 0 | 0 | 20 | 310 | 216 | 185 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 14 | 140 | 146 | 91 | 22 | 0 | 55 | 63 | 50 | 49 | 130 | 260 | 63 | 78 | 46 | 110 | 0 | 45 | 9 | 300 | 16 | 11 | 0 | 250 | 0 | 0 | 36 | 0 | 149 | 0 | 90 | 200 | 50 | 0 | 38 | 103 | 34 | 0 | 214 |  | 926 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 34 | 33 | 84 | 36 | 110 | 0 | 0 | 60 | 50 | 12 | 78 | 40 | 34 | 0 | 52 | 0 | 22 | 14 | 8 | 71 | 0 | 199 | 0 | 17 | 187 | 0 | 191 | 0 | 97 | 80 | 197 | 0 | 0 | 36 | 0 | 113 | 85 | 0 | 0 |  | 7870 | 3014 | 10884 | 3845 | 926 | 2144 | 2999 | 270 | 165 | 395 | 140 | 0 | 0 | 107.13
4:00 | 0 | 199 | 200 | 0 | 0 | 104 | 69 | 339 | 300 |  | 0 | 400 | 281 | 100 | 15 | 55 | 0 | 0 | 0 | 0 | 7 | 101 | 120 | 10 | 43 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 75 | 90 | 95 | 100 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 17 | 10 | 44 | 47 | 18 | 40 | 135 | 0 | 0 | 25 | 315 | 215 | 185 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 14 | 140 | 146 | 91 | 22 | 0 | 55 | 63 | 50 | 49 | 100 | 259 | 63 | 78 | 46 | 110 | 0 | 45 | 9 | 300 | 16 | 11 | 0 | 120 | 0 | 0 | 36 | 0 | 149 | 0 | 90 | 200 | 50 | 0 | 38 | 103 | 34 | 0 | 214 |  | 926 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 34 | 33 | 84 | 35 | 110 | 0 | 0 | 60 | 50 | 0 | 78 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 8 | 76 | 0 | 199 | 0 | 18 | 183 | 0 | 187 | 0 | 97 | 80 | 192 | 0 | 0 | 36 | 0 | 113 | 87 | 0 | 0 |  | 7535 | 2970 | 10505 | 3836 | 926 | 2038 | 2775 | 275 | 165 | 350 | 140 | 0 | 0 | 107.14
5:00 | 0 | 199 | 200 | 0 | 0 | 104 | 69 | 342 | 300 |  | 0 | 400 | 275 | 100 | 15 | 55 | 0 | 0 | 0 | 0 | 7 | 7 | 120 | 10 | 43 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 75 | 90 | 95 | 100 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 17 | 10 | 44 | 45 | 18 | 42 | 135 | 0 | 0 | 25 | 315 | 215 | 185 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 14 | 130 | 146 | 91 | 22 | 0 | 55 | 63 | 50 | 49 | 100 | 263 | 63 | 78 | 46 | 110 | 0 | 45 | 9 | 305 | 16 | 11 | 0 | 50 | 0 | 0 | 36 | 0 | 149 | 0 | 100 | 198 | 50 | 0 | 38 | 103 | 34 | 0 | 214 |  | 926 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 33 | 29 | 33 | 84 | 35 | 110 | 0 | 0 | 60 | 50 | 0 | 78 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 8 | 76 | 0 | 199 | 0 | 0 | 188 | 0 | 192 | 0 | 98 | 50 | 198 | 0 | 0 | 36 | 0 | 75 | 87 | 0 | 0 |  | 7375 | 2896 | 10271 | 3859 | 926 | 2046 | 2543 | 275 | 165 | 327 | 130 | 0 | 0 | 107.15
6:00 | 0 | 199 | 200 | 0 | 0 | 104 | 69 | 339 | 270 |  | 0 | 350 | 230 | 100 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 7 | 110 | 10 | 43 | 0 | 6 | 53 | 35 | 17 | 22 | 25 | 31 | 33 | 33 | 42 | 0 | 75 | 90 | 95 | 100 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 17 | 10 | 44 | 0 | 18 | 0 | 135 | 0 | 0 | 40 | 310 | 215 | 185 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 33 | 14 | 130 | 140 | 91 | 22 | 0 | 55 | 63 | 50 | 49 | 100 | 260 | 51 | 78 | 10 | 112 | 0 | 10 | 9 | 270 | 16 | 11 | 0 | 15 | 0 | 0 | 36 | 0 | 96 | 0 | 10 | 168 | 6 | 0 | 38 | 103 | 34 | 0 | 214 |  | 926 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 33 | 71 | 31 | 80 | 0 | 0 | 60 | 50 | 0 | 78 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 8 | 76 | 0 | 199 | 0 | 0 | 180 | 0 | 185 | 0 | 96 | 0 | 190 | 0 | 0 | 36 | 0 | 75 | 87 | 0 | 0 |  | 6640 | 2707 | 9347 | 3810 | 926 | 1812 | 1974 | 275 | 165 | 255 | 130 | 0 | 0 | 107.16
7:00 | 0 | 199 | 200 | 0 | 0 | 104 | 69 | 338 | 270 |  | 0 | 350 | 275 | 56 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 7 | 48 | 10 | 43 | 0 | 6 | 53.97 | 17.2 | 17 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 75 | 90 | 95 | 100 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 3 | 10 | 11 | 0 | 18 | 0 | 135 | 0 | 0 | 50 | 310 | 216 | 148 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 108 | 148 | 91 | 20 | 0.2 | 55 | 63 | 11 | 10 | 100 | 262 | 63 | 40 | 10 | 110 | 0 | 12 | 9 | 275 | 16.2 | 11 | 0 | 15 | 0 | 0 | 36 | 0 | 24 | 5.24 | 10 | 70 | 0 | 0 | 38 | 103 | 17 | 0.7 | 148 |  | 904 | 0 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 0 | 16 | 84 | 27 | 48 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 8 | 0 | 52 | 0 | 22 | 14 | 8 | 78 | 0 | 199 | 0 | 0 | 180 | 0 | 185 | 0 | 97 | 0 | 190 | 0 | 0 | 36 | 0 | 75 | 87 | 0 | 0 |  | 6082.51 | 2439 | 8521.51 | 3852.2 | 904 | 1663 | 1495.17 | 277 | 165 | 51 | 108 | 6.14 | 0 | 107.17
8:00 | 0 | 199 | 200 | 0 | 0 | 104 | 69 | 345 | 270 |  | 0 | 350 | 275 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 8 | 0 | 6 | 53 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 75 | 90 | 95 | 100 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 0 | 18 | 0 | 135 | 0 | 0 | 50 | 320 | 195 | 148 | 141 | 33 | 52 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 110 | 147 | 65 | 20 | 0.5 | 56 | 63 | 11 | 10 | 100 | 261 | 62 | 40 | 10 | 110 | 0 | 12 | 9 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 6 | 10 | 34 | 0 | 0 | 78 | 103 | 17 | 1 | 108 |  | 904 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 24 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 8 | 0 | 26 | 0 | 22 | 14 | 8 | 77 | 0 | 199 | 0 | 0 | 190 | 0 | 193 | 0 | 95 | 0 | 200 | 0 | 0 | 36 | 0 | 36 | 87 | 71 | 0 |  | 5814.5 | 2430 | 8244.5 | 3875 | 904 | 1678 | 1229 | 276 | 165 | 0 | 110 | 7.5 | 0 | 107.18
9:00 | 0 | 199 | 200 | 0 | 0 | 55 | 68 | 340 | 273 |  | 0 | 350 | 257 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 22 | 25 | 31 | 33 | 33 | 16 | 0 | 75 | 90 | 95 | 100 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 0 | 18 | 0 | 135 | 0 | 0 | 105 | 310 | 182 | 73 | 142 | 33 | 51 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 106 | 147 | 62 | 20 | 1 | 56 | 63 | 11 | 10 | 100 | 263 | 63 | 10 | 10 | 109 | 0 | 13 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 8.31 | 10 | 17 | 0 | 0 | 57 | 103 | 17 | 2.8 | 108 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 79 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 40 | 8 | 0 | 8 | 0 | 22 | 14 | 8 | 76 | 0 | 199 | 0 | 0 | 183 | 0 | 186 | 0 | 93 | 0 | 212 | 0 | 0 | 36 | 0 | 36 | 87 | 109 | 0 |  | 5635.11 | 2417 | 8052.11 | 3892 | 904 | 1512 | 1170 | 275 | 165 | 16 | 106 | 12.11 | 0 | 107.18
10:00 | 0 | 199 | 200 | 0 | 0 | 12 | 68 | 346 | 273 |  | 0 | 350 | 277 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 19 | 25 | 22 | 33 | 33 | 16 | 0 | 75 | 40 | 95 | 100 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 0 | 18 | 0 | 135 | 0 | 0 | 220 | 310 | 189 | 78 | 141 | 33 | 51 | 0 | 35 | 0 | 0 | 0 | 20 | 11 | 33 | 14 | 110 | 146 | 25 | 22 | 1.9 | 56 | 63 | 11 | 10 | 100 | 263 | 61 | 10 | 10 | 110 | 0 | 14 | 9 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 18.72 | 10 | 17 | 0 | 0 | 77 | 103 | 17 | 2 | 107 |  | 905 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 18 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 32 | 8 | 0 | 8 | 0 | 22 | 14 | 8 | 77 | 0 | 199 | 0 | 0 | 192 | 0 | 197 | 0 | 96 | 0 | 213 | 0 | 0 | 36 | 0 | 36 | 87 | 109 | 0 |  | 5700.62 | 2436 | 8136.62 | 4032 | 905 | 1496 | 1164 | 276 | 115 | 16 | 110 | 22.62 | 0 | 107.18
11:00 | 0 | 199 | 200 | 0 | 0 | 12 | 67 | 351 | 273 |  | 0 | 350 | 285 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 0 | 25 | 22 | 33 | 33 | 16 | 0 | 76 | 40 | 95 | 100 | 0 | 215 | 0 | 136 | 0 |  | 0 | 0 | 0 | 10 | 11 | 0 | 18 | 0 | 135 | 0 | 0 | 300 | 320 | 215 | 78 | 141 | 33 | 52 | 0 | 35 | 0 | 0 | 0 | 20 | 11 | 33 | 14 | 116 | 143 | 25 | 22 | 1.1 | 56 | 63 | 11 | 10 | 100 | 268 | 61 | 10 | 10 | 123 | 0 | 12 | 9 | 325 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 16.74 | 10 | 17 | 0 | 0 | 87 | 103 | 0 | 6.2 | 107 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 21 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 32 | 8 | 0 | 8 | 0 | 22 | 14 | 8 | 76 | 0 | 199 | 0 | 0 | 201 | 0 | 198 | 0 | 95 | 0 | 209 | 0 | 0 | 36 | 0 | 36 | 87 | 15 | 0 |  | 5847.04 | 2348 | 8195.04 | 4167 | 904 | 1506 | 1071 | 275 | 116 | 16 | 116 | 24.04 | 0 | 0
12:00 | 0 | 199 | 200 | 0 | 0 | 35 | 67 | 377 | 303 |  | 0 | 420 | 296 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 0 | 25 | 22 | 33 | 33 | 16 | 0 | 76 | 90 | 95 | 100 | 0 | 219 | 0 | 143 | 0 |  | 0 | 0 | 0 | 10 | 11 | 0 | 18 | 11 | 135 | 0 | 0 | 345 | 345 | 204 | 78 | 141 | 33 | 51 | 0 | 20 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 128 | 146 | 25 | 22 | 2.3 | 56 | 63 | 11 | 10 | 163 | 271 | 61 | 50 | 10 | 122 | 0 | 42 | 9 | 330 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 76 | 17 | 0 | 0 | 88 | 103 | 0 | 5.8 | 202 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 24 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 32 | 8 | 0 | 43 | 0 | 22 | 14 | 8 | 81 | 0 | 199 | 0 | 0 | 203 | 0 | 207 | 0 | 95 | 0 | 206 | 0 | 0 | 35 | 0 | 36 | 87 | 14 | 0 |  | 6444.1 | 2397 | 8841.1 | 4277 | 904 | 1765 | 1277 | 280 | 166 | 16 | 128 | 28.1 | 0 | 0
13:00 | 0 | 199 | 200 | 0 | 0 | 62 | 66 | 369 | 303 |  | 0 | 420 | 290 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 19 | 25 | 18 | 33 | 33 | 16 | 0 | 76 | 90 | 95 | 100 | 0 | 217 | 0 | 136 | 0 |  | 0 | 0 | 0 | 10 | 11 | 4 | 19 | 29 | 135 | 0 | 0 | 330 | 235 | 203 | 78 | 141 | 33 | 52 | 0 | 17 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 134 | 143 | 25 | 22 | 2.3 | 56 | 64 | 16 | 10 | 163 | 263 | 59 | 50 | 10 | 120 | 0 | 45 | 9 | 320 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 19 | 100 | 85 | 0 | 0 | 68 | 103 | 0 | 6.3 | 210 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 31 | 84 | 23 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 32 | 34 | 0 | 50 | 0 | 22 | 14 | 8 | 79 | 0 | 199 | 0 | 0 | 199 | 0 | 204 | 0 | 98 | 0 | 204 | 0 | 0 | 17 | 0 | 36 | 87 | 0 | 0 |  | 6434.6 | 2412 | 8846.6 | 4135 | 904 | 1807 | 1379 | 278 | 166 | 16 | 134 | 27.6 | 0 | 0
14:00 | 0 | 199 | 200 | 0 | 0 | 62 | 65 | 354 | 303 |  | 0 | 370 | 295 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 19 | 25 | 16 | 33 | 33 | 16 | 0 | 76 | 90 | 95 | 100 | 0 | 219 | 0 | 141 | 0 |  | 0 | 0 | 0 | 10 | 11 | 30 | 19 | 12 | 135 | 0 | 0 | 345 | 345 | 204 | 78 | 142 | 33 | 51 | 0 | 17 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 138 | 142 | 25 | 22 | 0.5 | 55 | 63 | 14 | 10 | 100 | 267 | 58 | 10 | 10 | 122 | 0 | 45 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 2 | 100 | 80 | 0 | 0 | 77 | 103 | 0 | 2.2 | 215 |  | 904 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 33 | 84 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 32 | 8 | 0 | 50 | 0 | 22 | 14 | 8 | 80 | 0 | 199 | 0 | 0 | 194 | 0 | 198 | 0 | 96 | 0 | 204 | 0 | 0 | 17 | 0 | 36 | 87 | 0 | 0 |  | 6372.7 | 2408 | 8780.7 | 4235 | 904 | 1610 | 1428 | 279 | 166 | 16 | 138 | 4.7 | 0 | 0
15:00 | 0 | 199 | 200 | 0 | 0 | 97 | 65 | 370 | 340 |  | 0 | 420 | 276 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 2 | 43 | 0 | 6 | 35 | 17 | 17 | 19 | 25 | 16 | 33 | 33 | 19 | 0 | 76 | 90 | 95 | 100 | 0 | 205 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 38 | 19 | 39 | 135 | 0 | 0 | 310 | 310 | 183 | 78 | 142 | 33 | 52 | 0 | 35 | 0 | 0 | 2 | 20 | 0 | 33 | 14 | 144 | 142 | 48 | 0 | 0.1 | 53 | 64 | 49 | 37 | 163 | 262 | 57 | 74 | 10 | 110 | 0 | 45 | 9 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 7 | 100 | 92 | 5 | 0 | 77 | 103 | 0 | 0.6 | 250 |  | 898 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 33 | 84 | 25 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 40 | 24 | 0 | 50 | 0 | 22 | 13 | 8 | 88 | 0 | 226 | 0 | 0 | 198 | 0 | 205 | 0 | 95 | 0 | 212 | 0 | 0 | 17 | 0 | 70 | 86 | 109 | 0 |  | 6736.7 | 2624 | 9360.7 | 4114 | 898 | 1978 | 1723 | 314 | 166 | 16 | 144 | 7.7 | 0 | 0
16:00 | 0 | 199 | 200 | 0 | 0 | 52 | 65 | 340 | 323 |  | 0 | 420 | 280 | 18 | 15 | 14 | 0 | 0 | 0 | 0 | 7 | 40 | 16 | 10 | 43 | 0 | 6 | 53 | 17 | 17 | 19 | 25 | 16 | 33 | 29 | 42 | 0 | 76 | 90 | 90 | 100 | 0 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 38 | 18 | 44 | 135 | 0 | 0 | 260 | 255 | 183 | 78 | 141 | 33 | 49 | 0 | 25 | 0 | 0 | 25 | 20 | 11 | 33 | 14 | 140 | 142 | 74 | 0 | 0.2 | 53 | 63 | 50 | 46 | 100 | 266 | 58 | 74 | 5 | 70 | 0 | 5 | 9 | 290 | 24 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 11 | 7 | 100 | 140 | 50 | 0 | 77 | 103 | 5 | 1.2 | 264 |  | 898 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 8 | 33 | 84 | 25 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 40 | 24 | 0 | 52 | 0 | 22 | 12 | 8 | 90 | 0 | 250 | 0 | 0 | 174 | 0 | 169 | 0 | 95 | 0 | 193 | 0 | 0 | 17 | 0 | 74 | 86 | 0 | 0 |  | 6634.4 | 2491 | 9125.4 | 3863 | 898 | 1789 | 1897 | 340 | 166 | 24 | 140 | 8.4 | 0 | 0
17:00 | 0 | 199 | 200 | 0 | 0 | 52 | 60 | 340 | 323 |  | 0 | 380 | 285 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 16 | 10 | 35 | 0 | 6 | 53 | 35 | 17 | 22 | 25 | 16 | 33 | 29 | 34 | 0 | 76 | 90 | 90 | 100 | 0 | 208 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 45 | 18 | 42 | 135 | 0 | 0 | 274 | 255 | 189 | 78 | 141 | 33 | 50 | 0 | 20 | 0 | 0 | 16 | 21 | 11 | 33 | 14 | 140 | 142 | 20 | 0 | 0.2 | 54 | 63 | 11 | 5 | 100 | 265 | 61 | 40 | 5 | 79 | 0 | 5 | 9 | 295 | 24 | 11 | 0 | 15 | 0 | 0 | 7 | 0 | 17 | 2 | 100 | 130 | 10 | 0 | 106 | 103 | 17 | 0.4 | 188 |  | 897 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 10 | 33 | 84 | 22 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 40 | 24 | 0 | 25 | 0 | 22 | 12 | 8 | 78 | 0 | 250 | 0 | 0 | 157 | 0 | 155 | 0 | 95 | 0 | 175 | 0 | 0 | 17 | 0 | 85 | 85 | 0 | 0 |  | 6349.6 | 2411 | 8760.6 | 3854 | 897 | 1626 | 1721 | 328 | 166 | 26 | 140 | 2.6 | 0 | 0
18:00 | 0 | 199 | 200 | 0 | 0 | 13 | 40 | 325 | 283 |  | 0 | 320 | 290 | 7 | 15 | 15 | 0 | 0 | 0 | 0 | 7 | 16 | 16 | 10 | 36 | 0 | 6 | 53 | 55 | 17 | 22 | 25 | 16 | 33 | 29 | 40 | 0 | 75 | 90 | 90 | 100 | 0 | 206 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 11 | 46 | 18 | 42 | 135 | 0 | 0 | 0 | 270 | 197 | 68 | 141 | 10 | 51 | 0 | 10 | 0 | 0 | 8 | 21 | 11 | 33 | 14 | 124 | 142 | 25 | 0 | 0.2 | 53 | 63 | 14 | 5 | 100 | 265 | 61 | 10 | 5 | 80 | 0 | 5 | 9 | 300 | 24 | 11 | 0 | 12 | 0 | 0 | 7 | 0 | 15 | 0.6 | 100 | 108 | 10 | 0 | 97 | 103 | 17 | 0 | 151 |  | 898 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 23 | 40 | 8 | 84 | 20 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 40 | 24 | 0 | 25 | 0 | 22 | 14 | 8 | 83 | 0 | 249 | 0 | 0 | 166 | 0 | 167 | 0 | 96 | 0 | 171 | 0 | 0 | 17 | 0 | 93 | 33 | 0 | 0 |  | 5796.8 | 2418 | 8214.8 | 3580 | 898 | 1427 | 1609 | 332 | 165 | 79 | 124 | 0.8 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 199 | 200 | 0 | 0 | 44 | 40 | 315 | 325 |  | 0 | 420 | 305 | 7 | 15 | 18 | 0 | 0 | 0 | 0 | 7 | 30 | 60 | 12 | 37 | 0 | 6 | 53 | 55 | 35 | 22 | 25 | 16 | 33 | 29 | 42 | 0 | 75 | 90 | 90 | 100 | 13 | 215 | 0 | 132 | 0 |  | 0 | 0 | 78 | 10 | 24 | 46 | 19 | 42 | 135 | 0 | 0 | 0 | 325 | 200 | 68 | 145 | 33 | 47 | 0 | 16 | 0 | 0 | 13 | 21 | 11 | 33 | 15 | 146 | 140 | 44 | 22 | 0 | 54 | 64 | 14 | 7 | 163 | 164 | 60 | 10 | 5 | 96 | 18 | 40 | 9 | 320 | 24 | 11 | 0 | 18 | 0 | 0 | 7 | 0 | 24 | 0 | 100 | 120 | 10 | 0 | 106 | 103 | 17 | 0 | 179 |  | 898 | 16 | 0 | 0 | 91 | 0 | 0 | 0 | 30 | 50 | 16 | 84 | 31 | 50 | 0 | 0 | 55 | 50 | 5 | 66 | 40 | 24 | 33 | 25 | 14 | 22 | 14 | 8 | 82 | 0 | 249 | 0 | 18 | 178 | 0 | 179 | 0 | 96 | 7 | 178 | 0 | 0 | 35 | 0 | 93 | 65 | 0 | 0 |  | 6441 | 2802 | 9243 | 3648 | 898 | 1733 | 1902 | 331 | 165 | 420 | 146 | 0 | 0 | 0
19:30 | 0 | 199 | 200 | 0 | 0 | 101 | 67 | 395 | 352 |  | 0 | 450 | 285 | 40 | 60 | 55 | 0 | 0 | 0 | 0 | 20 | 101 | 100 | 100 | 37 | 0 | 10 | 53 | 55 | 55 | 22 | 25 | 18 | 33 | 29 | 42 | 0 | 75 | 90 | 90 | 100 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 85 | 10 | 33 | 46 | 19 | 42 | 135 | 0 | 0 | 40 | 310 | 181 | 68 | 142 | 33 | 50 | 0 | 20 | 0 | 20 | 52 | 21 | 11 | 33 | 15 | 164 | 146 | 92 | 22 | 0 | 51 | 64 | 46 | 49 | 163 | 156 | 63 | 10 | 42 | 108 | 18 | 43 | 9 | 300 | 24 | 11 | 28 | 80 | 53 | 20 | 57 | 22 | 130 | 0 | 100 | 200 | 20 | 0 | 106 | 103 | 17 | 0 | 181 |  | 898 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 40 | 55 | 24 | 84 | 31 | 110 | 12 | 0 | 60 | 50 | 9 | 86 | 40 | 27 | 45 | 52 | 29 | 22 | 14 | 11 | 81 | 0 | 249 | 0 | 18 | 192 | 0 | 203 | 0 | 95 | 86 | 190 | 0 | 0 | 35 | 0 | 93 | 86 | 0 | 0 |  | 7688 | 3174 | 10862 | 3794 | 898 | 1974 | 2956 | 330 | 165 | 581 | 164 | 0 | 0 | 0
20:00 | 0 | 199 | 200 | 0 | 0 | 106 | 67 | 395 | 357 |  | 0 | 450 | 262 | 68 | 69 | 55 | 0 | 0 | 0 | 0 | 55 | 101 | 100 | 85 | 37 | 0 | 17 | 53 | 55 | 55 | 22 | 25 | 22 | 33 | 29 | 42 | 0 | 75 | 90 | 90 | 100 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 85 | 10 | 47 | 46 | 19 | 42 | 135 | 0 | 0 | 140 | 310 | 181 | 68 | 140 | 33 | 52 | 0 | 30 | 0 | 0 | 40 | 21 | 11 | 33 | 15 | 170 | 146 | 91 | 22 | 0 | 50 | 64 | 49 | 49 | 100 | 159 | 56 | 72 | 44 | 109 | 18 | 46 | 9 | 295 | 24 | 11 | 0 | 143 | 24 | 0 | 60 | 0 | 128 | 0 | 100 | 193 | 100 | 0 | 106 | 103 | 17 | 0 | 231 |  | 898 | 32 | 0 | 0 | 115 | 0 | 0 | 0 | 42 | 50 | 24 | 72 | 33 | 110 | 12 | 0 | 60 | 50 | 11 | 86 | 40 | 34 | 47 | 52 | 34 | 22 | 14 | 11 | 78 | 0 | 249 | 0 | 18 | 186 | 0 | 196 | 0 | 96 | 90 | 196 | 0 | 0 | 35 | 0 | 94 | 86 | 0 | 0 |  | 7926 | 3173 | 11099 | 3873 | 898 | 2001 | 3098 | 327 | 165 | 567 | 170 | 0 | 0 | 0
21:00 | 0 | 199 | 200 | 0 | 0 | 103 | 67 | 340 | 329 |  | 0 | 420 | 300 | 75 | 64 | 55 | 0 | 0 | 0 | 0 | 55 | 102 | 111 | 50 | 45 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 29 | 42 | 0 | 75 | 90 | 95 | 120 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 85 | 10 | 50 | 46 | 19 | 42 | 135 | 0 | 0 | 240 | 310 | 184 | 68 | 141 | 33 | 51 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 15 | 174 | 146 | 95 | 22 | 0 | 51 | 64 | 50 | 46 | 100 | 263 | 63 | 40 | 44 | 116 | 18 | 46 | 9 | 280 | 24 | 11 | 0 | 260 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 199 | 150 | 0 | 106 | 103 | 17 | 0 | 231 |  | 899 | 32 | 0 | 0 | 1 | 0 | 0 | 0 | 41 | 45 | 33 | 84 | 33 | 110 | 12 | 0 | 60 | 50 | 13 | 86 | 40 | 34 | 44 | 52 | 36 | 22 | 14 | 11 | 77 | 0 | 249 | 0 | 18 | 182 | 0 | 186 | 0 | 97 | 100 | 188 | 0 | 0 | 53 | 0 | 94 | 86 | 0 | 0 |  | 8395 | 3082 | 11477 | 4065 | 899 | 1904 | 3371 | 326 | 165 | 573 | 174 | 0 | 0 | 0
22:00 | 0 | 199 | 200 | 0 | 0 | 107 | 67 | 340 | 329 |  | 0 | 420 | 290 | 56 | 64 | 55 | 0 | 0 | 0 | 0 | 7 | 101 | 118 | 50 | 45 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 29 | 42 | 0 | 75 | 90 | 95 | 120 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 73 | 10 | 50 | 46 | 19 | 42 | 135 | 0 | 0 | 240 | 310 | 183 | 68 | 141 | 33 | 51 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 18 | 178 | 146 | 95 | 20 | 0 | 50 | 64 | 50 | 46 | 100 | 264 | 62 | 40 | 44 | 111 | 18 | 46 | 9 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 194 | 0 | 110 | 0 | 100 | 200 | 150 | 0 | 107 | 103 | 17 | 0 | 231 |  | 898 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 44 | 33 | 84 | 37 | 110 | 13 | 0 | 55 | 50 | 13 | 86 | 40 | 34 | 43 | 52 | 35 | 22 | 14 | 11 | 78 | 0 | 249 | 0 | 18 | 183 | 0 | 186 | 0 | 98 | 99 | 189 | 0 | 0 | 53 | 0 | 94 | 86 | 0 | 0 |  | 8355 | 3080 | 11435 | 4056 | 898 | 1933 | 3312 | 327 | 165 | 566 | 178 | 0 | 0 | 0
23:00 | 0 | 199 | 200 | 0 | 0 | 107 | 68 | 350 | 329 |  | 0 | 420 | 290 | 56 | 64 | 55 | 0 | 0 | 0 | 0 | 8 | 102 | 122 | 50 | 45 | 0 | 16 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 29 | 42 | 0 | 76 | 90 | 95 | 120 | 25 | 205 | 0 | 100 | 0 |  | 0 | 0 | 85 | 10 | 50 | 46 | 20 | 42 | 135 | 0 | 0 | 240 | 320 | 192 | 125 | 140 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 174 | 146 | 95 | 20 | 0 | 55 | 64 | 50 | 46 | 100 | 263 | 62 | 40 | 44 | 85 | 18 | 26 | 9 | 315 | 24 | 6 | 0 | 300 | 0 | 0 | 160 | 0 | 126 | 0 | 100 | 200 | 150 | 0 | 107 | 103 | 17 | 0 | 231 |  | 918 | 16 | 0 | 0 | 2 | 0 | 0 | 0 | 40 | 47 | 33 | 84 | 36 | 110 | 12 | 0 | 60 | 50 | 12 | 86 | 40 | 43 | 43 | 52 | 35 | 22 | 14 | 11 | 77 | 0 | 239 | 0 | 17 | 196 | 0 | 197 | 0 | 98 | 99 | 200 | 0 | 0 | 53 | 0 | 94 | 85 | 0 | 0 |  | 8343 | 3121 | 11464 | 4065 | 918 | 1986 | 3274 | 316 | 166 | 565 | 174 | 0 | 0 | 0
24:00 | 0 | 199 | 200 | 0 | 0 | 107 | 68 | 340 | 329 |  | 0 | 420 | 262 | 93 | 64 | 55 | 0 | 0 | 0 | 0 | 45 | 102 | 125 | 50 | 45 | 0 | 6 | 53 | 55 | 55 | 22 | 25 | 28 | 33 | 29 | 42 | 0 | 75 | 90 | 95 | 120 | 25 | 205 | 0 | 135 | 0 |  | 0 | 0 | 68 | 10 | 50 | 47 | 20 | 42 | 135 | 0 | 0 | 40 | 315 | 181 | 195 | 136 | 33 | 52 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 172 | 147 | 95 | 20 | 0 | 54 | 64 | 50 | 46 | 163 | 264 | 53 | 75 | 44 | 134 | 18 | 46 | 9 | 290 | 24 | 11 | 0 | 290 | 0 | 0 | 160 | 0 | 149 | 0 | 100 | 200 | 150 | 0 | 106 | 103 | 17 | 0 | 231 |  | 917 | 16 | 0 | 0 | 99 | 0 | 0 | 0 | 40 | 38 | 33 | 140 | 37 | 110 | 12 | 0 | 60 | 50 | 10 | 86 | 40 | 43 | 37 | 52 | 35 | 22 | 15 | 11 | 72 | 0 | 240 | 0 | 17 | 200 | 0 | 186 | 0 | 97 | 97 | 189 | 0 | 0 | 35 | 0 | 94 | 86 | 0 | 0 |  | 8386 | 3216 | 11602 | 3951 | 917 | 2150 | 3401 | 312 | 165 | 534 | 172 | 0 | 0 | 0
KWH | 0 | 5055600 | 4809000 | 0 | 0 | 2208000 | 1535072 | 8593624 | 7376000 |  | 0 | 9426500 | 6765847 | 1124160 | 813624 | 656666 | 0 | 0 | 0 | 0 | 454080 | 1176048 | 1572000 | 646635 | 736320 | 0 | 264768 | 1197360 | 903900 | 707737 | 404640 | 550000 | 591300 | 805800 | 773600 | 800340 | 0 | 1725704 | 2040000 | 2200000 | 2500000 | 201470 | 4946171 | 0 | 3214630 | 0 |  | 0 | 0 | 661906 | 293760 | 730560 | 720960 | 440784 | 688320 | 3282152 | 0 | 0 | 4330500 | 7604500 | 4827000 | 2609454 | 3328860 | 743256 | 1236000 | 0 | 861144 | 0 | 279928 | 629990 | 489924 | 250020 | 812700 | 340820 | 3477120 | 3408320 | 1662720 | 433313 | 9550 | 1291000 | 1518120 | 772200 | 828432 | 3137555 | 5793000 | 1440288 | 1241280 | 658080 | 2649610 | 96730 | 743440 | 209880 | 7461000 | 479424 | 252000 | 113280 | 2220544 | 86388 | 22810 | 1516800 | 61340 | 1598400 | 109620 | 1781760 | 3128640 | 1043781 | 0 | 1744800 | 2470800 | 470870 | 30000 | 4624255 |  | 21611636 | 184600 | 0 | 0 | 1432320 | 0 | 0 | 0 | 397920 | 483584 | 582000 | 2055379 | 677577 | 1463040 | 61878 | 0 | 1380000 | 595384 | 97461 | 947300 | 927110 | 532524 | 247835 | 993600 | 159938 | 507840 | 336240 | 203724 | 1786472 | 0 | 5304400 | 0 | 170000 | 4755627 | 0 | 4730809 | 0 | 2312362 | 421440 | 4928191 | 0 | 0 | 822240 | 0 | 1829280 | 1995120 | 339840 | 0 |  | 170526284 | 65274671 | 235800955 | 96310416 | 21611636 | 44826376 | 52709927 | 7090872 | 3765704 | 5859734 | 3477120 | 149170 | 0
Fuel Cost | 0 | 5460048 | 5145630 | 0 | 0 | 2141760 | 2241205.12 | 6187409.28 | 5605760 |  | 0 | 7541200 | 6089262.3 | 11466432 | 8811547.92 | 6737393.16 | 0 | 0 | 0 | 0 | 5040288 | 11948647.68 | 15578520 | 6776734.8 | 6700512 | 0 | 2478228.48 | 11482682.4 | 8623206 | 7049060.52 | 303480 | 412500 | 0 | 0 | 0 | 7667257.2 | 0 | 448683.04 | 530400 | 3366000 | 3825000 | 1936126.7 | 5193479.55 | 0 | 4082580.1 | 0 |  | 0 | 0 | 6943393.94 | 3022790.4 | 6947625.6 | 6748185.6 | 405521.28 | 1913529.6 | 3446259.6 | 0 | 0 | 3204570 | 6387780 | 4440840 | 2557264.92 | 4427383.8 | 609469.92 | 1273080 | 0 | 1231435.92 | 0 | 3280756.16 | 5921906 | 499722.48 | 187515 | 1536003 | 255615 | 23992128 | 2794822.4 | 15812467.2 | 441979.26 | 156620 | 1755760 | 2064643.2 | 1050192 | 1035540 | 3890568.2 | 5329560 | 2146029.12 | 2184652.8 | 730468.8 | 4027407.2 | 153800.7 | 869824.8 | 493218 | 5297310 | 359568 | 191520 | 1907635.2 | 23249095.68 | 1477234.8 | 380927 | 14591616 | 1024378 | 16127856 | 1265014.8 | 16606003.2 | 29346643.2 | 9780227.97 | 0 | 15301896 | 22014828 | 4449721.5 | 0 | 42635631.1 |  | 58351417.2 | 5399550 | 0 | 0 | 13807564.8 | 0 | 0 | 0 | 4615872 | 6334950.4 | 5755980 | 1644303.2 | 1050244.35 | 15713049.6 | 2051255.7 | 0 | 2594400 | 6632577.76 | 1193897.25 | 9378270 | 9614130.7 | 6235856.04 | 2986411.75 | 9896256 | 1575389.3 | 558624 | 554796 | 154219.068 | 11379826.64 | 0 | 21694996 | 0 | 4799100 | 4184951.76 | 0 | 4399652.37 | 0 | 3676655.58 | 7122336 | 4336808.08 | 0 | 0 | 7778390.4 | 0 | 16792790.4 | 17776519.2 | 3174105.6 | 0 |  | 511048470.6 | 273215147.148 | 784263617.748 | 95956231.368 | 58351417.2 | 45897330.09 | 453821026.35 | 33074822.64 | 979083.04 | 70769944.26 | 23992128 | 1421634.8 | 0
Yesterday Day Peak | 0 | 199 | 200 | 0 | 0 | 35 | 67 | 377 | 303 |  | 0 | 420 | 296 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 8 | 0 | 6 | 35 | 17 | 0 | 0 | 25 | 22 | 33 | 33 | 16 | 0 | 76 | 90 | 95 | 100 | 0 | 219 | 0 | 143 | 0 |  | 0 | 0 | 0 | 10 | 11 | 0 | 18 | 11 | 135 | 0 | 0 | 345 | 345 | 204 | 78 | 141 | 33 | 51 | 0 | 20 | 0 | 0 | 0 | 21 | 11 | 33 | 14 | 128 | 146 | 25 | 22 | 2.3 | 56 | 63 | 11 | 10 | 163 | 271 | 61 | 50 | 10 | 122 | 0 | 42 | 9 | 330 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 76 | 17 | 0 | 0 | 88 | 103 | 0 | 5.8 | 202 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 84 | 24 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 32 | 8 | 0 | 43 | 0 | 22 | 14 | 8 | 81 | 0 | 199 | 0 | 0 | 203 | 0 | 207 | 0 | 95 | 0 | 206 | 0 | 0 | 35 | 0 | 36 | 87 | 14 | 0 |  | 8841.1 | DayPeak
Yesterday Evening Peak | 0 | 199 | 200 | 0 | 0 | 103 | 67 | 340 | 329 | 0 | 0 | 420 | 300 | 75 | 64 | 55 | 0 | 0 | 0 | 0 | 55 | 102 | 111 | 50 | 45 | 0 | 48 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 29 | 42 | 0 | 75 | 90 | 95 | 120 | 25 | 205 | 0 | 135 | 0 | 0 | 0 | 0 | 85 | 10 | 50 | 46 | 19 | 42 | 135 | 0 | 0 | 240 | 310 | 184 | 68 | 141 | 33 | 51 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 15 | 174 | 146 | 95 | 22 | 0 | 51 | 64 | 50 | 46 | 100 | 263 | 63 | 40 | 44 | 116 | 18 | 46 | 9 | 280 | 24 | 11 | 0 | 260 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 199 | 150 | 0 | 106 | 103 | 17 | 0 | 231 |  | 899 | 32 | 0 | 0 | 1 | 0 | 0 | 0 | 41 | 45 | 33 | 84 | 33 | 110 | 12 | 0 | 60 | 50 | 13 | 86 | 40 | 34 | 44 | 52 | 36 | 22 | 14 | 11 | 77 | 0 | 249 | 0 | 18 | 182 | 0 | 186 | 0 | 97 | 100 | 188 | 0 | 0 | 53 | 0 | 94 | 86 | 0 | 0 |  | 11477 | EvPeak
Forecast for Evening | 0 | 199 | 200 | 0 | 0 | 106 | 78 | 370 | 360 | 0 | 0 | 450 | 335 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 102 | 145 | 100 | 45 | 0 | 50 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 75 | 90 | 100 | 120 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 77 | 85 | 100 | 100 | 40 | 22 | 25 | 135 | 0 | 0 | 0 | 360 | 220 | 195 | 142 | 33 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 15 | 182 | 150 | 95 | 22 | 0 | 55 | 63 | 51 | 44 | 163 | 260 | 66 | 86 | 46 | 125 | 18 | 44 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 110 | 100 | 100 | 0 | 260 |  | 908 | 32 | 0 | 0 | 115 | 150 | 0 | 0 | 33 | 80 | 33 | 195 | 36 | 110 | 32 | 0 | 60 | 50 | 30 | 95 | 40 | 42 | 45 | 52 | 36 | 22 | 15 | 11 | 77 | 0 | 250 | 0 | 17 | 215 | 0 | 210 | 0 | 95 | 100 | 215 | 0 | 0 | 105 | 0 | 94 | 90 | 100
Forecast for Day | 0 | 199 | 200 | 0 | 0 | 106 | 78 | 370 | 340 | 0 | 0 | 450 | 300 | 100 | 100 | 55 | 0 | 0 | 0 | 0 | 100 | 100 | 145 | 100 | 45 | 0 | 48 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 75 | 90 | 100 | 120 | 25 | 215 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 40 | 22 | 5 | 135 | 0 | 0 | 0 | 340 | 220 | 195 | 142 | 33 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 15 | 123 | 150 | 95 | 22 | 1.6 | 55 | 63 | 51 | 44 | 163 | 260 | 66 | 80 | 43 | 125 | 18 | 44 | 10 | 315 | 24 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 100 | 20 | 100 | 200 | 150 | 0 | 110 | 100 | 50 | 4.4 | 230 |  | 908 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 10 | 10 | 33 | 135 | 30 | 70 | 0 | 0 | 60 | 0 | 0 | 50 | 30 | 40 | 15 | 52 | 0 | 22 | 15 | 11 | 77 | 0 | 250 | 0 | 0 | 215 | 0 | 200 | 0 | 95 | 0 | 205 | 0 | 0 | 105 | 0 | 94 | 90 | 100
Generation at 08:00(Today) | 0 | 199 | 200 | 0 | 0 | 107 | 67 | 339 | 294 | 0 | 0 | 380 | 263 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 45 | 0 | 6 | 53 | 17 | 17 | 19 | 25 | 25 | 33 | 29 | 42 | 0 | 75 | 90 | 95 | 120 | 8 | 205 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 40 | 20 | 2 | 135 | 0 | 0 | 0 | 315 | 181 | 197 | 141 | 30 | 52 | 0 | 43 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 136 | 148 | 95 | 20 | 1.4 | 55 | 63 | 50 | 41 | 130 | 263 | 63 | 73 | 44 | 110 | 17 | 46 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 17 | 9.42 | 50 | 17 | 10 | 0 | 106 | 103 | 0 | 2.9 | 161 | 0 | 906 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 23 | 16 | 0 | 0 | 60 | 0 | 0 | 0 | 40 | 29 | 0 | 8 | 0 | 22 | 15 | 8 | 71 | 0 | 250 | 0 | 0 | 180 | 0 | 185 | 0 | 95 | 0 | 187 | 0 | 0 | 17 | 0 | 94 | 52 | 0 | 0 | 0
199
| Minimum Generation |  | 8052.11 | 9:00
| Highest Generation |  | 11602 | 24:00
| Day Peak Generation |  | 8841.1 | 12:00
| Evening Peak Generation |  | 11477 | 21:00
| HVDC Max Flow |  | 926 | 2:00
| HVDC EvPeak Flow |  | 899 | 21:00
| Load factor L.F |  | 84.68%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-07-20
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-07-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8841.1 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8787.72 | MW
Evening Peak Generation : |  | 11477 | MW Hour : | 21:00 | Available Max Generation : |  | 14010 | MW
E.P. Demand (at gen end) : |  | 11477 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12300 | MW
Maximum Generation : |  | 11602 | MW Hour : | 24:00 | Reserve(Generation end) |  | 1710 | MW
Total Gen. (MKWH) : |  | 235.801 | System Load Factor : | 84.68% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -670 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-07-20
Actual : | 107.2 | Ft.(MSL) , | Rule curve : | 87.04 | Ft.( MSL )
Gas Consumed : | Total = | 1265.27 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 141853561.458
|  | Coal : | 33074822.64 | Oil : | 524590970.61 | Total : | 699519354.708
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4360.4119 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1485.7718 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1331.7351 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1203.5242 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 1087.5031 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 877.584 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 486.8536 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 225.8525 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 676.8548 |  |  | 0 | 0%
Total | 0 |  | 11736.091 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-2. | 7) Baghabari 100 MW
|  |  |  | 2) Khulna ST 110 MW | 8) Ghorasal Unit-7
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ghorasal Unit-1 & 2
|  |  |  | 4) Bheramara 410 MW. | 10) Ghorasal Unit-5
|  |  |  | 5) Siddhirganj ST | 11) Bibiyna unit-3
|  |  |  | 6) Ashuganj #4,5 | 12) Sirajganj Unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Dhamrai 132/33 kV T1 transformer was under shut down from 08:56 to 16:10 for D/W.
b) Rangpur-Lalmonirhat 132 kV Ckt was under shut down from 09:10 to 14:07 for D/W. |  |  |  |  | About 50 MW power interruption occurred under Lalmonirhat S/S area
from 09:10 to 14:07.
c) Rangpur 132 kV A bus was shut down from 09:45 to 17:30 for D/W.
d) Ishurdi-Ghorasal 230 kV Ckt-2 was under shut down from 08:17 to 18:49 for D/W.
e) Ashuganj-Cumilla(N) 230 kV Ckt-1 was under shut down from 11:24 to 19:26 for D/W.
f) Ashuganj-Cumilla(N) 230 kV Ckt-2 was under shut down from 11:26 to 19:28 for D/W.
g) Anwara-Sikalbaha 230 kV Ckt-2 was under shut down from 10:55 to 12:40 for D/W.
h) Ishurdi 132/33 kV T2 transformer was under shut down from 09:56 to 12:11 due to oil leakage.
i) After maintenance Daudkandi 132/33 kV T3 transformer was switched on at 14:13.
j) Narsingdi-B.Baria 132 kV Ckt-1 was under shut down from 14:45 to 20:26 for project work.
k) Rangpur 33 kV bus was under shut down from 15:30 to 16:40 due to red hot maintenance at 33 kV Kotkitara para-2 feeder. |  |  |  |  | About 80 MW power interruption occurred under Rangpur S/S area
from 15:30 to 16:40.
l) Ashuganj(N) 450 MW tripped at 17:40 due to RMS problem and were synchronized GT & ST at 19:19 & 03:02 respectively again tripped
at 04:49(20/7/19)
m) Kurigram 132/33 kV T1 & T2 transformer were charge HT side at 18:15 & 18:20 respectively.
n) Shahazibazar 330 MW GT-2 tripped at 18:53 due to ventilation system problem and was synchronized at 20:18.
o) KPCL-2 tripped at 20:24 due to E/F relay and was synchronized at 20:59 again tripped at 21:09 showing same relay and was synchronized at 21:25 .
p) Madunaghat-Kulshi 132 kV Ckt-1 is under shut down since 06:12 for C/M.
q) Gulshan 132/33 kV T2 transformer was under shut down from 05:08 to 08:38(20/7/19) for C/M.
r) Fenchuganj 132/33 kV T-2 transformer tripped at 02:19 from both side showing backup protection and was switched on at 03:25(20/7/19) |  |  |  |  | About 20 MW power interruption occurred under Fenchuganj S/S area
from 02:19 to 03:25(20/7/19).
s) Cumilla(N) 132/33 kV T3(both side) & T4 transformer 33 kV side tripped at 04:26 showing lock out at T3 & high impedance differential |  |  |  |  | About 48 MW power interruption occurred under Cumilla(N) S/S area
protection relay at T4 and was switched on T4 at 05:21(20/7/19). |  |  |  |  | from 04:26 to 05:21(20/7/19).
t) Rangpur 132 kV B bus with 132/33 kV T2 transformer were shut down from 07:20 to 09:20 for C/M. |  |  |  |  | About 40 MW power interruption occurred under Rangpur S/S area
from 07:20 to 09:20(20/7/19).
u) HVDC block-2 filter 20DS31 tripped at 07:48(20/7/19) due to capacitor unbalance.
.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-07-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 199 | 5055600
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4809000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 67 | 1535072 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2208000
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Gas shortage
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8593624 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 329 | 7376000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 420 | 9426500
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 75 | 1124160 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 300 | 6765847 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 64 | 813624 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 656666
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 646635 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 404640
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 55 | 454080 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1176048
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 48 | 264768
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1197360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 111 | 1572000 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 903900
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 707737
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 45 | 736320 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1141300 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 805800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 29 | 773600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 800340 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 2220544 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 86388 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 22810 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 61340 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 135 | 1598400 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 103 | 2470800
| Dhaka area Total |  |  |  | 5723 | 3406 | 66408903
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2200000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2500000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 201470
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 109620
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 720960
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 165 | 3765704 | #1 under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 205 | 4946171 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 3214630 | FGMO
44 | Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 0 | 0 | Contract Expired
45 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 470870 | Transformer over load
46 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve
47 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 661906
48 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 293760 | Low demand
49 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1781760
50 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 440784
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 688320
51 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 730560 | Line over load
52 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30000
53 | Anwara 300 MW PP (United) |  | United Group | 300 MW | 300 | 231 | 4624255 | Transformer over load
| Chattogram area Total |  |  |  | 2053 | 1345 | 27380770
54 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 3282152
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
55 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 184 | 4827000 | FGMO
56 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 240 | 4330500 | Load increasing time.
57 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7604500 | FGMO
58 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 33 | 743256 | Engine problem
59 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1236000
60 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
61 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 2609454 | Gas shortage
62 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 861144 | Engine problem
63 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1043781
64 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
65 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 279928 | Reserve
66 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3328860
67 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 199 | 3128640
68 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 489924
69 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 174 | 3477120
70 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 812700
71 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 629990
72 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 340820 | Engine problem
73 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 113280 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1860 | 39389069
74 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 146 | 3408320 | GT-1 under maint.
75 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 433313
76 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 1662720
77 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9550
78 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 1516800 | Engine problem
79 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 106 | 1744800
| Mymensingh Area Total |  |  |  | 637 | 559 | 8775503
80 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 51 | 1291000
81 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 64 | 1518120
82 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3137555 | Frequency Control.
83 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 263 | 5793000
84 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 772200
85 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 46 | 828432
86 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 252000
87 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1440288 | FGMO
88 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 40 | 1241280 | Engine problem
89 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 44 | 658080
90 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 116 | 2649610 | FGMO
91 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 96730
92 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 46 | 743440
93 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 479424
94 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7461000 | FGMO
95 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 0 | 0 | Under maint.
96 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 209880
| Sylhet Area Total |  |  |  | 1834 | 1225 | 28572039
97 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 32 | 184600
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 899 | 21611636
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
98 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 1 | 1432320 | tripped at 20:59.
99 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 41 | 397920
100 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
101 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 45 | 483584 | Engine problem
102 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Under maint.
103 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 582000 | Engine problem
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
104 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 421440
105 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 822240 | Fuel shortage
106 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 86 | 1995120 | Engine problem
| Khulna Area Total |  |  |  | 2314 | 1290 | 27930860
107 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1463040
108 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 12 | 61878 | Low demand
109 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 677577
110 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 84 | 2055379
111 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 2312362
| Barisal Area Total |  |  |  | 462 | 336 | 6570236
112 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1380000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
113 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 595384
114 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 13 | 97461
115 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 40 | 927110 | Engine problem
116 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 532524 | Engine problem
117 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 247835
118 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 182 | 4755627 | FGMO
119 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 186 | 4730809 | FGMO
120 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4928191 | FGMO
121 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Under maint.
122 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 36 | 159938
123 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 507840
124 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 14 | 336240
125 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203724
126 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 993600
127 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 947300
128 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
129 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 94 | 1829280
| Rajshahi Area Total |  |  |  | 2070 | 1112 | 23172863
130 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 77 | 1786472
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
131 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 249 | 5304400
132 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
133 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 170000
| Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 0 | 0 | 339840 | On test
| Rangpur Area Total |  |  |  | 484 | 344 | 7600712
| Total |  |  |  | 18468 | 11477 | 235800955
| Eastern Grid Total |  |  |  | 13138 | 8395 | 170526284
| Western Grid Total |  |  |  | 5330 | 3082 | 65274671
| National Grid Total |  |  |  | 18468 | 11477 | 235800955
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
| Date: | 2019-07-19
| (a) ENTIRE EASTERN GRID : |  | 7508 | MW | (b) ENTIRE WESTERN GRID : |  | 3433 | MW
| i) Dhaka area |  | 3871 | MW | i) Khulna area |  | 1222 | MW
| ii) Chittagong area |  | 1108 | MW | ii) Rajshahi area |  | 1194 | MW
| iii) Comilla area |  | 1108 | MW | iii) Barisal area |  | 320 | MW
| iv) Mymensingh area |  | 943 | MW | iv) Rangpur area |  | 697 | MW
| v) Sylhet area |  | 478 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10941 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
SL NO | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
1 | Siddhirganj | 108 | 100 | Jamalpur | 114 | 2300 | Jessore | 104 | 2000
2 | Munsiganj | 134 | 2100 | Sherpur | 94 | 2300 | Benapol | 42 | 2100
3 | Sonargaon | 86 | 2100 | Srimongal | 36 | 2100 | Jhenida | 110 | 2000
4 | Shyampur | 180 | 100 | Shahjibazar | 116 | 1930 | Bottail | 102 | 100
5 | Bhulta | 184 | 100 | Fenchuganj | 53 | 2100 | G.K Project | 54 | 100
6 | Madanganj | 62 | 100 | Kulawara | 47 | 2100 | Faridpur | 160 | 1930
7 | Shitalakhya | 101 | 100 | Sylhet | 140 | 2100 | Madaripur | 116 | 100
8 | Rahim steel | 6 | 600 | Chatak | 32 | 2300 | Sariatpur | 37 | 2300
9 | Matuail | 86 | 700 | Sunamganj | 40 | 2100 | Gopalganj | 89 | 2300
10 | Ghorasal | 87 | 100 | Biani Bazar | 48 | 2000 | Bagerhat | 80 | 2400
11 | Narsingdi | 141 | 2100 | Comilla (S) | 178 | 2200 | Mongla | 30 | 100
12 | Haripur (SBU) | 92 | 100 | Comilla(N) | 121 | 2200 | Satkhira | 95 | 100
13 | Ullon | 86 | 1930 | Chandpur | 104 | 2300 | Gallamari | 46 | 100
14 | Hasnabad | 196 | 100 | Feni | 136 | 2200 | Magura | 47 | 2400
15 | Magbazar | 109 | 1600 | Chowmuhani | 180 | 2200 | Chuadanga | 90 | 400
16 | Maniknagar | 102 | 2100 | Ashuganj | 55 | 2200 | Barisal(N) | 41 | 2000
17 | Bangabhaban | 14 | 1500 | Daudkandi | 132 | 2100 | Barisal (S) | 104 | 2000
18 | Narinda | 78 | 1930 | B.Baria | 149 | 2100 | Patuakhali | 102 | 2200
19 | Dhanmondi | 123 | 1930 | Ramganj | 86 | 2000 | Bhandaria | 53 | 2300
20 | Lalbag | 56 | 1600 | Madunaghat | 57 | 1200 | Borhan Uddin | 36 | 2400
21 | Madartek | 56 | 100 | Hathazari | 89 | 2100 | Ishurdi | 62 | 2000
22 | Mirpur | 102 | 1900 | Khulshi | 189 | 100 | Ruppur Paromanobik | 2 | 700
23 | Kalyanpur | 117 | 1930 | Halishahar | 121 | 1500 | Natore | 122 | 2100
24 | Gulshan | 124 | 1500 | Baraulia | 155 | 400 | Bogra | 230 | 2100
25 | Uttara | 85 | 1930 | Sikalbaha | 32 | 100 | Noagaon | 108 | 2000
26 | Uttara New | 16 | 2100 | Dohazari | 86 | 2100 | Rajshahi | 157 | 1930
27 | Kamrangirchar | 60 | 1930 | Cox'sbazar | 92 | 2000 | C.Nawabganj | 78 | 2000
28 | Savar | 124 | 1200 | Chandraghona | 24 | 1930 | Amnura | 40 | 2000
29 | Bhasantec | 153 | 1930 | Kaptai | 4 | 1930 | Pabna | 111 | 100
30 | Agargaon | 54 | 1930 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 82 | 1930
31 | Satmosjid | 106 | 2000 | Bakulia | 93 | 1930 | Serajganj | 92 | 2100
32 | Tongi | 139 | 1500 | Julda | 20 | 100 | Niyamatpur | 67 | 2100
33 | Kabirpur | 157 | 1200 | TK chemical | 4 | 800 | Joypurhat | 56 | 1930
34 | Basundhara | 120 | 2000 | Modern Steel | 12 | 100 | Mohastangor | 16 | 2000
35 | Manikganj | 102 | 2100 | Shahmirpur | 33 | 100 | Rangpur | 137 | 2000
36 | Joydevpur | 204 | 100 | Khagrachhari | 16 | 1300 | Lalmonirhat | 79 | 1930
37 | New Tongi | 85 | 2100 | Matarbari | 28 | 2000 | Saidpur | 98 | 2000
38 | Korda | 210 | 2100 | Baroiar Hat | 28 | 1900 | Purbasadipur | 104 | 1930
39 | Dhamrai | 60 | 2100 | Rangamati | 12 | 2000 | Thakurgaon | 80 | 2000
40 | Valuka | 84 | 2000 | Abul Khair 230 | 12 | 1200 | Palashbari | 108 | 1930
41 | Tangail | 201 | 2100 | BSRM | 159 | 1830 | Barapukuria | 52 | 2000
42 | Mymensing | 236 | 2100 | Goalpara | 23 | 2300 | Panchagar | 37 | 1930
43 | Kishorganj | 132 | 2300 | Central (S) | 90 | 2000 | Joldhaka | 23 | 1930
44 | Netrokona | 103 | 2100 | Noapara | 91 | 1930
| Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
| Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  | (24) Director,System Planning,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2019-07-19
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min
|  |  |  | Voltage |  |  | Voltage |  | Voltage
SL NO | 400 KV | KV |  | KV |  |  | KV |  | 126
1 | Bibiyana | 392 | 6:00 | 381 | 15:00 | Kaliakoir | 371 | 6:00 | 361
2 | Bheramara | 394 | 8:00 | 384 | 1:00 | Bhulta | 383 | 2:00 | 372
3 | Ashuganj(N) | 388 | 1:00 | 375 | 18:00
SL NO | 230 KV | KV |  | KV |  | 230 KV | KV |  | 19:00
1 | Ghorasal | 235 | 13:00 | 228 | 14:00 | Hathazari | 222 | 4:00 | 219
2 | Ishurdi | 236 | 17:00 | 215 | 21:00 | Megnaghat | 223 | 1:00 | 218
3 | Ashuganj | 237 | 16:00 | 230 | 11:00 | Fenchuganj | 238 | 6:00 | 233
4 | Serajganj | 230 | 6:00 | 220 | 21:00 | Siddhirganj | 222 | 1:00 | 216
5 | Baghabari | 231 | 4:00 | 221 | 21:00 | Maniknagar | 221 | 5:00 | 214
6 | Barapukuria | 237 | 8:00 | 220 | 1:00 | Old Airport | 221 | 3:00 | 211
7 | Bogra | 225 | 10:00 | 208 | 21:00 | Barisal | 232 | 6:00 | 216
8 | Khulna South | 231 | 6:00 | 197 | 22:00 | AKSML | 218 | 2:00 | 215
9 | Rampura | 221 | 1:00 | 218 | 12:00 | BSRM | 221 | 7:00 | 214
10 | Haripur | 220 | 1:00 | 216 | 12:00 | Bibiyana | 233 | 4:00 | 229
11 | Hasnabad | 222 | 2:00 | 213 | 12:00 | Bhulta | 223 | 20:00 | 216
12 | Aminbazar | 226 | 6:00 | 212 | 13:00 | Ashuganj (S) | 235 | 6:00 | 230
13 | Tongi | 225 | 19:30 | 213 | 12:00 | Kaliakoir | 226 | 1:00 | 218
14 | Comilla (N) | 230 | 1:00 | 222 | 12:00
SL NO | 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
1 | Siddhirganj | 133 | 2000 | 127 | 1200 | Hathazari | 132 | 400 | 129
2 | Munsiganj | 135 | 2000 | 127 | 1100 | Khulshi | 129 | 1700 | 125
3 | Megnaghat | 132 | 1930 | 127 | 900 | Halishahar | 134 | 2000 | 128
4 | Shyampur | 133 | 300 | 126 | 1200 | Baraulia | 131 | 900 | 126
5 | Bhulta | 124 | 300 | 120 | 700 | Sikalbaha | 134 | 2000 | 130
6 | Madanganj | 136 | 100 | 125 | 1100 | Dohazari | 130 | 1600 | 126
7 | Shitalakhya | 140 | 2000 | 125 | 1200 | Cox'sbazar | 125 | 1830 | 118
8 | Rahim steal | 133 | 1900 | 128 | 1100 | Chandraghona | 133 | 600 | 130
9 | Matuail | 132 | 2000 | 127 | 1000 | Kaptai | 133 | 100 | 130
10 | Ghorasal | 138 | 100 | 135 | 1000 | A. Khaer Stl. | 130 | 1600 | 128
11 | Narsinghdi | 127 | 900 | 120 | 2100 | Bakulia | 132 | 2000 | 127
12 | Haripur (SBU) | 133 | 2000 | 128 | 1200 | Julda | 132 | 500 | 128
13 | Ullon | 132 | 100 | 128 | 1200 | TK Chemical | 135 | 1700 | 130
14 | Hasnabad | 135 | 100 | 127 | 1100 | Modern Steel | 132 | 2000 | 129
15 | Magbazar | 133 | 400 | 128 | 1200 | Shahmirpur | 132 | 1700 | 128
16 | Maniknagar | 134 | 400 | 130 | 1200 | Khagrachhari | 133 | 1200 | 130
17 | Bangabhaban | 134 | 400 | 130 | 1200 | Matarbari | 128 | 1830 | 121
18 | Narinda | 134 | 400 | 130 | 1200 | Baroiar Hat | 129 | 700 | 125
19 | Dhanmondi | 134 | 400 | 130 | 1200 | Rangamati | 132 | 300 | 130
20 | Lalbag | 137 | 2000 | 125 | 1200 | Goalpara | 138 | 600 | 114
21 | Madartek | 133 | 500 | 128 | 1200 | Central s/s | 137 | 600 | 114
22 | Mirpur | 135 | 600 | 127 | 1100 | Noapara | 134 | 600 | 111
23 | Kalyanpur | 135 | 200 | 129 | 1200 | Jessore | 128 | 1800 | 106
24 | Gulshan | 133 | 500 | 127 | 1200 | Benapol | 131 | 600 | 108
25 | Uttara | 133 | 500 | 124 | 1200 | Jhenida | 127 | 1800 | 104
26 | Uttara New | 135 | 300 | 126 | 1000 | Bottail | 134 | 1800 | 114
27 | Kamrangirchar | 135 | 100 | 124 | 1200 | G.K Project | 139 | 900 | 125
28 | Savar | 133 | 300 | 125 | 1200 | Faridpur | 134 | 1800 | 115
29 | Bhasantec | 133 | 300 | 126 | 1200 | Madaripur | 134 | 1800 | 115
30 | Agargaon | 134 | 300 | 129 | 1100 | Sariatpur | 133 | 1800 | 116
31 | Satmosjid | 134 | 300 | 127 | 1200 | Gopalganj | 141 | 1800 | 128
32 | Tongi | 136 | 1930 | 128 | 1100 | Bagerhat | 134 | 1800 | 110
33 | Kabirpur | 134 | 500 | 129 | 100 | Mongla | 130 | 1800 | 112
34 | Basundhara | 133 | 2000 | 125 | 1100 | Satkhira | 134 | 1800 | 110
35 | Manikganj | 140 | 500 | 130 | 1000 | Gallamari | 138 | 600 | 115
36 | Joydevpur | 138 | 100 | 132 | 1200 | Magura | 126 | 1800 | 102
37 | New Tongi | 135 | 2000 | 126 | 1100 | Chuadanga | 121 | 1800 | 95
38 | Kodda | 138 | 100 | 123 | 1100 | Barisal(N) | 138 | 1800 | 126
39 | Dhamrai | 134 | 600 | 129 | 2100 | Barisal (S) | 136 | 700 | 126
40 | Valuka | 130 | 900 | 112 | 100 | Patuakhali | 136 | 1800 | 120
41 | Tangail | 134 | 700 | 122 | 100 | Bhandaria | 134 | 1800 | 115
42 | Mymensing | 130 | 900 | 113 | 100 | Ishurdi | 138 | 1700 | 125
43 | Kishorganj | 130 | 700 | 120 | 100 | Ruppur Paromanobik | 138 | 600 | 125
44 | Netrokona | 131 | 1000 | 115 | 100 | Natore | 134 | 1830 | 122
45 | Jamalpur | 138 | 1500 | 121 | 100 | Bogra | 134 | 1800 | 121
46 | Sherpur | 135 | 2300 | 116 | 400 | Noagaon | 128 | 1830 | 115
47 | Srimongal | 139 | 600 | 134 | 2300 | Rajshahi | 132 | 1830 | 120
48 | Shahjibazar | 137 | 600 | 131 | 2200 | C.Nawabganj | 130 | 1900 | 118
49 | Fenchuganj | 138 | 500 | 133 | 1830 | Amnura | 132 | 1900 | 116
50 | Khulawara | 136 | 400 | 132 | 1900 | Pabna | 136 | 1900 | 124
51 | Sylhet | 136 | 400 | 132 | 1830 | Shahjadpur | 140 | 500 | 132
52 | Chatak | 135 | 500 | 131 | 1900 | Serajganj | 135 | 900 | 124
53 | Sunamganj | 135 | 600 | 128 | 2300 | Niyamatpur | 128 | 1900 | 110
54 | Biani Bazar | 134 | 500 | 130 | 1900 | Joypurhat | 128 | 900 | 112
55 | Comilla(s) | 125 | 500 | 120 | 1500 | Mohastangor | 133 | 900 | 118
56 | Comilla(n) | 136 | 700 | 133 | 2000 | Rangpur | 136 | 1600 | 112
57 | Chandpur | 132 | 2400 | 130 | 1500 | Lalmonirhat | 131 | 900 | 108
58 | Feni | 127 | 700 | 122 | 2400 | Saidpur | 132 | 900 | 112
59 | Chowmuhani | 124 | 1000 | 120 | 2000 | Purbasadipur | 131 | 1000 | 109
60 | Ashuganj | 138 | 600 | 133 | 2400 | Thakurgaon | 128 | 900 | 102
61 | Daudkandi | 130 | 700 | 125 | 1200 | Palashbari | 130 | 900 | 115
62 | B.Baria | 133 | 1600 | 127 | 2300 | Barapukuria | 137 | 800 | 120

## L-Curve
Date | 2019-07-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 580 | 8386 | 3216 | 11602 |  |  |  | QF-LDC-12
0:30 | 625 | 8349.5 | 3105 | 11454.5 | Date: | 2019-07-19
1:00 | 670 | 8313 | 2994 | 11307
1:30 | 605 | 8143.5 | 3042 | 11185.5
2:00 | 540 | 7974 | 3090 | 11064
2:30 | 540 | 7922 | 3052 | 10974 | [5 empty] | Gen. at Eve. Peak | 11477 | 11477 MW (21:00 )
3:00 | 540 | 7870 | 3014 | 10884 | [6 empty] | 21:00
3:30 | 540 | 7702.5 | 2992 | 10694.5 | [5 empty] | Gen. at Day Peak | 8841.1 | 8841.1 MW (12:00 )
4:00 | 540 | 7535 | 2970 | 10505 | [6 empty] | 12:00
4:30 | 540 | 7455 | 2933 | 10388 | [5 empty] | Highest Generation | 11602
5:00 | 540 | 7375 | 2896 | 10271 | [6 empty] | 24:00
5:30 | 430 | 7007.5 | 2801.5 | 9809
6:00 | 320 | 6640 | 2707 | 9347
6:30 | 270 | 6361.255 | 2573 | 8934.255
7:00 | 220 | 6082.51 | 2439 | 8521.51
7:30 | 190 | 5948.505 | 2434.5 | 8383.005
8:00 | 160 | 5814.5 | 2430 | 8244.5
8:30 | 115 | 5724.805 | 2423.5 | 8148.305
9:00 | 70 | 5635.11 | 2417 | 8052.11
9:30 | 90 | 5667.865 | 2426.5 | 8094.365
10:00 | 110 | 5700.62 | 2436 | 8136.62
10:30 | 60 | 5773.83 | 2392 | 8165.83
11:00 | 10 | 5847.04 | 2348 | 8195.04
11:30 | 30 | 6145.57 | 2372.5 | 8518.07
12:00 | 50 | 6444.1 | 2397 | 8841.1
12:30 | 180 | 6439.35 | 2404.5 | 8843.85
13:00 | 310 | 6434.6 | 2412 | 8846.6
13:30 | 295 | 6403.65 | 2410 | 8813.65
14:00 | 280 | 6372.7 | 2408 | 8780.7
14:30 | 260 | 6554.7 | 2516 | 9070.7
15:00 | 240 | 6736.7 | 2624 | 9360.7
15:30 | 265 | 6685.55 | 2557.5 | 9243.05
16:00 | 290 | 6634.4 | 2491 | 9125.4
16:30 | 210 | 6492 | 2451 | 8943
17:00 | 130 | 6349.6 | 2411 | 8760.6
17:30 | 85 | 6073.2 | 2414.5 | 8487.7
18:00 | 40 | 5796.8 | 2418 | 8214.8
18:30 | 80 | 6118.9 | 2610 | 8728.9
19:00 | 120 | 6441 | 2802 | 9243
19:30 | 450 | 7688 | 3174 | 10862
20:00 | 620 | 7926 | 3173 | 11099 |  |  |  | Executive Engineer
20:30 | 625 | 8160.5 | 3127.5 | 11288 |  |  |  | Network Operation Division
21:00 | 630 | 8395 | 3082 | 11477
21:30 | 620 | 8375 | 3081 | 11456
22:00 | 610 | 8355 | 3080 | 11435 |  |  |  |  | Page 6 of 7
22:30 | 565 | 8349 | 3100.5 | 11449.5
23:00 | 520 | 8343 | 3121 | 11464
23:30 | 550 | 8364.5 | 3168.5 | 11533
24:00 | 580 | 8386 | 3216 | 11602
11477 MW (21:00 )
8841.1 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-07-19 |  | Energy | 235800955
[10 empty] | 2019-07-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3951 | 917 | 2150 | 3401 | 312 | 165 | 534 | 0 | 172
0:30 | 4029 | 892.5 | 2050 | 3366 | 265.5 | 165 | 517.5 | 0 | 169 | Date: | 2019-07-19
1:00 | 4107 | 868 | 1950 | 3331 | 219 | 165 | 501 | 0 | 166
1:30 | 3988 | 897 | 2051.5 | 3221 | 244 | 165 | 456 | 0 | 163 | [7 empty] | Total Energy | 235.801 | Total Energy Gen 235.801 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.801 MKWHr
2:00 | 3869 | 926 | 2153 | 3111 | 269 | 165 | 411 | 0 | 160 | [7 empty] | Energy not Served | 0
2:30 | 3857 | 926 | 2148.5 | 3055 | 269.5 | 165 | 403 | 0 | 150 | [7 empty] | Energy Requirement | 235.801
3:00 | 3845 | 926 | 2144 | 2999 | 270 | 165 | 395 | 0 | 140
3:30 | 3840.5 | 926 | 2091 | 2887 | 272.5 | 165 | 372.5 | 0 | 140 | [6 empty] | Shortage
4:00 | 3836 | 926 | 2038 | 2775 | 275 | 165 | 350 | 0 | 140
4:30 | 3847.5 | 926 | 2042 | 2659 | 275 | 165 | 338.5 | 0 | 135
5:00 | 3859 | 926 | 2046 | 2543 | 275 | 165 | 327 | 0 | 130
5:30 | 3834.5 | 926 | 1929 | 2258.5 | 275 | 165 | 291 | 0 | 130
6:00 | 3810 | 926 | 1812 | 1974 | 275 | 165 | 255 | 0 | 130
6:30 | 3831.1 | 915 | 1737.5 | 1734.585 | 276 | 165 | 153 | 0 | 119 |  |  |  |  | Coal
7:00 | 3852.2 | 904 | 1663 | 1495.17 | 277 | 165 | 51 | 0 | 108
7:30 | 3863.6 | 904 | 1670.5 | 1362.085 | 276.5 | 165 | 25.5 | 0 | 109 |  |  |  | Oil |  |  |  | ,
8:00 | 3875 | 904 | 1678 | 1229 | 276 | 165 | 0 | 0 | 110
8:30 | 3883.5 | 904 | 1595 | 1199.5 | 275.5 | 165 | 8 | 0 | 108
9:00 | 3892 | 904 | 1512 | 1170 | 275 | 165 | 16 | 0 | 106
9:30 | 3962 | 904.5 | 1504 | 1167 | 275.5 | 140 | 16 | 0 | 108
10:00 | 4032 | 905 | 1496 | 1164 | 276 | 115 | 16 | 0 | 110
10:30 | 4099.5 | 904.5 | 1501 | 1117.5 | 275.5 | 115.5 | 16 | 0 | 113
11:00 | 4167 | 904 | 1506 | 1071 | 275 | 116 | 16 | 0 | 116
11:30 | 4222 | 904 | 1635.5 | 1174 | 277.5 | 141 | 16 | 0 | 122
12:00 | 4277 | 904 | 1765 | 1277 | 280 | 166 | 16 | 0 | 128
12:30 | 4206 | 904 | 1786 | 1328 | 279 | 166 | 16 | 0 | 131
13:00 | 4135 | 904 | 1807 | 1379 | 278 | 166 | 16 | 0 | 134
13:30 | 4135 | 904 | 1807 | 1379 | 278 | 166 | 16 | 0 | 134
14:00 | 4135 | 904 | 1807 | 1379 | 278 | 166 | 16 | 0 | 134
14:30 | 4124.5 | 901 | 1892.5 | 1551 | 296 | 166 | 16 | 0 | 139
15:00 | 4114 | 898 | 1978 | 1723 | 314 | 166 | 16 | 0 | 144
15:30 | 3988.5 | 898 | 1883.5 | 1810 | 327 | 166 | 20 | 0 | 142
16:00 | 3863 | 898 | 1789 | 1897 | 340 | 166 | 24 | 0 | 140
16:30 | 3858.5 | 897.5 | 1707.5 | 1809 | 334 | 166 | 25 | 0 | 140
17:00 | 3854 | 897 | 1626 | 1721 | 328 | 166 | 26 | 0 | 140
17:30 | 3717 | 897.5 | 1526.5 | 1665 | 330 | 165.5 | 52.5 | 0 | 132
18:00 | 3580 | 898 | 1427 | 1609 | 332 | 165 | 79 | 0 | 124
18:30 | 3614 | 898 | 1580 | 1755.5 | 331.5 | 165 | 249.5 | 0 | 135
19:00 | 3648 | 898 | 1733 | 1902 | 331 | 165 | 420 | 0 | 146
19:30 | 3794 | 898 | 1974 | 2956 | 330 | 165 | 581 | 0 | 164
20:00 | 3873 | 898 | 2001 | 3098 | 327 | 165 | 567 | 0 | 170
20:30 | 3969 | 898.5 | 1952.5 | 3234.5 | 326.5 | 165 | 570 | 0 | 172
21:00 | 4065 | 899 | 1904 | 3371 | 326 | 165 | 573 | 0 | 174
21:30 | 4060.5 | 898.5 | 1918.5 | 3341.5 | 326.5 | 165 | 569.5 | 0 | 176
22:00 | 4056 | 898 | 1933 | 3312 | 327 | 165 | 566 | 0 | 178
22:30 | 4060.5 | 908 | 1959.5 | 3293 | 321.5 | 165.5 | 565.5 | 0 | 176
23:00 | 4065 | 918 | 1986 | 3274 | 316 | 166 | 565 | 0 | 174
23:30 | 4008 | 917.5 | 2068 | 3337.5 | 314 | 165.5 | 549.5 | 0 | 173 | Max Temp. in Dhaka |  | 34.0° C
24:00 | 3951 | 917 | 2150 | 3401 | 312 | 165 | 534 | 0 | 172
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 235.801 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.801 MKWHr
Note on W13: Author:

## Generation
2019-07-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 75 |  | 75 | 75 | 75 | 75 | 75 | 76 | 75 | 1725704
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 40 | 40 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2040000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 90 | 90 | 90 |  | 90 | 90 | 90 | 95 | 95 | 95 | 95 | 2200000
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 2500000
5 | Raozan 25 MW PP | 25 | 25 | 0 | [16 empty] | 13 | 25 | 25 | 25 | 25 | 25 | 25 | 201470
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 5.24 | 6 | 8.31 | 18.72 | 16.74 | 20 | 19 | 2 | 7 | 7 | 2 | 0.6 | [8 empty] | 109620
6 | Sikalbaha 225MW CCPP (Gas) | 205 | 205 | 205 | 205 | 205 | 204 | 205 | 205 | 204 | 204 | 215 | 219 | 217 | 219 | 205 | 204 | 208 | 206 |  | 215 | 205 | 205 | 205 | 205 | 205 | 205 | 4946171
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 136 | 143 | 136 | 141 | 135 | 135 | 135 | 135 |  | 132 | 135 | 135 | 135 | 135 | 100 | 135 | 3214630
10 | Sikalbaha 150MW GTPP(Oil) | [26 empty] | 0
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 17 | 17 | 17 | 3 | 0 | [11 empty] | 78 | 85 | 85 | 85 | 73 | 85 | 68 | 661906
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 0 |  |  |  |  | 5 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 470870
| Daudkandi 200 MW PP (B.Trac) | 0 | [19 empty] | 28 | 0 | 0 |  |  |  | 113280
14 | Titas 50 MW Peaking PP | 50 | 0 | [18 empty] | 20 | 0 | 0 |  |  |  | 279928
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 250 | 250 | 120 | 50 | 15 | 15 | 0 | [6 empty] | 0 | 12 | 15 | 12 |  | 18 | 80 | 143 | 260 | 300 | 300 | 290 | 2220544
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 185 | 185 | 185 | 185 | 185 | 148 | 148 | 73 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 68 |  | 68 | 68 | 68 | 68 | 68 | 125 | 195 | 2609454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 |  | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 5055600
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4809000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3282152
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 10 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 743256
33 | Ashuganj 225 MW CCPP | 216 | 216 | 216 | 215 | 215 | 215 | 216 | 195 | 182 | 189 | 215 | 204 | 203 | 204 | 183 | 183 | 189 | 197 |  | 200 | 181 | 181 | 184 | 183 | 192 | 181 | 4827000
34 | Ashuganj 450 MW CCPP(South) | 310 | 320 | 310 | 315 | 315 | 310 | 310 | 320 | 310 | 310 | 320 | 345 | 235 | 345 | 310 | 255 | 255 | 270 |  | 325 | 310 | 310 | 310 | 310 | 320 | 315 | 7604500
| Ashuganj 450 MW CCPP(North) | 300 | 0 | 20 | 25 | 25 | 40 | 50 | 50 | 105 | 220 | 300 | 345 | 330 | 345 | 310 | 260 | 274 | 0 |  |  | 40 | 140 | 240 | 240 | 240 | 40 | 4330500
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 52 | 51 | 52 | 51 | 52 | 49 | 50 | 51 |  | 47 | 50 | 52 | 51 | 51 | 52 | 52 | 1236000
36 | Chandpur 150 MW CCPP | 140 | 141 | 140 | 140 | 140 | 140 | 140 | 141 | 142 | 141 | 141 | 141 | 141 | 142 | 142 | 141 | 141 | 141 |  | 145 | 142 | 140 | 141 | 141 | 140 | 136 | 3328860
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 357 | 343 | 339 | 342 | 339 | 338 | 345 | 340 | 346 | 351 | 377 | 369 | 354 | 370 | 340 | 340 | 325 |  | 315 | 395 | 395 | 340 | 340 | 350 | 340 | 8593624
40 | Meghnaghat 450 MW CCPP(MPL) | 400 | 420 | 420 | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 350 | 420 | 420 | 370 | 420 | 420 | 380 | 320 |  | 420 | 450 | 450 | 420 | 420 | 420 | 420 | 9426500
41 | Haripur 360MW CCPP(HPL) | 320 | 353 | 353 | 300 | 300 | 270 | 270 | 270 | 273 | 273 | 273 | 303 | 303 | 303 | 340 | 323 | 323 | 283 |  | 325 | 352 | 357 | 329 | 329 | 329 | 329 | 7376000
42 | RPCL 210MW CCPP | 144 | 144 | 146 | 146 | 146 | 140 | 148 | 147 | 147 | 146 | 143 | 146 | 143 | 142 | 142 | 142 | 142 | 142 |  | 140 | 146 | 146 | 146 | 146 | 146 | 147 | 3408320
43
44 | Fenchugonj CCPP Phase-1 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 53 | 53 | 54 | 53 |  | 54 | 51 | 50 | 51 | 50 | 55 | 54 | 1291000
45 | Fenchugonj CCPP Phase-2 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 64 | 63 | 64 | 63 | 63 | 63 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 1518120
46 | Shajibazar 330 MW CCPP | 263 | 266 | 260 | 259 | 263 | 260 | 262 | 261 | 263 | 263 | 268 | 271 | 263 | 267 | 262 | 266 | 265 | 265 |  | 164 | 156 | 159 | 263 | 264 | 263 | 264 | 5793000
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 63 | 63 | 63 | 51 | 63 | 62 | 63 | 61 | 61 | 61 | 59 | 58 | 57 | 58 | 61 | 61 |  | 60 | 63 | 56 | 63 | 62 | 62 | 53 | 1440288
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 40 | 40 | 10 | 10 | 10 | 50 | 50 | 10 | 74 | 74 | 40 | 10 |  | 10 | 10 | 72 | 40 | 40 | 40 | 75 | 1241280
49 | Shahjibazar 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 |  | 5 | 42 | 44 | 44 | 44 | 44 | 44 | 658080
50 | Sylhet 150 MW CCPP | 113 | 112 | 110 | 110 | 110 | 112 | 110 | 110 | 109 | 110 | 123 | 122 | 120 | 122 | 110 | 70 | 79 | 80 |  | 96 | 108 | 109 | 116 | 111 | 85 | 134 | 2649610
51 | Sylhet 20 MW GTPP | [19 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 96730
52 | Sylhet 50MW PP (EPL) | 45 | 45 | 45 | 45 | 45 | 10 | 12 | 12 | 13 | 14 | 12 | 42 | 45 | 45 | 45 | 5 | 5 | 5 |  | 40 | 43 | 46 | 46 | 46 | 26 | 46 | 743440
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 209880
54 | Hobiganj 11MW PP Cofidence-E | 8 | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 6 | 11 | 252000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 16 | 14 | 49 | 50 | 11 | 14 |  | 14 | 46 | 49 | 50 | 50 | 50 | 50 | 772200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16.2 | 16 | 16 | 16 | 16 | 16 | 24 | 16 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 479424
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 300 | 300 | 305 | 270 | 275 | 295 | 285 | 315 | 325 | 330 | 320 | 300 | 310 | 290 | 295 | 300 |  | 320 | 300 | 295 | 280 | 300 | 315 | 290 | 7461000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 0 | [6 empty] | 17 | 17 | 17 | 17 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 707737
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 440784
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 |  |  | 19 | 19 | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 404640
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | 0 |  |  |  |  | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 433313
63 | Impoprt (Tripura) | 166 | 160 | 140 | 140 | 130 | 130 | 108 | 110 | 106 | 110 | 116 | 128 | 134 | 138 | 144 | 140 | 140 | 124 |  | 146 | 164 | 170 | 174 | 178 | 174 | 172 | 3477120
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 39 | 40 | 42 | 0 |  |  |  |  | 0 | 11 | 29 | 12 | 39 | 44 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 688320
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 21 | 21 | 21 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 489924
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250020
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 812700
68 | Cumilla 25 MW PP (Summit) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 15 | 15 | 15 | 15 | 18 | 20 | 20 | 340820
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 550000
70 | Summit Madhabdi | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 22 | 22 | 22 | 18 | 16 | 16 | 16 | 16 | 16 |  | 16 | 18 | 22 | 31 | 31 | 31 | 28 | 591300
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 773600
73 | Ghorashal 108MW PP (Regent) | 107 | 107 | 107 | 104 | 104 | 104 | 104 | 104 | 55 | 12 | 12 | 35 | 62 | 62 | 97 | 52 | 52 | 13 |  | 44 | 101 | 106 | 103 | 107 | 107 | 107 | 2208000
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 24 | 24 | 7 | 7 | 7 | 0 | [7 empty] | 0 | 7 | 7 | 7 |  | 7 | 20 | 55 | 55 | 7 | 8 | 45 | 454080
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 42 | 42 | 42 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 42 | 34 | 40 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 800340
79 | Kodda 150MW PP | 120 | 120 | 120 | 120 | 120 | 110 | 48 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 60 | 100 | 100 | 111 | 118 | 122 | 125 | 1572000
80 | Jamalpur 95 MW PP(Powerpac) | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 65 | 62 | 25 | 25 | 25 | 25 | 25 | 48 | 74 | 20 | 25 |  | 44 | 92 | 91 | 95 | 95 | 95 | 95 | 1662720
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 8 | 0 | [7 empty] | 2 | 25 | 16 | 8 |  | 13 | 52 | 40 | 52 | 52 | 52 | 52 | 629990
| Gazipur 100 MW PP | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 2470800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0.7 | 1 | 2.8 | 2 | 6.2 | 5.8 | 6.3 | 2.2 | 0.6 | 1.2 | 0.4 | 0 |  | 0 | [6 empty] | 30000
82 | Madanganj 102 PP(Summit) | 98 | 47 | 47 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 60 | 69 | 64 | 64 | 64 | 64 | 813624
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 100 | 50 | 50 | 10 | 10 | 10 | 10 | 0 | [6 empty] | 2 | 10 | 10 | 10 |  | 12 | 100 | 85 | 50 | 50 | 50 | 50 | 646635
86 | Meghnaghat CCPP(Summit) | 275 | 283 | 263 | 281 | 275 | 230 | 275 | 275 | 257 | 277 | 285 | 296 | 290 | 295 | 276 | 280 | 285 | 290 |  | 305 | 285 | 262 | 300 | 290 | 290 | 262 | 6765847
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 100 | 56 | 0 | [6 empty] | 0 | 18 | 7 | 7 |  | 7 | 40 | 68 | 75 | 56 | 56 | 93 | 1124160
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 68 | 68 | 67 | 67 | 66 | 65 | 65 | 65 | 60 | 40 |  | 40 | 67 | 67 | 67 | 67 | 68 | 68 | 1535072
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 293760
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 37 | 46 | 5 | 5 |  | 7 | 49 | 49 | 46 | 46 | 46 | 46 | 828432
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 20 | 17 | 17 | 35 | 25 | 20 | 10 |  | 16 | 20 | 30 | 43 | 43 | 43 | 43 | 861144
94 | Gagnagar 102 MW PP (Digital Power) | 101 | 101 | 101 | 101 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 12 | 40 | 16 | 16 |  | 30 | 101 | 101 | 102 | 101 | 102 | 102 | 1176048
95 | Patenga 50MW PP (Baraka) | 47 | 47 | 47 | 47 | 45 | 0 | [5 empty] | 0 | 4 | 30 | 38 | 38 | 45 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 47 | 720960
96 | Chattogram 108 MW PP (ECPV) | 44 | 44 | 44 | 44 | 44 | 44 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 24 | 33 | 47 | 50 | 50 | 50 | 50 | 730560
97 | Katpotti 52 MW PP (Sinha) | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 10 | 17 | 48 | 48 | 16 | 6 | 264768
98 | Bosila 108MW PP(CLC) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 43 | 43 | 35 | 36 |  | 37 | 37 | 37 | 45 | 45 | 45 | 45 | 736320
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 0 | [6 empty] | 0 | 14 | 15 | 15 |  | 18 | 55 | 55 | 55 | 55 | 55 | 55 | 656666
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 35 | 17.2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 903900
101 | Kushiara 163 MW CCPP (KP) | 100 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 163 | 100 | 163 | 100 | 100 | 100 |  | 163 | 163 | 100 | 100 | 100 | 100 | 163 | 3137555
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0.2 | 0.5 | 1 | 1.9 | 1.1 | 2.3 | 2.3 | 0.5 | 0.1 | 0.2 | 0.2 | 0.2 |  | 0 | [6 empty] | 9550
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 53 | 53.97 | 53 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1197360
104 | Keranigonj 300 MW PP (APR) | 0 | [19 empty] | 53 | 24 | 0 | 0 |  |  | 86388
105 | Bramhangoan 100 MW PP (Aggreko) | 0 | [19 empty] | 20 | 0 | 0 |  |  |  | 22810
106 | Mymensingh 200 MW PP (United) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 7 | 7 | 7 |  | 7 | 57 | 60 | 190 | 194 | 160 | 160 | 1516800
112 | Aurahati 100MW PP (Aggreko) | 0 | [19 empty] | 22 | 0 | 0 |  |  |  | 61340
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 96 | 24 | 0 | [6 empty] | 0 | 11 | 17 | 15 |  | 24 | 130 | 128 | 135 | 110 | 126 | 149 | 1598400
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 100 | 10 | 10 | 10 | 10 | 10 | 10 | 76 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1781760
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 198 | 168 | 70 | 34 | 17 | 17 | 17 | 17 | 85 | 80 | 92 | 140 | 130 | 108 |  | 120 | 200 | 193 | 199 | 200 | 200 | 200 | 3128640
117 | Ashuganj 150MW PP (Midland) | 50 | 50 | 50 | 50 | 50 | 6 | 0 | [7 empty] | 5 | 50 | 10 | 10 |  | 10 | 20 | 100 | 150 | 150 | 150 | 150 | 1043781
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 58 | 58 | 38 | 38 | 38 | 38 | 38 | 78 | 57 | 77 | 87 | 88 | 68 | 77 | 77 | 77 | 106 | 97 |  | 106 | 106 | 106 | 106 | 107 | 107 | 106 | 1744800
| Anwara 300 MW PP (United) | 214 | 214 | 214 | 214 | 214 | 214 | 148 | 108 | 108 | 107 | 107 | 202 | 210 | 215 | 250 | 264 | 188 | 151 |  | 179 | 181 | 231 | 231 | 231 | 231 | 231 | 4624255
120 | Eastern Zone Total | 8313 | 7974 | 7870 | 7535 | 7375 | 6640 | 6082.51 | 5814.5 | 5635.11 | 5700.62 | 5847.04 | 6444.1 | 6434.6 | 6372.7 | 6736.7 | 6634.4 | 6349.6 | 5796.8 |  | 6441 | 7688 | 7926 | 8395 | 8355 | 8343 | 8386 | 170526284
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 115 | 115 | 115 | 115 | 115 | 110 | 29 | 32 | 16 | 16 | 16 | 16 | 16 | 49 | 50 | 66 | 66 | 66 |  | 91 | 115 | 115 | 1 | 0 | 2 | 99 | 1432320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 33 | 33 | 33 | 33 | 33 | 0 | [11 empty] | 23 |  | 30 | 40 | 42 | 41 | 41 | 40 | 40 | 397920
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 53 | 53 | 53 | 35 | 822240
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 80 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 50 | 110 | 110 | 110 | 110 | 110 | 110 | 1463040
136 | Barisal GT PP Unit-1& 2 | [19 empty] | 0 | 12 | 12 | 12 | 13 | 12 | 12 | 61878
137 | Bhola 95 MW PP (Aggreko) | 98 | 96 | 97 | 97 | 98 | 96 | 97 | 95 | 93 | 96 | 95 | 95 | 98 | 96 | 95 | 95 | 95 | 96 |  | 96 | 95 | 96 | 97 | 98 | 98 | 97 | 2312362
| Bhola 225 MW CCPP | 84 | 84 | 84 | 84 | 84 | 71 | 84 | 84 | 79 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 |  | 84 | 84 | 72 | 84 | 84 | 84 | 140 | 2055379
140 | Bhola 33 MW PP (Venture) | 37 | 36 | 36 | 35 | 35 | 31 | 27 | 24 | 22 | 18 | 21 | 24 | 23 | 22 | 25 | 25 | 22 | 20 |  | 31 | 31 | 33 | 33 | 37 | 36 | 37 | 677577
141 | Noapara 100 MW PP (Bangla Trac) | 99 | 99 | 80 | 80 | 50 | 0 | [13 empty] | 7 | 86 | 90 | 100 | 99 | 99 | 97 | 421440
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 8 | 8 | 8 | 8 | 8 | 31 | 33 | 33 | 33 | 33 | 8 |  | 16 | 24 | 24 | 33 | 33 | 33 | 33 | 582000
143 | Gopalganj 100 MW Peaking PP | 39 | 34 | 34 | 34 | 29 | 0 | [9 empty] | 8 | 10 | 40 |  | 50 | 55 | 50 | 45 | 44 | 47 | 38 | 483584
144 | Bheramara GTPP Unit-1,2 & 3 | 16 | 16 | 0 | [16 empty] | 16 | 32 | 32 | 32 | 32 | 16 | 16 | 184600
145 | Madhumati 100 MW PP | 86 | 87 | 85 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 85 | 33 |  | 65 | 86 | 86 | 86 | 86 | 85 | 86 | 1995120
146 | Bheramara HVDC | 868 | 926 | 926 | 926 | 926 | 926 | 904 | 904 | 904 | 905 | 904 | 904 | 904 | 904 | 898 | 898 | 897 | 898 |  | 898 | 898 | 898 | 899 | 898 | 918 | 917 | 21611636
147 | Bheramara 360 MW CCPP
148
149
150 | Barapukuria TPP Unit-1 | 20 | 70 | 71 | 76 | 76 | 76 | 78 | 77 | 76 | 77 | 76 | 81 | 79 | 80 | 88 | 90 | 78 | 83 |  | 82 | 81 | 78 | 77 | 78 | 77 | 72 | 1786472
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 199 | 226 | 250 | 250 | 249 |  | 249 | 249 | 249 | 249 | 249 | 239 | 240 | 5304400
153 | Baghabari 71 MW GTPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 60 | 60 | 60 | 55 | 60 | 60 | 1380000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 50 | 0 | [12 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 595384
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 181 | 193 | 187 | 183 | 188 | 180 | 180 | 190 | 183 | 192 | 201 | 203 | 199 | 194 | 198 | 174 | 157 | 166 |  | 178 | 192 | 186 | 182 | 183 | 196 | 200 | 4755627
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 185 | 195 | 191 | 187 | 192 | 185 | 185 | 193 | 186 | 197 | 198 | 207 | 204 | 198 | 205 | 169 | 155 | 167 |  | 179 | 203 | 196 | 186 | 186 | 197 | 186 | 4730809
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 191 | 202 | 197 | 192 | 198 | 190 | 190 | 200 | 212 | 213 | 209 | 206 | 204 | 204 | 212 | 193 | 175 | 171 |  | 178 | 190 | 196 | 188 | 189 | 200 | 189 | 4928191
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 0 | [18 empty] | 0
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 13 | 12 | 12 | 0 | [15 empty] | 5 | 9 | 11 | 13 | 13 | 12 | 10 | 97461
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507840
163 | Bogura 20 MW PP (Energyprima) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 12 | 12 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 336240
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 203724
165 | Amnura 50 MW PP(Sinha) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 32 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 927110
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 | 8 | 24 | 24 | 24 | 24 |  | 24 | 27 | 34 | 34 | 34 | 43 | 43 | 532524
167 | Katakhali 50 MW Peaking PP | 34 | 0 | [17 empty] | 33 | 45 | 47 | 44 | 43 | 43 | 37 | 247835
168 | Santahar 50 MW Peaking PP | [19 empty] | 14 | 29 | 34 | 36 | 35 | 35 | 35 | 159938
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 26 | 8 | 8 | 8 | 43 | 50 | 50 | 50 | 52 | 25 | 25 |  | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 993600
170 | Chapainawabganj 100 MW Peaking PP | 78 | 78 | 78 | 78 | 78 | 78 | 0 | [12 empty] | 66 | 86 | 86 | 86 | 86 | 86 | 86 | 947300
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 75 | 75 | 75 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 70 | 74 | 85 | 93 |  | 93 | 93 | 94 | 94 | 94 | 94 | 94 | 1829280
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 17 | 17 | 17 | 18 | 0 | [14 empty] | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 170000
176 | Rangpur 113 MW PP (Confidence) | [6 empty] | 0 | 71 | 109 | 109 | 15 | 14 | 0 |  | 109 | 0 | [10 empty] | 339840
177
178
178 | Western Zone Total | 2994 | 3090 | 3014 | 2970 | 2896 | 2707 | 2439 | 2430 | 2417 | 2436 | 2348 | 2397 | 2412 | 2408 | 2624 | 2491 | 2411 | 2418 |  | 2802 | 3174 | 3173 | 3082 | 3080 | 3121 | 3216 | 65274671