## QF-MIS-03
QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: May 2013
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | May 2013 |  | April 2013 |  | May 2012
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 6223 | 02/05/13 | 6326 | 13.04.13 | 5575 | 30/05/12 | 6350.5 | 2012-04-08
|  |  | 21:00 |  | 24:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 2804 | 07/05/13 | 2256 | 17.04.13 | 2550 | 04/05/12
|  |  | 6:00 |  | 8:00 |  | 7:00
3 | Maximum Evening Peak Generation (MW) | 6223 | 02/05/13 | 6314 | 13.04.13 | 5575 | 30/05/12 | 6350 | 04.08.12
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 5346 | 02/05/13 | 5341 | 25.04.13 | 4613 | 31/05/12
|  |  | 12:00 |  | 12:00 |  | 9:00
5 | Maximum Evening Peak Demand (MW) Estimated | 6350 | 02/05/13 | 6500 | 15.04.13 | 6600 | 30.05.12 | 6600 | 30.05.12
|  |  | 20:00 |  | 20:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 5731.06 |  | 5938.52 |  | 5205.1
7 | Average Generation (MW) at Day Peak | 4574.67 |  | 4804.97 |  | 4144.52
8 | Maximum Load Shed (MW) at Evening Peak | 370 | 20/05/13 | 487 | 03.04.13 | 1014 | 20.05.12 | 2087 | 15.12.07
|  |  | 21:00 |  | 21:00 |  | 20:00 |  | 19:00
9 | Generation During Max. Load Shed (MW) at Evening Peak | 5789 | 20/05/13 | 5659 | 03.04.13 | 5194 | 20.05.12
|  |  | 21:00 |  | 21:00 |  | 20:00
10 | Minimum Load Shed (MW) at Evening Peak | 112 | 03/05/13 | 103 | 13.04.13 | 179 | 01.05.12
|  |  | 21:00 |  | 21:00 |  | 19:30
11 | Generation During Min. Load Shed (MW) at Evening Peak | 6176 | 03/05/13 | 6314 | 13.04.13 | 4595 | 01.05.12
|  |  | 21:00 |  | 21:00 |  | 19:30
12 | Maximum Load Shed (MW) at Day Peak | 176 | 27/05/13 | 489 | 10.04.13 | 648 | 24.05.12
|  |  | 11:00 |  | 12:00 |  | 12:00
13 | Generation During Max. Load Shed (MW) at Day Peak | 5004 | 27/05/13 | 4882 | 10.04.13 | 4230 | 24.05.12
|  |  | 11:00 |  | 12:00 |  | 12:00
14 | Minimum Load Shed (MW) at Day Peak | 140 | 19/05/13 | 76 | 25.04.13 | 76 | 1.05.12
|  |  | 12:00 |  | 12:00 |  | 12:00
15 | Generation During Min. Load Shed (MW) at Day Peak | 4844 | 19/05/13 | 5341 | 25.04.13 | 3366 | 1.05.12
|  |  | 12:00 |  | 12:00 |  | 12:00
16 | Nos. of Days Load Shed at Evening Peak | 7 |  | 13 |  | 29
17 | Nos. of Days Load Shed at Day Peak | 2 |  | 15 |  | 30
18 | Gross Generation of BPDB (Mkwh) | 1759.1367 |  | 1707.73 |  | 1507.65
19 | Station Use of BPDB (Mkwh) | 101.8407 |  | 86.02 |  | 80.34
20 | Net Generation of BPDB (Mkwh) | 1657.296 |  | 1621.71 |  | 1427.31
21 | Net Generation of IPP, REB (Mkwh) | 601.17 |  | 751.7 |  | 810.04
|  | 130.97 |  | 127.93 |  | 114.23
22 | Net Generation of Rental Power Plant (MKWh) | 835.36 |  | 1004.68 |  | 770.23
23 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 3224.796 |  | 3506.02 |  | 3121.81
24 | Energy Generation by Gas (MKWh) | 2706.74 |  | 2738.39 |  | 2703.09
25 | Energy Generation by Diesel (MKWh) | 53.13 |  | 103.18 |  | 49.2
26 | Energy Generation by Furnace Oil (MKWh) | 501.1 |  | 602.59 |  | 321.93
27 | Energy Generation by Hydro (MKWh) | 56.23 |  | 51.81 |  | 23.7
28 | Energy Generation by Coal (MKWh) | 101.31 |  | 96.05 |  | 104.58
29 | Monthly Load Factor (%) | 73.84% |  | 78.86% |  | 77.21%

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: MAY 2013
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  |  | 2013-05-02 | 21:00
Generation Period
| Dhaka | MW | 2307
| Chittagong | MW | 568
| Comilla | MW | 453
| Mymensingh | MW | 365
| Sylhet | MW | 279
a) | Total supply in East zone | MW | 3972
| Khulna | MW | 602
| Barisal | MW | 115
| Rajshahi | MW | 717
| Rangpur | MW | 275
b) | Total supply in West zone | MW | 1709
c) | Total supply in both zone ( a+b) | MW | 5681
Ref: | PGCB/IMD/4.01/2013/32 | Date: 10.06.2013
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Director, O&M/ P&D, PGCB, Dhaka
(3) General Manager, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) DGM, LDC/SPM/Planning/Grid Circle, Dhaka/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Manager, MIS/System Planning/EMD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: May 2013
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 1400 | 06.05.13 | 13:00
| b) Ishurdi end | MW | -
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | MW | -
| b) Ishurdi end | MW | 420 | 06.05.13 | 13:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 7.07 | 06.05.13
| b) Ishurdi end | MKWH | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | 6.84 | 06.05.13
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 160.09
| b) Ishurdi end | MKWH | -
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | 153.58
23 | Transmission loss of EWI/ NO-1 | % | 4.0665
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 11.05.13 | 2:00
| b)Serajganj end | MW
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | -
| b)Sirajganj end | MW | 430 | 11.05.13 | 2:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 9.328 | 16.05.13
| b)Sirajganj end | MKWH | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 9.194 | 16.05.13
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 204.31
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 201.02
30 | Transmission loss of EWI /NO-2 | % | 1.6103
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2013
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :
Kishorganj | 132/33 kV Transformer T3 | 2013-05-07 11:24 | 2013-05-07 11:34 | 0:10 | T | Tripped showing O/C, lock out relay | 0 | 0 | No Interruption
Kishorganj | 132/33 kV Transformer T3 | 2013-05-07 20:06 | 2013-05-07 20:20 | 0:14 | E/O | Due to red hot maintenance of breaker | 5 | 0.83333 | No Interruption
Tongi | 132/33 kV Transformer T1 | 2013-05-09 11:22 | 2013-05-09 17:38 | 6:16 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Mymensingh | 132/33 kV Transformer T1 | 2013-05-13 20:10 | 2013-05-13 20:47 | 0:37 | E/O | Due to red hot maintenance | 28 | 17.2667 | Power Interruption
Hasnabad | 230/132 kV Transformer TR1 | 2013-05-16 09:05 | 2013-05-16 17:38 | 8:33 | T | Tripped showing lock out relay | 0 | 0 | No Interruption
Haripur | 230/132 kV Transformer TR1 | 2013-05-17 06:26 | 2013-05-17 07:10 | 0:44 | T | Tripped showing DFR-87T relay | 0 | 0 | No Interruption
Ullon | 132/33 kV Transformer T3 | 2013-05-17 07:22 | 2013-05-17 09:13 | 1:51 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Tongi | 132/33 kV Transformer T2 | 2013-05-23 08:45 | 2013-05-23 15:56 | 7:11 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Narsingdi | 132/33 kV Transformer T1 | 2013-05-23 22:17 | 2013-05-23 23:16 | 0:59 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Jamalpur | 132/33 kV Transformer T3 | 2013-05-26 12:05 | 2013-05-26 14:20 | 2:15 | E/O | Due to red hot maintenance | 8 | 18 | Power Interruption
Tongi | 132/33 kV Transformer T1 & T3 | 2013-05-28 12:58 | 2013-05-28 18:40 | 5:42 | T | Tripped showing E/F & O/C relays | 35 | 199.5 | Power Interruption
Kishoreganj | 132/33 kV Transformer T2 | 2013-05-29 20:37 | 2013-05-29 20:50 | 0:13 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Rampura | 230/132 kV Transformer T1 | 2013-05-30 12:48 | 2013-05-30 12:59 | 0:11 | T | Tripped showing HSOIC, ABC, dist relay | 0 | 0 | No Interruption
|  |  | Total | 34:56 |  |  |  | 235.6
Chittagong Grid Circle :
Juldah | 132/33 kV Transformer T1 | 2013-05-10 07:40 | 2013-05-10 07:55 | 0:15 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Halishahar | 132/33 kV Transformer T2 | 2013-05-16 14:12 | 2013-05-16 15:13 | 1:01 | E/O | Due to red hot maintenance at CT joint. | 0 | 0 | No Interruption
|  |  | Total | 1:16 |  | unserved energy : |  | 0
Comilla Grid Circle:
B.Baria | 132/33 kV Transformer T1 | 2013-05-07 14:24 | 2013-05-07 15:11 | 0:47 | T | Due to over voltage | 22 | 17.2333 | Power Interruption
| 132/33 kV Transformer T2 | 2013-05-07 14:24 | 2013-05-07 15:12 | 0:48 | T
Chowmuhani | 132/33 kV Transformer T1 | 2013-05-09 18:45 | 2013-05-09 18:50 | 0:05 | T | Due to winding temperature high | 0 | 0 | No Interruption
| 132/33 kV Transformer T3 | 2013-05-12 14:42 | 2013-05-12 14:46 | 0:04 | T | Due to winding temperature high | 0 | 0 | No Interruption
Chattak | 132/33 kV Transformer T1 | 2013-05-13 15:50 | 2013-05-13 16:10 | 0:20 | T | Tripped showing O/C relay | 5 | 1.6667 | Power Interruption
Chandpur | 132/33 kV Transformer T1 | 2013-05-16 09:33 | 2013-05-16 18:20 | 8:47 | T | Tripped showing lock out relay | 0 | 0 | No Interruption
Fenchuganj | 230/132 kV Transformer TR. | 2013-05-16 23:45 | 2013-05-17 00:13 | 0:28 | T | Tripped showing winding temp. high. | 0 | 0 | No Interruption
Chowmuhani | 132/33 kV Transformer T1 | 2013-05-19 19:35 | 2013-05-19 21:20 | 1:45 | T | Due to red hot maintenance | 0 | 0 | No Interruption
Chandpur | 132/33 kV Transformer T1 & T2 | 2013-05-23 18:50 | 2013-05-23 18:59 | 0:09 | T | Tripped showing E/F relay | 48 | 7.2 | Power Interruption
| 132/33 kV Transformer T1 | 2013-05-23 23:50 | 2013-05-24 00:28 | 0:38 | E/O | Due to red hot maintenance | 18 | 11.4 | Power Interruption
Daudkandi | 132/33 kV Transformer T2 | 2013-05-25 11:05 | 2013-05-25 11:15 | 0:10 | T | Tripped showing O/C and E/F relays | 10 | 1.6667 | Power Interruption
Chandpur | 132/33 kV Transformer T1 | 2013-05-26 14:51 | 2013-05-26 15:30 | 0:39 | E/O | Due to red hot maintenance | 20 | 13 | Power Interruption
Chowmuhani | 132/33 kV Transformer T1 | 2013-05-28 08:31 | 2013-05-28 10:25 | 1:54 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Feni | 132/33 kV Transformer T1 | 2013-05-28 13:25 | 2013-05-28 13:54 | 0:29 | T | Tripped due to DC fail | 16 | 7.7333 | Power Interruption
| 132/33 kV Transformer T1 & T2 | 2013-05-31 14:05 | 2013-05-31 14:23 | 0:18 | T | Tripped showing O/C and E/F relay | 0 | 0 | No Interruption
|  |  | Total : | 17:21 |  | unserved energy : |  | 59.9
Khulna Grid Circle:
Bagerhat | 132/33 kV Transformer T1 | 2013-05-07 19:35 | 2013-05-07 20:12 | 0:37 | E/O | Due to red hot maintenance at breaker | 0 | 0 | No Interruption
Mongla | 132/33 kV Transformer T1 | 2013-05-09 00:45 | 2013-05-09 01:28 | 0:43 | T | Tripped showing E/F relay | 24 | 17.2 | Power Interruption
| 132/33 kV Transformer T2 | 2013-05-09 00:45 | 2013-05-09 01:33 | 0:48 | T
| 132/33 kV Transformer T1 | 2013-05-09 06:28 | 2013-05-09 06:37 | 0:09 | T
Khulna ( C ) | 132/33 kV Transformer T2 | 2013-05-09 06:28 | 2013-05-09 06:40 | 0:12 | T | Tripped showing E/F relay | 21 | 3.15 | Power Interruption
| 132/33 kV Transformer T3 | 2013-05-09 06:28 | 2013-05-09 06:42 | 0:14 | T
Jhenaidah | 132/33 kV Transformer T1&T2 | 2013-05-19 12:21 | 2013-05-19 12:30 | 0:09 | T | Tripped showing E/F relay | 28 | 4.2 | Power Interruption
Bhandaria | 132/33 kV Transformer T2 | 2013-05-19 18:40 | 2013-05-19 20:38 | 1:58 | T | Due to SF6 density metre problem | 0 | 0 | No Interruption
Barisal | 132/33 kV Transformer T2 | 2013-05-20 07:20 | 2013-05-20 10:50 | 3:30 | T | Due to red hot maintenance | 0 | 0 | No Interruption
|  |  | Total : | 8:20 |  | unserved energy : |  | 24.55
Bogra Grid Circle:
Pabna | 132/33 kV Transformer T1 | 2013-05-10 07:16 | 2013-05-10 10:47 | 3:31 | E/O | Due to oil leakage from transformer | 10 | 35.1667 | Power Interruption
Lalmonirhat | 132/33 kV Transformer T4 | 2013-05-11 10:18 | 2013-05-11 10:40 | 0:22 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Pabna | 132 kV Bus | 2013-05-12 04:55 | 2013-05-12 06:45 | 1:50 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Rajshahi | 132/33 kV Transformer T2 | 2013-05-12 19:05 | 2013-05-12 19:17 | 0:12 | T | Tripped showing O/C relay | 0 | 0 | No Interruption
| 132/33 kV Transformer T1 | 2013-05-13 18:15 | 2013-05-13 18:25 | 0:10 | E/O | Due to red hot maintenance | 20 | 3.3333 | Power Interruption
Natore | 132/33 kV Transformer T1&T2 | 2013-05-13 21:35 | 2013-05-13 22:17 | 0:42 | T | Tripped showing E/F & lock out relay | 0 | 0 | No Interruption
| 132/33 kV Transformer T1 | 2013-05-14 19:51 | 2013-05-14 20:27 | 0:36 | E/O | Due to red hot maintenance | 25 | 15 | Power Interruption
Bogra | 132/33 kV Transformer T3 | 2013-05-15 10:04 | 2013-05-15 11:05 | 1:01 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Saidpur | 132/33 kV Transformer T3 | 2013-05-17 10:35 | 2013-05-17 11:20 | 0:45 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Natore | 132/33 kV Transformer T3 | 2013-05-26 11:05 | 2013-05-26 11:30 | 0:25 | E/O | Due to red hot maintenance | 3 | 1.25 | Power Interruption
Ishurdi | 132/33 kV Transformer T2 | 2013-05-30 12:48 | 2013-05-30 13:12 | 0:24 | T | Tripped showing O/C, Ins. E/F relay | 0 | 0 | No Interruption
Natore | 132/33 kV Transformer T1 | 2013-05-31 08:55 | 2013-05-31 09:15 | 0:20 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Ishurdi | 132/33 kV Transformer T2 | 2013-05-31 09:15 | 2013-05-31 09:47 | 0:32 | T | Tripped showing Instt. E/F relay | 0 | 0 | No Interruption
| 132/33 kV Transformer T2 | 2013-05-31 11:44 | 2013-05-31 13:07 | 1:23 | T | Tripped showing Instt. E/F relay | 8 | 11.0667 | Power Interruption
|  |  | Total : | 12:13 |  | unserved energy : |  | 30.65
Others (BPDP + DPDC) :
| 230/132 kV Transformer OAT11 | 2013-05-06 14:02 | 2013-05-06 16:11 | 2:09 | T | Tripped showing master trip relay 1 & 2 | 0 | 0 | No Interruption
Ashuganj | 230/132 kV Transformer OAT12 | 2013-05-06 14:02 | 2013-05-06 15:22 | 1:20 | T
| 230/132 kV Transformer OAT11 | 2013-05-07 14:05 | 2013-05-07 16:13 | 2:08 | T | Due to tripping of 132 kV bus. | 0 | 0 | No Interruption
| 230/132 kV Transformer OAT12 | 2013-05-07 14:05 | 2013-05-07 15:02 | 0:57 | T
|  |  | Total | 6:34
Total outage period of Sub-station Equipment : |  |  |  | 80:40 | Hours |  |  | Manager
T = Tripping | [7 empty] | Information Management Division
E/O = Emergency Outage | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
Power Grid Company of Bangladesh Ltd QF-LDC-24
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2013
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2013-05-01 20:42 | 2013-05-01 21:25 | 0:43 | T | Mymensingh: Dist. Relay Jamalpur: PT fail dist. C relay | 0 | 0 | Tripped at both end
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2013-05-04 01:57 | 2013-05-04 02:31 | 0:34 | T | Tripped showing dist, ABC, Z2 relay | 0 | 0 | No Interruption
Hasnabad | Hasnabad-Aminbazar 230 kV line-2 | 2013-05-04 11:17 | 2013-05-04 11:34 | 0:17 | E/O | Due to a mental disorder man was climbing the tower (No:11) | 0 | 0 | No Interruption
Meghnaghat | Meghnaghat-Comilla (N) 230 kV line-1 | 2013-05-04 11:50 | 2013-05-04 13:25 | 1:35 | T | Tripped showing dist.B, Z1 relay | 0 | 0 | No Interruption
Meghnaghat | Meghnaghat-Comilla (N) 230 kV line-2 | 2013-05-04 13:15 | 2013-05-04 13:18 | 0:03 | T | Tripped showing dist.B, Z3 relay | 0 | 0 | No Interruption
Haripur | Haripur-Sonargaon 132 kV line-1 | 2013-05-04 15:30 | 2013-05-04 16:00 | 0:30 | T | Tripped showing O/C & E/F relay | 0 | 0 | No Interruption
| Mymensingh-Netrokon 132 kV line-1 | 2013-05-05 00:40 | 2013-05-05 01:15 | 0:35 | T | Tripped showing Instant E/F relay | 11 | 1.8333 | Power Interruption
Mymensingh | Mymensingh-Netrokon 132 kV line-2 | 2013-05-05 00:40 | 2013-05-05 00:50 | 0:10 | T
| Mymensingh-Jamalpur 132 kV line-1&2 | 2013-05-05 04:14 | 2013-05-05 15:23 | 11:09 | T | Tripped showing dist A, Z1 relay. | 0 | 0 | No Interruption
Tongi | Tongi-Bashudhara 132 kV line-1 | 2013-05-06 00:39 | 2013-05-06 01:17 | 0:38 | T | Tongi: C-phase Z2 relay, Bashundhara: Z1, CN relay | 0 | 0 | No Interruption
Rampura | Rampura-Magbazar 132 kV line-2 | 2013-05-07 12:15 | 2013-05-07 13:17 | 1:02 | E/O | Due to red hot maintenance at R-phase DS. | 0 | 0 | No Interruption
Maniknagar | Maniknagar- Siddhirganj 132 kV line-2 | 2013-05-08 16:23 | 2013-05-08 16:45 | 0:22 | T | Tripped showing dist. A relay | 0 | 0 | No Interruption
Ullon | Ullon-Shiddhirganj 132 kV line-1 | 2013-05-08 16:25 | 2013-05-08 17:32 | 1:07 | T | Tripped howing 86T, VAJ relay | 0 | 0 | No Interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2013-05-08 14:24 | 2013-05-08 16:31 | 2:07 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-1 | 2013-05-11 01:03 | 2013-05-11 02:17 | 1:14 | T | Tripped showing dist. A -phase relay | 0 | 0 | No Interruption
Siddhirganj | Siddhirganj-Maniknagar-Ullon 132 kV line-2 | 2013-05-11 20:52 | 2013-05-11 21:43 | 0:51 | T | Siddhirganj: E/F, O/C & Ullon: dist. B-phase, Z1 relay | 0 | 0 | Tripped at both end
Meghnaghat | Meghnaghat-Comilla 230 kV line-1 | 2013-05-12 12:10 | 2013-05-12 12:28 | 0:18 | T | Meghnaghat: dist. Z1 & Comilla: dist. Z2 relay | 0 | 0 | Tripped at both end
Rampura | Rampura-Bashundhara 132 kV line-1 | 2013-05-12 20:39 | 2013-05-12 20:45 | 0:06 | T | Tripped showing high impedence differencial relay | 0 | 0 | No Interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2013-05-16 09:56 | 2013-05-16 11:06 | 1:10 | E/O | Due to red hot maintenance at wave trap loop conector | 0 | 0 | No Interruption
Meghnaghat | Meghnaghat-Daudkandi 132 kV line-1 | 2013-05-16 14:10 | 2013-05-16 15:38 | 1:28 | T | Tripped showing O/C & E/F relay | 0 | 0 | No Interruption
Ullon | Ullon-Rampura 132 kV line-1 | 2013-05-16 23:44 | 2013-05-16 23:57 | 0:13 | T | Tripped showing dist. A-phase, Z3 relay | 0 | 0 | No Interruption
Haripur | Haripur-Matuail 132 kV line | 2013-05-18 22:09 | 2013-05-19 00:04 | 1:55 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Netrokona | Netrokona-Mymensingh 132 kV line-1 | 2013-05-20 12:29 | 2013-05-20 12:50 | 0:21 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
| Netrokona-Mymensingh 132 kV line-2 | 2013-05-20 12:29 | 2013-05-20 12:48 | 0:19 | T
Uttara | Uttara-Mirpur 132 kV line | 2013-05-23 07:05 | 2013-05-23 07:25 | 0:20 | T | Tripped and reclosed automatically | 0 | 0 | No Interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2013-05-23 18:50 | 2013-05-23 22:30 | 3:40 | T | Tripped showing main protection relay | 0 | 0 | No Interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2013-05-24 01:08 | 2013-05-24 01:15 | 0:07 | T | Tripped showing dist. Relay | 0 | 0 | No Interruption
Haripur | Haripur-Bhulta 132 kV line-1 | 2013-05-27 23:57 | 2013-05-28 18:33 | 18:36 | T | Tripped showing dist. Relay | 0 | 0 | No Interruption
Ghorasal | Ghorasal-Bhulta 132 kV line-2 | 2013-05-28 14:48 | 2013-05-28 15:13 | 0:25 | T | Tripped showing over current relay | 50 | 20.8333 | Power Interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-1 | 2013-05-29 19:06 | 2013-05-29 19:19 | 0:13 | T | Tripped showing O/C & dist. A phase relay | 0 | 0 | No Interruption
| Kishoreganj-Ashuganj 132 kV line-2 | 2013-05-29 19:06 | 2013-05-29 19:20 | 0:14 | T
Rampura | Rampura-Haripur 230 kV line-1 | 2013-05-30 12:47 | 2013-05-30 18:45 | 5:58 | T | Tripped showing dist B, Z1, SOFT relay | 0 | 0 | No Interruption
Bashundhara | Bashundhara-Rampura 132 kV line-1 | 2013-05-30 12:48 | 2013-05-30 13:48 | 1:00 | T | Tripped showing dist, Z1, CN, MPT relay | 0 | 0 | No Interruption
Tongi | Tongi-Bashudhara 132 kV line-1 | 2013-05-30 12:48 | 2013-05-30 13:03 | 0:15 | T | Tripped showing HS trip relay | 0 | 0 | No Interruption
Ghorasal | Ghorasal-Ashuganj 132 kV line-1 | 2013-05-31 11:55 | 2013-05-31 12:08 | 0:13 | T | Tripped showing dist. AB, prot. Relay | 0 | 0 | No Interruption
|  |  | Total : | 59:48 |  |  |  | 22.6667
Chittagong Grid Circle :
Dohazari | Dohazari-Coxbazar 132 kV line -1 | 2013-05-04 16:10 | 2013-05-04 17:09 | 0:59 | T | Tripped showing dist R, Z1 relay | 0 | 0 | No Interruption
| Dohazari-Coxbazar 132 kV line-2 | 2013-05-04 16:10 | 2013-05-04 16:50 | 0:40 | T | Tripped showing dist. ABC 3-phase, Z1 relay | 0 | 0 | No Interruption
Dohazari | Dohazari-Sikalbaha 132 kV line-2 | 2013-05-04 15:38 | 2013-05-04 17:04 | 1:26 | T | Tripped showing dist, Z1, Z2 & E/F relay | 0 | 0 | No Interruption
Hathazari | Hathazari-Feni 132 kV line-1 | 2013-05-07 09:49 | 2013-05-07 10:05 | 0:16 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Coxbazar | Coxbazar-Dohazari 132 kV line-2 | 2013-05-08 16:50 | 2013-05-08 17:58 | 1:08 | T | Tripped showing dist. ABC & Z1 relay | 0 | 0 | No Interruption
Kaptai | Kaptai-Madunaghat 132 kV line-1 | 2013-05-09 16:25 | 2013-05-09 17:55 | 1:30 | T | Kaptai: dist. Z1 & Madunaght: dist. C relay | 0 | 0 | Tripped at both end
Dohazari | Dohazari-Sikalbaha 132 kV line-1 | 2013-05-11 10:59 | 2013-05-11 11:11 | 0:12 | T | Dohazari: dist. RY phase & Sikalbaha: O/C relay | 0 | 0 | Tripped at both end
Khulsi | Khulsi-Bakulia 132 kV line-2 | 2013-05-16 13:05 | 2013-05-16 16:27 | 3:22 | T | Tripped showing O/C & E/F relay | 0 | 0 | No Interruption
Dohazari | Dohazari-Coxbazar 132 kV line-1 | 2013-05-25 01:35 | 2013-05-25 01:40 | 0:05 | T | Tripped showing dist. R-B Corona, Zone-2 & E/F relays. | 23 | 1.9167 | No Interruption
| Dohazari-Coxbazar 132 kV line-2 | 2013-05-25 01:35 | 2013-05-25 01:58 | 0:23 | T
|  |  | Total : | 10:01 |  |  |  | 1.9167
Comilla Grid Circle :
Sreemongal | Sreemongal-Fenchuganj 132 kV line-1 | 2013-05-01 22:20 | 2013-05-02 11:10 | 12:50 | T | Tripped showing dist. C & dist. 3-phase Z1 relay. | 0 | 0 | No Interruption
Feni | Feni-Hathazari 132 kV line-2 | 2013-05-04 08:26 | 2013-05-04 08:33 | 0:07 | T | Feni: dist. Z, B1 relay Hathazari: E/F, O/C (Y-phase) relay | 0 | 0 | Tripped at both end
Comilla (N) | Comilla (N)-Hathazari 230 kV line-1 | 2013-05-04 13:15 | 2013-05-04 13:40 | 0:25 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
|  | 2013-05-04 15:30 | 2013-05-04 16:07 | 0:37 | T
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2013-05-04 16:15 | 2013-05-04 17:22 | 1:07 | T | Tripped showing Gen. trip, DOC relay | 0 | 0 | No Interruption
|  | 2013-05-04 18:13 | 2013-05-04 20:22 | 2:09 | T
|  | 2013-05-06 05:01 | 2013-05-06 05:35 | 0:34 | T
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2013-05-06 06:06 | 2013-05-06 06:48 | 0:42 | T | Tripped showing auto reclose block relay | 0 | 0 | No Interruption
|  | 2013-05-06 08:07 | 2013-05-06 08:58 | 0:51 | T
|  | 2013-05-06 09:21 | 2013-05-06 23:32 | 14:11 | T
Ashuganj | Ashuganj-Comilla 230 kV line-2 | 2013-05-06 09:33 | 2013-05-06 10:28 | 0:55 | T | Tripped showing secondary protection & E/F relay | 0 | 0 | No Interruption
Chandpur | Chandpur-Chowmuhani 132 kV line-1 | 2013-05-06 13:13 | 2013-05-06 13:58 | 0:45 | T | Tripped showing dist relay. | 0 | 0 | No Interruption
Feni | Feni-Comilla(N) 132 kV line-2 | 2013-05-07 08:39 | 2013-05-07 17:20 | 8:41 | T | Tripped showing dist B,C, SOFT relay | 0 | 0 | No Interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2013-05-07 15:09 | 2013-05-07 16:02 | 0:53 | T | Tripped showing auto reclose block relay | 0 | 0 | No Interruption
Ashuganj | Ashuganj-Comilla (N) 230 kV line-2 | 2013-05-08 10:19 | 2013-05-08 11:44 | 1:25 | T | Tripped showing distance relay | 0 | 0 | No Interruption
| Ashuganj-Comilla (N) 230 kV line-1 | 2013-05-08 11:01 | 2013-05-08 12:28 | 1:27 | E/O | Due to removing kite | 0 | 0 | No Interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2013-05-09 19:31 | 2013-05-09 19:49 | 0:18 | T | Tripped showing dist. Z1 relay | 0 | 0 | No Interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV line-1 | 2013-05-11 02:50 | 2013-05-11 03:50 | 1:00 | T | Tripped showing dist. Relay | 0 | 0 | No Interruption
Feni | Feni-Hathazari 132 kV line-1&2 | 2013-05-20 11:10 | 2013-05-20 11:22 | 0:12 | T | Feni: dist. C, Z1 relay Hathazari: dist, BC, Z2, E/F relay | 0 | 0 | No Interruption
Ashuganj | Ashuganj-Serajgnaj 230 kV line-2 | 2013-05-23 05:52 | 2013-05-23 11:20 | 5:28 | T | Tripped showing ARC block relay | 0 | 0 | No Interruption
Feni | Feni-Hathazari 132 kV line-1 | 2013-05-27 12:50 | 2013-05-27 13:16 | 0:26 | E/O | Due to red hot maintenance work | 0 | 0 | No Interruption
Sylhet | Sylhet-Fenchugnaj 132 kV line-2 | 2013-05-29 20:30 | 2013-05-29 20:45 | 0:15 | T | Tripped showing dist. C phase relay | 0 | 0 | No Interruption
|  |  | Total | 55:18 | Hours |  |  | 0
Khulna Grid Circle :
Faridpur | Faridpur-Bheramara 132 kV line-2 | 2013-05-04 10:28 | 2013-05-04 16:12 | 5:44 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
| Barisal-Patuakhali 132 kV line | 2013-05-04 11:20 | 2013-05-04 12:16 | 0:56 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Barisal | Barisal-Bhandaria 132 kV line | 2013-05-05 09:39 | 2013-05-05 09:50 | 0:11 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
| Barisal-Patuakhali 132 kV line | 2013-05-05 09:39 | 2013-05-05 09:42 | 0:03 | T | Tripped due to voltage fluctuation | 0 | 0 | No Interruption
Faridpur | Faridpur-Madaripur 132 kV line-1 | 2013-05-06 14:35 | 2013-05-06 14:50 | 0:15 | T | Tripped showing dist. B,C relay | 0 | 0 | No Interruption
Goalpara | Goalpara-Bagerhat 132 kV line | 2013-05-14 09:56 | 2013-05-14 11:14 | 1:18 | E/O | Due to red hot maintenance | 45 | 58.5 | Power Interruption
Bheramara | Bheramara-Ishurdi 132 kV line-1 | 2013-05-17 12:55 | 2013-05-17 13:07 | 0:12 | T | Tripped showing CAR, CAS, CAT, CD, CE, Z2, Z3 relays
| Bheramara-Ishurdi 132 kV line-2 | 2013-05-17 12:55 | 2013-05-17 13:08 | 0:13 | T
| Bottail-Bheramara 132 kV line-2 | 2013-05-17 12:55 | 2013-05-17 13:15 | 0:20 | T | Tripped showing ABC, dist. Z1 relays
Bottail | Bottail-Jhenaidah 132 kV line-1 | 2013-05-17 12:55 | 2013-05-17 13:18 | 0:23 | T | Tripped but showing no signals
| Bottail-Jhenaidah 132 kV line-2 | 2013-05-17 12:55 | 2013-05-17 13:19 | 0:24 | T |  | 217 | 47.0167 | Power Interruption
Madaripur | Madaripur-Barisal 132 kV line-1 | 2013-05-17 12:55 | 2013-05-17 13:11 | 0:16 | T | Tripped showing dist. Z3 relay
Bhandaria | Bhandaria-Barisal 132 kV line | 2013-05-17 12:55 | 2013-05-17 13:17 | 0:22 | T | Tripped showing dist. O/C relay
Jessore | Jessore-Jhenaidah 132 kV line-1 | 2013-05-17 12:55 | 2013-05-17 13:21 | 0:26 | T | Tripped showing dist. Z2, Z3 relay
| Jessore-Jhenaidah 132 kV line-2 | 2013-05-17 12:55 | 2013-05-17 18:49 | 5:54 | T
Goalpara | Goalpara-Bagerhat 132 kV line | 2013-05-17 20:53 | 2013-05-17 21:05 | 0:12 | T | Tripped showing dist. Relay | 45 | 9 | Power Interruption
Bhandaria | Bhandaria-Bagerhat 132 kV line | 2013-05-18 00:22 | 2013-05-18 00:26 | 0:04 | T | Tripped showing dist. Z2 relay | 0 | 0 | No Interruption
Barisal | Barisal-Bhandaria 132 kV line | 2013-05-18 00:26 | 2013-05-18 00:30 | 0:04 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Khulna (S) | Khulna (S)-Gallamari 132 kV line-1 | 2013-05-24 18:07 | 2013-05-24 18:31 | 0:24 | T | Tripped showing main & backup protection & O/C relay | 0 | 0 | No Interruption
|  |  | Total | 17:41 | Hours |  |  | 114.5167
Bogra Grid Circle :
Rajshahi | Rajshahi-Chapai Nawabganj 132 kV line-1 | 2013-05-04 20:40 | 2013-05-04 21:35 | 0:55 | T | Tripped showing dist, SF6 lock out relay | 54 | 49.5 | Power Interruption
| Rajshahi-Chapai Nawabganj 132 kV line-2 | 2013-05-04 20:40 | 2013-05-04 23:20 | 2:40 | T | Tripped showing O/C & E/F relay
Bogra | Bogra-Palashbari 132 kV line-1&2 | 2013-05-12 10:36 | 2013-05-12 10:58 | 0:22 | T | Due to CT burst at Palashbari end | 0 | 0 | No Interruption
Rangpur | Rangpur-Palashbari 132 kV line-1&2 | 2013-05-12 10:36 | 2013-05-12 10:59 | 0:23 | T | Due to CT burst at Palashbari end | 0 | 0 | No Interruption
Serajganj | Serajganj-Baghabari 230 kV line-1 | 2013-05-13 11:27 | 2013-05-13 14:08 | 2:41 | E/O | Due to red hot maintenance work | 0 | 0 | No Interruption
Rajshahi | Rajshahi-Chapai Nawabganj 132 kV line-2 | 2013-05-13 20:20 | 2013-05-13 20:54 | 0:34 | T | Tripped showing E/F relay | 0 | 0 | No Interruption
Baghabari | Baghabari-Ishurdi 132 kV line-3 | 2013-05-13 22:39 | 2013-05-13 23:46 | 1:07 | T | Tripped showing dist. Z1 relay | 0 | 0 | No Interruption
Palashbari | Palashbari-Rangpur 132 kV line-1 | 2013-05-18 02:51 | 2013-05-18 03:20 | 0:29 | T | Tripped showing dist. C-phase relay | 0 | 0 | No Interruption
Rangpur | Rangpur-Saidpur 132 kV line-1 | 2013-05-27 11:24 | 2013-05-27 17:15 | 5:51 | T | Tripped showing dist. Relay | 0 | 0 | No Interruption
|  |  | Total : | 15:02 | Hours |  |  | 49.5
Others (DPDC+BPDB) :
| Ashuganj-Shahjibazar 132 kV line-3 | 2013-05-07 14:05 | 2013-05-07 15:17 | 1:12 | T
| Ashuganj-B.Baria 132 kV line-1 | 2013-05-07 14:05 | 2013-05-07 14:05 | 0:00 | T
Ashuganj | Ashuganj-B.Baria 132 kV line-2 | 2013-05-07 14:05 | 2013-05-07 15:08 | 1:03 | T | Tripped showing bus differential relay | 0 | 0 | No Interruption
| Ashuganj-Ghorasal 132 kV line-1 | 2013-05-07 14:05 | 2013-05-07 16:07 | 2:02 | T
| Ashuganj-Ghorasal 132 kV line-2 | 2013-05-07 14:05 | 2013-05-07 15:14 | 1:09 | T
| Ashuganj-Kishoreganj 132 kV line | 2013-05-07 14:05 | 2013-05-07 16:26 | 2:21 | T
Matuail | Matuail-Haripur 132 kV line | 2013-05-08 16:24 | 2013-05-08 17:58 | 1:34 | T | Tripped showing dist. C & E/F relay | 21 | 32.9 | Power Interruption
Maniknagar | Maniknagar-Haripur 132 kV line-2 | 2013-05-08 16:28 | 2013-05-08 16:32 | 0:04 | T | Tripped showing O/C & E/F relay | 60 | 4 | Power Interruption
Haripur | Haripur-Matuail 132 kV line | 2013-05-09 21:18 | 2013-05-09 22:10 | 0:52 | E/O | Due to red hot maintenance | 0 | 0 | No Interruption
Madanganj | Madanganj-Munshiganj 132 kV line-1 | 2013-05-23 07:43 | 2013-05-23 09:35 | 1:52 | T | Tripped showing differential relay | 0 | 0 | No Interruption
|  |  |  | 12:09 | Hours |  |  | 36.9
Total outage period of Transmission Lines : |  |  |  | 169:59 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/1 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2013
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :
Hasnabad | 132 kV main bus | 2013-05-11 05:30 | 2013-05-11 18:00 | 12:30 | S/O | Due to project work | 0 | 0 | No Interruption
Haripur | 132/33 kV REB Transformer | 2013-05-27 12:13 | 2013-05-27 13:05 | 0:52 | S/O | Due to maintenance work | 0 | 0 | No Interruption
Netrokona | 132/33 kV Transformer T1 | 2013-05-31 09:40 | 2013-05-31 10:30 | 0:50 | S/O | Due to oil filling | 0 | 0 | No Interruption
|  |  | Total : | 14:12 |  | unserved energy : |  | 0
Chittagong Grid Circle : Nil
|  |  | Total | 0:00 |  | unserved energy : |  | 0
Comilla Grid Circle :
Daudkandi | 132/33 kV Transformer T2 | 2013-05-07 15:10 | 2013-05-07 16:18 | 1:08 | S/O | Due to turn loop maintenance work | 0 | 0 | No Interruption
|  |  | Total | 1:08 |  | unserved energy : |  | 0
Khulna Grid Circle :
Madaripur | 132/33 kV Transformer T3 | 2013-05-17 10:25 | 2013-05-17 12:24 | 1:59 | S/O | Due to jumper maintenance work | 0 | 0 | No Interruption
Khulna ( C ) | 132/33 kV Transformer T1 | 2013-05-25 08:36 | 2013-05-25 12:46 | 4:10 | S/O | Due to TEI project work | 0 | 0 | No Interruption
Faridpur | 132/33 kV Transformer T1 | 2013-05-30 09:30 | 2013-05-30 14:10 | 4:40 | S/O | Due to E/F & Lock out relay | 0 | 0 | No Interruption
|  |  | Total : | 10:49 |  | unserved energy : |  | 0
Bogra Grid Circle:
Barapukuria | 132/33 kV Transformer T4 | 2013-05-31 12:20 | 2013-05-31 12:57 | 0:37 | S/O | Due to repairment of broken earth ware | 0 | 0 | No Interruption
|  |  | Total | 0:37 |  | unserved energy : |  | 0
Others (BPDB + DPDC) :
Bhulta | 132/33 kV Transformer T2 | 2013-05-25 13:00 | 2013-05-25 16:28 | 3:28 | S/O | Due to TEI project work | 0 | 0 | No Interruption
| 132/33 kV Transformer T1 | 2013-05-25 08:06 | 2013-05-25 12:02 | 3:56 | S/O | Due to project work | 30 | 118 | Power Interruption
|  |  | Total | 7:24 |  | unserved energy : |  | 118
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 34:10 | Hours
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/1 | [8 empty] | QF-LDC-26
Power Grid company of Bangladesh LTD.
|  | Efficiency Divn. LDC, Dhaka | Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to scheduled maintenance/project work
Month: May 2013
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka Grid Circle :
Madanganj | Madanganj-Bashundhara Cement Factory 132 kV line | 2013-05-01 12:05 | 2013-05-01 12:51 | 0:46 | S/O | Due to project work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar-Ullon 132 kV line-1 | 2013-05-10 06:12 | 2013-05-10 07:16 | 1:04 | S/O | Due to project work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar-Ullon 132 kV line-2 | 2013-05-11 13:31 | 2013-05-11 16:05 | 2:34 | S/O | Due to project work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV line-2 | 2013-05-12 14:46 | 2013-05-13 14:42 | 23:56 | S/O | Due to tight the R- phase isolator loop | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2013-05-17 08:15 | 2013-05-17 16:51 | 8:36 | S/O | Due to cable insulation maintenance work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2013-05-19 09:37 | 2013-05-19 21:20 | 11:43 | S/O | Due to provide safety for maintenance | 0 | 0 | No interruption
| Siddhirganj-Ullon 132 kV line-1 | 2013-05-21 08:46 | 2013-05-21 22:45 | 13:59 | S/O | Due to project work | 0 | 0 | No interruption
Ullon | Ullon-Siddhirganj 132 kV line-1 | 2013-05-23 09:03 | 2013-05-23 22:28 | 13:25 | S/O | Due to project work | 0 | 0 | No interruption
| Ullon-Siddhirganj 132 kV line-1 | 2013-05-25 06:10 | 2013-05-25 18:05 | 11:55 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Shyampur 132 kV line | 2013-05-25 06:12 | 2013-05-25 10:59 | 4:47 | S/O | Due to project work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matuail 132 kV line | 2013-05-25 06:45 | 2013-05-25 10:16 | 3:31 | S/O | Due to project work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Tongi 132 kV line-2 | 2013-05-25 11:45 | 2013-05-25 17:11 | 5:26 | S/O | Due to maintenance work | 30 | 163 | Power Interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2013-05-30 07:36 | 2013-05-30 08:15 | 0:39 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total | 102:21 |  | unserved energy : |  | 163
Chittagong Grid Circle :
Kaptai | Kaptai-Chandroghona 132 kV line-2 | 2013-05-12 16:12 | 2013-05-12 17:06 | 0:54 | S/O | Due to gas filling in 132 kV breaker | 0 | 0 | No Interruption
Halishahar | Halishahar-Khulsi 132 kV line-2 | 2013-05-19 10:15 | 2013-05-19 13:09 | 2:54 | S/O | Due to maintenance work | 0 | 0 | No Interruption
Khulsi | Khulsi-Madunaghat 132 kV line-1 | 2013-05-29 12:10 | 2013-05-29 15:08 | 2:58 | S/O | Due to maintenance work | 0 | 0 | No Interruption
|  |  | Total | 6:46 |  | unserved energy : |  | 0
Comilla Grid Circle :
Feni | Feni-Hathazari 132 kV line-2 | 2013-05-20 14:54 | 2013-05-20 19:22 | 4:28 | S/O | Due to right of way | 0 | 0 | No Interruption
Comilla (N) | Comilla (N)-Meghnaghat 230 kV line-1 | 2013-05-22 17:02 | 2013-05-22 17:32 | 0:30 | S/O | Due to removal of nest from the structure | 0 | 0 | No Interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line-1 | 2013-05-27 23:46 | 2013-05-28 01:40 | 1:54 | S/O | Due to maintenance work | 0 | 0 | No Interruption
|  |  | Total | 6:52 |  | unserved energy : |  | 0
Khulna Grid Circle :
Jhenaidah | Jhanaidah-Bottail 132 kV line-1 | 2013-05-01 08:04 | 2013-05-01 13:35 | 5:31 | S/O | Due to oil leakage maintenance | 0 | 0 | No Interruption
Khulna ( C ) | Khulna ( C )-Noapara 132 kV line-2 | 2013-05-25 08:34 | 2013-05-25 13:07 | 4:33 | S/O | Due to project work | 0 | 0 | No Interruption
| Khulna ( C )-Khulna (S) 132 kV line | 2013-05-25 08:32 | 2013-05-25 13:21 | 4:49 | S/O | Due to project work | 0 | 0 | No Interruption
|  |  | Total | 14:53 |  | unserved energy : |  | 0
Bogra Grid Circle :
Shahjadpur | Shahjadpur-Baghabari 132 kV line | 2013-05-09 09:50 | 2013-05-09 16:10 | 6:20 | S/O | Due to maintenance work of PT | 0 | 0 | No Interruption
Natore | Natore-Bogra 132 kV line-2 | 2013-05-10 08:24 | 2013-05-10 13:15 | 4:51 | S/O | Due to replacement of B-phase CVT | 0 | 0 | No Interruption
Rajshahi | Rajshahi-Chapai Nawabganj 132 kV line-1 | 2013-05-11 10:05 | 2013-05-11 11:58 | 1:53 | S/O | Due to tight the jumper joint point | 0 | 0 | No Interruption
Purbasadipur | Purbasadipur-Saidpur 132 kV line-1 | 2013-05-12 09:54 | 2013-05-12 10:10 | 0:16 | S/O | Due to right the way of Ximission line | 0 | 0 | No Interruption
Ishurdi | Ishurdi-Ghorasal 230 kV line-2 | 2013-05-21 11:58 | 2013-05-21 16:47 | 4:49 | S/O | Due to connect open wave trape loop | 0 | 0 | No Interruption
|  |  | Total | 18:09 |  | unserved energy : |  | 0
Others (DPDC+BPDB) :
| Ashuganj-Sirajganj 230 kV line-1 | 2013-05-22 10:35 | 2013-05-22 11:00 | 0:25 | S/O | Due to maintenance of bus isolator | 0 | 0 | No Interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2013-05-24 21:10 | 2013-05-25 14:53 | 17:43 | S/O | Due to breaker maintenance work | 0 | 0 | No Interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2013-05-25 08:40 | 2013-05-25 14:53 | 6:13 | S/O | Due to breaker maintenance work | 0 | 0 | No Interruption
Matuail | Matuail-Maniknagar 132 kV line | 2013-05-31 06:16 | 2013-05-31 17:20 | 11:04 | S/O | Due to project work | 0 | 0 | No Interruption
|  |  | Total | 35:25 |  | unserved energy : |  | 0
Total outage period of Transmission Lines due to schedule
maintenance: |  |  |  | 184:26 | Hours |  |  | Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | POWER GRID COMPANY OF BANGLADESH LTD. | [7 empty] | QF-LDC-27
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month: May 2013
| Area | Previous Month (April 2013) |  |  |  | Current Month (May 2013)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka grid circle. | 19 | 6 | 31 | 56 | 36 | 12 | 16 | 64
2 | Chittagong grid circle. | 6 | 0 | 23 | 29 | 11 | 1 | 3 | 15
3 | Comilla grid circle. | 13 | 0 | 0 | 13 | 32 | 5 | 4 | 41
4 | Khulna grid circle. | 6 | 3 | 8 | 17 | 24 | 4 | 6 | 34
5 | Bogra grid circle. | 5 | 2 | 0 | 7 | 15 | 8 | 6 | 29
6 | Others (BPDB+DPDC). | 6 | 2 | 12 | 20 | 13 | 1 | 6 | 20
| Total | 55 | 13 | 74 | 142 | 131 | 31 | 41 | 203
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | POWER GRID COMPANY OF BANGLADESH LTD. | [7 empty] | QF-LDC-28
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: May 2013
| Area | Previous Month (April 2013) |  |  |  | Current Month (May 2013)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka grid circle. | 626.71 | 0 | 12.67 | 639.38 | 222.17 | 36.1 | 163 | 421.27
2 | Chittagong grid circle. | 1.4 | 0 | 0 | 1.4 | 1.92 | 0 | 0 | 1.92
3 | Comilla grid circle. | 160.43 | 0 | 0 | 160.43 | 35.5 | 24.4 | 0 | 59.9
4 | Khulna grid circle. | 18.7 | 0 | 0 | 18.7 | 80.57 | 58.5 | 0 | 139.07
5 | Bogra grid circle. | 0 | 105 | 0 | 105 | 60.57 | 54.75 | 0 | 115.32
6 | Others | 0 | 0 | 0 | 0 | 36.9 | 0 | 118 | 154.9
| Total | 807.24 | 105 | 12.67 | 924.91 | 437.63 | 173.75 | 281 | 892.38
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
|  | POWER GRID COMPANY OF BANGLADESH LTD. | [7 empty] | QF-LDC-29
|  |  | Information Management Division, LDC, Dhaka. | [6 empty] | page 1 of 1
Consolidated Statement of Sub-Station performance
Month: May 2013
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka | 6998 | 4 | - | 4 | 1 | 1 | 2 | 235.6
2 | Chittagong | 1814 | - | - | - | - | - | - | -
3 | Khulna | 2117 | 3 | - | 3 | 2 | 1 | - | 24.55
4 | Bogra | 3481 | 5 | - | 5 | 2 | 1 | 2 | 30.65
5 | Comilla | 1861 | 7 | - | 7 | 4 | 3 | - | 59.9
| Total | 16271 | [6 empty] | 350.7
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka | 99.92% | [6 empty] | Manager
2 | Chittagong | 99.99% | [6 empty] | Information Management Division
3 | Khulna | 99.94% | [6 empty] | LDC, PGCB, Dhaka.
4 | Bogra | 99.97%
5 | Comilla | 99.99%

## QF-LDC-30
|  | POWER GRID COMPANY OF BANGLADESH LTD. | [8 empty] | QF-LDC-30
|  |  | Information Management Division, LDC, Dhaka. | [7 empty] | page 1 of 1
Consolidated Statement of Transmission line's performance
Month: May 2013
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka | 2324.85 | 54+15(Partial) | 2 | 1 | - | 2 | - | 1 | 185
2 | Chittagong | 916.2 | 20+9(Partial) | 1 | - | - | - | - | - | 1.92
3 | Khulna | 1351.94 | 21 | 3 | - | - | - | - | - | 114.52
4 | Bogra | 2565.81 | 38 | 1 | - | - | - | - | - | 49.5
5 | Comilla | 1688.45 | 17 | - | - | - | - | - | - | -
| Total | 8847.25 | 150+24(Partial) | [6 empty] | 350.94
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3 | [7 empty] | Manager
1 | Dhaka | 99.87% | [7 empty] | Information Management Division
2 | Chittagong | 99.94% | [7 empty] | LDC, PGCB, Dhaka.
3 | Khulna | 99.6%
4 | Bogra | 99.89%
5 | Comilla | 99.97%

## QF-LDC-31
|  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-31
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month: May 2013
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | X- Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2013-05-01 | 10 | 01/40 | - | - | - | - | - | - | 1 | 00/13 | - | -
Note:-If U/F operates due to tripping of a generator is accounted in the category "Trouble in Generation System ".
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month: May 2013
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishorganj | 1 | 0:14 | 5 | 0.83 | Due to Emergency Outage of Transformer T3
Mymensingh | 1 | 0:37 | 28 | 17.2667 | Due to Emergency Outage of Transformer T1
Mymensingh | 1 | 0:10 | 11 | 1.83 | Due to Tripping of Mymensingh-Netrokona 132 kV lines 1 & 2
Jamalpur | 1 | 2:15 | 8 | 18 | Due to Emergency Outage of Transformer T3
Tongi | 1 | 5:42 | 35 | 199.5 | Due to Tripping of Transformer T1 & T3
Ghorasal | 1 | 5:26 | 30 | 163 | Due to Schedule Outage of Ghorasal-Tongi 132 kV line-2
| 1 | 0:25 | 50 | 20.83 | Due to Tripping of Ghorasal-Bhulta 132 kV line-2
Dohazari | 1 | 0:05 | 23 | 1.92 | Due to Tripping of Dohazari-coxbazar 132 kV line-1&2
B.Baria | 1 | 0:47 | 22 | 17.2333 | Due to Tripping of Transformer T1
Chattak | 1 | 0:20 | 5 | 1.6667 | Due to Tripping of Transformer T1
Chandpur | 1 | 0:09 | 48 | 7.2 | Due to Tripping of Transformer T1 & T2
Chandpur | 2 | 1:17 | 38 | 24.4 | Due to Emergency Outage of Transformer T1
Daudkandi | 1 | 0:10 | 10 | 1.67 | Due to Tripping of Transformer T2
Feni | 1 | 0:29 | 16 | 7.73 | Due to Tripping of Transformer T1
Mongla | 1 | 0:43 | 24 | 17.2 | Due to Tripping of Transformer T1
Khulna ( C ) | 1 | 0:12 | 21 | 3.15 | Due to Tripping of Transformer T1, T2 & T3
Jhenaidah | 1 | 0:09 | 28 | 4.2 | Due to Tripping of Transformer of T1 & T2
Goalpara | 2 | 1:30 | 45 | 67.5 | Due to E/O of Goalpara-Bagerhat 132 kV line
Bheramara | 1 | 0:13 | 217 | 47.02 | Due to Tripping of Bheramara-Ishurdi 132 kV line-1 & 2
Jessore | 1 |  |  |  | Due to Tripping of Jessore-Jhenaidah 132 kV line-1 & 2
Rajshahi | 1 | 0:10 | 20 | 3.33 | Due to Emergency Outage of Transformer T1
|  | 0:55 | 54 | 49.5 | Due to Trippiing of Rajshahi-Chapainawabganj 132 kV line-1 & 2
Natore | 1 | 0:25 | 3 | 1.25 | Due to Emergency Outage of Transformer T3
| 1 | 0:36 | 25 | 15 | Due to Emergency Outage of Transformer T1
Pabna | 1 | 3:31 | 10 | 35.17 | Due to Emergency Outage of Transformer T1
Ishurdi | 1 | 1:23 | 8 | 11.07 | Due to Tripping of Transformer T2
Bhulta | 1 | 3:56 | 30 | 118 | Due to Schedule Outage of Transformer T1
Matuail | 1 | 1:34 | 21 | 32.9 | Due to Tripping of Matuail-Haripur 132 kV line
Maniknagar | 1 | 0:04 | 60 | 4 | Due to Tripping of Maniknagar-Haripur 132 kV line-2
| Total unserved energy : |  |  | 892.3667 | MWH
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: May 2013
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 106 | 2 | May' 13 | 10:00
2 | Munshiganj | 52 | 2 | May' 13 | 22:00
3 | Meghnaghat | 65 | 2 | May' 13 | 20:00
4 | Shyampur | 115 | 20 | May' 13 | 9:00
5 | Bhulta | 140 | 26 | May' 13 | 21:00
6 | Madanganj | 128 | 29 | May' 13 | 21:00
7 | Shitalakhya | 87 | 22 | May' 13 | 11:00
8 | Rahim steel Mill | 10 | 21 | May' 13 | 9:00
9 | Matuail | 33.8 | 2 | May' 13 | 24:0
10 | Ghorashal | 48 | 9 | May' 13 | 21:00
11 | Narsingdi | 62 | 13 | May' 13 | 21:00
12 | Ullon | 105 | 11 | May' 13 | 15:00
13 | Hasnabad | 134 | 1 | May' 13 | 19:00
14 | Magbazar | 127 | 24 | May' 13 | 18:00
15 | Maniknagar | 120 | 21 | May' 13 | 1:00
16 | Bangabhaban | 49 | 29 | May' 13 | 8:00
17 | Narinda | 90 | 15 | May' 13 | 13:00
18 | Dhanmondi | 101 | 2 | May' 13 | 20:00
19 | Mirpur | 136.5 | 2 | May' 13 | 19:00
20 | Kallyanpur | 159 | 11 | May' 13 | 19:00
21 | Gulshan | 128 | 2 | May' 13 | 1:00
22 | Uttara | 87.2 | 2 | May' 13 | 19:00
23 | Kamrangirchar | 97 | 10 | May' 13 | 19:30
24 | Savar | 64 | 26 | May' 13 | 20:00
25 | Tongi | 654 | 14 | May' 13 | 20:00
26 | Kabirpur | 195 | 30 | May' 13 | 8:00
27 | Bashundhara | 122 | 2 | May' 13 | 15:00
28 | Manikganj | 86 | 5 | May' 13 | 20:00
29 | Joydevpur | 145 | 5 | May' 13 | 22:00
30 | New Tongi | 88 | 30 | May' 13 | 19:30
31 | Tangail | 109 | 15 | May' 13 | 19:30
32 | Mymensingh | 119 | 17 | May' 13 | 19:30
33 | Kishorganj | 46 | 1 | May' 13 | 19:00
34 | Netrakona | 42 | 2 | May' 13 | 19:30
35 | Jamalpur | 91 | 15 | May' 13 | 21:00
36 | Srimongal | 34 | 14 | May' 13 | 21:00
37 | Shahjibazar | 42 | 22 | May' 13 | 19:00
38 | Fenchuganj | 45 | 15 | May' 13 | 19:30
39 | Sylhet | 136 | 25 | May' 13 | 20:00
40 | Chatak | 126 | 6 | May' 13 | 19:00
41 | B.Baria | 138 | 6 | May' 13 | 20:00
42 | Comilla(S) | 141 | 1 | May' 13 | 19:00
43 | Comilla(N) | 26 | 17 | May' 13 | 20:00
44 | Chandpur | 55 | 11 | May' 13 | 21:00
45 | Feni | 70 | 1 | May' 13 | 21:00
46 | Chowmuhani | 100 | 1 | May' 13 | 19:00
47 | Ashuganj | 50 | 12 | May' 13 | 20:00
48 | Daudkandi | 57 | 15 | May' 13 | 19:30
49 | Madanhat | 48.9 | 15 | May' 13 | 17:00
50 | Hathazari | 48 | 1 | May' 13 | 4:00
51 | Khulshi | 138 | 15 | May' 13 | 14:00
52 | Halishahar | 137 | 18 | May' 13 | 19:30
53 | Baraulia | 68 | 8 | May' 13 | 1:00
54 | Sikalbaha | 54 | 27 | May' 13 | 20:00
55 | Dohazari | 58 | 2 | May' 13 | 19:00
56 | Cox'sBazar | 50 | 2 | May' 13 | 20:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: MARCH 2013
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
57 | Chandraghona | 23.6 | 17 | May' 13 | 20:00
58 | Kaptai | 5 | 12 | May' 13 | 18:30
59 | A. Khayer Steel Mill | 16.1 | 21 | May' 13 | 9:00
60 | Bakulia | 89 | 19 | May' 13 | 20:00
61 | Julda | 20 | 19 | May' 13 | 10:00
62 | TK chemical | 12.8 | 8 | May' 13 | 13:00
63 | Modern Steal | 16 | 2 | May' 13 | 13:00
64 | Goalpara | 39 | 19 | May' 13 | 19:30
65 | Khulna Central | 77 | 25 | May' 13 | 19:30
66 | Noapara | 46 | 26 | May' 13 | 20:00
67 | Jessore | 110 | 9 | May' 13 | 20:00
68 | Jhenidah | 58 | 3 | May' 13 | 21:00
69 | Bottail | 69 | 9 | May' 13 | 21:00
70 | Bheramara | 36 | 25 | May' 13 | 21:00
71 | Faridpur | 77 | 11 | May' 13 | 19:00
72 | Madaripur | 71 | 10 | May' 13 | 20:00
73 | Gopalganj | 130 | 12 | May' 13 | 18:30
74 | Bagerhat | 135 | 12 | May' 13 | 18:30
75 | Mongla | 28 | 2 | May' 13 | 10:00
76 | Satkhira | 43 | 25 | May' 13 | 19:30
77 | Gallamari | 32 | 8 | May' 13 | 21:00
78 | Magura | 24 | 1 | May' 13 | 19:00
79 | Chuadanga | 43 | 20 | May' 13 | 19:30
80 | Barisal | 78 | 14 | May' 13 | 19:30
81 | Patuakhali | 50 | 27 | May' 13 | 19:00
82 | Bhandaria | 26 | 12 | May' 13 | 19:00
83 | Ishurdi | 38 | 8 | May' 13 | 21:00
84 | Natore | 67 | 1 | May' 13 | 20:00
85 | Bogra | 156 | 2 | May' 13 | 21:00
86 | Naogaon | 83 | 2 | May' 13 | 19:30
87 | Rajshahi | 90 | 13 | May' 13 | 19:30
88 | C.Nawabganj | 70 | 2 | May' 13 | 21:00
89 | Pabna | 63 | 2 | May' 13 | 20:00
90 | Shahjadpur | 56 | 3 | May' 13 | 2:00
91 | Serajganj | 57 | 15 | May' 13 | 20:00
92 | Niyamatpur | 61 | 2 | May' 13 | 20:00
93 | Joypurhat | 16 | 2 | May' 13 | 20:00
94 | Rangpur | 78 | 18 | May' 13 | 20:00
95 | Lalmonirhat | 44 | 25 | May' 13 | 20:00
96 | Saidpur | 63 | 3 | May' 13 | 19:00
97 | Purbasadipur | 56 | 1 | May' 13 | 20:00
98 | Thakurgaon | 55 | 25 | May' 13 | 21:00
99 | Palashbari | 77 | 25 | May' 13 | 20:00
100 | Barapukuria | 27 | 22 | May' 13 | 19:00
101 | Panchagar | 15 | 4 | May' 13 | 21:00
Manager
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: May 2013
Area | MW | Date | Hour | Remarks
Dhaka | 2322 | 02.05.2013 | 16:00
Chittagong | 597 | 26.05.2013 | 21:00
Khulna | 711 | 03.05.2013 | 21:00
Rajshahi | 717 | 02.05.2013 | 21:00
Comilla | 466 | 02.05.2013 | 22:00
Mymensingh | 391 | 15.05.2013 | 21:00
Sylhet | 315 | 25.05.2013 | 19:00
Barisal | 144 | 14.05.2013 | 19:00
Rangpur | 362 | 25.05.2013 | 21:00
Manager
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May 2013
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Hathazari | 230 | 216 | 16 | May' 13 | 13:00 | 209 | 31 | May' 13 | 18:00
2 | Comilla(N) | 230 | 222 | 17 | May' 13 | 8:00 | 215 | 14 | May' 13 | 11:00
3 | Ashuganj | 230 | 224 | 17 | May' 13 | 9:00 | 202 | 21 | May' 13 | 1:00
4 | Ghorashal | 230 | 220 | 24 | May' 13 | 19:00 | 200 | 4 | May' 13 | 17:00
5 | Rampura | 230 | 222 | 18 | May' 13 | 21:00 | 198 | 2 | May' 13 | 11:00
6 | Tongi | 230 | 220 | 25 | May' 13 | 23:00 | 190 | 2 | May' 13 | 11:00
7 | Aminbazar | 230 | 213 | 23 | May' 13 | 8:00 | 191 | 4 | May' 13 | 17:00
8 | Hasnabad | 230 | 222 | 17 | May' 13 | 8:00 | 200 | 4 | May' 13 | 18:00
9 | Magnaghat | 230 | 218 | 17 | May' 13 | 5:00 | 200 | 2 | May' 13 | 10:00
10 | Haripur | 230 | 214 | 17 | May' 13 | 9:00 | 200 | 2 | May' 13 | 10:00
11 | Ishurdi | 230 | 220 | 21 | May' 13 | 21:00 | 196 | 4 | May' 13 | 16:00
12 | Baghabari | 230 | 224 | 21 | May' 13 | 13:00 | 196 | 4 | May' 13 | 16:00
13 | Serajganj | 230 | 218 | 7 | May' 13 | 2:00 | 200 | 4 | May' 13 | 17:00
14 | Bogra | 230 | 223 | 6 | May' 13 | 10:00 | 201 | 16 | May' 13 | 20:00
15 | Barapukuria | 230 | 230 | 7 | May' 13 | 1:00 | 216 | 9 | May' 13 | 19:30
16 | Khulna (South) | 230 | 224 | 19 | May' 13 | 9:00 | 197 | 16 | May' 13 | 15:00
132 kV Substation
1 | Shiddhirganj | 132 | 134 | 23 | May' 13 | 9:00 | 116 | 4 | May' 13 | 16:00
2 | Munshiganj | 132 | 131 | 1 | May' 13 | 19:00 | 116 | 31 | May' 13 | 1:00
3 | Meghnaghat | 132 | 131 | 8 | May' 13 | 20:00 | 115 | 4 | May' 13 | 17:00
4 | Shyampur | 132 | 134 | 23 | May' 13 | 9:00 | 110 | 11 | May' 13 | 11:00
5 | Bhulta | 132 | 123 | 1 | May' 13 | 19:00 | 107 | 14 | May' 13 | 12:00
6 | Madanganj | 132 | 132 | 23 | May' 13 | 8:00 | 116 | 14 | May' 13 | 10:00
7 | Shitalakhya | 132 | 133 | 23 | May' 13 | 9:00 | 117 | 4 | May' 13 | 16:00
8 | Rahim steel | 132 | 132 | 1 | May' 13 | 19:00 | 118 | 14 | May' 13 | 11:00
9 | Matuail | 132 | 131 | 23 | May' 13 | 8:00 | 115 | 14 | May' 13 | 12:00
10 | Ghorashal | 132 | 135 | 11 | May' 13 | 21:00 | 122 | 2 | May' 13 | 11:00
11 | Narsinghdi | 132 | 132 | 24 | May' 13 | 17:00 | 117 | 12 | May' 13 | 11:00
12 | Ullon | 132 | 133 | 25 | May' 13 | 1:00 | 114 | 14 | May' 13 | 12:00
13 | Hasnabad | 132 | 133 | 23 | May' 13 | 10:00 | 116 | 11 | May' 13 | 17:00
14 | Magbazar | 132 | 134 | 17 | May' 13 | 8:00 | 115 | 4 | May' 13 | 16:00
15 | Maniknagar | 132 | 132 | 10 | May' 13 | 19:00 | 115 | 4 | May' 13 | 16:00
16 | Bangabhaban | 132 | 132 | 10 | May' 13 | 19:00 | 115 | 4 | May' 13 | 16:00
17 | Narinda | 132 | 132 | 10 | May' 13 | 19:00 | 115 | 4 | May' 13 | 16:00
18 | Dhanmondi | 132 | 133 | 26 | May' 13 | 6:00 | 115 | 4 | May' 13 | 16:00
19 | Mirpur | 132 | 133 | 17 | May' 13 | 3:00 | 115 | 4 | May' 13 | 10:00
20 | Kallyanpur | 132 | 135 | 17 | May' 13 | 6:00 | 120 | 11 | May' 13 | 12:00
21 | Gulshan | 132 | 134 | 17 | May' 13 | 6:00 | 115 | 2 | May' 13 | 12:00
22 | Uttara | 132 | 130 | 23 | May' 13 | 8:00 | 110 | 2 | May' 13 | 11:00
23 | Kamrangirchar | 132 | 132 | 11 | May' 13 | 21:00 | 114 | 11 | May' 13 | 12:00
24 | Savar | 132 | 133 | 23 | May' 13 | 8:00 | 118 | 4 | May' 13 | 1:00
25 | Tongi | 132 | 136 | 23 | May' 13 | 8:00 | 24 | 18 | May' 13 | 19:00
26 | Kabirpur | 132 | 128 | 23 | May' 13 | 8:00 | 112 | 2 | May' 13 | 11:00
27 | Bashundhara | 132 | 129 | 23 | May' 13 | 9:00 | 106 | 12 | May' 13 | 16:00
28 | Manikganj | 132 | 133 | 23 | May' 13 | 8:00 | 112 | 2 | May' 13 | 10:00
29 | Joydevpur | 132 | 135 | 11 | May' 13 | 22:00 | 117 | 4 | May' 13 | 8:00
30 | New Tongi | 132 | 132 | 11 | May' 13 | 21:00 | 114 | 2 | May' 13 | 12:00
31 | Tangail | 132 | 132 | 11 | May' 13 | 21:00 | 109 | 2 | May' 13 | 11:00
32 | Mymensingh | 132 | 133 | 1 | May' 13 | 24:00 | 117 | 26 | May' 13 | 23:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May 2013
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
33 | Kishorganj | 132 | 135 | 14 | May' 13 | 1:00 | 122 | 26 | May' 13 | 23:00
34 | Netrakona | 132 | 139 | 10 | May' 13 | 7:00 | 116 | 25 | May' 13 | 21:00
35 | Jamalpur | 132 | 132 | 14 | May' 13 | 1:00 | 114 | 25 | May' 13 | 19:30
36 | Srimongal | 132 | 142 | 10 | May' 13 | 24:00 | 134 | 5 | May' 13 | 12:00
37 | Shahjibazar | 132 | 144 | 6 | May' 13 | 10:00 | 135 | 5 | May' 13 | 12:00
38 | Fenchuganj | 132 | 143 | 25 | May' 13 | 1:00 | 132 | 13 | May' 13 | 8:00
39 | Sylhet | 132 | 140 | 4 | May' 13 | 5:00 | 129 | 13 | May' 13 | 8:00
40 | Chatak | 132 | 139 | 10 | May' 13 | 24:00 | 129 | 4 | May' 13 | 19:00
41 | B.Baria | 132 | 138 | 6 | May' 13 | 10:00 | 129 | 31 | May' 13 | 11:00
42 | Comilla(S) | 132 | 133 | 16 | May' 13 | 7:00 | 125 | 6 | May' 13 | 10:00
43 | Comilla(N) | 132 | 135 | 30 | May' 13 | 1:00 | 126 | 8 | May' 13 | 15:00
44 | Chandpur | 132 | 138 | 16 | May' 13 | 9:00 | 120 | 8 | May' 13 | 15:00
45 | Feni | 132 | 127 | 16 | May' 13 | 14:00 | 118 | 6 | May' 13 | 10:00
46 | Chowmuhani | 132 | 132 | 4 | May' 13 | 14:00 | 119 | 6 | May' 13 | 10:00
47 | Ashuganj | 132 | 144 | 24 | May' 13 | 17:00 | 114 | 21 | May' 13 | 16:00
48 | Daudkandi | 132 | 133 | 10 | May' 13 | 19:00 | 122 | 31 | May' 13 | 10:00
49 | Madanhat | 132 | 134 | 1 | May' 13 | 19:00 | 122 | 23 | May' 13 | 9:00
50 | Hathazari | 132 | 131 | 1 | May' 13 | 19:00 | 120 | 14 | May' 13 | 7:00
51 | Khulshi | 132 | 134 | 4 | May' 13 | 16:00 | 121 | 25 | May' 13 | 10:00
52 | Halishahar | 132 | 130 | 4 | May' 13 | 16:00 | 118 | 9 | May' 13 | 9:00
53 | Baraulia | 132 | 132 | 16 | May' 13 | 14:00 | 119 | 18 | May' 13 | 12:00
54 | Sikalbaha | 132 | 130 | 1 | May' 13 | 19:00 | 116 | 9 | May' 13 | 10:00
55 | Dohazari | 132 | 130 | 24 | May' 13 | 19:30 | 115 | 23 | May' 13 | 9:00
56 | Cox'sBazar | 132 | 131 | 1 | May' 13 | 19:00 | 118 | 1 | May' 13 | 2:00
57 | Chandraghona | 132 | 135 | 16 | May' 13 | 13:00 | 118 | 20 | May' 13 | 11:00
58 | Kaptai | 132 | 132 | 4 | May' 13 | 19:30 | 118 | 23 | May' 13 | 9:00
59 | A. Khayer Steel Mill | 132 | 132 | 5 | May' 13 | 21:00 | 119 | 23 | May' 13 | 9:00
60 | Bakulia | 132 | 128 | 1 | May' 13 | 20:00 | 115 | 23 | May' 13 | 9:00
61 | Julda | 132 | 131 | 4 | May' 13 | 16:00 | 115 | 9 | May' 13 | 10:00
62 | TK Chemical | 132 | 133 | 16 | May' 13 | 14:00 | 119 | 12 | May' 13 | 10:00
63 | Modern Steal | 132 | 130 | 16 | May' 13 | 14:00 | 116 | 23 | May' 13 | 9:00
64 | Goalpara | 132 | 138 | 7 | May' 13 | 15:00 | 119 | 13 | May' 13 | 9:00
65 | Central s/s | 132 | 139 | 11 | May' 13 | 19:00 | 120 | 16 | May' 13 | 15:00
66 | Noapara | 132 | 139 | 12 | May' 13 | 19:00 | 120 | 16 | May' 13 | 15:00
67 | Jessore | 132 | 139 | 12 | May' 13 | 19:30 | 117 | 17 | May' 13 | 13:00
68 | Jhenidah | 132 | 138 | 11 | May' 13 | 20:00 | 117 | 1 | May' 13 | 21:00
69 | Bottail | 132 | 137 | 17 | May' 13 | 6:00 | 120 | 1 | May' 13 | 21:00
70 | Bheramara | 132 | 140 | 11 | May' 13 | 19:00 | 122 | 4 | May' 13 | 11:00
71 | Faridpur | 132 | 139 | 11 | May' 13 | 21:00 | 120 | 1 | May' 13 | 9:00
72 | Madaripur | 132 | 137 | 23 | May' 13 | 11:00 | 114 | 18 | May' 13 | 10:00
73 | Gopalganj | 132 | 144 | 11 | May' 13 | 21:00 | 119 | 1 | May' 13 | 13:00
74 | Bagerhat | 132 | 135 | 12 | May' 13 | 3:00 | 110 | 14 | May' 13 | 11:00
75 | Mongla | 132 | 137 | 9 | May' 13 | 1:00 | 114 | 14 | May' 13 | 11:00
76 | Satkhira | 132 | 138 | 1 | May' 13 | 17:00 | 119 | 16 | May' 13 | 15:00
77 | Gallamari | 132 | 140 | 19 | May' 13 | 9:00 | 122 | 16 | May' 13 | 15:00
78 | Magura | 132 | 140 | 12 | May' 13 | 18:30 | 115 | 1 | May' 13 | 21:00
Page: 3/3
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May 2013
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
79 | Chuadanga | 132 | 141 | 11 | May' 13 | 19:00 | 115 | 1 | May' 13 | 20:00
80 | Barisal | 132 | 142 | 12 | May' 13 | 19:00 | 118 | 13 | May' 13 | 8:00
81 | Patuakhali | 132 | 138 | 27 | May' 13 | 4:00 | 112 | 18 | May' 13 | 10:00
82 | Bhandaria | 132 | 137 | 20 | May' 13 | 14:00 | 108 | 18 | May' 13 | 10:00
83 | Ishurdi | 132 | 137 | 20 | May' 13 | 14:00 | 118 | 12 | May' 13 | 8:00
84 | Natore | 132 | 137 | 12 | May' 13 | 19:00 | 116 | 4 | May' 13 | 16:00
85 | Bogra | 132 | 137 | 17 | May' 13 | 6:00 | 116 | 4 | May' 13 | 16:00
86 | Naogaon | 132 | 135 | 12 | May' 13 | 9:00 | 110 | 1 | May' 13 | 11:00
87 | Rajshahi | 132 | 136 | 11 | May' 13 | 19:00 | 111 | 4 | May' 13 | 16:00
88 | C.Nawabganj | 132 | 135 | 11 | May' 13 | 19:00 | 107 | 4 | May' 13 | 16:00
89 | Pabna | 132 | 135 | 11 | May' 13 | 20:00 | 118 | 4 | May' 13 | 16:00
90 | Shahjadpur | 132 | 135 | 11 | May' 13 | 20:00 | 122 | 12 | May' 13 | 7:00
91 | Serajganj | 132 | 132 | 7 | May' 13 | 2:00 | 118 | 4 | May' 13 | 16:00
92 | Niyamatpur | 132 | 136 | 7 | May' 13 | 2:00 | 104 | 3 | May' 13 | 10:00
93 | Joypurhat | 132 | 137 | 17 | May' 13 | 6:00 | 111 | 31 | May' 13 | 20:00
94 | Rangpur | 132 | 134 | 12 | May' 13 | 9:00 | 116 | 10 | May' 13 | 19:00
95 | Lalmonirhat | 132 | 132 | 12 | May' 13 | 9:00 | 114 | 4 | May' 13 | 19:30
96 | Saidpur | 132 | 130 | 12 | May' 13 | 9:00 | 114 | 1 | May' 13 | 12:00
97 | Purbasadipur | 132 | 131 | 17 | May' 13 | 6:00 | 113 | 16 | May' 13 | 20:00
98 | Thakurgaon | 132 | 130 | 25 | May' 13 | 6:00 | 108 | 16 | May' 13 | 19:00
99 | Palashbari | 132 | 132 | 23 | May' 13 | 18:30 | 113 | 1 | May' 13 | 20:00
100 | Barapukuria | 132 | 130 | 7 | May' 13 | 1:00 | 116 | 9 | May' 13 | 20:00
101 | Panchagar | 132 | 128 | 12 | May' 13 | 7:00 | 107 | 31 | May' 13 | 20:00
Manager
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: May 2013
Name of the | Auto transofrmer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
| TR1 | 225 | 90 | 365
Hasnabad | TR2 | 225 | 80 | 355 | 15.05.13 | 24:00
| TR3 | 225 | 80 | 325
| TR1 | 225 | 130 | 430
Tongi | TR2 | 225 | 130 | 430 | 20.05.13 | 09:00
| TR3 | 225 | 130 | 430
| TR1 | 225 | 130 | 375
Haripur | TR2 | 225 | 130 | 375 | 13.05.13 | 23:00
| TR3 | 225 | 130 | 375
| TR1 | 225 | 148 | 580
Rampura | TR2 | 225 | 148 | 580 | 02.05.13 | 15:00
| TR3 | 225 | 148 | 580
| TR1 | 225 | 117 | 360
Aminbazar | TR2 | 225 | 117 | 360 | 11.05.13 | 08:00
| TR3 | 225 | 121 | 376
Comilla(N) | TR1 | 225 | 120 | 340 | 19.05.13 | 01:00
| TR2 | 225 | 115 | 330
| TR1 | 150 | 100 | 290
Hathazari | TR2 | 150 | 100 | 290 | 09.05.13 | 10:00
| TR3 | 150 | 100 | 290
| TR4 | 150 | 100 | 290
| TR1 | 225 | 125 | 410
Ishurdi | TR2 | 225 | 125 | 410 | 01.05.13 | 23:00
| TR3 | 225 | 125 | 410
Khulna(S) | TR1 | 225 | 86 | 240 | 05.05.13 | 7:00
| TR2 | 225 | 86 | 240
Bogra | TR1 | 225 | 230 | 643 | 01.05.13 | 24:00
Baghabari | TR1 | 225 | 28 | 140 | 11.05.13 | 20:00
| TR2 | 225 | 28 | 140
Barapukuria | TR1 | 225 | 135 | 675 | 04.05.13 | 19:00
| TR2 | 225 | 135 | 675
Manager
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: May 2013 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May 2013 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-05-13 | 5982 | 5982 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 01-05-13 | 4647 | 4647 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
02-05-13 | 6223 | 6350 | 140 | 21:00 | 23 | 22 | 23 | 13 | 12 | 10 | 11 | 7 | 19 | Due to Generation shortage & gas restriction | 02-05-13 | 5346 | 5346 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
03-05-13 | 6176 | 6300 | 112 | 21:00 | 33 | 10 | 14 | 16 | 10 | 15 | 0 | 4 | 10 | Do | 03-05-13 | 5031 | 5031 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
04-05-13 | 5586 | 5586 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 04-05-13 | 4847 | 4847 | 0 | 9:00 | - | - | - | - | - | - | - | - | - | -
05-05-13 | 5523 | 5523 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 05-05-13 | 3550 | 3550 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
06-05-13 | 5037 | 5037 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 06-05-13 | 4144 | 4144 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
07-05-13 | 5542 | 5542 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 07-05-13 | 4275 | 4275 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
08-05-13 | 5434 | 5542 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 08-05-13 | 4691 | 4691 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
09-05-13 | 5723 | 5723 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 09-05-13 | 4475 | 4475 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
10-05-13 | 5863 | 5863 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 10-05-13 | 4472 | 4472 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
11-05-13 | 5736 | 5736 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 11-05-13 | 4915 | 4915 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
12-05-13 | 5608 | 5608 | 0 | 19:00 | - | - | - | - | - | - | - | - | - | - | 12-05-13 | 4256 | 4256 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
13-05-13 | 6170 | 6170 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 13-05-13 | 4810 | 4810 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
14-05-13 | 6106 | 6106 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 14-05-13 | 4513 | 4513 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
15-05-13 | 6087 | 6087 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 15-05-13 | 5063 | 5063 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
16-05-13 | 5215 | 5215 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 16-05-13 | 3504 | 3504 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
17-05-13 | 5806 | 5806 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 17-05-13 | 4102 | 4102 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
18-05-13 | 5882 | 6000 | 118 | 21:00 | 29 | 13 | 16 | 17 | 12 | 17 | 0 | 0 | 14 | Due to Generation shortage & gas restriction | 18-05-13 | 4827 | 4827 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
19-05-13 | 5935 | 6100 | 145 | 21:00 | 43 | 18 | 17 | 19 | 16 | 12 | 8 | 3 | 9 | Do | 19-05-13 | 4844 | 5000 | 140 | 12:00 | 72 | 18 | 15 | 13 | 9 | 6 | 0 | 2 | 5 | Due to Generation shortage & gas restriction
20-05-13 | 5789 | 6200 | 370 | 21:00 | 130 | 41 | 59 | 28 | 37 | 34 | 0 | 11 | 30 | Do | 20-05-13 | 5044 | 5044 | 0 | 10:00 | - | - | - | - | - | - | - | - | - | -
21-05-13 | 5972 | 5972 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 21-05-13 | 4908 | 4908 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
22-05-13 | 5847 | 6000 | 165 | 21:00 | 48 | 19 | 11 | 22 | 17 | 20 | 5 | 2 | 21 | Due to Generation shortage & gas restriction | 22-05-13 | 4920 | 4920 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
23-05-13 | 5644 | 5644 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 23-05-13 | 4163 | 4163 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
24-05-13 | 5198 | 5198 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 24-05-13 | 4001 | 4001 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
25-05-13 | 5966 | 5966 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 25-05-13 | 4617 | 4617 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
26-05-13 | 6028 | 6028 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 26-05-13 | 5081 | 5081 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
27-05-13 | 5956 | 5956 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 27-05-13 | 5004 | 5200 | 176 | 11:00 | 55 | 25 | 23 | 22 | 15 | 12 | 10 | 4 | 10 | Due to Generation shortage & gas restriction
28-05-13 | 5910 | 6100 | 171 | 20:00 | 32 | 22 | 30 | 27 | 19 | 17 | 4 | 3 | 17 | Due to Generation shortage & gas restriction | 28-05-13 | 5165 | 5165 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
29-05-13 | 5647 | 5647 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 29-05-13 | 4918 | 4918 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
30-05-13 | 5112 | 5112 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 30-05-13 | 4215 | 4215 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
31-05-13 | 4960 | 4960 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 31-05-13 | 3467 | 3467 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
| Information Management Division, LDC, Dhaka. |  |  |  | QF-LDC-38
Report on Generation System
Month: May 2013
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 6223 | 2013-02-05 | 21:00
2 | Maximum day peak Genaration | MW | 5346 | 2013-02-05 | 12:00
3 | Peak Demand | MW | 6350 | 02/05/13 | 21:00
4 | Minimum Generation | MW | 2804 | 07/05/13 | 6:00
5 | Average of the daily evening peak Genaration | MW | 5731.06
6 | Average of the daily day peak Genaration | MW | 4574
7 | Maximum load shed | MW | 370 | 20/05/13 | 21:00
8 | Minimum load shed | MW | 112 | 2013-03-05 | 21:00
9 | Total nos. of load shed days | Day | 8
10 | Average load shed ( Avg. of the 31 days in the month) | MW | 39.39
11 | Total Generation | MKWH | 3418.51
12 | Total Generation by IPP | MKWH | 601.17 | % of Total Gen. | 17.59%
13 | Total Generation by BPDB | MKWH | 1759.14 | " | 51.46%
14 | A) Total Generation by RPCL | MKWH | 91.89 |  | 2.69%
| B) Total Generation by REB | MKWH | 130.97 | " | 3.83%
| C) Total Generation by RENTAL | MKWH | 835.36 | " | 24.44%
15 | Fuel wise Generation.
| A) Gas | MKWH | 2706.74 | % of Total Gen. | 79.18%
| B) Oil | MKWH | 554.23 | '' | 16.21%
| C) Hydro | MKWH | 56.23 | '' | 1.64%
| D) Coal | MKWH | 101.31 | '' | 2.96%
16 | Maximun of the daily total Generation . | MKWH | 127.99 | 2013-02-05
17 | Monthly Load factor | % | 73.84%
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 10103.5
a) | Gas | M.Taka | 2118.98
b) | Liquid fuel | M.Taka | 7579.11
c) | Coal | M.Taka | 405.4
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 480.63 | 20/5/13
a) | Gas | M.Taka | 79.44 | 2013-01-05
b) | Liquid fuel | M.Taka | 396.02 | 20/5/13
c) | Coal | M.Taka | 17.82 | 2013-05-05
20 | Fuel cost of per unit Generation
a) | Including Hydro | Taka/KWHR | 2.96
b) | Excluding Hydro | Taka/KWHR | 3
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76 | 31/05/2013 | 06:00
b) | Actual | FT (MSL) | 79.9 | 31/05/2013 | 06:00
22 | Peak Genaration of May'12 | MW | 5575 | 30/05/12 | 21:00
23 | Peak Demand of May'12 | MW | 6600 | 30.05.12 | 21:00
24 | Maximum peak Generation recorded upto 31/05/13 | MW | 6350 | 04/08/12 | 21:00
25 | Maximum peak Demand recorded upto 31/05/13 | MW | 6600 | 30/05/12 | 21:00
26 | Maximum load shed recorded upto 31/05/13 | MW | 2087 | 15/12/07 | 19:00
Manager
Information Management Division
LDC,PGCB, Dhaka.