## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-07-11 | Wednesday
|  | Date (day): | 2018-07-11 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11104 | MW |  |  | (b) At Evening Peak Hour : |  | 12122 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-07-10 | 2018-07-11 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 64 | 61 | 65 | 65
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 290 | 330 | 300 | 330 | 35
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 30 | 30 | 50 | 50 | 18
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 26 | 20 | 85 | 85 | 88 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 340 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 26 | 98 | 98 | 110
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 246 | 242 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 380 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 305 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 64 | 81 | 81 | 81 |  |  | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 87 | 87 | 88 | 88 |  |  | Engine problem
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 22 | 60 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 93 | 93 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 70 | 70 | 70 | 70 |  |  | Gas shortage
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | ACE Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 50 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 82 | 87 | 88 | 88
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 50 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 51 | 50 | 50
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 301 | 302 | 300 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 9 | 0 | 0 |  |  | On test
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 73 | 50 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 0 | 100
| Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 0 | 0 | 150 | 150 | 150 | 150
| Dhaka area Total |  |  |  |  | 5635 | 5399 | 3250 | 3895 | 4121 | 4313 | 556 | 515
37 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
39 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 44 | 50 | 50 | 50
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 164 | 167 | 168 | 168 |  | 62 | # 2 & 3 under maint
41 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
42 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 227 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 70 | 100 | 100 | 135
44 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 40 | 37 | 51 | 51
45 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 40 | 48 | 48
46 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 31 | 56 | 68 | 68
47 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 80 | 80 |  | 20 | Engine problem
48 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 27 | 10 | 20
49 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 92 | 104 | 98 | 104 |  | 4
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 777 | 923 | 933 | 984 | 360 | 138
50 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 0 | 0 | 0 | 135 |  | Under shut down
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 120 | 100 | 120 | 9 |  | Gas shortage
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34 |  | Gas shortage
51 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 207 | 225 | 225 |  |  | FGMO
52 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 300 | 360 | 360 |  |  | FGMO
53 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 294 | 301 | 360 | 360
54 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 43 | 43 | 43 |  | 5 | Engine problem
55 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
56 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 5 | 53
57 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 73 | 73 | 73 | 122 |  | Gas shortage
58 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 45 | 51 | 51 | 51
59 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
60 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
61 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST under maint.
62 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
63 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 132 | 120 | 122 | 167
64 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
65 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 8 | 8 | 52
66 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 22 | 22 | 22 |  | 3 | Engine problem
67 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 170 | 0 | 170
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1544 | 1817 | 1717 | 2094 | 300 | 126
68 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 40 | 44 | 100 | 100 | 102 |  | Gas shortage
69 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
70 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
71 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 2 | 0
72 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 160 | 163 | 150 | 163
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 252 | 322 | 367 | 378 | 102 | 0
73 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 68 | 68 | 68
74 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 73 | 74 | 74 | 74
75 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
76 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 208 | 190 | 240 | 240
77 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 53 | 53
78 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 47 | 50 | 50 | 50
79 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
80 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 54 | 60 | 60
81 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
82 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 47 | 50 | 50
83 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint. |  | 2018-10-07
84 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
85 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 46 | 46 | 45 | 45 |  | 5 | Engine problem
86 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 23 | 23 |  | 2
87 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 341 | 341 |  |  | FGMO
88 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1153 | 1120 | 1274 | 1274 | 0 | 169
89 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 32 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 468 | 458 | 473 | 473
90 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 51 | 81 | 50 | 90 |  | 20 | Engine problem
91 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 96 | 92 | 115 | 115 |  | 16
92 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 49 | 36 | 50
93 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 232 | 225 | 225 |  |  | FGMO
94 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 75 | 70 | 75
95 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 235 | 220 | 250 | 250 | 160 |  | Gas shortage
96 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 33 | 40 | 40
97 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 55 | 0 | 55
98 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 97 | 97 | 97
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 1010 | 1424 | 1356 | 1518 | 160 | 36
99 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 80 | 110 | 110 | 110
100 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 30
101 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 38 | 33 | 33
102 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 186 | 194 | 194
103 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 95 | 98 | 98
| Barisal Area Total |  |  |  |  | 472 | 462 | 383 | 441 | 435 | 465 | 0 | 0
104 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
105 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 51 | 0 | 51
106 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 38 | 0 | 38
107 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 33 | 50 | 50 | 50 |  | 0
108 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
109 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 45 | 45
110 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 151 | 214 | 214 | 214
111 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 152 | 220 | 130 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
112 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Transformer problem.
113 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
114 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 9 | 9 | 10 | 10
115 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
116 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52 |  | 0
117 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 101 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 460 | 852 | 673 | 852 | 71 | 161
118 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
119 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 210 | 210
120 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 16
121 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 181 | 228 | 244 | 0 | 170
| Total |  |  |  |  | 15953 | 15410 | 8979 | 10975 | 11104 | 12122 | 1549 | 1315
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8554.3894 | 10456 | 10578.8997 | 11548.7592
A. |  | 2018-07-10 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10975 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 7971.5 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10975 | MW
3 | Day peak Generation : |  |  | 8979 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10456 | MW
4 | Evening peak Generation : |  |  | 10975 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 220.0687 | MKWHr | By Solar | 0.0019 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 118.1115 | MKWHr |  | By Oil: | 80.2454 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.6653 | MKWHr |  | By Hydro: | 3.8621 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1549 | MW | Dhaka | 3962 | 3962 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1315 | MW | Chittagong | 1034 | 1034 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2864 | MW | Khulna | 1331 | 1331 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 988.09 | MMCFD |  |  | Rajshahi | 1112 | 1112 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 83335453.41 | ii) Oil : | Taka | 790327168.39 | Comilla | 968 | 968 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14148058 | Total | Taka | 887810679.8 | Mymensingh | 738 | 738 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 8.5825 | MKWHr. | Sylhet | 417 | 417 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -680 | MW at | 21:00 | hrs | Barisal | 278 | 278 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -770 | MW at | 5:00 | hrs | Rangpur | 616 | 616 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.8° C |  |  | Total | 10456 | 10456 |  | 0
B. |  | 2018-07-11 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12122 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 822 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 226.5855 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7856.4 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.1498 | MKWHr. | ii) HVDC Flow at Peak Time |  | 458 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0326 | MKWHr. | iii) Maximum HVDC Flow : |  | 468 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 104.84 |  | (b) Today: | 104.76 |  | (c) Rule Curve: |  | 85.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-07-10
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | ACE Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 395 | 282 | 110 | 0 | 390 | 200 | 100 | 97 | 55 | 70 | 0 | 0 | 34 | 93 | 102 | 149 | 88 | 80 | 50 | 40 | 54 | 55 | 0 | 22 | 25 | 32 | 33 | 33 | 42 | 0 | 82 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 50 | 0 | 51 | 48 | 51 | 80 | 98 | 50 | 19 | 31 | 100 | 0 | 100 | 270 | 272 | 179 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 33 | 22 | 132 | 45 | 95 | 20 | 0 | 30 | 73 | 53 | 50 | 163 | 190 | 61 | 86 | 47 | 0 | 0 | 47 | 10 | 300 | 23 | 11 | 0 | 300 | 0 | 0 | 156 | 0 | 150 |  | 467 | 0 | 259 | 69 | 113 | 150 | 0 | 55 | 48 | 56 | 40 | 192 | 27 | 110 | 0 | 0 | 0 | 51 | 25 | 100 | 50 | 43 | 45 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 14 | 14 | 0 | 130 | 0 | 131 | 95 | 0 | 0 | 0 |  | 7443 | 2523 | 9966 | 3126 | 467 | 1937 | 2728 | 150 | 162 | 1264 | 132 | 0 | 0 | 104.94
2:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 380 | 313 | 55 | 0 | 410 | 200 | 100 | 97 | 55 | 70 | 0 | 0 | 0 | 93 | 102 | 115 | 88 | 80 | 10 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 46 | 0 | 82 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 50 | 0 | 51 | 48 | 59 | 80 | 98 | 50 | 19 | 37 | 100 | 0 | 100 | 270 | 272 | 182 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 33 | 22 | 130 | 45 | 95 | 20 | 0 | 30 | 73 | 53 | 50 | 163 | 198 | 61 | 86 | 47 | 0 | 0 | 47 | 9 | 295 | 23 | 11 | 0 | 300 | 0 | 0 | 156 | 0 | 150 |  | 467 | 0 | 260 | 68 | 113 | 120 | 0 | 0 | 48 | 20 | 40 | 192 | 11 | 110 | 0 | 0 | 0 | 51 | 0 | 100 | 50 | 43 | 45 | 34 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 15 | 16 | 0 | 130 | 0 | 130 | 97 | 0 | 0 | 0 |  | 7392 | 2347 | 9739 | 3123 | 467 | 1974 | 2584 | 150 | 162 | 1149 | 130 | 0 | 0 | 104.92
3:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 345 | 323 | 0 | 0 | 450 | 200 | 100 | 97 | 55 | 70 | 0 | 0 | 0 | 84 | 7 | 32 | 88 | 80 | 10 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 29 | 0 | 82 | 80 | 0 | 0 | 8 | 0 | 200 | 0 | 50 | 0 | 51 | 24 | 28 | 80 | 98 | 50 | 19 | 39 | 100 | 0 | 100 | 280 | 287 | 194 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 33 | 22 | 126 | 45 | 64 | 20 | 0 | 30 | 73 | 53 | 50 | 163 | 190 | 61 | 86 | 47 | 0 | 0 | 47 | 9 | 305 | 23 | 11 | 0 | 301 | 0 | 0 | 163 | 0 | 150 |  | 467 | 0 | 266 | 63 | 113 | 120 | 0 | 0 | 48 | 20 | 40 | 192 | 34 | 80 | 0 | 0 | 0 | 51 | 0 | 100 | 50 | 43 | 0 | 8 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 15 | 16 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 7105 | 2269 | 9374 | 3123 | 467 | 2058 | 2324 | 150 | 162 | 964 | 126 | 0 | 0 | 104.9
4:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 350 | 344 | 0 | 0 | 450 | 200 | 65 | 97 | 55 | 70 | 0 | 0 | 0 | 84 | 7 | 32 | 10 | 80 | 10 | 40 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 82 | 80 | 0 | 0 | 8 | 0 | 200 | 0 | 50 | 0 | 51 | 24 | 28 | 80 | 92 | 50 | 19 | 40 | 100 | 0 | 100 | 270 | 272 | 184 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 33 | 19 | 116 | 45 | 40 | 20 | 0 | 30 | 73 | 53 | 50 | 163 | 200 | 61 | 86 | 47 | 0 | 0 | 47 | 9 | 290 | 23 | 11 | 0 | 300 | 0 | 0 | 163 | 0 | 150 |  | 467 | 0 | 271 | 10 | 114 | 120 | 0 | 0 | 18 | 20 | 40 | 192 | 33 | 80 | 0 | 0 | 0 | 51 | 0 | 100 | 50 | 43 | 0 | 8 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 15 | 16 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 6932 | 2191 | 9123 | 3105 | 467 | 2064 | 2125 | 150 | 162 | 934 | 116 | 0 | 0 | 104.88
5:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 350 | 344 | 0 | 0 | 450 | 200 | 30 | 70 | 55 | 70 | 0 | 0 | 0 | 84 | 7 | 16 | 10 | 80 | 10 | 40 | 36 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 51 | 9 | 28 | 80 | 92 | 50 | 19 | 40 | 100 | 0 | 100 | 270 | 272 | 182 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 19 | 116 | 45 | 8 | 20 | 0 | 30 | 73 | 53 | 50 | 163 | 200 | 61 | 86 | 47 | 0 | 0 | 47 | 9 | 295 | 23 | 11 | 0 | 300 | 0 | 0 | 163 | 0 | 150 |  | 467 | 0 | 270 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 40 | 192 | 31 | 80 | 0 | 0 | 0 | 51 | 0 | 100 | 50 | 43 | 0 | 8 | 0 | 18 | 9 | 8 | 0 | 0 | 150 | 15 | 16 | 0 | 130 | 0 | 130 | 95 | 0 | 0 | 0 |  | 6772 | 2049 | 8821 | 3100 | 467 | 2066 | 1890 | 150 | 166 | 866 | 116 | 0 | 0 | 104.86
6:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 350 | 348 | 0 | 0 | 450 | 200 | 7 | 30 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 36 | 55 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 86 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 40 | 0 | 17 | 80 | 92 | 50 | 19 | 40 | 100 | 0 | 100 | 270 | 272 | 188 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 19 | 104 | 45 | 8 | 20 | 0 | 30 | 73 | 53 | 50 | 163 | 200 | 61 | 84 | 47 | 0 | 0 | 47 | 9 | 305 | 23 | 11 | 0 | 97 | 0 | 0 | 100 | 0 | 150 |  | 467 | 0 | 282 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 43 | 0 | 8 | 0 | 18 | 9 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 6153 | 1880 | 8033 | 3114 | 467 | 2073 | 1195 | 150 | 166 | 764 | 104 | 0 | 0 | 104.84
7:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 350 | 321 | 0 | 0 | 450 | 200 | 7 | 15 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 37 | 36 | 22 | 25 | 33 | 33 | 33 | 8 | 0 | 87 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 50 | 0 | 40 | 0 | 17 | 80 | 92 | 50 | 19 | 30 | 100 | 0 | 100 | 290 | 279 | 190 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 114 | 45 | 8 | 20 | 0.5 | 30 | 73 | 53 | 50 | 163 | 201 | 60 | 84 | 47 | 0 | 0 | 47 | 9 | 320 | 23 | 11 | 0 | 97 | 0 | 0 | 100 | 0 | 150 |  | 467 | 0 | 282 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 22 | 32 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 8 | 0 | 18 | 9 | 6 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 6143.5 | 1828 | 7971.5 | 3148 | 467 | 2048 | 1162 | 150 | 167 | 715 | 114 | 0.5 | 0 | 104.82
8:00 | 64 | 120 | 0 | 0 | 250 | 85 | 30 | 365 | 284 | 0 | 0 | 400 | 200 | 7 | 30 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 10 | 12 | 18 | 37 | 36 | 22 | 25 | 33 | 33 | 33 | 8 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 217 | 0 | 50 | 0 | 40 | 0 | 16 | 80 | 92 | 50 | 19 | 10 | 100 | 0 | 100 | 315 | 312 | 208 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 16 | 11 | 33 | 19 | 112 | 45 | 8 | 20 | 0.6 | 30 | 73 | 53 | 50 | 163 | 217 | 60 | 84 | 47 | 0 | 0 | 46 | 9 | 320 | 23 | 11 | 0 | 97 | 0 | 0 | 100 | 0 | 150 |  | 468 | 0 | 280 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 21 | 32 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 8 | 0 | 18 | 9 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 6181.6 | 1825 | 8006.6 | 3246 | 468 | 1939 | 1195 | 150 | 167 | 729 | 112 | 0.6 | 0 | 104.82
9:00 | 64 | 120 | 0 | 0 | 250 | 84 | 30 | 380 | 261 | 0 | 0 | 400 | 240 | 30 | 30 | 25 | 70 | 0 | 0 | 0 | 20 | 16 | 48 | 50 | 82 | 51 | 21 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 22 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 211 | 0 | 100 | 0 | 40 | 0 | 16 | 80 | 92 | 50 | 19 | 5 | 100 | 0 | 100 | 270 | 272 | 184 | 73 | 100 | 20 | 0 | 5 | 0 | 85 | 0 | 1 | 16 | 11 | 33 | 0 | 114 | 46 | 24 | 20 | 0 | 27 | 73 | 53 | 50 | 163 | 192 | 50 | 86 | 47 | 0 | 0 | 47 | 9 | 275 | 23 | 11 | 0 | 115 | 0 | 0 | 132 | 0 | 150 |  | 468 | 0 | 270 | 25 | 45 | 120 | 0 | 0 | 0 | 0 | 24 | 189 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 40 | 43 | 0 | 8 | 0 | 13 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 6376 | 1891 | 8267 | 3066 | 468 | 1813 | 1684 | 150 | 167 | 805 | 114 | 0 | 0 | 104.82
10:00 | 64 | 120 | 0 | 0 | 280 | 55 | 30 | 350 | 262 | 0 | 0 | 380 | 200 | 100 | 55 | 55 | 70 | 0 | 0 | 0 | 75 | 40 | 48 | 87 | 82 | 11 | 40 | 54 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 40 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 219 | 0 | 70 | 0 | 40 | 0 | 16 | 80 | 92 | 44 | 19 | 4 | 100 | 0 | 100 | 295 | 298 | 202 | 73 | 100 | 20 | 0 | 5 | 35 | 85 | 0 | 24 | 16 | 11 | 33 | 20 | 128 | 45 | 32 | 20 | 0 | 27 | 73 | 53 | 50 | 163 | 206 | 62 | 84 | 47 | 0 | 0 | 46 | 7 | 285 | 23 | 11 | 0 | 200 | 0 | 0 | 139 | 0 | 150 |  | 468 | 0 | 250 | 14 | 49 | 120 | 0 | 0 | 0 | 0 | 33 | 193 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 43 | 0 | 25 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 0 | 0 | 0 |  | 6760 | 1848 | 8608 | 3163 | 468 | 1808 | 1998 | 150 | 160 | 733 | 128 | 0 | 0 | 104.82
11:00 | 64 | 120 | 0 | 0 | 290 | 26 | 30 | 370 | 256 | 13 | 0 | 380 | 200 | 100 | 65 | 55 | 70 | 0 | 0 | 3 | 75 | 58 | 64 | 87 | 82 | 11 | 40 | 54 | 55 | 36 | 22 | 25 | 30 | 33 | 25 | 38 | 0 | 86 | 80 | 0 | 0 | 16 | 0 | 205 | 0 | 70 | 0 | 40 | 0 | 26 | 80 | 92 | 44 | 19 | 2 | 100 | 0 | 100 | 270 | 287 | 186 | 73 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 25 | 16 | 11 | 33 | 22 | 128 | 46 | 32 | 20 | 0 | 32 | 73 | 50 | 47 | 163 | 187 | 60 | 84 | 45 | 0 | 0 | 45 | 9 | 290 | 23 | 11 | 0 | 235 | 0 | 0 | 160 | 0 | 150 |  | 468 | 0 | 240 | 46 | 68 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 43 | 0 | 52 | 0 | 15 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 160 | 0 | 145 | 96 | 0 | 0 | 0 |  | 6805 | 1977 | 8782 | 3105 | 468 | 1776 | 2199 | 150 | 166 | 790 | 128 | 0 | 0 | 104.81
12:00 | 64 | 120 | 0 | 0 | 290 | 26 | 30 | 345 | 246 | 26 | 0 | 380 | 200 | 100 | 64 | 55 | 70 | 0 | 0 | 22 | 93 | 84 | 50 | 87 | 82 | 0 | 40 | 54 | 55 | 36 | 22 | 25 | 25 | 33 | 25 | 50 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 217 | 0 | 70 | 0 | 40 | 0 | 31 | 80 | 92 | 44 | 19 | 4 | 100 | 0 | 100 | 290 | 294 | 184 | 73 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 34 | 16 | 11 | 33 | 22 | 132 | 40 | 32 | 20 | 0 | 40 | 73 | 53 | 47 | 163 | 208 | 60 | 84 | 46 | 0 | 0 | 46 | 9 | 290 | 23 | 11 | 0 | 301 | 0 | 0 | 160 | 0 | 150 |  | 468 | 0 | 235 | 51 | 96 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 19 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 43 | 0 | 43 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 151 | 0 | 152 | 95 | 0 | 0 | 0 |  | 6976 | 2003 | 8979 | 3118 | 468 | 1773 | 2383 | 150 | 164 | 791 | 132 | 0 | 0 | 104.8
13:00 | 64 | 120 | 0 | 0 | 290 | 25 | 30 | 354 | 241 | 26 | 0 | 380 | 240 | 100 | 64 | 55 | 70 | 0 | 0 | 36 | 93 | 102 | 48 | 87 | 90 | 0 | 40 | 54 | 55 | 36 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 70 | 0 | 40 | 0 | 31 | 80 | 98 | 31 | 19 | 5 | 100 | 0 | 80 | 270 | 272 | 172 | 73 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 34 | 16 | 11 | 33 | 22 | 130 | 33 | 32 | 20 | 0 | 48 | 73 | 53 | 50 | 163 | 190 | 60 | 83 | 46 | 0 | 0 | 45 | 9 | 300 | 23 | 11 | 0 | 301 | 0 | 0 | 153 | 0 | 150 |  | 468 | 0 | 223 | 68 | 96 | 140 | 0 | 0 | 0 | 0 | 40 | 184 | 23 | 80 | 0 | 0 | 0 | 51 | 0 | 32 | 0 | 43 | 0 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 146 | 0 | 167 | 97 | 0 | 0 | 0 |  | 6964 | 2097 | 9061 | 3032 | 468 | 1785 | 2442 | 149 | 167 | 888 | 130 | 0 | 0 | 104.79
14:00 | 64 | 120 | 0 | 0 | 290 | 25 | 30 | 355 | 241 | 26 | 0 | 380 | 200 | 100 | 64 | 55 | 70 | 0 | 0 | 36 | 93 | 102 | 16 | 50 | 89 | 10 | 39 | 54 | 55 | 36 | 0 | 25 | 30 | 33 | 33 | 34 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 209 | 0 | 70 | 0 | 40 | 0 | 31 | 80 | 98 | 24 | 19 | 8 | 100 | 0 | 80 | 286 | 287 | 134 | 73 | 100 | 20 | 0 | 5 | 51 | 85 | 0 | 34 | 16 | 11 | 33 | 21 | 136 | 31 | 16 | 20 | 0 | 48 | 72 | 53 | 49 | 163 | 200 | 60 | 84 | 46 | 0 | 0 | 46 | 9 | 300 | 23 | 11 | 0 | 301 | 0 | 0 | 158 | 0 | 150 |  | 468 | 0 | 208 | 66 | 96 | 160 | 0 | 0 | 0 | 0 | 40 | 191 | 4 | 80 | 0 | 0 | 0 | 51 | 0 | 93 | 0 | 35 | 12 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 133 | 0 | 130 | 95 | 0 | 0 | 0 |  | 6830 | 2102 | 8932 | 3002 | 468 | 1774 | 2329 | 150 | 168 | 905 | 136 | 0 | 0 | 104.78
15:00 | 64 | 120 | 0 | 0 | 305 | 23 | 30 | 392 | 241 | 80 | 0 | 360 | 305 | 100 | 64 | 55 | 70 | 0 | 0 | 36 | 93 | 102 | 16 | 87 | 88 | 50 | 39 | 54 | 56 | 36 | 0 | 25 | 30 | 33 | 33 | 34 | 0 | 86 | 80 | 0 | 0 | 16 | 0 | 205 | 0 | 135 | 0 | 40 | 0 | 31 | 80 | 98 | 25 | 0 | 8 | 0 | 0 | 90 | 282 | 261 | 116 | 73 | 100 | 10 | 0 | 5 | 51 | 85 | 0 | 34 | 16 | 11 | 33 | 12 | 148 | 31 | 40 | 20 | 0 | 59 | 72 | 50 | 50 | 163 | 190 | 60 | 64 | 46 | 0 | 0 | 44 | 9 | 320 | 21 | 2 | 0 | 301 | 0 | 8 | 156 | 26 | 150 |  | 468 | 0 | 208 | 61 | 46 | 190 | 0 | 12 | 0 | 0 | 40 | 189 | 25 | 80 | 0 | 0 | 0 | 51 | 0 | 93 | 25 | 35 | 39 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 134 | 0 | 130 | 96 | 0 | 0 | 0 |  | 7034 | 2162 | 9196 | 2866 | 468 | 1770 | 2604 | 150 | 166 | 1024 | 148 | 0 | 0 | 104.77
16:00 | 64 | 120 | 0 | 0 | 305 | 25 | 30 | 345 | 241 | 98 | 0 | 360 | 305 | 100 | 80 | 55 | 70 | 0 | 0 | 30 | 93 | 102 | 16 | 87 | 87 | 50 | 40 | 54 | 55 | 0 | 22 | 25 | 30 | 33 | 0 | 46 | 0 | 86 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 40 | 0 | 31 | 80 | 98 | 26 | 18 | 3 | 0 | 0 | 130 | 270 | 298 | 45 | 73 | 100 | 22 | 0 | 5 | 51 | 50 | 0 | 34 | 16 | 11 | 33 | 21 | 148 | 33 | 90 | 20 | 0 | 68 | 72 | 5 | 5 | 100 | 200 | 58 | 50 | 5 | 0 | 0 | 46 | 9 | 280 | 21 | 5 | 30 | 302 | 0 | 10 | 156 | 72 | 150 |  | 468 | 0 | 208 | 63 | 66 | 200 | 0 | 12 | 0 | 17 | 40 | 185 | 23 | 80 | 0 | 0 | 0 | 51 | 22 | 101 | 25 | 35 | 44 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 132 | 0 | 130 | 95 | 30 | 0 | 0 |  | 6792 | 2267 | 9059 | 2859 | 468 | 1483 | 2789 | 150 | 166 | 996 | 148 | 0 | 0 | 104.76
17:00 | 64 | 120 | 0 | 0 | 305 | 25 | 30 | 355 | 241 | 98 | 0 | 360 | 305 | 70 | 81 | 55 | 70 | 0 | 0 | 35 | 50 | 102 | 16 | 50 | 87 | 51 | 40 | 54 | 55 | 0 | 22 | 25 | 9 | 33 | 33 | 51 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 40 | 0 | 58 | 80 | 98 | 26 | 19 | 4 | 0 | 0 | 130 | 270 | 301 | 45 | 73 | 100 | 43 | 0 | 5 | 51 | 20 | 0 | 34 | 19 | 11 | 33 | 21 | 140 | 45 | 48 | 20 | 0.2 | 68 | 73 | 5 | 5 | 100 | 192 | 60 | 20 | 5 | 0 | 0 | 45 | 9 | 300 | 20 | 11 | 30 | 302 | 0 | 10 | 158 | 30 | 150 |  | 468 | 0 | 200 | 63 | 90 | 200 | 0 | 0 | 0 | 30 | 40 | 186 | 22 | 80 | 0 | 0 | 0 | 51 | 38 | 101 | 25 | 35 | 44 | 29 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 133 | 0 | 130 | 96 | 30 | 0 | 0 |  | 6652.2 | 2279 | 8931.2 | 2914 | 468 | 1443 | 2598 | 150 | 165 | 1053 | 140 | 0.2 | 0 | 104.75
18:00 | 64 | 120 | 0 | 0 | 250 | 25 | 30 | 320 | 240 | 98 | 0 | 360 | 200 | 40 | 80 | 55 | 70 | 0 | 0 | 35 | 20 | 50 | 16 | 20 | 87 | 10 | 40 | 54 | 55 | 36 | 22 | 25 | 9 | 33 | 33 | 51 | 0 | 72 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 50 | 0 | 40 | 0 | 55 | 80 | 98 | 29 | 19 | 6 | 18 | 0 | 130 | 285 | 316 | 85 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 34 | 19 | 11 | 33 | 0 | 104 | 44 | 48 | 20 | 0.2 | 68 | 73 | 5 | 5 | 100 | 200 | 60 | 20 | 5 | 0 | 0 | 45 | 9 | 270 | 21 | 11 | 10 | 161 | 0 | 10 | 161 | 0 | 150 |  | 458 | 0 | 202 | 67 | 102 | 135 | 0 | 0 | 18 | 42 | 8 | 187 | 22 | 80 | 0 | 0 | 0 | 51 | 38 | 101 | 25 | 43 | 44 | 8 | 0 | 10 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 133 | 0 | 130 | 96 | 10 | 0 | 0 |  | 6184.2 | 2180 | 8364.2 | 2902 | 458 | 1471 | 2111 | 150 | 152 | 1016 | 104 | 0.2 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 64 | 120 | 0 | 0 | 330 | 24 | 30 | 330 | 241 | 98 | 0 | 360 | 305 | 54 | 81 | 55 | 70 | 0 | 0 | 35 | 22 | 58 | 16 | 79 | 87 | 51 | 40 | 54 | 55 | 42 | 22 | 25 | 22 | 33 | 33 | 51 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 217 | 0 | 100 | 0 | 34 | 36 | 55 | 80 | 104 | 45 | 19 | 3 | 0 | 50 | 100 | 335 | 334 | 70 | 73 | 100 | 43 | 0 | 5 | 51 | 86 | 46 | 34 | 19 | 11 | 33 | 22 | 122 | 43 | 74 | 20 | 0 | 68 | 75 | 41 | 22 | 163 | 214 | 60 | 30 | 5 | 0 | 0 | 45 | 9 | 310 | 23 | 11 | 10 | 165 | 0 | 11 | 163 | 0 | 150 |  | 458 | 16 | 220 | 77 | 100 | 120 | 0 | 55 | 50 | 83 | 33 | 190 | 27 | 80 | 8 | 0 | 0 | 51 | 38 | 101 | 12 | 43 | 45 | 8 | 0 | 17 | 9 | 11 | 0 | 0 | 150 | 17 | 18 | 0 | 135 | 0 | 136 | 95 | 93 | 0 | 0 |  | 7007 | 2496 | 9503 | 3120 | 458 | 1646 | 2554 | 150 | 165 | 1288 | 122 | 0 | 0 | 105.32
19:30 | 61 | 120 | 0 | 0 | 330 | 23 | 30 | 351 | 241 | 98 | 0 | 360 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 35 | 50 | 102 | 90 | 87 | 87 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 217 | 0 | 135 | 0 | 34 | 40 | 55 | 80 | 104 | 50 | 19 | 9 | 0 | 105 | 100 | 315 | 316 | 79 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 50 | 34 | 19 | 11 | 33 | 22 | 120 | 46 | 95 | 20 | 0 | 68 | 75 | 52 | 47 | 163 | 203 | 60 | 86 | 44 | 0 | 0 | 45 | 9 | 320 | 23 | 11 | 178 | 237 | 0 | 73 | 163 | 90 | 150 |  | 457 | 32 | 222 | 77 | 105 | 150 | 0 | 55 | 49 | 78 | 33 | 191 | 32 | 110 | 10 | 0 | 0 | 51 | 38 | 101 | 41 | 43 | 45 | 21 | 0 | 20 | 9 | 11 | 0 | 0 | 150 | 16 | 18 | 0 | 198 | 0 | 210 | 96 | 98 | 0 | 0 |  | 7870 | 2767 | 10637 | 3169 | 457 | 1800 | 3193 | 150 | 165 | 1583 | 120 | 0 | 0 | 0
20:00 | 61 | 120 | 0 | 0 | 330 | 20 | 30 | 360 | 241 | 98 | 0 | 360 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 50 | 65 | 94 | 149 | 87 | 87 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 32 | 40 | 56 | 80 | 104 | 50 | 19 | 19 | 0 | 115 | 100 | 300 | 301 | 142 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 49 | 34 | 19 | 11 | 33 | 22 | 124 | 44 | 95 | 20 | 0 | 68 | 75 | 50 | 47 | 163 | 190 | 60 | 86 | 46 | 0 | 0 | 46 | 9 | 310 | 23 | 11 | 170 | 258 | 28 | 73 | 163 | 100 | 150 |  | 458 | 32 | 220 | 76 | 105 | 190 | 0 | 55 | 49 | 78 | 33 | 188 | 32 | 110 | 12 | 0 | 0 | 51 | 38 | 101 | 50 | 43 | 47 | 52 | 0 | 20 | 9 | 11 | 0 | 0 | 150 | 16 | 16 | 0 | 205 | 0 | 220 | 96 | 98 | 0 | 0 |  | 8051 | 2861 | 10912 | 3201 | 458 | 1798 | 3303 | 150 | 167 | 1711 | 124 | 0 | 0 | 105.31
21:00 | 61 | 120 | 0 | 0 | 330 | 20 | 30 | 340 | 242 | 98 | 0 | 380 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 60 | 93 | 102 | 149 | 87 | 87 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 100 | 0 | 37 | 40 | 56 | 80 | 104 | 50 | 19 | 27 | 0 | 120 | 100 | 300 | 301 | 207 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 49 | 8 | 19 | 11 | 33 | 22 | 120 | 44 | 95 | 20 | 0 | 68 | 74 | 53 | 50 | 130 | 190 | 54 | 86 | 47 | 0 | 0 | 46 | 9 | 290 | 23 | 0 | 170 | 302 | 9 | 73 | 163 | 100 | 150 |  | 458 | 32 | 220 | 81 | 92 | 232 | 0 | 55 | 49 | 75 | 33 | 186 | 38 | 110 | 12 | 0 | 0 | 51 | 38 | 101 | 50 | 43 | 45 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 16 | 15 | 0 | 214 | 0 | 220 | 95 | 97 | 0 | 0 |  | 8077 | 2898 | 10975 | 3231 | 458 | 1784 | 3344 | 150 | 167 | 1721 | 120 | 0 | 0 | 105.31
22:00 | 61 | 120 | 0 | 0 | 330 | 23 | 40 | 340 | 241 | 98 | 0 | 380 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 60 | 93 | 102 | 149 | 87 | 87 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 50 | 0 | 40 | 48 | 56 | 80 | 105 | 50 | 19 | 36 | 0 | 120 | 100 | 300 | 300 | 165 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 49 | 8 | 16 | 11 | 33 | 22 | 120 | 44 | 95 | 20 | 0 | 68 | 74 | 53 | 50 | 100 | 196 | 61 | 86 | 47 | 0 | 0 | 46 | 9 | 280 | 23 | 0 | 120 | 280 | 74 | 70 | 163 | 100 | 150 |  | 458 | 48 | 222 | 80 | 94 | 233 | 0 | 55 | 49 | 70 | 40 | 181 | 38 | 110 | 12 | 0 | 0 | 51 | 38 | 101 | 50 | 43 | 45 | 52 | 0 | 21 | 9 | 11 | 0 | 0 | 150 | 15 | 15 | 0 | 206 | 0 | 185 | 95 | 97 | 0 | 0 |  | 7977 | 2874 | 10851 | 3195 | 458 | 1768 | 3346 | 150 | 167 | 1647 | 120 | 0 | 0 | 105.3
23:00 | 37 | 120 | 0 | 0 | 330 | 23 | 40 | 360 | 250 | 98 | 0 | 380 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 60 | 93 | 102 | 149 | 87 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 226 | 0 | 135 | 0 | 40 | 48 | 57 | 80 | 105 | 50 | 19 | 38 | 0 | 100 | 100 | 307 | 312 | 167 | 73 | 100 | 20 | 0 | 5 | 51 | 85 | 49 | 8 | 16 | 11 | 33 | 22 | 124 | 44 | 95 | 20 | 0 | 68 | 74 | 53 | 50 | 130 | 216 | 60 | 86 | 47 | 0 | 0 | 46 | 9 | 310 | 23 | 11 | 80 | 302 | 0 | 71 | 160 | 100 | 150 |  | 458 | 32 | 220 | 74 | 63 | 131 | 0 | 55 | 49 | 70 | 40 | 191 | 35 | 110 | 0 | 0 | 0 | 51 | 38 | 101 | 50 | 43 | 45 | 52 | 0 | 21 | 9 | 10 | 0 | 0 | 150 | 14 | 15 | 0 | 160 | 0 | 150 | 96 | 97 | 0 | 0 |  | 8042 | 2630 | 10672 | 3206 | 458 | 1837 | 3215 | 150 | 162 | 1520 | 124 | 0 | 0 | 105.3
24:00 | 37 | 120 | 0 | 0 | 330 | 24 | 40 | 365 | 262 | 98 | 0 | 400 | 260 | 100 | 81 | 55 | 70 | 0 | 0 | 35 | 93 | 60 | 149 | 87 | 89 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 82 | 80 | 0 | 0 | 16 | 0 | 226 | 0 | 135 | 0 | 40 | 48 | 47 | 80 | 105 | 50 | 19 | 29 | 0 | 100 | 100 | 290 | 290 | 205 | 73 | 100 | 20 | 0 | 5 | 51 | 85 | 49 | 8 | 16 | 11 | 33 | 22 | 128 | 44 | 95 | 20 | 0 | 63 | 74 | 53 | 50 | 163 | 200 | 60 | 86 | 47 | 0 | 0 | 46 | 9 | 320 | 23 | 11 | 80 | 301 | 0 | 70 | 163 | 100 | 150 |  | 467 | 32 | 220 | 73 | 99 | 132 | 0 | 55 | 0 | 58 | 40 | 192 | 35 | 110 | 0 | 0 | 0 | 51 | 38 | 101 | 50 | 43 | 45 | 52 | 0 | 21 | 9 | 10 | 0 | 0 | 150 | 10 | 15 | 0 | 148 | 0 | 145 | 96 | 97 | 0 | 0 |  | 7977 | 2594 | 10571 | 3190 | 467 | 1904 | 3141 | 150 | 162 | 1429 | 128 | 0 | 0 | 105.3
KWH | 1292000 | 2741760 | 0 | 0 | 6768727 | 1199659 | 923552 | 8627200 | 6489000 | 1171600 | 0 | 8726251 | 5942196 | 1862400 | 1751952 | 1183833 | 1736292 | 0 | 0 | 578880 | 1723200 | 1661904 | 1486080 | 1569697 | 1803840 | 588390 | 896784 | 1184040 | 1276265 | 1017262 | 454500 | 600000 | 669420 | 815800 | 751400 | 941064 | 0 | 1943029 | 1919100 | 0 | 0 | 320940 | 0 | 4976855 | 0 | 1726112 | 0 | 1009440 | 408288 | 893158 | 1856040 | 2326080 | 1057440 | 437136 | 456000 | 1512558 | 564015 | 2434374 | 7279400 | 7156500 | 3889000 | 1806545 | 2384940 | 800928 | 0 | 120000 | 1021666 | 1751952 | 305344 | 452150 | 422496 | 244260 | 816900 | 465930 | 3032640 | 1011840 | 1254435 | 457452 | 1900 | 1074000 | 1751102 | 1098000 | 1027000 | 3543463 | 4677567 | 1429000 | 1821120 | 960480 | 0 | 0 | 1099160 | 213120 | 7634500 | 540984 | 220464 | 721920 | 6212506 | 111645 | 407769 | 3609600 | 675674 | 0 |  | 11149818 | 166000 | 5814720 | 1166880 | 1824000 | 3811200 | 0 | 375560 | 108000 | 629376 | 770250 | 4618053 | 601716 | 1944000 | 35020 | 0 | 0 | 836704 | 336722 | 1845938 | 901140 | 966608 | 560700 | 754080 | 0 | 413520 | 212220 | 228880 | 0 | 0 | 3665300 | 155000 | 174000 | 0 | 3738681 | 0 | 3580736 | 2303004 | 600000 | 0 | 0 |  | 165780865 | 54287826 | 220068691 | 74689598 | 11149818 | 43421928 | 54471464 | 3665300 | 3862129 | 25773914 | 3032640 | 1900 | 0
Fuel Cost | 1111120 | 2357913.6 | 0 | 0 | 4331985.28 | 971723.79 | 868138.88 | 5262592 | 3958290 | 11259076 | 0 | 5846588.17 | 90261957.24 | 11695872 | 11703039.36 | 7233219.63 | 1128589.8 | 0 | 0 | 9007372.8 | 10770000 | 10951947.36 | 14370393.6 | 9998969.89 | 10805001.6 | 9408356.1 | 5981549.28 | 8442205.2 | 7976656.25 | 6378232.74 | 340875 | 450000 | 0 | 0 | 0 | 8902465.44 | 0 | 0 | 0 | 0 | 0 | 3039301.8 | 0 | 67934070.75 | 0 | 37819113.92 | 0 | 8872977.6 | 4397261.76 | 8690427.34 | 11488887.6 | 15026476.8 | 6915657.6 | 371565.6 | 0 | 1376427.78 | 513253.65 | 2215280.34 | 4513228 | 4937985 | 2722300 | 1246516.05 | 2289542.4 | 536621.76 | 0 | 110400 | 837766.12 | 1664354.4 | 3309928.96 | 3354953 | 325321.92 | 183195 | 629013 | 349447.5 | 20743257.6 | 758880 | 11528257.65 | 352238.04 | 0 | 1116960 | 1821146.08 | 1054080 | 924300 | 2763901.14 | 3274296.9 | 1629060 | 1948598.4 | 1056528 | 0 | 0 | 1022218.8 | 198201.6 | 4886080 | 405738 | 167552.64 | 12510873.6 | 45102793.56 | 1934807.85 | 6952461.45 | 25808640 | 11520241.7 | 0 |  | 56864071.8 | 4838900 | 3895862.4 | 9346708.8 | 15120960 | 61284096 | 0 | 5993937.6 | 1216080 | 7414049.28 | 6069570 | 3186456.57 | 595698.84 | 14385600 | 1179473.6 | 0 | 0 | 9580260.8 | 3609659.84 | 16539604.48 | 7794861 | 8602811.2 | 5971455 | 7480473.6 | 0 | 454872 | 199486.8 | 173262.16 | 0 | 0 | 14148058 | 4995650 | 4657980 | 0 | 0 | 0 | 52493589.76 | 0 | 10398000 | 0 | 0 |  | 626926519.67 | 338491489.53 | 965418009.2 | 52727710.42 | 56864071.8 | 30607742.99 | 480025173.3 | 14148058 | 0 | 310301995.09 | 20743257.6 | 0 | 0
Yesterday Day Peak | 64 | 120 | 0 | 0 | 290 | 26 | 30 | 345 | 246 | 26 | 0 | 380 | 200 | 100 | 64 | 55 | 70 | 0 | 0 | 22 | 93 | 84 | 50 | 87 | 82 | 0 | 40 | 54 | 55 | 36 | 22 | 25 | 25 | 33 | 25 | 50 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 217 | 0 | 70 | 0 | 40 | 0 | 31 | 80 | 92 | 44 | 19 | 4 | 100 | 0 | 100 | 290 | 294 | 184 | 73 | 100 | 20 | 0 | 5 | 45 | 85 | 0 | 34 | 16 | 11 | 33 | 22 | 132 | 40 | 32 | 20 | 0 | 40 | 73 | 53 | 47 | 163 | 208 | 60 | 84 | 46 | 0 | 0 | 46 | 9 | 290 | 23 | 11 | 0 | 301 | 0 | 0 | 160 | 0 | 150 |  | 468 | 0 | 235 | 51 | 96 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 19 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 43 | 0 | 43 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 151 | 0 | 152 | 95 | 0 | 0 | 0 |  | 8979 | DayPeak
Yesterday Evening Peak | 61 | 120 | 0 | 0 | 330 | 20 | 30 | 340 | 242 | 98 | 0 | 380 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 60 | 93 | 102 | 149 | 87 | 87 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 87 | 80 | 0 | 0 | 16 | 0 | 227 | 0 | 100 | 0 | 37 | 40 | 56 | 80 | 104 | 50 | 19 | 27 | 0 | 120 | 100 | 300 | 301 | 207 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 49 | 8 | 19 | 11 | 33 | 22 | 120 | 44 | 95 | 20 | 0 | 68 | 74 | 53 | 50 | 130 | 190 | 54 | 86 | 47 | 0 | 0 | 46 | 9 | 290 | 23 | 0 | 170 | 302 | 9 | 73 | 163 | 100 | 150 |  | 458 | 32 | 220 | 81 | 92 | 232 | 0 | 55 | 49 | 75 | 33 | 186 | 38 | 110 | 12 | 0 | 0 | 51 | 38 | 101 | 50 | 43 | 45 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 16 | 15 | 0 | 214 | 0 | 220 | 95 | 97 | 0 | 0 |  | 10975 | EvPeak
Forecast for Evening | 65 | 120 | 0 | 0 | 330 | 85 | 50 | 412 | 360 | 110 | 0 | 450 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 100 | 93 | 102 | 149 | 88 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 135 | 0 | 51 | 48 | 68 | 80 | 104 | 50 | 19 | 20 | 0 | 120 | 100 | 360 | 360 | 225 | 73 | 100 | 43 | 0 | 53 | 51 | 85 | 50 | 52 | 19 | 11 | 33 | 22 | 167 | 100 | 95 | 20 | 0 | 68 | 74 | 53 | 50 | 163 | 240 | 60 | 86 | 50 | 0 | 0 | 45 | 10 | 341 | 23 | 11 | 170 | 300 | 0 | 100 | 163 | 100 | 150 |  | 473 | 48 | 250 | 90 | 115 | 225 | 0 | 55 | 50 | 75 | 40 | 194 | 33 | 110 | 30 | 0 | 0 | 51 | 38 | 100 | 50 | 43 | 45 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 210 | 16 | 18 | 0 | 214 | 0 | 220 | 98 | 97
Forecast for Day | 65 | 120 | 0 | 0 | 300 | 85 | 50 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 81 | 55 | 70 | 0 | 0 | 100 | 93 | 102 | 149 | 88 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 100 | 0 | 51 | 48 | 68 | 80 | 98 | 50 | 19 | 10 | 0 | 100 | 100 | 360 | 360 | 225 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 33 | 22 | 122 | 100 | 95 | 20 | 2 | 68 | 74 | 53 | 50 | 163 | 240 | 60 | 86 | 50 | 0 | 0 | 45 | 10 | 341 | 23 | 11 | 0 | 300 | 0 | 50 | 150 | 0 | 150 |  | 473 | 0 | 250 | 50 | 115 | 225 | 0 | 0 | 36 | 70 | 40 | 194 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 45 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 210 |  | 18 | 0 | 214 | 0 | 130 | 98 | 97
Generation at 08:00(Today) | 37 | 120 | 0 | 0 | 330 | 25 | 50 | 355 | 312 | 0 | 0 | 370 | 200 | 7 | 14 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 89 | 0 | 33 | 18 | 18 | 17 | 19 | 25 | 31 | 33 | 33 | 0 | 0 | 87 | 80 | 0 | 0 | 0 | 0 | 226 | 0 | 50 | 0 | 24 | 0 | 0 | 80 | 19 | 24 | 19 | 10 | 0 | 100 | 100 | 300 | 294 | 199 | 73 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 20 | 103 | 34 | 8 | 17 | 0.4 | 68 | 74 | 53 | 50 | 100 | 219 | 55 | 86 | 45 | 0 | 0 | 44 | 9 | 310 | 23 | 11 | 0 | 285 | 0 | 0 | 0 | 0 | 150 | 0 | 470 | 0 | 275 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 24 | 191 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 43 | 0 | 8 | 0 | 21 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7971.5 | 7:00
| Highest Generation |  | 10975 | 21:00
| Day Peak Generation |  | 8979 | 12:00
| Evening Peak Generation |  | 10975 | 21:00
| HVDC Max Flow |  | 468 | 8:00
| HVDC EvPeak Flow |  | 458 | 21:00
| Load factor L.F |  | 83.55%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-07-11
Till now the maximum generation is : - |  |  | 11059 | 20:00 | Hrs on | 2018-07-07
The Summary of Yesterday's |  | 2018-07-10 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8979 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 7856.4 | MW
Evening Peak Generation : |  | 10975 | MW Hour : | 21:00 | Available Max Generation : |  | 12122 | MW
E.P. Demand (at gen end) : |  | 10975 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11300 | MW
Maximum Generation : |  | 10975 | MW Hour : | 21:00 | Reserve(Generation end) |  | 822 | MW
Total Gen. (MKWH) : |  | 220.0687 | System Load Factor : | 83.55% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -770 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-07-11
Actual : | 104.76 | Ft.(MSL) , | Rule curve : | 85.6 | Ft.( MSL )
Gas Consumed : | Total = | 988.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 83335453.41
|  | Coal : | 14148058 | Oil : | 790327168.39 | Total : | 887810679.8
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4007.7863 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1363.303 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1221.5516 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1103.8024 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 997.4751 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 804.9282 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 449.5179 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 207.2326 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 620.8033 |  |  | 0 | 0%
Total | 0 |  | 10776.4006 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
|  |  |  | 3) Ghorasal Unit-4,5 |  | 12) Santahar Peaking
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Ashuganj-Sirajganj 230 KV Ckt-2 tripped at 08:20 from both ends showing Dist Z1 3-phase at both sides
and was switched on at 16:27.
b) Amnura 132 kV bay of Chapainawabganj 100 MW PP was under shut down from 10:03 to 10:55 for relay
installation.
c) Bibiyana 230 kV dia-5 was under shut down from 13:31 for D/W.
d) Amnura 132 kV bay of Amnura 50 MW PP was under shut down from 13:14 to 13:47 for relay
installation.
e) Ashuganj-Kishoreganj 132 kV Ckt-1 tripped at 14:42 showing no relay and was switched on at 15:28.
f) Ashuganj-B.Baria 132 kV Ckt-2 tripped at 14:42 showing no relay and was switched on at 15:28.
g) Ashuganj-Shahjibazar 132 kV Ckt tripped at 14:42 showing no relay and was switched on at 15:28.
h) Ashuganj-Ghorasal 132 kV Ckt-1 tripped at 14:42 showing no relay and was switched on at 15:35.
i) Ashuganj bus-2 tripped at 14:42 showing no relay and was switched on at 15:46.
j) Maniknagar 132/33 kV T1 transformer associated 33 kV bus was under shut down from 14:32 to 15:46 for red
hot maintenance at Y-phase DS.
k) Mongla 132/33 kV T1 transformer was under shut down from 17:45 to 18:05 for maintenance. |  |  |  | About 15 MW Power interruption occurred under Mongla S/S
area from 17:45 to 18:05.
l) Ashuganj 225 MW ST tripped at 14:43 due to 132 kV bus-B failure and was synchronized at 19:26.
m) Ashuganj ST Unit-3 tripped at 14:53 due to auxiliary power fail and was synchronized at 17:54 again
tripped at 18:36.
n) Ashuganj Unit-4 was synchronized at 18:03.
o) Natore 132/33 kV T3 transformer LT was under shut down from 20:15 to 21:08 for red hot maintenance |  |  |  | About 26 MW Power interruption occurred under Natore S/S
at Y-phase CT connector. |  |  |  | area from 20:15 to 21:08 .
p) Siddhirganj 132/33 kV T2 transformer was shut down at 06:00 to 08:40(11/07/2018) for C/M. |  |  |  | About 15 MW Power interruption occurred under Siddhirganj S/S
area from 06:00 to 08:40(11/07/2018).
q) Jamalpur United-Jamalpur S/S 132 kV Ckt-1 & 2 tripped at 07:43(11/07/2018) showing dist O/C and were |  |  |  | About 26 MW Power interruption occurred under Sherpur S/S
switched on at 07:57. At the same time Jamalpur 200 MW P/S got tripped due to tripping of above lines. |  |  |  | area from 07:43 to 07:57.
r) Mymensingh 132/33 kV T1 & T2 transformers tripped at 07:40(11/07/2018) showing O/C and were |  |  |  | About 112 MW Power interruption occurred under Mymensingh S/S
switched on at 08:01. |  |  |  | area from 07:40 to 08:01(11/07/2018).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-07-10 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 61 | 1292000 | Gas shortage
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2741760 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 330 | 6768727 | Gas shortage
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 30 | 923552 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 20 | 1199659 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8627200 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 98 | 1171600 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 242 | 6489000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 380 | 8726251 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1862400
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 5942196
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 81 | 1751952
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1183833
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 87 | 1569697 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 454500
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 60 | 578880 | Low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 93 | 1723200 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 70 | 1736292 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 588390
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1661904
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 896784 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1184040
25 | ACE Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1486080
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1276265
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1017262
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 87 | 1803840 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1269420 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 815800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 751400
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 51 | 941064
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 302 | 6212506
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 9 | 111645
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 73 | 407769
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 675674
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 0 | 150 | 0
| Dhaka area Total |  |  |  | 5399 | 3895 | 75842542
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 320940 | Engine problem
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 50 | 1057440
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 3862129 | # 5 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 227 | 4976855 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 1726112
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 37 | 1009440
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 40 | 408288
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 56 | 893158
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1856040 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 437136
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 27 | 456000
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 104 | 2326080 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 923 | 19329618
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 1512558 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 120 | 564015 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2434374 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 207 | 3889000 | FGMO
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7279400 | FGMO
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 301 | 7156500 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 43 | 800928
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 73 | 1806545
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 1021666
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1751952
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 49 | 305344
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2384940 | ST S/D
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 422496
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244260
** | Tripura |  | Imported power | 0 | 160 | 120 | 3032640 | Low demand
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816900
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 8 | 452150 | Low demand
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 465930
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 170 | 721920 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1817 | 37183518
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 44 | 1011840 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 457452
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1254435
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 1900
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 163 | 3609600
| Mymensingh Area Total |  |  |  | 522 | 322 | 6335227
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 68 | 1074000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 74 | 1751102
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3543463
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 190 | 4677567
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1098000
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1027000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 0 | 220464 | Machine tripped.
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 54 | 1429000 | FGMO
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1821120
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 960480
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 0 | Under maint.
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 1099160
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 540984
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 290 | 7634500 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 213120
| Sylhet Area Total |  |  |  | 1549 | 1120 | 27089960
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 32 | 166000
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 458 | 11149818
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 81 | 1166880 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 92 | 1824000
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 49 | 108000
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 232 | 3811200
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 75 | 629376
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 220 | 5814720 | Gas shortage
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 33 | 770250
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 55 | 375560
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 97 | 600000
| Khulna Area Total |  |  |  | 1769 | 1424 | 26415804
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1944000
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 12 | 35020 | Low demand
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 38 | 601716
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 186 | 4618053
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 2303004
| Barisal Area Total |  |  |  | 462 | 441 | 9501793
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 51 | 836704
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 38 | 336722
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 901140
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 966608 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 560700
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 0 | FGMO
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 413520
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 9 | 212220
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 228880
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 754080
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 101 | 1845938
| Rajshahi Area Total |  |  |  | 1123 | 852 | 7056512
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 150 | 3665300
120 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 155000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 15 | 174000
| Rangpur Area Total |  |  |  | 484 | 181 | 3994300
| Total |  |  |  | 15410 | 10975 | 212749274
| Eastern Grid Total |  |  |  | 11572 | 8077 | 165780865
| Western Grid Total |  |  |  | 3838 | 2898 | 46968409
| National Grid Total |  |  |  | 15410 | 10975 | 212749274
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-07-10 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7119 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3337 | MW
i) Dhaka area |  |  | 3962 | MW | i) Khulna area |  |  | 1331 | MW
ii) Chittagong area |  |  | 1034 | MW | ii) Rajshahi area |  |  | 1112 | MW
iii) Comilla area |  |  | 968 | MW | iii) Barisal area |  |  | 278 | MW
iv) Mymensingh area |  |  | 738 | MW | iv) Rangpur area |  |  | 616 | MW
v) Sylhet area |  |  | 417 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10456 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 900 | Kishorganj | 94 | 2200 | Goalpara | 38 | 2100
Munsiganj | 110 | 2100 | Netrokona | 82 | 2200 | Central s/s | 72 | 2100
Sonargaon | 53 | 2100 | Jamalpur | 114 | 2200 | Noapara | 90 | 1930
Shyampur | 170 | 1700 | Sherpur | 80 | 2300 | Jessore | 140 | 1930
Bhulta | 175 | 2100 | Srimongal | 36 | 1900 | Jhenida | 98 | 2000
Madanganj | 61 | 2100 | Shahjibazar | 96 | 2000 | Bottail | 126 | 2000
Shitalakhya | 112 | 1100 | Fenchuganj | 44 | 2000 | G.K Project | 54 | 2100
Rahim steel | 7 | 700 | Kulawara | 41 | 2100 | Faridpur | 142 | 2200
Matuail | 92 | 1000 | Sylhet | 134 | 1900 | Madaripur | 139 | 2100
Ghorasal | 78 | 2200 | Chatak | 27 | 1930 | Gopalganj | 83 | 2200
Narsingdi | 126 | 2100 | Sunamganj | 34 | 2100 | Bagerhat | 85 | 2000
Haripur (SBU) | 89 | 2300 | Biani Bazar | 44 | 2000 | Mongla | 36 | 100
Ullon | 93 | 2100 | Comilla (S) | 148 | 1600 | Satkhira | 91 | 1930
Hasnabad | 205 | 2100 | Comilla(N) | 133 | 1930 | Gallamari | 42 | 100
Magbazar | 138 | 1700 | Chandpur | 118 | 2000 | Magura | 50 | 1930
Maniknagar | 100 | 1200 | Feni | 126 | 2000 | Chuadanga | 76 | 2100
Bangabhaban | 40 | 1300 | Chowmuhani | 186 | 2000 | Barisal | 118 | 2000
Narinda | 94 | 1700 | Ashuganj | 57 | 2300 | Patuakhali | 91 | 2100
Dhanmondi | 110 | 1600 | Daudkandi | 100 | 2100 | Bhandaria | 48 | 2200
Lalbag | 94 | 2100 | B.Baria | 131 | 2200 | Ishurdi | 55 | 2100
Madartek | 51 | 1600 | Ramganj | 30 | 1930 | Ruppur Paromanobik | 2 | 1400
Mirpur | 108 | 1600 | Madunaghat | 63 | 2000 | Natore | 110 | 2000
Kalyanpur | 120 | 1500 | Hathazari | 88 | 2300 | Bogra | 237 | 2100
Gulshan | 142 | 1930 | Khulshi | 202 | 1600 | Noagaon | 102 | 2100
Uttara | 95 | 1600 | Halishahar | 135 | 1600 | Rajshahi | 151 | 2100
Kamrangirchar | 76 | 1500 | Baraulia | 137 | 2400 | C.Nawabganj | 71 | 2000
Savar | 140 | 1200 | Sikalbaha | 36 | 2100 | Amnura | 43 | 2000
Bhasantec | 158 | 1300 | Dohazari | 84 | 2100 | Pabna | 115 | 2000
Agargaon | 49 | 2000 | Cox'sbazar | 86 | 2100 | Shahjadpur | 87 | 2100
Satmosjid | 97 | 1100 | Chandraghona | 33 | 2000 | Serajganj | 85 | 2100
Tongi | 136 | 1200 | Kaptai | 4 | 2100 | Niyamatpur | 56 | 2100
Kabirpur | 213 | 1500 | A. Khaer Stl. | 13 | 900 | Joypurhat | 39 | 100
Basundhara | 127 | 2100 | Bakulia | 106 | 2100 | Rangpur | 117 | 1930
Manikganj | 107 | 2100 | Julda | 17 | 1100 | Lalmonirhat | 79 | 2000
Joydevpur | 238 | 1700 | TK chemical | 3 | 1600 | Saidpur | 100 | 2000
New Tongi | 116 | 2100 | Modern Steel | 13 | 2100 | Purbasadipur | 89 | 2000
Korda | 253 | 2100 | Shahmirpur | 30 | 2100 | Thakurgaon | 65 | 2000
Dhamrai | 23 | 2200 | Abul Khair 230 | 192 | 1100 | Palashbari | 103 | 700
Tangail | 173 | 2100 | BSRM | 112 | 1000 | Barapukuria | 45 | 2100
Mymensing | 238 | 2100 | Khagrachhari | 17 | 1900 | Panchagar | 38 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-07-10
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 404 | 7:00 | 394 | 20:00 | Kaliakoir | 396 | 18:00 | 383 | 10:00
Bheramara | 229 | 2:00 | 222 | 8:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 223 | 15:00 | 215 | 9:00
Ishurdi | 232 | 9:00 | 221 | 20:00 | Comilla (N) | 230 | 5:00 | 224 | 10:00
Ashuganj | 235 | 15:00 | 232 | 1:00 | Hathazari | 221 | 6:00 | 211 | 16:00
Serajganj | 225 | 7:00 | 214 | 23:00 | Megnaghat | 229 | 24:00 | 221 | 11:00
Baghabari | 222 | 7:00 | 217 | 1:00 | Fenchuganj | 238 | 6:00 | 230 | 18:30
Barapukuria | 231 | 18:00 | 220 | 20:00 | Siddhirganj | 225 | 1:00 | 220 | 9:00
Bogra | 220 | 18:30 | 201 | 21:00 | Maniknagar | 223 | 1:00 | 217 | 10:00
Khulna South | 241 | 17:00 | 229 | 20:00 | Old Airport | 224 | 2:00 | 217 | 10:00
Rampura | 222 | 4:00 | 218 | 10:00 | Barisal | 231 | 7:00 | 221 | 21:00
Haripur | 223 | 24:00 | 220 | 8:00 | AKSML | 218 | 5:00 | 209 | 21:00
Hasnabad | 225 | 1:00 | 220 | 9:00 | BSRM | 222 | 5:00 | 214 | 1:00
Aminbazar | 225 | 24:00 | 219 | 11:00 | Bibiyana | 233 | 5:00 | 228 | 18:30
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 2000 | 131 | 800 | B.Baria | 138 | 700 | 128 | 1900
Munsiganj | 136 | 1600 | 131 | 600 | Ramganj | 130 | 1000 | 119 | 2200
Megnaghat | 134 | 1800 | 130 | 1600 | Madanhat | 132 | 400 | 129 | 1300
Shyampur | 133 | 2000 | 125 | 1400 | Hathazari | 130 | 600 | 125 | 1600
Bhulta | 131 | 400 | 121 | 1100 | Khulshi | 128 | 700 | 123 | 1100
Madanganj | 138 | 100 | 129 | 800 | Halishahar | 130 | 400 | 125 | 1400
Shitalakhya | 140 | 2000 | 131 | 800 | Baraulia | 128 | 600 | 125 | 100
Rahim steal | 135 | 100 | 132 | 500 | Sikalbaha | 131 | 700 | 126 | 1600
Matuail | 134 | 200 | 129 | 1000 | Dohazari | 128 | 500 | 123 | 2100
Ghorasal | 138 | 1400 | 134 | 1830 | Cox'sbazar | 124 | 600 | 113 | 2100
Narsinghdi | 132 | 1600 | 126 | 1200 | Chandraghona | 131 | 600 | 128 | 100
Haripur (SBU) | 135 | 1900 | 131 | 100 | Kaptai | 130 | 2400 | 128 | 1900
Ullon | 134 | 600 | 128 | 1200 | A. Khaer Stl. | 128 | 600 | 124 | 1200
Hasnabad | 137 | 100 | 130 | 1700 | Bakulia | 129 | 600 | 125 | 1100
Magbazar | 135 | 600 | 127 | 1200 | Julda | 130 | 600 | 126 | 1500
Maniknagar | 134 | 600 | 130 | 1200 | TK Chemical | 133 | 600 | 128 | 2200
Bangabhaban | 134 | 600 | 130 | 1200 | Modern Steel | 128 | 300 | 125 | 1000
Narinda | 134 | 600 | 130 | 1200 | Shahmirpur | 129 | 700 | 126 | 1300
Dhanmondi | 134 | 600 | 128 | 1200 | Khagrachhari | 130 | 600 | 127 | 2100
Lalbag | 137 | 2100 | 127 | 1200 | Goalpara | 138 | 1700 | 131 | 2000
Madartek | 134 | 600 | 128 | 1200 | Central s/s | 138 | 1900 | 121 | 500
Mirpur | 134 | 300 | 130 | 1000 | Noapara | 137 | 1900 | 128 | 2000
Kalyanpur | 136 | 300 | 131 | 1000 | Jessore | 130 | 900 | 122 | 19300
Gulshan | 133 | 300 | 127 | 1000 | Jhenida | 129 | 900 | 117 | 2100
Uttara | 133 | 500 | 126 | 1200 | Bottail | 135 | 1700 | 127 | 2100
Kamrangirchar | 136 | 100 | 129 | 800 | G.K.Project | 141 | 1830 | 135 | 2000
Savar | 134 | 500 | 128 | 1000 | Faridpur | 133 | 700 | 123 | 2100
Bhasantec | 133 | 400 | 127 | 1000 | Madaripur | 134 | 700 | 123 | 2100
Agargaon | 133 | 200 | 128 | 1000 | Gopalganj | 136 | 100 | 125 | 1500
Satmosjid | 133 | 200 | 127 | 1000 | Bagerhat | 136 | 1700 | 128 | 2000
Tongi | 134 | 1500 | 127 | 900 | Mongla | 134 | 1800 | 126 | 2000
Kabirpur | 134 | 400 | 129 | 2100 | Satkhira | 135 | 1800 | 127 | 2100
Basundhara | 132 | 300 | 125 | 1300 | Gallamari | 137 | 1800 | 131 | 500
Manikganj | 137 | 1700 | 133 | 2100 | Magura | 130 | 1800 | 115 | 1930
Joydevpur | 140 | 1400 | 128 | 1830 | Chuadanga | 127 | 1700 | 109 | 2000
New Tongi | 135 | 2400 | 127 | 1000 | Barisal | 138 | 700 | 133 | 2100
Kodda | 139 | 2100 | 127 | 2400 | Patuakhali | 135 | 100 | 125 | 2000
Dhamrai | 134 | 400 | 129 | 1930 | Bhandaria | 135 | 700 | 128 | 2100
Tangail | 135 | 1700 | 125 | 2100 | Ishurdi | 140 | 1700 | 133 | 1930
Mymensing | 129 | 1600 | 116 | 2100 | Ruppur Paromanobik | 140 | 1800 | 130 | 1300
Kishorganj | 130 | 700 | 118 | 2000 | Natore | 139 | 1500 | 127 | 1930
Netrokona | 130 | 400 | 117 | 2000 | Bogra | 134 | 1800 | 119 | 1930
Jamalpur | 133 | 1100 | 125 | 2000 | Noagaon | 126 | 1800 | 108 | 2100
Sherpur | 134 | 1500 | 124 | 2100 | Rajshahi | 137 | 1830 | 126 | 1930
Srimongal | 140 | 600 | 132 | 2000 | C.Nawabganj | 138 | 1800 | 125 | 1200
Shahjibazar | 139 | 900 | 130 | 1900 | Amnura | 140 | 1500 | 126 | 1200
Fenchuganj | 137 | 600 | 131 | 1930 | Pabna | 135 | 1800 | 125 | 1930
Khulawara | 136 | 600 | 130 | 2000 | Shahjadpur | 140 | 1830 | 132 | 1930
Sylhet | 135 | 600 | 128 | 1900 | Serajganj | 133 | 1900 | 121 | 2100
Chatak | 134 | 600 | 125 | 2000 | Niyamatpur | 124 | 1800 | 103 | 2100
Sunamganj | 129 | 1000 | 125 | 2100 | Joypurhat | 125 | 1800 | 109 | 2100
Biani Bazar | 135 | 700 | 125 | 2000 | Rangpur | 118 | 1830 | 100 | 2000
Comilla(s) | 126 | 1100 | 123 | 1900 | Lalmonirhat | 115 | 1800 | 90 | 2100
Comilla(n) | 135 | 700 | 132 | 1300 | Saidpur | 117 | 1800 | 96 | 2000
Chandpur | 127 | 1830 | 123 | 2100 | Purbasadipur | 130 | 1800 | 112 | 100
Feni | 121 | 700 | 115 | 2200 | Thakurgaon | 120 | 700 | 100 | 2000
Chowmuhani | 124 | 700 | 114 | 2100 | Palashbari | 122 | 1800 | 100 | 100
Ashuganj | 138 | 800 | 130 | 1700 | Barapukuria | 131 | 1800 | 120 | 2000
Daudkandi | 138 | 1930 | 128 | 800 | Panchagar | 118 | 900 | 96 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-07-10
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 680 | 7977 | 2594 | 10571 |  |  |  | QF-LDC-12
0:30 | 680 | 7710 | 2558.5 | 10268.5 | Date: | 2018-07-10
1:00 | 680 | 7443 | 2523 | 9966
1:30 | 700 | 7417.5 | 2435 | 9852.5
2:00 | 720 | 7392 | 2347 | 9739
2:30 | 710 | 7248.5 | 2308 | 9556.5 | [5 empty] | Gen. at Eve. Peak | 10975 | 10975 MW (21:00 )
3:00 | 700 | 7105 | 2269 | 9374 | [6 empty] | 21:00
3:30 | 730 | 7018.5 | 2230 | 9248.5 | [5 empty] | Gen. at Day Peak | 8979 | 8979 MW (12:00 )
4:00 | 760 | 6932 | 2191 | 9123 | [6 empty] | 12:00
4:30 | 765 | 6852 | 2120 | 8972 | [5 empty] | Highest Generation | 10975
5:00 | 770 | 6772 | 2049 | 8821 | [6 empty] | 21:00
5:30 | 735 | 6462.5 | 1964.5 | 8427
6:00 | 700 | 6153 | 1880 | 8033
6:30 | 670 | 6148.25 | 1854 | 8002.25
7:00 | 640 | 6143.5 | 1828 | 7971.5
7:30 | 590 | 6162.55 | 1826.5 | 7989.05
8:00 | 540 | 6181.6 | 1825 | 8006.6
8:30 | 510 | 6278.8 | 1858 | 8136.8
9:00 | 480 | 6376 | 1891 | 8267
9:30 | 500 | 6568 | 1869.5 | 8437.5
10:00 | 520 | 6760 | 1848 | 8608
10:30 | 470 | 6782.5 | 1912.5 | 8695
11:00 | 420 | 6805 | 1977 | 8782
11:30 | 465 | 6890.5 | 1990 | 8880.5
12:00 | 510 | 6976 | 2003 | 8979
12:30 | 515 | 6970 | 2050 | 9020
13:00 | 520 | 6964 | 2097 | 9061
13:30 | 510 | 6897 | 2099.5 | 8996.5
14:00 | 500 | 6830 | 2102 | 8932
14:30 | 480 | 6932 | 2132 | 9064
15:00 | 460 | 7034 | 2162 | 9196
15:30 | 390 | 6913 | 2214.5 | 9127.5
16:00 | 320 | 6792 | 2267 | 9059
16:30 | 280 | 6722.1 | 2273 | 8995.1
17:00 | 240 | 6652.2 | 2279 | 8931.2
17:30 | 150 | 6418.2 | 2229.5 | 8647.7
18:00 | 60 | 6184.2 | 2180 | 8364.2
18:30 | 210 | 6595.6 | 2338 | 8933.6
19:00 | 360 | 7007 | 2496 | 9503
19:30 | 640 | 7870 | 2767 | 10637
20:00 | 680 | 8051 | 2861 | 10912 |  |  |  | Executive Engineer
20:30 | 680 | 8064 | 2879.5 | 10943.5 |  |  |  | Network Operation Division
21:00 | 680 | 8077 | 2898 | 10975
21:30 | 680 | 8027 | 2886 | 10913
22:00 | 680 | 7977 | 2874 | 10851 |  |  |  |  | Page 6 of 7
22:30 | 680 | 8009.5 | 2752 | 10761.5
23:00 | 680 | 8042 | 2630 | 10672
23:30 | 680 | 8009.5 | 2612 | 10621.5
24:00 | 680 | 7977 | 2594 | 10571
10975 MW (21:00 )
8979 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-07-10 |  | Energy | 220068691
[10 empty] | 2018-07-10 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3190 | 467 | 1904 | 3141 | 150 | 162 | 1429 | 0 | 128
0:30 | 3158 | 467 | 1920.5 | 2934.5 | 150 | 162 | 1346.5 | 0 | 130 | Date: | 2018-07-10
1:00 | 3126 | 467 | 1937 | 2728 | 150 | 162 | 1264 | 0 | 132
1:30 | 3124.5 | 467 | 1955.5 | 2656 | 150 | 162 | 1206.5 | 0 | 131 | [7 empty] | Total Energy | 220.0687 | Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
2:00 | 3123 | 467 | 1974 | 2584 | 150 | 162 | 1149 | 0 | 130 | [7 empty] | Energy not Served | 0
2:30 | 3123 | 467 | 2016 | 2454 | 150 | 162 | 1056.5 | 0 | 128 | [7 empty] | Energy Requirement | 220.0687
3:00 | 3123 | 467 | 2058 | 2324 | 150 | 162 | 964 | 0 | 126
3:30 | 3114 | 467 | 2061 | 2224.5 | 150 | 162 | 949 | 0 | 121 | [6 empty] | Shortage
4:00 | 3105 | 467 | 2064 | 2125 | 150 | 162 | 934 | 0 | 116
4:30 | 3102.5 | 467 | 2065 | 2007.5 | 150 | 164 | 900 | 0 | 116
5:00 | 3100 | 467 | 2066 | 1890 | 150 | 166 | 866 | 0 | 116
5:30 | 3107 | 467 | 2069.5 | 1542.5 | 150 | 166 | 815 | 0 | 110
6:00 | 3114 | 467 | 2073 | 1195 | 150 | 166 | 764 | 0 | 104
6:30 | 3131 | 467 | 2060.5 | 1178.5 | 150 | 166.5 | 739.5 | 0 | 109 |  |  |  |  | Coal
7:00 | 3148 | 467 | 2048 | 1162 | 150 | 167 | 715 | 0 | 114
7:30 | 3197 | 467.5 | 1993.5 | 1178.5 | 150 | 167 | 722 | 0 | 113 |  |  |  | Oil |  |  |  | ,
8:00 | 3246 | 468 | 1939 | 1195 | 150 | 167 | 729 | 0 | 112
8:30 | 3156 | 468 | 1876 | 1439.5 | 150 | 167 | 767 | 0 | 113
9:00 | 3066 | 468 | 1813 | 1684 | 150 | 167 | 805 | 0 | 114
9:30 | 3114.5 | 468 | 1810.5 | 1841 | 150 | 163.5 | 769 | 0 | 121
10:00 | 3163 | 468 | 1808 | 1998 | 150 | 160 | 733 | 0 | 128
10:30 | 3134 | 468 | 1792 | 2098.5 | 150 | 163 | 761.5 | 0 | 128
11:00 | 3105 | 468 | 1776 | 2199 | 150 | 166 | 790 | 0 | 128
11:30 | 3111.5 | 468 | 1774.5 | 2291 | 150 | 165 | 790.5 | 0 | 130
12:00 | 3118 | 468 | 1773 | 2383 | 150 | 164 | 791 | 0 | 132
12:30 | 3075 | 468 | 1779 | 2412.5 | 149.5 | 165.5 | 839.5 | 0 | 131
13:00 | 3032 | 468 | 1785 | 2442 | 149 | 167 | 888 | 0 | 130
13:30 | 3032 | 468 | 1785 | 2442 | 149 | 167 | 888 | 0 | 130
14:00 | 3032 | 468 | 1785 | 2442 | 149 | 167 | 888 | 0 | 130
14:30 | 2949 | 468 | 1777.5 | 2523 | 149.5 | 166.5 | 956 | 0 | 139
15:00 | 2866 | 468 | 1770 | 2604 | 150 | 166 | 1024 | 0 | 148
15:30 | 2862.5 | 468 | 1626.5 | 2696.5 | 150 | 166 | 1010 | 0 | 148
16:00 | 2859 | 468 | 1483 | 2789 | 150 | 166 | 996 | 0 | 148
16:30 | 2886.5 | 468 | 1463 | 2693.5 | 150 | 165.5 | 1024.5 | 0 | 144
17:00 | 2914 | 468 | 1443 | 2598 | 150 | 165 | 1053 | 0 | 140
17:30 | 2908 | 463 | 1457 | 2354.5 | 150 | 158.5 | 1034.5 | 0 | 122
18:00 | 2902 | 458 | 1471 | 2111 | 150 | 152 | 1016 | 0 | 104
18:30 | 3011 | 458 | 1558.5 | 2332.5 | 150 | 158.5 | 1152 | 0 | 113
19:00 | 3120 | 458 | 1646 | 2554 | 150 | 165 | 1288 | 0 | 122
19:30 | 3169 | 457 | 1800 | 3193 | 150 | 165 | 1583 | 0 | 120
20:00 | 3201 | 458 | 1798 | 3303 | 150 | 167 | 1711 | 0 | 124
20:30 | 3216 | 458 | 1791 | 3323.5 | 150 | 167 | 1716 | 0 | 122
21:00 | 3231 | 458 | 1784 | 3344 | 150 | 167 | 1721 | 0 | 120
21:30 | 3213 | 458 | 1776 | 3345 | 150 | 167 | 1684 | 0 | 120
22:00 | 3195 | 458 | 1768 | 3346 | 150 | 167 | 1647 | 0 | 120
22:30 | 3200.5 | 458 | 1802.5 | 3280.5 | 150 | 164.5 | 1583.5 | 0 | 122
23:00 | 3206 | 458 | 1837 | 3215 | 150 | 162 | 1520 | 0 | 124
23:30 | 3198 | 462.5 | 1870.5 | 3178 | 150 | 162 | 1474.5 | 0 | 126 | Max Temp. in Dhaka |  | 32.8° C
24:00 | 3190 | 467 | 1904 | 3141 | 150 | 162 | 1429 | 0 | 128
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 165.409 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 165.409 MKWHr
Note on W13: Author:

## Generation
2018-07-10
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 82 | 82 | 82 | 82 | 86 | 86 | 87 | 87 | 87 | 80 | 86 | 84 | 87 | 88 | 86 | 86 | 85 | 72 |  | 85 | 85 | 87 | 87 | 87 | 82 | 82 | 1943029
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1919100
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 320940
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 202 | 202 | 200 | 200 | 201 | 201 | 202 | 217 | 211 | 219 | 205 | 217 | 203 | 209 | 205 | 202 | 202 | 203 |  | 217 | 217 | 227 | 227 | 227 | 226 | 226 | 4976855
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 100 | 70 | 70 | 70 | 70 | 70 | 135 | 50 | 50 | 50 |  | 100 | 135 | 135 | 100 | 50 | 135 | 135 | 1726112
| Dohazari Peaking | 51 | 59 | 28 | 28 | 28 | 17 | 17 | 16 | 16 | 16 | 26 | 31 | 31 | 31 | 31 | 31 | 58 | 55 |  | 55 | 55 | 56 | 56 | 56 | 57 | 47 | 893158
12 | Hathazari peaking | 48 | 48 | 24 | 24 | 9 | 0 | [11 empty] | 0 |  | 36 | 40 | 40 | 40 | 48 | 48 | 48 | 408288
| Daudkandi bangla trak | [14 empty] | 0 | 30 | 30 | 10 |  | 10 | 178 | 170 | 170 | 120 | 80 | 80 | 721920
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 46 | 50 | 49 | 49 | 49 | 49 | 49 | 305344
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1736292
18 | Summit Gazipur | 300 | 300 | 301 | 300 | 300 | 97 | 97 | 97 | 115 | 200 | 235 | 301 | 301 | 301 | 301 | 302 | 302 | 161 |  | 165 | 237 | 258 | 302 | 280 | 302 | 301 | 6212506
19 | Ashuganj 195MW Modular | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1806545
20 | Ghorasal ST: Unit-1,2 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 64 | 61 | 61 | 61 | 61 | 37 | 37 | 1292000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2741760
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 290 | 290 | 290 | 290 | 305 | 305 | 305 | 250 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 6768727
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 |  | 0 | 18 |  | 0 | [6 empty] | 1512558
29 | Ashuganj ST: Unit- 4 | [17 empty] | 0 |  | 50 | 105 | 115 | 120 | 120 | 100 | 100 | 564015
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 90 | 130 | 130 | 130 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2434374
32 | Ashuganj Engines TSK | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 22 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 20 | 20 | 800928
33 | Ashuganj CCPP 225 MW | 179 | 182 | 194 | 184 | 182 | 188 | 190 | 208 | 184 | 202 | 186 | 184 | 172 | 134 | 116 | 45 | 45 | 85 |  | 70 | 79 | 142 | 207 | 165 | 167 | 205 | 3889000
34 | Ashuganj CCPP(South) | 272 | 272 | 287 | 272 | 272 | 272 | 279 | 312 | 272 | 298 | 287 | 294 | 272 | 287 | 261 | 298 | 301 | 316 |  | 334 | 316 | 301 | 301 | 300 | 312 | 290 | 7156500
| Ashuganj CCPP(North) | 270 | 270 | 280 | 270 | 270 | 270 | 290 | 315 | 270 | 295 | 270 | 290 | 270 | 286 | 282 | 270 | 270 | 285 |  | 335 | 315 | 300 | 300 | 300 | 307 | 290 | 7279400
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2384940
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 395 | 380 | 345 | 350 | 350 | 350 | 350 | 365 | 380 | 350 | 370 | 345 | 354 | 355 | 392 | 345 | 355 | 320 |  | 330 | 351 | 360 | 340 | 340 | 360 | 365 | 8627200
40 | Meghnaghat CCPP 450MW | 390 | 410 | 450 | 450 | 450 | 450 | 450 | 400 | 400 | 380 | 380 | 380 | 380 | 380 | 360 | 360 | 360 | 360 |  | 360 | 360 | 360 | 380 | 380 | 380 | 400 | 8726251
41 | Haripur Power CCPP 360MW | 282 | 313 | 323 | 344 | 344 | 348 | 321 | 284 | 261 | 262 | 256 | 246 | 241 | 241 | 241 | 241 | 241 | 240 |  | 241 | 241 | 241 | 242 | 241 | 250 | 262 | 6489000
42 | Mymensingh RPCL 210MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 46 | 45 | 46 | 40 | 33 | 31 | 31 | 33 | 45 | 44 |  | 43 | 46 | 44 | 44 | 44 | 44 | 44 | 1011840
43 | Haripur NEPC 110MW | 110 | 55 | 0 | [6 empty] | 0 | 13 | 26 | 26 | 26 | 80 | 98 | 98 | 98 |  | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 1171600
44 | Fenchugonj CCPP-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 27 | 27 | 32 | 40 | 48 | 48 | 59 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 63 | 1074000
45 | Fenchugonj CCPP-2 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 72 | 72 | 72 | 73 | 73 |  | 75 | 75 | 75 | 74 | 74 | 74 | 74 | 1751102
46 | Shajibazar 330 MW | 190 | 198 | 190 | 200 | 200 | 200 | 201 | 217 | 192 | 206 | 187 | 208 | 190 | 200 | 190 | 200 | 192 | 200 |  | 214 | 203 | 190 | 190 | 196 | 216 | 200 | 4677567
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 61 | 61 | 61 | 61 | 61 | 60 | 60 | 50 | 62 | 60 | 60 | 60 | 60 | 60 | 58 | 60 | 60 |  | 60 | 60 | 60 | 54 | 61 | 60 | 60 | 1429000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 84 | 86 | 84 | 84 | 84 | 83 | 84 | 64 | 50 | 20 | 20 |  | 30 | 86 | 86 | 86 | 86 | 86 | 86 | 1821120
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 45 | 46 | 46 | 46 | 46 | 5 | 5 | 5 |  | 5 | 44 | 46 | 47 | 47 | 47 | 47 | 960480
50 | Sylhet GT 150 MW
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 47 | 46 | 45 | 46 | 45 | 46 | 44 | 46 | 45 | 45 |  | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 1099160
53 | Sylhet (Desh) 10MW | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 213120
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 5 | 11 | 11 |  | 11 | 11 | 11 | 0 | 0 | 11 | 11 | 220464
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 53 | 53 | 53 | 50 | 5 | 5 | 5 |  | 41 | 52 | 50 | 53 | 53 | 53 | 53 | 1098000
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 21 | 21 | 20 | 21 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 540984
57 | Summit Bibiana- 2 | 300 | 295 | 305 | 290 | 295 | 305 | 320 | 320 | 275 | 285 | 290 | 290 | 300 | 300 | 320 | 280 | 300 | 270 |  | 310 | 320 | 310 | 290 | 280 | 310 | 320 | 7634500
58 | Southern 55MW | 0 | 55 | 55 | 55 | 55 | 55 | 36 | 36 | 55 | 35 | 36 | 36 | 36 | 36 | 36 | 0 | 0 | 36 |  | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 1017262
59 | Sikalbaha (Energis) | 51 | 51 | 51 | 51 | 51 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 34 | 34 | 32 | 37 | 40 | 40 | 40 | 1009440
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 437136
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 454500
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 457452
63 | Tripura | 132 | 130 | 126 | 116 | 116 | 104 | 114 | 112 | 114 | 128 | 128 | 132 | 130 | 136 | 148 | 148 | 140 | 104 |  | 122 | 120 | 124 | 120 | 120 | 124 | 128 | 3032640
64 | Malancha, Ctg. EPZ (United) | 31 | 37 | 39 | 40 | 40 | 40 | 30 | 10 | 5 | 4 | 2 | 4 | 5 | 8 | 8 | 3 | 4 | 6 |  | 3 | 9 | 19 | 27 | 36 | 38 | 29 | 456000
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 422496
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244260
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816900
68 | Summit Comilla 25MW | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 19 | 0 | 20 | 22 | 22 | 22 | 21 | 12 | 21 | 21 | 0 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 32 | 31 | 30 | 25 | 30 | 30 | 30 | 30 | 9 | 9 |  | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 669420
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815800
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 0 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 751400
73 | Ghorashal (Regent) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 55 | 26 | 26 | 25 | 25 | 23 | 25 | 25 | 25 |  | 24 | 23 | 20 | 20 | 23 | 23 | 24 | 1199659
76 | Siddhirganj (Desh) | 34 | 0 | [7 empty] | 0 | 3 | 22 | 36 | 36 | 36 | 30 | 35 | 35 |  | 35 | 35 | 50 | 60 | 60 | 60 | 35 | 578880
77 | Siddhirganj (Dutch Bangla) | 93 | 93 | 84 | 84 | 84 | 7 | 7 | 7 | 20 | 75 | 75 | 93 | 93 | 93 | 93 | 93 | 50 | 20 |  | 22 | 50 | 65 | 93 | 93 | 93 | 93 | 1723200
78 | Gazipur (RPCL) | 42 | 46 | 29 | 25 | 8 | 8 | 8 | 8 | 22 | 40 | 38 | 50 | 50 | 34 | 34 | 46 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 941064
79 | ACE Kodda 149 MW | 149 | 115 | 32 | 32 | 16 | 16 | 16 | 16 | 48 | 48 | 64 | 50 | 48 | 16 | 16 | 16 | 16 | 16 |  | 16 | 90 | 149 | 149 | 149 | 149 | 149 | 1486080
80 | Jamalpur 95MW | 95 | 95 | 64 | 40 | 8 | 8 | 8 | 8 | 24 | 32 | 32 | 32 | 32 | 16 | 40 | 90 | 48 | 48 |  | 74 | 95 | 95 | 95 | 95 | 95 | 95 | 1254435
81 | Lakdhanvi 52 MW | 8 | 8 | 8 | 8 | 0 |  |  | 0 | 1 | 24 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 8 | 8 | 8 | 8 | 452150
82 | Madanganj 102MW | 97 | 97 | 97 | 97 | 70 | 30 | 15 | 30 | 30 | 55 | 65 | 64 | 64 | 64 | 64 | 80 | 81 | 80 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1751952
83 | Pagla (DPA ) | 50 | 10 | 10 | 10 | 10 | 0 | 0 | 10 | 51 | 11 | 11 | 0 | 0 | 10 | 50 | 50 | 51 | 10 |  | 51 | 51 | 51 | 51 | 51 | 50 | 51 | 588390
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 | 20 | 85 |  | 86 | 85 | 85 | 85 | 85 | 85 | 85 | 1751952
85 | Keraniganj (Powerpac) 100MW | 88 | 88 | 88 | 10 | 10 | 10 | 10 | 10 | 50 | 87 | 87 | 87 | 87 | 50 | 87 | 87 | 50 | 20 |  | 79 | 87 | 87 | 87 | 87 | 87 | 87 | 1569697
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 240 | 200 | 200 | 200 | 240 | 200 | 305 | 305 | 305 | 200 |  | 305 | 305 | 305 | 305 | 305 | 305 | 260 | 5942196
87 | Meghnaghat (IEL) | 100 | 100 | 100 | 65 | 30 | 7 | 7 | 7 | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 40 |  | 54 | 100 | 100 | 100 | 100 | 100 | 100 | 1862400
88 | Ghorashal 78MW (MAX) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 923552
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1856040
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 49 | 50 | 5 | 5 | 5 |  | 22 | 47 | 47 | 50 | 50 | 50 | 50 | 1027000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 0 | 35 | 45 | 45 | 45 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1021666
94 | Gagnagar (Orion) | 102 | 102 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 40 | 58 | 84 | 102 | 102 | 102 | 102 | 102 | 50 |  | 58 | 102 | 94 | 102 | 102 | 102 | 60 | 1661904
95 | Patenga 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 44 | 44 | 44 | 31 | 24 | 25 | 26 | 26 | 29 |  | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 1057440
96 | Chittagong ECPV 108 MW | 98 | 98 | 98 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 98 | 98 | 98 | 98 | 98 | 98 |  | 104 | 104 | 104 | 104 | 105 | 105 | 105 | 2326080
97 | Katpotti 51 MW | 40 | 40 | 40 | 40 | 40 | 12 | 12 | 12 | 21 | 40 | 40 | 40 | 40 | 39 | 39 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 896784
98 | Bosila 108MW | 80 | 80 | 80 | 80 | 80 | 8 | 8 | 8 | 82 | 82 | 82 | 82 | 90 | 89 | 88 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 88 | 89 | 1803840
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1183833
100 | Northern 55 MW | 55 | 55 | 55 | 56 | 56 | 36 | 37 | 37 | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1276265
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 100 | 100 | 100 |  | 163 | 163 | 163 | 130 | 100 | 130 | 163 | 3543463
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.5 | 0.6 | 0 | [6 empty] | 0 | 0.2 | 0.2 |  | 0 | [6 empty] | 1900
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 36 | 18 | 18 | 18 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1184040
104 | APR Energy , Keranigonj | [19 empty] | 0 | 0 | 28 | 9 | 74 | 0 | 0 | 111645
105 | Bramhangoan 100 MW (Aggreko) | [13 empty] | 0 | 8 | 10 | 10 | 10 |  | 11 | 73 | 73 | 73 | 70 | 71 | 70 | 407769
106 | United Mymensingh PPL | 156 | 156 | 163 | 163 | 163 | 100 | 100 | 100 | 132 | 139 | 160 | 160 | 153 | 158 | 156 | 156 | 158 | 161 |  | 163 | 163 | 163 | 163 | 163 | 160 | 163 | 3609600
112 | Aggreko Aurahati 100MW | [13 empty] | 0 | 26 | 72 | 30 | 0 |  | 0 | 90 | 100 | 100 | 100 | 100 | 100 | 675674
114 | Summit Gazipur-1 150MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150
115
116
117
118
120 | Eastern Zone Total | 7443 | 7392 | 7105 | 6932 | 6772 | 6153 | 6143.5 | 6181.6 | 6376 | 6760 | 6805 | 6976 | 6964 | 6830 | 7034 | 6792 | 6652.2 | 6184.2 | 0 | 7007 | 7870 | 8051 | 8077 | 7977 | 8042 | 7977 | 165780865
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 69 | 68 | 63 | 10 | 10 | 10 | 10 | 10 | 25 | 14 | 46 | 51 | 68 | 66 | 61 | 63 | 63 | 67 |  | 77 | 77 | 76 | 81 | 80 | 74 | 73 | 1166880
125 | Khulna (KPCL-2) | 113 | 113 | 113 | 114 | 16 | 16 | 16 | 16 | 45 | 49 | 68 | 96 | 96 | 96 | 46 | 66 | 90 | 102 |  | 100 | 105 | 105 | 92 | 94 | 63 | 99 | 1824000
126
127 | Khulna (Aggreko) 55MW | 55 | [12 empty] | 0 | 12 | 12 | 0 | 0 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 375560
128 | Faridpur Peaking | 48 | 48 | 48 | 18 | [12 empty] | 0 | 18 |  | 50 | 49 | 49 | 49 | 49 | 49 | 0 | 108000
129 | Khulna CCPP 225MW | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 140 | 160 | 190 | 200 | 200 | 135 |  | 120 | 150 | 190 | 232 | 233 | 131 | 132 | 3811200
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 80 | 80 | 80 | 32 | 32 | 32 | 48 | 48 | 64 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 110 | 110 | 110 | 110 | 110 | 110 | 1944000
136 | Barisal GT: Unit-1, 2 | [17 empty] | 0 |  | 8 | 10 | 12 | 12 | 12 | 0 |  | 35020
137 | Bhola Aggreko 95MW | 95 | 97 | 96 | 96 | 95 | 96 | 96 | 96 | 96 | 95 | 96 | 95 | 97 | 95 | 96 | 95 | 96 | 96 |  | 95 | 96 | 96 | 95 | 95 | 96 | 96 | 2303004
| Bhola CCPP 194MW | 192 | 192 | 192 | 192 | 192 | 191 | 191 | 191 | 189 | 193 | 189 | 189 | 184 | 191 | 189 | 185 | 186 | 187 |  | 190 | 191 | 188 | 186 | 181 | 191 | 192 | 4618053
140 | Bhola (Venture) 33MW | 27 | 11 | 34 | 33 | 31 | 25 | 22 | 21 | 22 | 22 | 21 | 19 | 23 | 4 | 25 | 23 | 22 | 22 |  | 27 | 32 | 32 | 38 | 38 | 35 | 35 | 601716
141 | Bangla Trak Noapara | [14 empty] | 0 | 30 | 30 | 10 |  | 93 | 98 | 98 | 97 | 97 | 97 | 97 | 600000
142 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 24 | 33 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 8 |  | 33 | 33 | 33 | 33 | 40 | 40 | 40 | 770250
143 | Gopalganj Peaking | 56 | 20 | 20 | 20 | [10 empty] | 0 | 17 | 30 | 42 |  | 83 | 78 | 78 | 75 | 70 | 70 | 58 | 629376
144 | Bheramara GT-1,2,3 | [17 empty] | 0 |  | 16 | 32 | 32 | 32 | 48 | 32 | 32 | 166000
145
146 | Bheramara HVDC | 467 | 467 | 467 | 467 | 467 | 467 | 467 | 468 | 468 | 468 | 468 | 468 | 468 | 468 | 468 | 468 | 468 | 458 |  | 458 | 457 | 458 | 458 | 458 | 458 | 467 | 11149818
147 | Bheramara 360 MW | 259 | 260 | 266 | 271 | 270 | 282 | 282 | 280 | 270 | 250 | 240 | 235 | 223 | 208 | 208 | 208 | 200 | 202 |  | 220 | 222 | 220 | 220 | 222 | 220 | 220 | 5814720
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3665300
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 51 | 51 | 51 | 51 | 51 | 0 | [5 empty] | 0 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 836704
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 160 | 151 | 146 | 133 | 134 | 132 | 133 | 133 |  | 135 | 198 | 205 | 214 | 206 | 160 | 148 | 3738681
Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 131 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 145 | 152 | 167 | 130 | 130 | 130 | 130 | 130 |  | 136 | 210 | 220 | 220 | 185 | 150 | 145 | 3580736
159 | Sirajgonj Unit-3 225 MW(Gas)
160 | Sirajgonj Unit-3 225 MW(Oil)
161 | Bera Peaking | 25 | 0 | [12 empty] | 0 | 22 | 38 | 38 |  | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 336722
162 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 13 | 18 | 15 | 18 | 18 | 18 | 18 | 18 | 18 | 10 |  | 17 | 20 | 20 | 18 | 21 | 21 | 21 | 413520
163 | Bogra (EPL) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 212220
164 | Ullapara (Summit) | 10 | 10 | 10 | 10 | 8 | 5 | 6 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 228880
165 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 0 | 0 | 25 | 25 | 25 | 25 |  | 12 | 41 | 50 | 50 | 50 | 50 | 50 | 901140
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 966608
167 | Katakhali Peaking | 45 | 45 | 0 | [9 empty] | 0 | 12 | 39 | 44 | 44 | 44 |  | 45 | 45 | 47 | 45 | 45 | 45 | 45 | 560700
168 | Santahar Peaking
169 | Rajlanka 52 MW | 52 | 34 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 52 | 43 | 52 | 52 | 52 | 52 | 29 | 8 |  | 8 | 21 | 52 | 52 | 52 | 52 | 52 | 754080
170 | Chapainawabganj-100 MW | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 0 |  | 0 | 32 | 93 | 93 | 101 | 101 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 1845938
171
172
173 | Rangpur GT | 14 | 15 | 15 | 15 | 15 | 0 | [11 empty] | 0 |  | 17 | 16 | 16 | 16 | 15 | 14 | 10 | 155000
175 | Saidpur GT | 14 | 16 | 16 | 16 | 16 | 0 | [11 empty] | 0 |  | 18 | 18 | 16 | 15 | 15 | 15 | 15 | 174000
176
177
178
178 | Western Zone Total | 2523 | 2347 | 2269 | 2191 | 2049 | 1880 | 1828 | 1825 | 1891 | 1848 | 1977 | 2003 | 2097 | 2102 | 2162 | 2267 | 2279 | 2180 | 0 | 2496 | 2767 | 2861 | 2898 | 2874 | 2630 | 2594 | 54287826
176
177