## Daily Gen
Hourly Generation & Demand
Date | 2014-04-08
Time | Generation | Demand | Shortage | Remarks
Hour | MW | MW | MW
1:00 | 6189 | 6189 | 0
2:00 | 6013 | 6013 | 0
3:00 | 5771 | 5771 | 0
4:00 | 5712 | 5712 | 0
5:00 | 5613 | 5613 | 0
6:00 | 5440 | 5440 | 0
7:00 | 5025 | 5025 | 0
8:00 | 5452 | 5452 | 0
9:00 | 5843 | 5843 | 0
10:00 | 5997 | 5997 | 0
11:00 | 6019 | 6019 | 0
12:00 | 6103 | 6103 | 0 | Day peak
13:00 | 6154 | 6154 | 0
14:00 | 6101 | 6101 | 0
15:00 | 6219 | 6219 | 0
16:00 | 6231 | 6231 | 0
17:00 | 6158 | 6158 | 0
18:00 | 6086 | 6086 | 0
18:30 | 6569 | 6569 | 0
19:00 | 6691 | 6691 | 0 | Evening Peak
19:30 | 6666 | 6666 | 0
20:00 | 6582 | 6582 | 0
21:00 | 6608 | 6608 | 0
22:00 | 6669 | 6669 | 0
23:00 | 6502 | 6502 | 0
24:00 | 6251 | 6251 | 0

## forecast
[7 empty] | POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-07
SUMMARY OF DAILY ELECTRICITY GENERATION
|  | Month : |  | 2014-04-09 |  |  | Day : | Wednesday |  |  |  | Date : | 2014-04-09
| Probable Maximum Generation : |  |  |  | (a) At Day Peak Hour : |  | 5681 | MW |  | (b) At Evening Peak Hour : |  |  | 6900 | MW
| Water Level of Kaptai Lake at 06:00 AM (ft) |  |  |  | (a) Yesterday : |  | 84.08 |  |  | (b) Today: | 83.86 | (c) Rule Curve: |  | 86.4
Sl. | Name of the Power Station |  | Fuel | Producer | Instslled Capacity |  | Derated/ | Actual Generation |  | Available Geneneration |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[7 empty] | Present | On | 2014-04-08 | On | 2014-04-09 | for Fuel | for Plants S/D | Shut down (Date) / |  | Start up
[7 empty] | Capacity | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | or M/C prob. | Remarks |  | Date
[6 empty] | MW | MW | MW | MW | MW | MW | MW | MW
1a | Ghorasal ST 1 & 2 |  | Gas | PDB | 2X55 | 110 | 78 | 63 | 63 | 63 | 63
1b | Ghorasal ST 3 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 2014-05-04 |  | Unkhown
1c | Ghorasal ST 4 |  | Gas | PDB | 1x210 | 210 | 180 | 160 | 160 | 160 | 160 |  | 20
1d | Ghorasal ST 5 |  | Gas | PDB | 1x210 | 210 | 190 | 190 | 190 | 190 | 190
1e | Ghorasal ST 6 |  | Gas | PDB | 1x210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6(18/07/10) |  | Unknown
2 | Ghorashal 100 MW |  | Gas | QRPP 3yrs | 128X0.85 | 100 | 100 | 97 | 101 | 0 | 100
3 | Ghorashal 45 MW |  | Gas | QRPP 3yrs | 50X0.85 | 45 | 45 | 46 | 45 | 0 | 45
4 | Ghorashal MAX |  | Gas | RPP | 4x19.6 | 78 | 78 | 75 | 75 | 78 | 78
5 | Ghorashal Regent | [6 empty] | 13 | 0 | 0 | 0 |  |  | On test
6 | Haripur SBU GT 1, 2 & 3 |  | Gas | SBU,PDB | 3x32 | 96 | 60 | 0 | 0 | 0 | 0 | 40 | 20 | #1&#2(22/10/13),#3(18/06/09) |  | Unkhown
7 | Haripur EGCB 360 MW |  | Gas | EGCB |  | 412 | 412 | 214 | 213 | 217 | 213 | 199 |  | On test
8 | Haripur NEPC |  | HFO | IPP | 8x15 | 110 | 110 | 95 | 110 | 97 | 110
9 | Haripur P. Ltd CCPP |  | Gas | IPP | 235+125 | 360 | 360 | 256 | 251 | 266 | 251 | 109
10 | Meghnaghat P.Ltd CCPP |  | Gas | IPP | 3X150 | 450 | 450 | 226 | 228 | 226 | 228 | 222 |  | ST-2 (07/04/2014) |  | 2014-10-04
11 | Meghnaghat IEL |  | HFO | RPP | 12x8.9 | 100 | 100 | 83 | 92 | 92 | 92 |  | 8 | 1 Machine problem
12 | Meghnaghat Summit | [6 empty] | 0 | 0 | 0 | 0
13 | Madanganj 102 MW |  | HFO | QRPP 3yrs | 6x17.08 | 102 | 100 | 97 | 100 | 95 | 100
14 | Keraniganj |  | HFO | RPP | 8x14.4 | 100 | 100 | 101 | 82 | 102 | 100
15 | Narshingdi |  | Gas | SIPP,REB | 8X2.90 | 22 | 22 | 0 | 19 | 20 | 19 |  | 3 | Synchronized at 33KV, 1 Machine problem
16a | Siddhirgonj ST |  | Gas | PDB | 1x210 | 210 | 150 | 100 | 100 | 105 | 100 | 50
16b | Siddhirgonj GT-1, 2 |  | Gas | EGCB | 2x120 | 210 | 210 | 0 | 0 | 0 | 0 | 210
17 | Siddhirganj 100MW |  | HSD | QRPP 3yrs | 96x1.2 | 96 | 96 | 68 | 71 | 66 | 80 |  | 25 | 20 Machine problem
18 | Dutch Bangla 100 MW |  | HFO | RPP | 12x8.9 | 100 | 100 | 93 | 93 | 92 | 100
19 | DPA Power 50MW |  | HSD | QRPP 3yrs | 100X0.5 | 50 | 50 | 40 | 43 | 43 | 50 |  | 7 | Expired, run as per instruction of DS (Gen)
20 | Gaharnagar | [6 empty] | 0 | 0 | 0 | 0 |  |  | On test
21 | Summit Power (Dhaka) |  | Gas | SIPP,REB |  | 146 | 146 | 92 | 74 | 110 | 108 |  |  | Synchronized at 33KV
22 | Gazipur RPCL |  | HFO | IPP | 6x8.9 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | 1 Machine problem
23 | Tongi GT |  | Gas | PDB | 1X 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105
| Dhaka Area Total |  |  |  |  | 3894 | 3664 | 2152 | 2153 | 2065 | 2230 | 935 | 462
24a | Chittagong Raozan ST 1 |  | Gas | PDB | 1x210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | 2014-03-04 |  | Unkhown
24b | Chittagong Raozan ST 2 |  | Gas | PDB | 1x210 | 210 | 180 | 100 | 120 | 110 | 120 | 60
25 | Raozan 25 MW |  | HFO | RPCL | 3x8.9 | 25 | 25 | 17 | 17 | 26 | 26 |  | 8 | 1 Machine problem
26 | Patenga 50 MW |  | HFO | IPP | 8x6.9 |  |  | 0 | 0 | 0 | 0 |  |  | On test
27 | Kaptai Hydro unit 1,2,3,4 & 5 |  |  | PDB | 2X40+3X50 | 230 | 220 | 42 | 186 | 40 | 199
28a | Sikalbaha ST |  | Gas | PDB | 1X60 | 60 | 40 | 0 | 0 | 0 | 0 | 40 |  | 2013-07-11 |  | Unknown
28b | Sikalbaha GT |  | Gas | PDB | 1x150 | 150 | 150 | 50 | 80 | 80 | 80 | 70
29 | Sikalbaha |  | HFO | RPP 3yrs | 4X12.5+2X11.9+1X3+1X1.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | contract date expired 06/05/2013
30 | Hathazari |  | HFO | PDB | 11x8.9 | 98 | 98 | 0 | 98 | 0 | 98
31 | Dohazari |  | HFO | PDB | 6x17 | 102 | 102 | 0 | 102 | 0 | 102
32 | Juldah |  | HFO | RPP | 8x13.45 | 100 | 100 | 92 | 92 | 0 | 92 |  | 8
33 | Barabkunda |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Synchronized at 33KV, 2 Machine problem
34 | Malancha,Ctg EPZ |  | Gas |  |  |  |  | 3 | 29 | 2 | 29
| Chittagong area Total |  |  |  |  | 1207 | 1117 | 320 | 740 | 274 | 762 | 350 | 22
35a | Ashuganj ST 1 & 2 |  | Gas | APSCL | 2x64 | 128 | 110 | 90 | 90 | 90 | 90 |  | 20
35b | Ashuganj ST 3 |  | Gas | APSCL | 1x150 | 150 | 140 | 140 | 140 | 140 | 140
35c | Ashuganj ST 4 |  | Gas | APSCL | 1x150 | 150 | 150 | 140 | 140 | 140 | 140 |  | 10
35d | Ashuganj ST 5 |  | Gas | APSCL | 1x152 | 150 | 140 | 120 | 120 | 120 | 120 |  | 20
35e | Ashuganj CCPP |  | Gas | APSCL | 2x56+34 | 146 | 91 | 0 | 0 | 0 | 20 |  | 91 | ST(08/09/2013), #1 (06/01/2014) |  | Unknown
35f | Ashuganj 50 MW TSK |  | Gas | APSCL | 16x3.35 | 53 | 51 | 36 | 39 | 36 | 39 |  | 12 | 3 Machine problem
36 | Ashuganj Precision |  | Gas | RPP 3yrs | 15x4 | 55 | 55 | 52 | 53 | 57 | 55
37 | Ashuganj Aggrekko |  | Gas | RPP | 82x1.1 | 80 | 80 | 78 | 83 | 82 | 80
38 | Ashuganj UP-53 MW |  | Gas | RPP | 14x4 | 53 | 53 | 53 | 53 | 49 | 53
39 | Ashuganj Midland |  | Gas | IPP | 6x9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | 1 Machine problem
40 | Brahmanbaria 70MW |  | Gas | QRPP 3yrs | 72x1 | 70 | 70 | 70 | 73 | 71 | 70
41 | Daudkandi 50 MW |  | FO | PDB | 6x8.92 | 52 | 52 | 48 | 50 | 0 | 50
42 | Chandpur CCPP |  | Gas | PDB | 1x106+1x57 | 163 | 163 | 163 | 165 | 163 | 163
43 | Feni |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 16 | 18 | 18 | 18 |  | 4 | 1 Machine problem
44 | Mahipal,Feni |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 0 | 10 | 11 | 10 |  | 1 | Synchronized at 33KV,
45 | Jangalia |  | Gas | SIPP,PDB | 4X8.73 | 33 | 33 | 25 | 25 | 8 | 25 |  | 8 | Synchronized at 33KV, 1 Machine problem
46 | Summit Power (Comilla) |  | Gas | SIPP,REB | 3x3.67+2x6.97 | 25 | 25 | 20 | 21 | 21 | 21 |  |  | Synchronized at 33KV, 1 Machine problem
| Comilla Area Total |  |  |  |  | 1392 | 1297 | 1094 | 1123 | 1049 | 1137 | 0 | 174
47 | RPCL CCPP,Mymensingh |  | Gas | IPP | 4X35+1x70 | 210 | 197 | 151 | 154 | 154 | 154 | 43
48 | Tangail |  | Gas | SIPP,PDB | 8X2.90 | 22 | 22 | 16 | 16 | 19 | 19 |  | 6 | Synchronized at 33KV, 2 Machine problem
| Mymensingh Area Total |  |  |  |  | 232 | 219 | 167 | 170 | 173 | 173 | 43 | 6
49a | Fenchugonj CCPP (old) |  | Gas | PDB | 2x32+1x33 | 97 | 90 | 52 | 54 | 52 | 54 |  | 36 | ST (26/02/2014) |  | Unknown
49b | Fenchugonj CCPP (new) |  | Gas | PDB | 2x35+1x35 | 104 | 104 | 85 | 84 | 85 | 84 |  | 20
50 | Fenchugonj BEDL |  | Gas | RPP 15yrs | 19X2.90 | 51 | 51 | 35 | 41 | 47 | 41 |  | 10 | 3 Machine problem.
51 | Fenchuganj Prima 50 MW |  | Gas | RPP | 12x3.3+5x2 | 44 | 44 | 47 | 50 | 41 | 50
52 | Hobiganj |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 0 | 2 | 0 | 8 |  | 9 | Synchronized at 33KV, 3 Machine problem
53 | Shahjibazar GT 8,9 |  | Gas | PDB | 2X35 | 70 | 66 | 62 | 44 | 66 | 66
54 | Shahjibazar 86 MW |  | Gas | RPP 15yrs | 32X2.90 | 86 | 86 | 73 | 73 | 71 | 73 |  | 13 | 4 Machine problem
55 | Shahjibazar 50 MW |  | Gas | RPP 3yrs | 27X2.0 | 50 | 50 | 49 | 46 | 46 | 46
56 | Sylhet 150 MW |  | Gas | PDB | 1x150+1x75 | 142 | 142 | 117 | 142 | 68 | 142
57 | Sylhet GT |  | Gas | PDB | 1X20 | 20 | 20 | 19 | 20 | 20 | 20
58 | Sylhet 50MW |  | Gas | RPP 3yrs | 29x1.95 | 50 | 50 | 42 | 47 | 43 | 47
59 | Shahjahanulla 25MW |  | Gas | CIPP | 3x9.34 | 25 | 25 | 14 | 25 | 0 | 25
60 | Sylhet 11 MW |  | Gas | RPP 15yrs | 6X1.95 | 10 | 10 | 8 | 8 | 0 | 8
| Sylhet Area Total |  |  |  |  | 760 | 749 | 603 | 636 | 539 | 664 | 0 | 88
61 | Bheramara GT 1, 2 & 3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 32 | 16 | 32 |  | 14 | # 2 (03/04/14) |  | unknowb.
62 | Bheramara |  | HSD | RPP 3yrs | 12X8.5+2X6+2X13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | 16 Machine problem |  | Unknown
63 | HVDC C/B Interconnector |  |  | India |  | 500 | 500 | 451 | 338 | 456 | 343
64a | Khulna ST 110MW |  | FO | PDB | 1X110 | 110 | 55 | 60 | 60 | 60 | 60
64b | Khulna ST 60 MW |  | FO | PDB | 1X60 | 60 | 30 | 0 | 0 | 0 | 0 |  | 30 | 24/01/12 |  | Unknown
65 | KPCL ,Khulna. |  | HFO | IPP | 19x6.5 | 110 | 110 | 100 | 110 | 93 | 110
66 | KPCL ,Khulna.(new) |  | HFO | IPP | 7x17 | 115 | 115 | 99 | 99 | 99 | 99 |  | 16 | 1 Machine problem.
67 | Faridpur |  | FO | PDB | 8x6.89 | 54 | 54 | 0 | 45 | 0 | 50
68 | Khulna 150MW |  | HSD | NWZPGCL | 1x150 | 150 | 150 | 156 | 155 | 161 | 160
69 | Gopalganj 110 MW |  | HFO | PDB | 16x6.98 | 109 | 109 | 47 | 68 | 43 | 68 |  | 41 | 6 Machine problem.
70 | Noapara (105 MW)Quantam |  | HFO | RPP | 9.9x5+9.5x6+9.2x2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | 13 Machine problem
71 | Noapara (40 MW),KZA |  | HFO | RPP | 5x8 | 40 | 40 | 40 | 40 | 40 | 40
72 | Khulna 40 MW |  | HSD | RPP 3yrs | 50X0.80 | 40 | 40 | 0 | 0 | 0 | 0 |  |  | Contact date expired 16/08/13
73 | Khulna 55 MW |  | HSD | QRPP 3yrs | 71X0.85 | 55 | 55 | 40 | 43 | 32 | 55 |  |  | Expired , run as per instr. of DS (Gen)
| Khulna Area Total |  |  |  |  | 1609 | 1510 | 993 | 990 | 1000 | 1017 | 0 | 307
74 | Barisal GT 1 & 2 |  | HSD | PDB | 2X20 | 40 | 32 | 0 | 31 | 0 | 31
75 | Bhola |  | Gas | RPP 3yrs | 1X34.50 | 33 | 33 | 0 | 0 | 0 | 0 |  | 33 | 2013-10-08 |  | Unknown
| Barisal Area Total |  |  |  |  | 73 | 65 | 0 | 31 | 0 | 31 | 0 | 33
76a | Baghabari GT 1 |  | Gas | SBU,PDB | 1X71 | 71 | 71 | 70 | 70 | 72 | 71
76b | Baghabari GT 2 |  | Gas | SBU,PDB | 1X100 | 100 | 100 | 90 | 93 | 95 | 100
77 | Baghabari 50 MW |  | HFO | PDB | 6x8.9 | 52 | 52 | 40 | 40 | 0 | 40 | 12 |  | 1 Machine problem
78 | Baghabari Westmont |  | Gas | IPP | 2X45 | 90 | 70 | 0 | 0 | 0 | 0 |  | 70 | #1(1/5/12),#2(24/4/13) |  | Unknown
79 | Bera 70 MW |  | HFO | PDB | 9x8.29 | 71 | 71 | 30 | 70 | 0 | 71
80 | Amnura 50 MW |  | HFO | RPP | 7x7.79 | 50 | 50 | 54 | 54 | 0 | 54
81 | Katakhali NPS 50 MW |  | HFO | RPP | 6x8.92 | 50 | 50 | 50 | 50 | 50 | 50
82 | Katakhali PPP 50 MW |  | HFO | PDB | 6x8.7 | 50 | 50 | 46 | 45 | 0 | 50
83 | Sirajganj 150 MW |  | Gas | NWPGCL | 1x150 | 150 | 150 | 134 | 140 | 137 | 145
84 | Santahar 50 MW |  | HFO | PDB | 6x8.7 | 50 | 50 | 46 | 46 | 0 | 46
85 | Bogra GBB |  | Gas | RPP 15yrs | 6X4 | 20 | 22 | 20 | 20 | 22 | 20 |  |  | Synchronized at 33KV
86 | Bogra 20MW |  | Gas | RPP 3yrs | 5x3.3+5x2 | 20 | 20 | 13 | 15 | 15 | 15 |  | 5 | 1 Machine problem
87 | Summit Power (Ullapara) |  | Gas | SIPP,REB | 4X2.90 | 11 | 11 | 8 | 8 | 0 | 8 |  | 3 | Synchronized at 33KV, 1 Machine problem
88 | Rajlanka 52 MW |  | FO | IPP |  | 52 | 52 | 52 | 52 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 837 | 819 | 653 | 703 | 443 | 722 | 12 | 78
89a | Barapukuria ST 1 |  | Coal | PDB | 1x125 | 125 | 100 | 88 | 84 | 89 | 84 |  | 16
89b | Barapukuria ST 2 |  | Coal | PDB | 1x125 | 125 | 100 | 0 | 0 | 0 | 0 |  | 100 | 2014-07-04 |  | Unkhown
90 | Rangpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 12 | 15 | 20
91 | Sayadpur GT |  | HSD | PDB | 1X20 | 20 | 20 | 0 | 15 | 0 | 20
92 | Thakurgaon |  | HSD | RPP 3yrs | 20X1.5+21X1.1 | 47 | 47 | 33 | 34 | 34 | 40 |  |  | expired , run as per instr. of DS (Gen)
| Rangpur Area Total |  |  |  |  | 337 | 287 | 121 | 145 | 138 | 164 | 0 | 116
| Total |  |  |  |  | 10341 | 9727 | 6103 | 6691 | 5681 | 6900 | 1340 | 1286
| Useable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5563.9366 | 6100 | 5179.2109 | 6290
A. |  | 2014-04-08 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 6691 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 5025 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6691 | MW
3 | Day peak Generation : |  |  | 6103 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6100 | MW
4 | Evening peak Generation : |  |  | 6691 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 134.4124 | MKWHr |  |  | 15. Area wise Demand ( S/S end), Supply( S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 83.4492 | MKWHr |  | By Oil: | 38.2682 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 2.0675 | MKWHr |  | By Hydro: | 1.6413 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 1340 | For Oil: | 0 | MW | Dhaka | 2689 | 2689 | 0 |  |  | Hour |  | MW
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 539 | 539 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 1286 | MW | Khulna | 671 | 671 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 909.7 | MMCFD |  |  |  | Rajshahi | 669 | 669 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 74966713.852 | ii) Oil : Taka |  | 554251505.862 | Comilla | 429 | 429 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 8046671.08 | Total | Taka | 637264890.794 | Mymensing | 340 | 340 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 320 | 320 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -130 | MW at | 19:00 | hrs | Barisal | 139 | 139 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | 500 | MW at | 5:00 | hrs | Rangpur | 304 | 304 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.2° C |  |  | Total | 6100 | 6100 | 0
B. |  | 2014-04-09 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand (Generation end) |  |  |  | 6850 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 6900 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Shortage (Generation end) |  |  |  | -50 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensing | Sylhet | Barisal | Rangpur
4 | Total Energy Generation |  |  |  | 134 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
5 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5404 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 8.9862 | MKWHr.
ii) During peak Demand : |  |  | 451 | MW at | 19:00 | hrs
iii) Maximum : |  |  | 451 | MW at | 7:00 | hrs
Cost for HVDC energy is not usaually included in the total fuel cost.

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2014-04-09
Till now the maximum generation is : - |  |  | 7356 MW | 20:00 | Hrs on | 2014-03-30
The Summary of Yesterday's ( |  | 2014-04-08 | ) Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6103 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 5404 | MW
Evening Peak Generation : |  | 6691 | MW Hour : | 19:00 | Max Generation : |  | 6900 | MW
E.P. Demand (at gen end) : |  | 6691 | MW Hour : | 19:00 | Max Demand : |  | 6850 | MW
Maximum Generation : |  | 6691 | MW Hour : | 19:00 | Shortage : |  | -50 | MW
Total Gen. (MKWH) : |  | 134.4124 | System L/ Factor : | 78.37% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 500 | MW at | 5:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2014-04-09
Actual : | 87.64 | Ft.(MSL) , | Rule curve : | 86.4 | Ft.( MSL )
Gas Consumed : | Total | 909.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : Gas : |  |  | 74966713.852
|  | Coal : | 8046671.08 | Oil : | 554251505.862 | Total : | 637264890.794
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand(s/s end) |  | Estimated Shedding (s/s end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | - | 0:00 | 2521 |  |  | - | -
Chittagong Area | - | 0:00 | 650 |  |  | - | -
Khulna Area | - | 0:00 | 712 |  |  | - | -
Rajshahi Area | - | 0:00 | 689 |  |  | - | -
Comilla Area | - | 0:00 | 473 |  |  | - | -
Mymensingh Area | - | 0:00 | 389 |  |  | - | -
Sylhet Area | - | 0:00 | 317 |  |  | - | -
Barisal Area | - | 0:00 | 141 |  |  | - | -
Rangpur Area | - | 0:00 | 398 |  |  | - | -
-
Total | 0 |  | 6290 |  |  | 0
Information of the Generating machines under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
| 1) Haripur SBU GT-3 (18/06/09) |  |  | 1) Ghorasal #6 (18/07/10) |  | 9) Megnaghat 450 MW (GT-2) (07/04/2014)
2) Khulna-60MW (24/1/12)
3) Shahjibazar #5 & 6 (21/7/11)
4) WMPL #1(1/5/12)
5) WMPL #2(24/4/13)
6) Ashuganj #GT1(CCPP) (06/01/14)
7) Barapukuria #2 (07/04/2014)
8) Ghorasal-3(5/4/14)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Forced load shaded / Interrupted Areas
a) Tongi 230 kV bus-2 was shut down from 09:48 to 17:35 due to CVT change.
b) Bogra-sirajgonj 132 kV Ckt-1tripped at 06:13(09/04/14) from both end showing dist Z1 soft
at sirajganj end & Z2 ABC at Bogra end and was switched on at 07:40
c) Fenchuganj 132/33 kV T1 transformer tripped at 23:06 showing TCS-1,TCS-2 fail
and was switched on at 23:49 and again tripped at 00:05(9/4/14) due to same reason
and was switched on at 01:38(9/4/14) and again tripped at 06:17(9/4/14) due to same
reason and was switched on at 06:39(9/4/14).

## P2
POWER GRID COMPANY OF BANGLADESH LTD.
Description of the generation of various Power Stations
| Date : | 2014-04-08 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1 |  |  | 1 | PDB | 48 | 43 | 1415000
2 | Ghorasal Power Station |  | 2 | PDB | 30 | 20
3 |  |  | 3 | PDB | 180 | 0 | 0 | Under maint.
4 |  |  | 4 | PDB | 180 | 160 | 3683610 | Machine problem
5 |  |  | 5 | PDB | 190 | 190 | 4347000
6 |  |  | 6 | PDB | 190 | 0 | 0 | Under maint.on 18/07/10.
7 | Ghorashal 100MW QRPP |  | 128x0.85 | QRPP 3yrs | 100 | 101 | 2435490
8 | Ghorashal 45MW QRPP |  | 50x0.85 | QRPP 3yrs | 45 | 45 | 1035970
9 | Ghorashal 78 MW MAX |  | 4x19.6 | RPP | 78 | 75 | 1740000
| Ghorashal Regent |  |  |  | 0 | 0 | 110000
10 |  |  | GT-1 | SBU, PDB | 20 | 0 | 0 | Gas pressure low
11 | Haripur SBU |  | GT-2 | SBU, PDB | 20 | 0 | 0 | Gas pressure low
12 |  |  | GT-3 | SBU, PDB | 20 | 0 | 0 | Under maint. since 18/06/09
| Haripur EGCB 360 MW |  |  | EGCB | 412 | 213 | 4208792 | On test
13 | Haripur NEPC |  | 7 x 15.5 | IPP | 110 | 110 | 2372200
14 | Haripur Power Ltd |  | CCPP | IPP | 360 | 251 | 685600 | Gas pressure low
15 | Meghnaghat Power Ltd |  | CCPP | IPP | 450 | 228 | 5075000 | GT-2 under maint
16 | Meghnaghat IEL |  | 12x8.9 | 100 | 100 | 92 | 2015040 | Machine problem
| Meghnaghat Summit |  |  |  | 0 | 0 | 0
17 | Madanganj |  | 6x17.08 | QRPP 3yrs | 100 | 100 | 2305344
18 | Keraniganj |  |  | RPP | 100 | 82 | 2224500 | Machine problem
19 | Narsingdi (REB) |  | 8 x 2.9 | SIPP, REB | 22 | 19 | 352692 | Synchronized at 33KV, Machine problem
20 | Siddhirgonj Power Station |  | 210MW | PDB | 150 | 100 | 2463300 | Gas pressure low
21 |  |  | GT1 & GT-2 | EGCB | 210 | 0 | 0 | Gas pressure low
22 | Siddhirgonj |  | 96x1.2 | QRPP 3yrs | 96 | 71 | 1316160 | Machine problem
23 | Dutch-Bangla 100 MW |  | 12x8.9 | RPP | 100 | 93 | 2052480 | Machine problem
24 | DPA Power QRPP |  | 100x0.5 | QRPP 3yrs | 50 | 43 | 816340 | Contact expired, run as per instruction of DS (Gen)
| Gaharnagar |  |  |  | 0 | 0 | 0
25 | Summit Power Ltd (Dhaka) |  |  | SIPP, REB | 146 | 74 | 2496797 | Synchronized at 33KV, Machine problem
26 | Gazipur RPCL |  | 6x8.9 | IPP | 52 | 43 | 785280 | Machine problem
27 | Tongi Power Station |  | 1 | PDB | 105 | 0 | 428815 | Gas pressure low
| Dhaka Area Total |  |  |  | 3664 | 2153 | 44365410
28 | Chitagong Power Station |  | 1 | PDB | 180 | 0 | 0 | Under maint.
29 |  |  | 2 | PDB | 180 | 120 | 2600000 | Gas pressure low
30 | Raozan 25 MW |  |  | RPCL | 25 | 17 | 364680 | Machine problem
31 | Patenga 50 MW |  |  | IPP | 50 | 0 | 0 | On test
32 |  |  | 1 | PDB | 30 | 30 | 1268330
33 |  |  | 2 | PDB | 40 | 40 | 0
34 | Karnafuli Hydro Power Station |  | 3 | PDB | 50 | 46 | 0
35 |  |  | 4 | PDB | 50 | 35 | 373000
36 |  |  | 5 | PDB | 50 | 35 | 0
37 | Shikalbaha Power station |  | Steam | PDB | 40 | 0 | 0 | Gas pressure low
38 |  |  | GT | PDB | 150 | 80 | 1695129 | Gas pressure low
39 | Hathazari |  | 11x8.9 | PDB | 100 | 98 | 944360
40 | Dohazari |  | 6x17 | PDB | 100 | 102 | 995733
41 | Juldah |  | 8x13.45 | RPP | 100 | 92 | 2186400 | Machine problem
42 | Shikalbaha RPP |  | 4x12.5+2x11.9+1x3 | RPP 3yrs | 0 | 0 | 0 | Contact expired date (06/05/2013)
43 | Barabkunda RPP |  | 8x2.90 | SIPP, PDB | 22 | 16 | 371520 | Synchronized at 33KV, Machine problem
| Malancha, Ctg EPZ |  |  |  |  | 29 | 420480 | Synchronized at 33KV
44 | Chittagong Area Total |  |  |  | 1167 | 740 | 11219632
45 |  |  | 1 | APSCL | 55 | 45 | 1970151
46 |  |  | 2 | APSCL | 55 | 45 | 0
47 | Ashugonj Power Station |  | 3 | APSCL | 140 | 140 | 3321696
48 |  |  | 4 | APSCL | 150 | 140 | 3304930
49 |  |  | 5 | APSCL | 140 | 120 | 2875166 | Machine problem
50 |  |  | GT-1 | APSCL | 35 | 0 | 0 | Gas pressure low
51 |  |  | GT-2 | APSCL | 40 | 0 | 194248 | Gas pressure low
52 |  |  | ST. | APSCL | 16 | 0 | 0 | Under maint. Since 08/09/13
53 | Ashuganj-50 MW |  | 16x3.35 | APSCL | 51 | 39 | 840528 | Machine problem
54 | Ashugonj RPP |  | 15x4 | RPP 3yrs | 55 | 53 | 1294080
55 | Ashuganj Aggekko |  | 82x1.1 | RPP | 80 | 83 | 1954210
| Ashuganj United Power |  | 14x4 | RPP | 53 | 53 | 854000
56 | Ashuganj Midland Power |  |  |  | 51 | 43 | 1038764 | Machine problem
57 | Brahmanbaria |  | 72x1 | QRPP 3yrs | 70 | 73 | 1725000
58 | Daudkandi 50 MW |  | 6 x 8.92 | PDB | 52 | 50 | 632312
59 | Chandpur CCPP |  | 1x106+1x57 | PDB | 163 | 165 | 3692547
60 | Feni SIPP |  | 8 X 2.94 | SIPP, PDB | 22 | 18 | 371052 | Machine problem
61 | Feni (Mohipal) |  | 4x2.9 | SIPP, REB | 11 | 10 | 232740 | Synchronized at 33KV
62 | Jangalia RPP |  | 4x8.73 | SIPP, PDB | 33 | 25 | 574700 | Synchronized at 33KV, Machine problem
| Comilla Summit Power |  |  | SIPP, REB | 25 | 21 | 521870 | Machine problem
63 | Comilla Area Total |  |  |  | 1297 | 1123 | 25397994
64 | RPCL, Mymensingh CCPP |  | GT1-4 | IPP | 197 | 154 | 349100 | Gas pressure low
| Tangail SIPP |  | 8 x 2.50 | SIPP,PDB | 22 | 16 | 398736 | Synchronized at 33KV, Machine problem
65 | Mymensingh Area Total |  |  |  | 219 | 170 | 747836
66 | Fenchugonj Comb. Cycle |  | GT-1, 2 & St | PDB | 90 | 54 | 1167000 | Machine problem
67 |  |  | GT-3,4 & St | PDB | 104 | 84 | 2027640 | Machine problem
68 | Fenchugonj RPP (51 MW) |  | 2.9X19 | RPP 15yrs | 51 | 50 | 1145400
69 | Fenchuganj Prima 50 MW |  | 12x3.3+5x2 | RPP | 50 | 41 | 670000 | Machine problem
70 | Hobiganj (REB) (11MW) |  | 4x2.9 | SIPP, REB | 11 | 2 | 25999 | Synchronized at 33KV, Machine problem
71 | Shahjibazar Power Station |  | 5,6 | PDB | 0 | 0 | 0
72 |  |  | 8,9 | PDB | 66 | 44 | 1526000
73 | Shahjibazar P. co (SPCL) |  | 32X2.88 | RPP 15yrs | 86 | 73 | 1627200 | Machine problem
74 | Shahjibazar RPP |  | 1.85X27 | RPP 15yrs | 50 | 46 | 959400
75 | Sylhet 150 MW |  | 1x100+1x50 | PDB | 142 | 142 | 2905350
76 | Sylhet Power Station |  | GT | PDB | 20 | 20 | 466000
| Sylhet 50 MW RPP |  | 27 x 1.95 | RPP 3yrs | 50 | 47 | 1040300
77 | Shahjahanulla 25MW |  | 3 x 9.34 |  | 25 | 25 | 290952
| Sylhet 11 MW RPP |  | 6x1.95 | RPP 15yrs | 10 | 8 | 195300 | Synchronized at 33KV, Machine problem
78 | Sylhet Area Total |  |  |  | 755 | 636 | 14046541
79 |  |  | GT-1 | PDB | 16 | 16 | 0
80 | Bheramara Power Station |  | GT-2 | PDB | 14 | 0 | 185700 | No demand
81 |  |  | GT-3 | PDB | 16 | 16 | 0
| Bheramara 110 MW |  | 12x8.5+2x6+2x13 | RPP 3yrs | 105 | 0 | 0 | Machine problem
82 | HVDC C/B Interconnector |  | India |  | 500 | 338 | 8986182
83 | Khulna Power Station |  | 110MW | PDB | 55 | 60 | 1405943
84 |  |  | 60MW | PDB | 30 | 0 | 0 | Under S/D Since 24/1/12
85 | Khulna Power Co Ltd. |  | 19x6.5 | IPP | 110 | 110 | 2070400
86 | KPCL ,Khulna.(New) |  | 7x17 | IPP | 115 | 99 | 2289600 | Machine problem
| Faridpur |  | 8x6.89 | PDB | 54 | 45 | 532320
87 | Khulna 150 MW |  | 1x150 |  | 150 | 155 | 2872320
88 | Gopalganj 110 MW |  | 16x6.98 | PDB | 109 | 68 | 1348000 | Machine problem
89 | Noapara (105 MW),Quantam |  | 9.9x5+9.5x6+9.2x2 | RPP | 101 | 0 | 0 | Machine problem
90 | Noapara (40 MW),KZA |  | 5x8 | RPP | 40 | 40 | 948750 | Synchronized at 33KV
91 | Khulna RPP 40MW |  | 50X0.80 | RPP 3yrs | 40 | 0 | 0 | Contact Date Expired
| Khulna RPP 55MW |  | 71X0.85 | QRPP 3yrs | 55 | 43 | 699960 | expired , run as per instr. of DS (Gen)
94 | Khulna Area Total |  |  |  | 1510 | 990 | 21339175
95 | Barisal Power Station |  | GT-1 | PDB | 16 | 16 | 0
96 |  |  | GT-2 | PDB | 16 | 15 | 164046
| Bhola RPP |  | 34.5 | RPP 3yrs | 33 | 0 | 0 | Synchronized at 33KV, Under S/D since 10/08/13
97 | Barisal Area Total |  |  |  | 65 | 31 | 164046
98 | Baghabari Power Station |  | 71 MW | SBU, PDB | 71 | 70 | 1607000
99 |  |  | 100 MW | SBU, PDB | 100 | 93 | 2280000
100 | Baghabari 50 MW |  | 6x8.9 | PDB | 52 | 40 | 601683 | Machine problem
101 | Baghabari West Mont (WMPL) |  | GT 1 & 2 | IPP | 70 | 0 | 0 | #1 Under S/D since 1/5/12,#2 Under S/D since 25/4/13
102 | Bera 70 MW |  | 9x8.29 | PDB | 71 | 70 | 833606
103 | Amnura 50 MW |  | 7x7.79 | RPP | 50 | 54 | 841300
104 | Katakhali NPS 50 MW |  |  | RPP | 50 | 50 | 964204
105 | Rajshahi PPP 50 MW |  | 6x8.7 | PDB | 50 | 45 | 675324
106 | Sirajganj 150 MW |  | 1x150 | NWPGCL | 150 | 140 | 3391900
107 | Santahar 50 MW |  | 6x8.7 | PDB | 50 | 46 | 763933
108 | Bogra RPP |  | 6x4 | RPP 15yrs | 22 | 20 | 494600
109 | Bogra prima |  | 5x3.3+5x2 | RPP 3yrs | 20 | 15 | 358956 | Machine problem
110 | Ullapara Summit |  | 4 X 2.90 | SIPP, REB | 11 | 8 | 191502 | Synchronized at 33KV, Machine problem
| Rajlanka 52 MW |  |  | IPP | 52 | 52 | 1242240
110 | Rajshahi Area Total |  |  |  | 819 | 703 | 14246248
111 | Barapukuria power station |  | ST 1 | PDB | 100 | 84 | 2067490 | Machine problem
112 | Barapukuria power station |  | ST 2 | PDB | 100 | 0 | 0 | Under maintenance
113 | Rangpur Power Station |  | GT | PDB | 20 | 12 | 109000
114 | Saidpur Power Station |  | GT | PDB | 20 | 15 | 83000
115 | Thakurgaon Rental |  | 20x1.5+21x1.1 | RPP 3yrs | 47 | 34 | 626050 | Contact Date Expired
| Rangpur Area Total |  |  |  | 287 | 145 | 2885540
Public Sector Total
Private Sector Total
| Eastern Grid Total |  |  |  | 7102 | 4822 | 95777413
| Western Grid Total |  |  |  | 2681 | 1869 | 38635009
| National Grid Total |  |  |  | 9783 | 6691 | 134412422
* Data collected from respective power station over telephone.

## P3
| POWER GRID COMPANY OF BANGLADESH LTD. | [6 empty] | QF-LDC-09
NATIONAL LOAD DESPATCH CENTER
PEAK HOUR DEMAND (AT S/S END) OF DIFFERENT AREAS
Date: | 2014-04-08
(a) ENTIRE EASTERN GRID : |  |  | 4317 | MW | (b) ENTIRE WESTERN GRID : |  |  | 1783 | MW
i) Dhaka area |  |  | 2689 | MW | i) Khulna area |  |  | 671 | MW
ii) Chittagong area |  |  | 539 | MW | ii) Rajshahi area |  |  | 669 | MW
iii) Comilla area |  |  | 429 | MW | iii) Barisal area |  |  | 139 | MW
iv) Mymensingh area |  |  | 340 | MW | iv) Rangpur area |  |  | 304 | MW
v) Sylhet area |  |  | 320 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6100 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUBSTATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 1200 | Netrokona | 46 | 1830 | Jhenida | 58 | 2300
Munsiganj | 74 | 1830 | Jamalpur | 105 | 1900 | Bottail | 65 | 2300
Megnaghat | 31 | 2100 | Srimongal | 34 | 1830 | G.K Project | 38 | 2100
Shyampur | 132 | 2400 | Shahjibazar | 41 | 1900 | Faridpur | 88 | 1900
Bhulta | 117 | 2400 | Fenchuganj | 33 | 1900 | Madaripur | 81 | 2200
Madanganj | 36 | 100 | Sylhet | 125 | 1930 | Gopalganj | 32.4 | 1900
Shitalakhya | 81 | 1500 | Chatak | 34 | 1830 | Bagerhat | 44 | 2300
Rahim steel | 1 | 900 | B.Baria | 66 | 1800 | Mongla | 27.8 | 2400
Matuail | 37 | 1000 | Comilla(S) | 133 | 2200 | Satkhira | 54 | 2100
Ghorasal | 74 | 2200 | Comilla(N) | 35 | 1600 | Gallamari | 37.2 | 2300
Narsingdi | 69 | 1900 | Chandpur | 60 | 2100 | Magura | 24 | 2100
Haripur (SBU) | 59 | 1930 | Feni | 67 | 1900 | Chuadanga | 37 | 2400
Ullon | 84 | 1900 | Chowmuhani | 105 | 2200 | Barisal | 94 | 2100
Hasnabad | 126 | 100 | Ashuganj | 140 | 2100 | Patuakhali | 30 | 1900
Magbazar | 116 | 1100 | Daudkandi | 38 | 1830 | Bhandaria | 23 | 1900
Maniknagar | 96 | 1900 | Madanhat | 47.1 | 2200 | Ishurdi | 32 | 1900
Bangabhaban | 34 | 1300 | Hathazari | 73 | 1900 | Natore | 70 | 1800
Narinda | 88 | 1900 | Khulshi | 116 | 1400 | Bogra | 159 | 2000
Dhanmondi | 145 | 1200 | Halishahar | 144 | 2100 | Noagaon | 71 | 100
Mirpur | 91.5 | 19 | Baraulia | 69 | 2000 | Rajshahi | 97 | 1900
Kalyanpur | 141 | 1830 | Sikalbaha | 34 | 2000 | C.Nawabganj | 70 | 1900
Gulshan | 96 | 1600 | Dohazari | 68 | 2200 | Pabna | 66 | 1830
Uttara | 81.9 | 1900 | Cox'sbazar | 53.5 | 2000 | Shahjadpur | 58 | 1900
Kamrangirchar | 94 | 1930 | Chandraghona | 25.2 | 2000 | Serajganj | 49 | 1930
Savar | 64 | 1930 | Kaptai | 3.9 | 1900 | Niyamatpur | 79 | 1900
Bhasantec | 62 | 1900 | A. Khaer Stl. | 6.5 | 2200 | Joypurhat | 30 | 1900
Tongi | 69 | 1930 | Bakulia | 92 | 1930 | Rangpur | 80 | 1830
Kabirpur | 122 | 900 | Julda | 19 | 100 | Lalmonirhat | 45 | 700
Basundhara | 129 | 1900 | TK chemical | 8.8 | 1300 | Saidpur | 70 | 1900
Manikganj | 68 | 1830 | Modern Steel | 13 | 1200 | Purbasadipur | 57 | 1300
Joydevpur | 172 | 2000 | Shahmirpur | 2.3 | 900 | Thakurgaon | 58 | 2000
New Tongi | 85 | 2100 | Goalpara | 32 | 1930 | Palashbari | 46 | 1500
Tangail | 118 | 2100 | Central s/s | 66 | 2100 | Barapukuria | 29 | 1900
Mymensing | 126 | 2200 | Noapara | 46 | 1900 | Panchagar | 18 | 1900
Kishorganj | 47 | 2000 | Jessore | 114 | 2200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB

## L.curve
Date | 2014-03-17 01:35
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | 270 | 4699 | 1771 | 6470 | 270 | 6470 | 0:00 | POWER GRID COMPANY OF BANGLADESH LTD.
0:30 | 270 | 4599 | 1730.5 | 6329.5 | 270 | 6329.5 | 1:00
1:00 | 270 | 4499 | 1690 | 6189 | 230 | 6189 | 2:00 |  | DAILY LOAD CURVE |  |  | QF-LDC-11
1:30 | 250 | 4460.5 | 1640.5 | 6101 | 380 | 6101 | 3:00 |  |  | Date: | 2014-04-08
2:00 | 230 | 4422 | 1591 | 6013 | 460 | 6013 | 4:00
2:30 | 305 | 4395 | 1497 | 5892 | 500 | 5892 | 5:00
3:00 | 380 | 4368 | 1403 | 5771 | 500 | 5771 | 6:00
3:30 | 420 | 4379.5 | 1362 | 5741.5 | 430 | 5741.5 | 7:00
4:00 | 460 | 4391 | 1321 | 5712 | 360 | 5712 | 8:00
4:30 | 480 | 4375 | 1287.5 | 5662.5 | 160 | 5662.5 | 9:00
5:00 | 500 | 4359 | 1254 | 5613 | 140 | 5613 | 10:00
5:30 | 500 | 4263.5 | 1263 | 5526.5 | 120 | 5526.5 | 11:00
6:00 | 500 | 4168 | 1272 | 5440 | 50 | 5440 | 12:00
6:30 | 465 | 3986.5 | 1246 | 5232.5 | 120 | 5232.5 | 13:00
7:00 | 430 | 3805 | 1220 | 5025 | 120 | 5025 | 14:00
7:30 | 395 | 3966.5 | 1272 | 5238.5 | 100 | 5238.5 | 15:00
8:00 | 360 | 4128 | 1324 | 5452 | 240 | 5452 | 16:00
8:30 | 260 | 4199.5 | 1448 | 5647.5 | 170 | 5647.5 | 17:00
9:00 | 160 | 4271 | 1572 | 5843 | 170 | 5843 | 18:00
9:30 | 150 | 4325 | 1595 | 5920 | 10 | 5920 | 18:30
10:00 | 140 | 4379 | 1618 | 5997 | 130 | 5997 | 19:00
10:30 | 130 | 4372 | 1636 | 6008 | 160 | 6008 | 19:30
11:00 | 120 | 4365 | 1654 | 6019 | 164 | 6019 | 20:00
11:30 | 85 | 4350.5 | 1710.5 | 6061 | 120 | 6061 | 21:00
12:00 | 50 | 4336 | 1767 | 6103 | 140 | 6103 | 22:00
12:30 | 85 | 4367 | 1761.5 | 6128.5 | 200 | 6128.5 | 23:00
13:00 | 120 | 4398 | 1756 | 6154 | 180 | 6154 | 24:00
13:30 | 120 | 4396.5 | 1731 | 6127.5 |  | 6127.5
14:00 | 120 | 4395 | 1706 | 6101 | 128.92 | 6101
14:30 | 110 | 4432 | 1728 | 6160 | 86.5 | 6160
15:00 | 100 | 4469 | 1750 | 6219 |  | 6219
15:30 | 170 | 4505.5 | 1719.5 | 6225 | 7867500 | 6225
16:00 | 240 | 4542 | 1689 | 6231 |  | 6231
16:30 | 205 | 4554 | 1640.5 | 6194.5 |  | 6194.5
17:00 | 170 | 4566 | 1592 | 6158 | 700 | 6158
17:30 | 170 | 4566 | 1556.5 | 6122.5 | 1800 | 6122.5
18:00 | 170 | 4566 | 1521 | 6087 | 100 | 6087
18:30 | 10 | 4734 | 1835 | 6569 | 1400 | 6569
19:00 | 130 | 4822 | 1869 | 6691 | 100 | 6691 | [5 empty] | Executive Engineer
19:30 | 160 | 4790 | 1876 | 6666 | 1800 | 6666 | [5 empty] | Network Operation Division
20:00 | 164 | 4722 | 1860 | 6582 | 1800 | 6582
20:30 | 142 | 4731 | 1864 | 6595 | 1800 | 6595
21:00 | 120 | 4740 | 1868 | 6608 | 2100 | 6608
21:30 | 130 | 4772 | 1866.5 | 6638.5 | 1900 | 6638.5
22:00 | 140 | 4804 | 1865 | 6669 | 1900 | 6669
22:30 | 170 | 4754 | 1831.5 | 6585.5 |  | 6585.5
23:00 | 200 | 4704 | 1798 | 6502 |  | 6502
23:30 | 190 | 4596.5 | 1780 | 6376.5 |  | 6376.5
24:00 | 180 | 4489 | 1762 | 6251 |  | 6251
*MAX.GEN.(E.P.) |  | 6691 |  | 0.79167
*MAX.GEN.(D.P.) |  | 6103 |  | 0.5
6103 MW (12:00)
6691 MW (19:00)

## En.Curve
Date | 40275 |  | Energy | 134412422
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE
0:00 | 1479 | 334 | 2506 | 1482 | 84 | 46 | 655 | 0 | POWER GRID COMPANY OF BANGLADESH LTD.
0:30 | 1478 | 334 | 2550.5 | 1431.5 | 84 | 46 | 511.5 | 0 | NATIONAL LOAD DISPATCH CENTER
1:00 | 1477 | 334 | 2595 | 1381 | 84 | 46 | 368 | 0
1:30 | 1475.5 | 334 | 2572.5 | 1384.5 | 83.5 | 43 | 302.5 | 0 | [5 empty] | QF-LDC-12
2:00 | 1474 | 334 | 2550 | 1388 | 83 | 40 | 237 | 0 |  |  | DAILY ENERGY CURVE
2:30 | 1485 | 334 | 2511.5 | 1317.5 | 84 | 40 | 195 | 0 |  |  |  | Date: | 2014-04-08
3:00 | 1496 | 334 | 2473 | 1247 | 85 | 40 | 153 | 0
3:30 | 1498.5 | 334 | 2540 | 1148.5 | 84.5 | 40 | 153 | 0
4:00 | 1501 | 334 | 2607 | 1050 | 84 | 40 | 153 | 0
4:30 | 1490 | 392.5 | 2587.5 | 971 | 84.5 | 40 | 154 | 0
5:00 | 1479 | 451 | 2568 | 892 | 85 | 40 | 155 | 0
5:30 | 1492 | 450.5 | 2586 | 789.5 | 85 | 43 | 155.5 | 0
6:00 | 1505 | 450 | 2604 | 687 | 85 | 46 | 156 | 0
6:30 | 1492.5 | 450.5 | 2503.5 | 601 | 84.5 | 45 | 155.5 | 0
7:00 | 1480 | 451 | 2403 | 515 | 84 | 44 | 155 | 0
7:30 | 1445 | 451 | 2397.5 | 784.5 | 84.5 | 43.5 | 155 | 0
8:00 | 1410 | 451 | 2392 | 1054 | 85 | 43 | 155 | 0
8:30 | 1455 | 451 | 2447.5 | 1142.5 | 85 | 43 | 174 | 0
9:00 | 1500 | 451 | 2503 | 1231 | 85 | 43 | 193 | 0
9:30 | 1485 | 451 | 2526.5 | 1263 | 84 | 42.5 | 243.5 | 0
10:00 | 1470 | 451 | 2550 | 1295 | 83 | 42 | 294 | 0
10:30 | 1465 | 450.5 | 2572 | 1274 | 83.5 | 42 | 314.5 | 0
11:00 | 1460 | 450 | 2594 | 1253 | 84 | 42 | 335 | 0
11:30 | 1427 | 450.5 | 2574.5 | 1303 | 86 | 42 | 167.5 | 0
12:00 | 1394 | 451 | 2555 | 1353 | 88 | 42 | 0 | 0
12:30 | 1395.5 | 423.5 | 2551 | 1350.5 | 89 | 77.5 | 214.5 | 0
13:00 | 1397 | 396 | 2547 | 1348 | 90 | 113 | 429 | 0
13:30 | 1391 | 397 | 2558.5 | 1327.5 | 88 | 78 | 457 | 0
14:00 | 1385 | 398 | 2570 | 1307 | 86 | 43 | 485 | 0
14:30 | 1383.5 | 393 | 2572 | 1314 | 85 | 44.5 | 531.5 | 0
15:00 | 1382 | 388 | 2574 | 1321 | 84 | 46 | 578 | 0
15:30 | 1385 | 342 | 2569.5 | 1329 | 84 | 46 | 615 | 0
16:00 | 1388 | 296 | 2565 | 1337 | 84 | 46 | 652 | 0
16:30 | 1392 | 296 | 2581.5 | 1269 | 84.5 | 46 | 641.5 | 0
17:00 | 1396 | 296 | 2598 | 1201 | 85 | 46 | 631 | 0
17:30 | 1421 | 296 | 2608 | 1120.5 | 85 | 46 | 640 | 0
18:00 | 1446 | 296 | 2618 | 1040 | 85 | 46 | 649 | 0
18:30 | 1428 | 338 | 2634 | 1355 | 84 | 118 | 694 | 0
19:00 | 1460 | 338 | 2610 | 1380 | 84 | 186 | 689 | 0
19:30 | 1454 | 338 | 2629 | 1340 | 86 | 180 | 695 | 0
20:00 | 1399 | 338 | 2540 | 1343 | 85 | 176 | 685 | 0
20:30 | 1429 | 338.5 | 2553.5 | 1351.5 | 86 | 173 | 685.5 | 0 |  | Max Temp. in Dhaka |  | 34.2° C
21:00 | 1459 | 339 | 2567 | 1360 | 87 | 170 | 686 | 0
21:30 | 1470 | 338.5 | 2592.5 | 1363.5 | 85 | 166 | 680.5 | 0
22:00 | 1481 | 338 | 2618 | 1367 | 83 | 162 | 675 | 0
22:30 | 1453 | 338 | 2624.5 | 1386.5 | 85.5 | 162 | 613 | 0 | [5 empty] | Executive Engineer
23:00 | 1425 | 338 | 2631 | 1406 | 88 | 162 | 551 | 0 | [5 empty] | Network Operation Division
23:30 | 1436.5 | 338 | 2586.5 | 1410 | 89 | 104 | 507.5 | 0
24:00 | 1448 | 338 | 2542 | 1414 | 90 | 46 | 464 | 0
|  | 1490 |  |  |  |  | 2380 | 0

## volt
NATIONAL LOAD DESPATCH CENTER
The Maximum & Minimum Voltages of different Sub-Stations.
Date : | 2014-04-08
| Maxm |  | Minm |  |  | Maxm |  | Minm
Substation | Voltage | Hour | Voltage | Hour | Substation | Voltage | Hour | Voltage | Hour
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Hathazari | 210 | 600 | 204 | 1600 | Megnaghat | 213 | 500 | 208 | 1000
Comilla(N) | 222 | 700 | 215 | 1500 | Haripur | 214 | 700 | 208 | 1200
Ashuganj | 227 | 800 | 225 | 100 | Ishurdi | 232 | 1800 | 220 | 200
Ghorasal | 220 | 1700 | 210 | 1930 | Baghabari | 223 | 2100 | 213 | 1200
Rampura | 213 | 700 | 205 | 1200 | Serajganj | 226 | 1900 | 215 | 1300
Tongi | 207 | 500 | 200 | 1930 | Bogra | 226 | 1700 | 215 | 1200
Aminbazar | 211 | 400 | 203 | 100 | Barapukuria | 225 | 200 | 219 | 1000
Hasnabad | 228 | 300 | 220 | 1830 | Khulna South | 230 | 1800 | 210 | 200
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 500 | 131 | 1200 | Khulshi | 129 | 2000 | 123 | 1600
Munsiganj | 132 | 1400 | 127 | 500 | Halishahar | 124 | 700 | 118 | 1000
Megnaghat | 135 | 2100 | 131 | 1000 | Baraulia | 124 | 1900 | 119 | 1000
Shyampur | 131 | 300 | 125 | 1200 | Sikalbaha | 123 | 1930 | 118 | 1100
Bhulta | 122 | 400 | 116 | 1930 | Dohazari | 122 | 600 | 116 | 1600
Madanganj | 130 | 600 | 123 | 1200 | Cox'sbazar | 122 | 400 | 114 | 1600
Shitalakhya | 133 | 800 | 126 | 2300 | Chandraghona | 126 | 700 | 120 | 1500
Rahim steal | 134 | 1500 | 130 | 1200 | Kaptai | 127 | 1830 | 120 | 900
Matuail | 133 | 500 | 129 | 1200 | A. Khaer Stl. | 124 | 1930 | 119 | 1600
Ghorasal | 135 | 100 | 132 | 1000 | Bakulia | 122 | 700 | 116 | 1600
Narsinghdi | 135 | 500 | 129 | 1500 | Julda | 122 | 500 | 117 | 1500
Haripur (SBU) | 134 | 700 | 130 | 1200 | TK Chemical | 126 | 1830 | 121 | 1600
Ullon | 133 | 200 | 129 | 1200 | Modern Steel | 122 | 500 | 118 | 1100
Hasnabad | 131 | 400 | 128 | 900 | Shahmirpur | 122 | 600 | 118 | 1000
Magbazar | 127 | 400 | 120 | 1200 | Goalpara | 139 | 2200 | 124 | 200
Maniknagar | 131 | 800 | 126 | 1200 | Central s/s | 137 | 1400 | 124 | 200
Bangabhaban | 131 | 800 | 126 | 1200 | Noapara | 135 | 1400 | 120 | 200
Narinda | 131 | 800 | 126 | 1200 | Jessore | 128 | 800 | 117 | 200
Dhanmondi | 131 | 800 | 126 | 1200 | Jhenida | 129 | 900 | 114 | 200
Mirpur | 130 | 500 | 121 | 1200 | Bottail | 137 | 1800 | 129 | 1000
Kalyanpur | 133 | 700 | 125 | 200 | G.K.Project | 135 | 300 | 129 | 1200
Gulshan | 133 | 400 | 119 | 1200 | Faridpur | 134 | 600 | 122 | 1930
Uttara | 128 | 300 | 120 | 1830 | Madaripur | 136 | 600 | 118 | 1930
Kamrangirchar | 130 | 500 | 122 | 1200 | Gopalganj | 138 | 1800 | 123 | 1200
Savar | 131 | 600 | 124 | 1900 | Bagerhat | 132 | 500 | 123 | 1100
Bhasantec | 126 | 400 | 120 | 1200 | Mongla | 133 | 800 | 120 | 1000
Tongi | 134 | 700 | 126 | 1830 | Satkhira | 136 | 1400 | 123 | 200
Kabirpur | 131 | 1300 | 126 | 1000 | Gallamari | 137 | 1400 | 125 | 200
Basundhara | 121 | 500 | 114 | 1300 | Magura | 128 | 600 | 116 | 2200
Manikganj | 127 | 500 | 118 | 1830 | Chuadanga | 129 | 900 | 115 | 300
Joydevpur | 135 | 100 | 129 | 2100 | Barisal | 135 | 500 | 121 | 2000
New Tongi | 131 | 400 | 122 | 1900 | Patuakhali | 135 | 300 | 115 | 1930
Tangail | 134 | 500 | 116 | 1900 | Bhandaria | 131 | 800 | 121 | 1930
Mymensing | 135 | 200 | 123 | 2200 | Ishurdi | 136 | 1900 | 128 | 1200
Kishorganj | 135 | 400 | 125 | 2200 | Natore | 132 | 2000 | 122 | 1300
Netrokona | 136 | 500 | 122 | 2100 | Bogra | 132 | 500 | 120 | 1200
Jamalpur | 128 | 400 | 120 | 2200 | Noagaon | 128 | 1830 | 119 | 1100
Srimongal | 140 | 100 | 136 | 800 | Rajshahi | 134 | 1800 | 119 | 1300
Shahjibazar | 143 | 1100 | 140 | 500 | C.Nawabganj | 130 | 1800 | 115 | 1300
Fenchuganj | 137 | 100 | 136 | 1500 | Pabna | 130 | 1600 | 125 | 1300
Sylhet | 137 | 100 | 136 | 200 | Shahjadpur | 136 | 700 | 130 | 500
Chatak | 136 | 100 | 134 | 1900 | Serajganj | 130 | 1700 | 123 | 1200
B.Baria | 136 | 100 | 133 | 800 | Niyamatpur | 126 | 2000 | 112 | 1200
Comilla(S) | 133 | 700 | 128 | 1500 | Joypurhat | 130 | 1900 | 115 | 1000
Comilla(N) | 133 | 800 | 130 | 1000 | Rangpur | 124 | 1800 | 118 | 1200
Chandpur | 131 | 500 | 125 | 2000 | Lalmonirhat | 124 | 1600 | 115 | 1000
Feni | 125 | 700 | 119 | 1500 | Saidpur | 123 | 1830 | 116 | 1000
Chowmuhani | 127 | 800 | 120 | 1500 | Purbasadipur | 126 | 1830 | 116 | 1000
Ashuganj | 143 | 600 | 140 | 2100 | Thakurgaon | 122 | 1500 | 112 | 1200
Daudkandi | 133 | 700 | 125 | 1600 | Palashbari | 125 | 1800 | 116 | 1300
Madanhat | 126 | 600 | 120 | 1600 | Barapukuria | 125 | 200 | 119 | 1000
Hathazari | 125 | 400 | 121 | 1500 | Panchagar | 120 | 1500 | 108 | 1000