## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2019-09-05 | Thursday
|  | Date (day): | 2019-09-05 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13270 | MW |  |  | (b) At Evening Peak Hour : |  | 14720 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2019-09-04 | 2019-09-05 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | Gas | PDB | 2*55 | 110 | 85 | 70 | 70 | 70 | 70
| Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 200 | 200 | 200 | 200
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 60 | 68 | 70 | 70 |  | 8 | Engine problem
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 97 | 94 | 97 |  | 13 | Engine problem
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 |  | 40 | Machine problem
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 320 | 342 | 350 | 395 |  |  | FGMO
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 254 | 303 | 290 | 290 |  |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 330 | 330 | 330 |  |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 240 | 275 | 150 | 150 |  | 110 | GT-2 under maint.
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 98 | 100 | 100
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 42 | 41 | 42 |  | 13 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 100 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| Siddhirganj Desh |  | HSD | QRPP | 96*1.2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217 | 217 | 217 | 328 | 333 | 335 | 335
| Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 75 | 101 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 13 | 40 | 40 | 40
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 53 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 135 | 133 | 133 |  | 16 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 72 | 72 | 72 | 72 |  | 36 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 56 | 57 | 57 |  | 23 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 34 | 43 | 43 | 43 |  | 9 | Engine problem
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 300 | 200 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 0 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 100 | 135 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 70 | 70 | 70 |  | 35 | Engine problem
| Dhaka area Total |  |  |  |  | 5929 | 5693 | 2659 | 3751 | 3556 | 4205 | 315 | 953
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 95 | 100 | 100 | 80 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
38 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 25 | 25 | 25
39 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3.97 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 20 | 39 | 50 | 50
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 213 | 211 | 215 | 215
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 204 | 215 | 215
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 92 | 130 | 130 | 130
| Sikalbaha 51 MW PP(Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 17 | 50 | 100
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 3 | 0 | 0 |  | 98 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 50 | 80
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 50 | 100 | 100
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 30 | 10 | 30
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 25 | 97 | 90 | 90 |  | 18 | Engine problem
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5.3 | 0 | 4.4 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 100 | 106 | 230 | 260
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 34 | 17 | 54 | 54
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 50 | 113 | 113
| Chattogram area Total |  |  |  |  | 2226 | 2166 | 1095.27 | 1384 | 1698.4 | 1804 | 140 | 116
55 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100
56 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 139 | 142 | 225 | 225
57 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 345 | 360 | 360 |  |  | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 200 | 360 | 360
59 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 30 | 30 | 30 | 30 |  | 15 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 51 | 55 | 55
61 | Ashuganj 53MW PP (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 0 | 0 | 0 | 0 |  |  | Contract expired
62 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 75 | 68 | 68 | 68 | 127 |  | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 50 | 50 | 150 | 150
65 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 0 | 0 | 0 | 0 |  |  | Contract expired
66 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
67 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 84 | 200 | 200 | 200
69 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
70 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 144 | 188 | 149 | 191
71 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
72 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
73 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 20 | 20 |  | 5 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Cumilla Area Total |  |  |  |  | 2951 | 2891 | 1437 | 1604 | 1878 | 2170 | 391 | 191
75 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 150 | 153 | 150 | 150 | 52 |  | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
77 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 64 | 95 | 95 | 95
78 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1.4 | 0 | 1.6 | 0
79 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 7 | 190 | 200 | 200
80 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| Mymensingh Area Total |  |  |  |  | 645 | 637 | 359.4 | 575 | 583.6 | 582 | 52 | 0
81 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 60 | 60 | 60 | 60
82 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | !F71 | 104 | 90 | 41 | 42 | 42 | 42
83 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 100 | 163 | 163
84 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 256 | 242 | 259 | 259 |  |  | FGMO
85 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 51 | 51 | 51
86 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 49 | 48 | 50 | 50
87 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
88 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 65 | 66 | 66 |  |  | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 70 | 72 | 77 | 77
90 | Shahjibazar 50MW PP (EPL) |  | Gas | RPP | 27*2.0 | 50 | 50 | 44 | 46 | 45 | 46
91 | Sylhet 150 MW CCPP |  | Gas | PDB | 1*142 | 142 | 142 | 48 | 48 | 0 | 0 |  | 150 | Under maint.
92 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 0 | 18 | 18
93 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 39 | 46 | 46 | 46
94 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
95 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 315 | 320 |  |  | FGMO
96 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285 MW | 285 | 285 | 0 | 0 | 0 | 0 |  | 285 | Under S/D
97 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1879 | 1834 | 1189 | 1155 | 1237 | 1243 | 0 | 435
98 | Bheramara GTPP Unit-1,2 & 3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 30
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 906 | 906 | 925 | 925
| Khulna 115 MW PP (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract expired
99 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 115 | 115 | 115
100 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 24 | 0 | 40
101 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200
102 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 63 | 0 | 70
103 | Bheramara 360 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 340 | 380 | 410
104 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
| Khulna (Aggreeco) 55MW |  | HSD | QRPP | 71*0.85 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 80 | 100
106 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
107 | Madhumati 100 MW PP |  | HFO | IPP | 100 MW | 105 | 105 | 95 | 103 | 100 | 100
| Khulna Area Total |  |  |  |  | 2328 | 2314 | 1412 | 1796 | 1945 | 2135 | 0 | 0
108 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 70 | 110
109 | Barisal GT PP Unit-1& 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
110 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 39 | 25 | 35
111 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 179 | 179 | 180 | 180
112 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 220 | 424 | 370 | 450 | 0 | 0
113 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 55 | 55 | 60 | 60 | 11 |  | Gas Shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
115 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 43 | 0 | 43
116 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 50 | 40 | 50
117 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 30 | 31
119 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 202 | 186 | 215 | 215 |  |  | FGMO
120 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas Shortage
121 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 196 | 205 | 215 |  |  | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 330 | 400 | 400
123 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 0 | 35
124 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
125 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 10 | 10 | 10
126 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
127 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 16 | 51 | 52 | 52
128 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 80 | 100
129 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
130 | Bagura 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 74 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2080 | 2070 | 986 | 1305 | 1530 | 1649 | 231 | 108
131 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 71 | 71 | 71 | 71
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 275 | 270 | 280 | 280
133 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
134 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
135 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 74 | 91 | 113 | 113 |  |  | On test
136 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4.4 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 424.4 | 432 | 472 | 482 | 0 | 105
| Total |  |  |  |  | 19195 | 18672 | 9782.07 | 12426 | 13270 | 14720 | 1129 | 1908
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9397.9037 | 11938 | 12748.854 | 14141.9089
A. |  | 2019-09-04 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 12426 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 8940 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12426 | MW
3 | Day peak Generation : |  |  | 9782.07 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11938 | MW
4 | Evening peak Generation : |  |  | 12426 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 251.8819 | MKWHr | By Solar | 0.20195 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 148.9023 | MKWHr |  | By Oil: | 64.5902 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 8.1228 | MKWHr |  | By Hydro: | 4.5251 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1129 | MW | Dhaka | 4249 | 4249 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1908 | MW | Chittagong | 1190 | 1190 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3037 | MW | Khulna | 1446 | 1446 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1323.84 | MMCFD |  |  | Rajshahi | 1277 | 1277 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 145251716.144 | ii) Oil : | Taka | 564829677.64 | Comilla | 1156 | 1156 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 36997932 | Total | Taka | 747079325.784 | Mymensingh | 1013 | 1013 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0.291 | MKWHr. | Sylhet | 533 | 533 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -45 | MW (E to W) at | 20:00 | hrs | Barisal | 329 | 329 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -95 | MW at | 22:00 | hrs | Rangpur | 745 | 745 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.5° C |  |  | Total | 11938 | 11938 |  | 0
B. |  | 2019-09-05 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14720 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
4 | Reserve(Generation end) |  |  |  | 1820 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 261.4901 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8992 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7418 | MKWHr. | ii) HVDC Flow at Peak Time |  | 906 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7978 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.48 |  | (b) Today: | 105.48 |  | (c) Rule Curve: |  | 0
.

## YesterdayGen
2019-09-04
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj Desh | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Sikalbaha 51 MW PP(Energis) | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 150 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-1,2 & 3 | Bheramara 360 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence) | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 70 | 0 | 200 | 110 | 0 | 97 | 69 | 185 | 330 |  | 0 | 320 | 265 | 100 | 45 | 15 | 336 | 0 | 0 | 0 | 0 | 64 | 133 | 0 | 72 | 0 | 27 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 120 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 51 | 50 | 22 | 39 | 0 | 0 | 100 | 320 | 275 | 144 | 68 | 0 | 26 | 53 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 174 | 155 | 95 | 22 | 0 | 60 | 41 | 53 | 49 | 130 | 243 | 67 | 73 | 46 | 48 | 18 | 42 | 10 | 270 | 24 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 138 | 0 | 100 | 180 | 100 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 905 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 24 | 55 | 40 | 180 | 31 | 110 | 0 | 0 | 55 | 50 | 37 | 88 | 12 | 42 | 30 | 8 | 22 | 22 | 7 | 11 | 71 | 0 | 260 | 0 | 15 | 186 | 0 | 0 | 0 | 95 | 20 | 191 | 0 | 415 | 105 | 0 | 113 | 104 | 105 | 0 | 0 |  | 7672 | 3888 | 11560 | 4255 | 905 | 2262 | 2952 | 331 | 210 | 471 | 174 | 0 | 0 | 105.53
2:00 | 70 | 0 | 200 | 110 | 0 | 97 | 69 | 375 | 330 |  | 0 | 320 | 269 | 60 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 40 | 65 | 0 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 120 | 90 | 95 | 120 | 25 | 213 | 0 | 130 | 0 |  | 0 | 0 | 17 | 10 | 51 | 50 | 22 | 39 | 0 | 0 | 100 | 340 | 275 | 144 | 68 | 0 | 26 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 170 | 154 | 95 | 22 | 0 | 60 | 41 | 52 | 49 | 130 | 241 | 67 | 73 | 46 | 48 | 18 | 41 | 10 | 285 | 24 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 72 | 0 | 100 | 180 | 100 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 906 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 180 | 31 | 96 | 0 | 0 | 55 | 0 | 37 | 88 | 12 | 42 | 30 | 8 | 22 | 22 | 7 | 11 | 69 | 0 | 260 | 0 | 15 | 185 | 0 | 0 | 0 | 97 | 0 | 189 | 0 | 415 | 105 | 0 | 113 | 104 | 98 | 0 | 0 |  | 7531 | 3716 | 11247 | 4463 | 906 | 2279 | 2616 | 329 | 210 | 274 | 170 | 0 | 0 | 105.52
3:00 | 70 | 0 | 200 | 110 | 0 | 97 | 70 | 395 | 330 |  | 0 | 320 | 262 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 16 | 65 | 0 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 120 | 90 | 95 | 120 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 51 | 50 | 22 | 39 | 0 | 0 | 100 | 320 | 275 | 144 | 68 | 0 | 0 | 55 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 166 | 154 | 95 | 22 | 0 | 60 | 41 | 53 | 49 | 130 | 241 | 67 | 73 | 46 | 49 | 18 | 41 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 20 | 0 | 100 | 180 | 100 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 906 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 30 | 32 | 0 | 0 | 55 | 0 | 0 | 88 | 12 | 42 | 30 | 8 | 22 | 22 | 7 | 11 | 69 | 0 | 261 | 0 | 0 | 187 | 0 | 0 | 0 | 97 | 0 | 190 | 0 | 415 | 105 | 0 | 113 | 104 | 98 | 0 | 0 |  | 7302 | 3602 | 10904 | 4433 | 906 | 2295 | 2359 | 330 | 210 | 205 | 166 | 0 | 0 | 105.51
4:00 | 70 | 0 | 200 | 110 | 0 | 97 | 69 | 360 | 330 |  | 0 | 320 | 270 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 16 | 36 | 0 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 118 | 90 | 95 | 120 | 8 | 204 | 0 | 135 | 0 |  | 0 | 0 | 0 | 10 | 51 | 50 | 22 | 41 | 0 | 0 | 100 | 335 | 275 | 144 | 68 | 0 | 0 | 54 | 0 | 43 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 164 | 156 | 95 | 22 | 0 | 60 | 41 | 53 | 49 | 130 | 240 | 67 | 73 | 46 | 49 | 18 | 41 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 100 | 180 | 100 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 906 | 0 | 380 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 40 | 179 | 30 | 0 | 0 | 0 | 55 | 0 | 0 | 88 | 12 | 42 | 0 | 8 | 0 | 22 | 7 | 11 | 69 | 0 | 260 | 0 | 0 | 186 | 0 | 0 | 0 | 95 | 0 | 190 | 0 | 415 | 105 | 0 | 113 | 104 | 98 | 0 | 0 |  | 7186 | 3481 | 10667 | 4418 | 906 | 2283 | 2235 | 329 | 208 | 124 | 164 | 0 | 0 | 105.5
5:00 | 70 | 0 | 200 | 110 | 0 | 97 | 70 | 356 | 330 |  | 0 | 320 | 272 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 72 | 0 | 13 | 53 | 35 | 17 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 118 | 90 | 95 | 120 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 51 | 47 | 22 | 35 | 0 | 0 | 100 | 345 | 275 | 144 | 68 | 0 | 0 | 54 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 152 | 156 | 75 | 22 | 0 | 60 | 41 | 50 | 49 | 130 | 243 | 67 | 73 | 46 | 48 | 18 | 42 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 100 | 180 | 50 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 906 | 0 | 380 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 16 | 179 | 24 | 0 | 0 | 0 | 55 | 0 | 0 | 88 | 12 | 42 | 0 | 8 | 0 | 22 | 7 | 11 | 69 | 0 | 260 | 0 | 0 | 187 | 0 | 0 | 0 | 94 | 0 | 190 | 0 | 360 | 105 | 0 | 113 | 104 | 98 | 0 | 0 |  | 6970 | 3396 | 10366 | 4420 | 906 | 2224 | 2019 | 329 | 208 | 108 | 152 | 0 | 0 | 105.49
6:00 | 70 | 0 | 200 | 110 | 0 | 97 | 50 | 350 | 300 |  | 0 | 320 | 260 | 0 | 0 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 69 | 0 | 13 | 53 | 35 | 17 | 22 | 25 | 30 | 25 | 33 | 43 | 0 | 118 | 90 | 95 | 120 | 8 | 203 | 0 | 90 | 0 |  | 0 | 0 | 0 | 10 | 51 | 44 | 22 | 40 | 0 | 0 | 100 | 295 | 275 | 144 | 68 | 0 | 0 | 54 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 138 | 159 | 64 | 22 | 0 | 60 | 41 | 50 | 49 | 130 | 240 | 69 | 71 | 46 | 48 | 18 | 42 | 10 | 260 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 100 | 140 | 50 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 906 | 0 | 300 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 8 | 167 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 88 | 12 | 42 | 0 | 8 | 0 | 22 | 7 | 8 | 69 | 0 | 260 | 0 | 0 | 180 | 0 | 0 | 0 | 97 | 0 | 181 | 0 | 320 | 96 | 0 | 113 | 103 | 98 | 0 | 0 |  | 6629 | 3192 | 9821 | 4215 | 906 | 2096 | 1825 | 329 | 208 | 104 | 138 | 0 | 0 | 105.48
7:00 | 70 | 0 | 200 | 110 | 0 | 97 | 50 | 342 | 300 |  | 0 | 300 | 265 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 13 | 35 | 35 | 17 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 120 | 90 | 95 | 120 | 8 | 205 | 0 | 90 | 0 |  | 0 | 0 | 0 | 10 | 25 | 17 | 22 | 31 | 0 | 0 | 100 | 260 | 315 | 145 | 68 | 0 | 20 | 54 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 128 | 158 | 64 | 22 | 0 | 60 | 41 | 50 | 49 | 100 | 240 | 69 | 71 | 46 | 48 | 18 | 43 | 10 | 255 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 50 | 70 | 50 | 0 | 115 | 70 | 17 | 0 | 71 | 34 | 17 |  | 907 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 167 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 24 | 0 | 8 | 0 | 22 | 7 | 8 | 70 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 0 | 62 | 0 | 159 | 0 | 270 | 17 | 0 | 74 | 100 | 73 | 0 | 0 |  | 6342 | 2799 | 9141 | 4173 | 907 | 1949 | 1413 | 330 | 210 | 24 | 128 | 7 | 0 | 105.39
8:00 | 70 | 0 | 200 | 110 | 0 | 96 | 50 | 343 | 270 |  | 0 | 300 | 265 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 40 | 0 | 13 | 35 | 35 | 17 | 22 | 25 | 31 | 33 | 33 | 34 | 0 | 120 | 90 | 95 | 120 | 8 | 205 | 0 | 90 | 0 |  | 0 | 0 | 0 | 10 | 25 | 0 | 22 | 10 | 0 | 0 | 100 | 260 | 305 | 146 | 68 | 0 | 27 | 50 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 20 | 132 | 158 | 65 | 22 | 0 | 60 | 41 | 11 | 49 | 100 | 240 | 68 | 40 | 46 | 48 | 18 | 42 | 10 | 270 | 24 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 10 | 50 | 70 | 50 | 0 | 115 | 70 | 17 | 1 | 71 | 34 | 17 |  | 907 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 166 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 24 | 0 | 8 | 0 | 22 | 7 | 8 | 70 | 0 | 260 | 0 | 0 | 165 | 0 | 0 | 0 | 23 | 0 | 161 | 0 | 240 | 17 | 0 | 74 | 105 | 70 | 0 | 0 |  | 6205 | 2735 | 8940 | 4167 | 907 | 1765 | 1394 | 330 | 210 | 24 | 132 | 11 | 0 | 0
9:00 | 70 | 0 | 200 | 110 | 0 | 93 | 50 | 352 | 270 |  | 0 | 300 | 270 | 0 | 0 | 0 | 338 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 40 | 0 | 13 | 35 | 35 | 21 | 22 | 25 | 30 | 25 | 33 | 34 | 0 | 121 | 90 | 100 | 120 | 8 | 230 | 0 | 91 | 0 |  | 0 | 0 | 0 | 10 | 25 | 0 | 22 | 3 | 0 | 0 | 100 | 270 | 295 | 143 | 68 | 0 | 30 | 50 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 0 | 136 | 155 | 64 | 22 | 1 | 59 | 41 | 11 | 49 | 100 | 240 | 66 | 40 | 46 | 47 | 18 | 41 | 10 | 275 | 24 | 4 | 0 | 0 | 0 | 0 | 7 | 0 | 66 | 17 | 50 | 70 | 50 | 0 | 115 | 70 | 17 | 4 | 68 | 34 | 17 |  | 906 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 17 | 0 | 0 | 0 | 60 | 0 | 0 | 24 | 12 | 24 | 0 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 275 | 0 | 0 | 166 | 0 | 0 | 0 | 23 | 0 | 167 | 0 | 280 | 17 | 0 | 74 | 97 | 70 | 0 | 1 |  | 6294 | 2803 | 9097 | 4193 | 906 | 1798 | 1460 | 346 | 211 | 24 | 136 | 23 | 0 | 0
10:00 | 70 | 0 | 200 | 110 | 0 | 90 | 50 | 368 | 274 |  | 0 | 300 | 240 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 40 | 0 | 13 | 35 | 35 | 35 | 22 | 25 | 30 | 33 | 33 | 34 | 0 | 122 | 90 | 95 | 120 | 8 | 216 | 0 | 93 | 0 |  | 0 | 0 | 0 | 10 | 25 | 1 | 22 | 2 | 0 | 0 | 100 | 360 | 290 | 144 | 68 | 0 | 30 | 51 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 33 | 17 | 138 | 153 | 64 | 22 | 1 | 60 | 41 | 11 | 49 | 100 | 247 | 65 | 40 | 46 | 48 | 18 | 39 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 96 | 18 | 50 | 70 | 50 | 0 | 115 | 70 | 17 | 3 | 69 | 34 | 17 |  | 906 | 0 | 270 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 14 | 0 | 0 | 0 | 55 | 0 | 0 | 24 | 12 | 42 | 0 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 275 | 0 | 0 | 170 | 0 | 0 | 0 | 23 | 0 | 173 | 0 | 350 | 17 | 0 | 74 | 87 | 70 | 0 | 2 |  | 6500 | 2884 | 9384 | 4313 | 906 | 1904 | 1501 | 346 | 212 | 40 | 138 | 24 | 0 | 0
11:00 | 70 | 0 | 200 | 110 | 0 | 87 | 50 | 363 | 274 |  | 0 | 300 | 240 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 0 | 50 | 16 | 23 | 40 | 0 | 13 | 35 | 35 | 35 | 22 | 25 | 26 | 33 | 33 | 34 | 0 | 121 | 90 | 95 | 120 | 8 | 212 | 0 | 96 | 0 |  | 0 | 0 | 0 | 10 | 25 | 17 | 22 | 2 | 0 | 0 | 100 | 360 | 285 | 140 | 68 | 0 | 30 | 53 | 0 | 43 | 0 | 0 | 8 | 18 | 8 | 33 | 17 | 140 | 151 | 64 | 22 | 1 | 60 | 41 | 14 | 49 | 100 | 243 | 63 | 60 | 44 | 48 | 18 | 39 | 10 | 310 | 25 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 20 | 50 | 70 | 50 | 0 | 115 | 70 | 17 | 2 | 69 | 34 | 17 |  | 906 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 180 | 17 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 8 | 0 | 22 | 7 | 8 | 71 | 0 | 275 | 0 | 0 | 205 | 0 | 0 | 0 | 23 | 0 | 177 | 0 | 350 | 17 | 0 | 74 | 93 | 70 | 0 | 3 |  | 6560 | 2939 | 9499 | 4356 | 906 | 1922 | 1576 | 346 | 211 | 16 | 140 | 26 | 0 | 0
12:00 | 70 | 0 | 200 | 110 | 0 | 88 | 60 | 320 | 254 |  | 0 | 300 | 240 | 0 | 0 | 15 | 328 | 0 | 0 | 0 | 0 | 75 | 16 | 50 | 72 | 0 | 13 | 35 | 35 | 35 | 22 | 25 | 26 | 33 | 33 | 34 | 0 | 123 | 90 | 95 | 120 | 8 | 218 | 0 | 92 | 0 |  | 0 | 0 | 0 | 10 | 25 | 20 | 22 | 5 | 0 | 0 | 100 | 360 | 275 | 139 | 75 | 0 | 30 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 17 | 144 | 150 | 64 | 22 | 1 | 60 | 41 | 47 | 49 | 100 | 256 | 62 | 70 | 44 | 48 | 18 | 39 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 3 | 90 | 84 | 50 | 0 | 115 | 70 | 17 | 5 | 100 | 34 | 17 |  | 906 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 16 | 0 | 22 | 7 | 8 | 71 | 0 | 275 | 0 | 0 | 202 | 0 | 0 | 0 | 22 | 0 | 198 | 0 | 350 | 17 | 0 | 74 | 95 | 74 | 0 | 4 |  | 6738 | 3042 | 9780 | 4399 | 906 | 1966 | 1777 | 346 | 213 | 16 | 144 | 13 | 0 | 0
13:00 | 70 | 0 | 200 | 110 | 0 | 94 | 67 | 280 | 254 |  | 0 | 300 | 240 | 0 | 0 | 32 | 331 | 0 | 0 | 0 | 0 | 93 | 16 | 50 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 34 | 0 | 124 | 90 | 95 | 120 | 8 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 43 | 40 | 22 | 8 | 0 | 0 | 100 | 325 | 145 | 143 | 75 | 0 | 30 | 51 | 0 | 43 | 0 | 0 | 25 | 19 | 8 | 33 | 17 | 140 | 151 | 83 | 22 | 1 | 60 | 41 | 47 | 48 | 100 | 240 | 57 | 70 | 44 | 48 | 18 | 38 | 10 | 265 | 24 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 100 | 5 | 100 | 139 | 50 | 0 | 115 | 70 | 17 | 5 | 105 | 34 | 17 |  | 906 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 24 | 166 | 18 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 7 | 8 | 71 | 0 | 275 | 0 | 0 | 193 | 0 | 0 | 0 | 22 | 0 | 206 | 0 | 350 | 30 | 0 | 94 | 0 | 95 | 0 | 4 |  | 6728 | 2981 | 9709 | 4162 | 906 | 1933 | 1977 | 346 | 214 | 16 | 140 | 15 | 0 | 0
14:00 | 70 | 0 | 200 | 110 | 0 | 94 | 66 | 280 | 254 |  | 0 | 300 | 240 | 0 | 0 | 42 | 329 | 0 | 0 | 0 | 0 | 101 | 16 | 50 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 43 | 0 | 113 | 90 | 95 | 120 | 15 | 204 | 0 | 130 | 0 |  | 0 | 5 | 0 | 10 | 51 | 48 | 22 | 7 | 0 | 0 | 100 | 335 | 70 | 142 | 75 | 0 | 30 | 50 | 0 | 43 | 0 | 0 | 52 | 18 | 8 | 33 | 17 | 142 | 154 | 95 | 22 | 2 | 59 | 41 | 50 | 48 | 163 | 238 | 63 | 70 | 44 | 47 | 18 | 41 | 10 | 270 | 24 | 11 | 0 | 0 | 0 | 0 | 81 | 0 | 100 | 11 | 100 | 151 | 50 | 0 | 115 | 70 | 17 | 5 | 106 | 34 | 17 |  | 906 | 0 | 370 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 24 | 166 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 42 | 0 | 16 | 0 | 22 | 7 | 8 | 70 | 0 | 275 | 0 | 0 | 195 | 0 | 0 | 0 | 22 | 0 | 199 | 0 | 418 | 53 | 0 | 107 | 59 | 102 | 0 | 3 |  | 6914 | 3188 | 10102 | 4122 | 906 | 2074 | 2268 | 345 | 203 | 21 | 142 | 21 | 0 | 0
15:00 | 70 | 0 | 200 | 110 | 0 | 94 | 66 | 300 | 254 |  | 0 | 300 | 240 | 0 | 0 | 42 | 326 | 0 | 0 | 0 | 0 | 101 | 16 | 50 | 72 | 0 | 13 | 53 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 43 | 0 | 112 | 90 | 95 | 120 | 25 | 217 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 51 | 50 | 22 | 4 | 0 | 0 | 100 | 360 | 70 | 139 | 68 | 0 | 26 | 48 | 0 | 43 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 148 | 150 | 95 | 22 | 0 | 59 | 41 | 50 | 48 | 163 | 246 | 62 | 70 | 44 | 48 | 18 | 41 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 16 | 100 | 175 | 50 | 0 | 115 | 70 | 17 | 3 | 106 | 34 | 17 |  | 908 | 0 | 400 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 24 | 180 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 16 | 0 | 21 | 7 | 8 | 70 | 0 | 269 | 0 | 0 | 197 | 0 | 0 | 0 | 52 | 0 | 198 | 0 | 414 | 53 | 0 | 113 | 104 | 105 | 0 | 5 |  | 7023 | 3321 | 10344 | 4222 | 908 | 2096 | 2389 | 339 | 202 | 16 | 148 | 24 | 0 | 0
16:00 | 70 | 0 | 200 | 110 | 0 | 93 | 65 | 375 | 255 |  | 0 | 300 | 240 | 0 | 0 | 26 | 328 | 0 | 0 | 0 | 0 | 101 | 16 | 50 | 72 | 0 | 13 | 53 | 55 | 40 | 22 | 0 | 19 | 33 | 33 | 43 | 0 | 112 | 90 | 95 | 120 | 25 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 51 | 0 | 22 | 5 | 0 | 0 | 100 | 335 | 25 | 141 | 68 | 0 | 26 | 48 | 0 | 43 | 0 | 0 | 52 | 18 | 11 | 33 | 20 | 146 | 151 | 95 | 22 | 1 | 60 | 42 | 50 | 48 | 163 | 240 | 65 | 70 | 45 | 48 | 18 | 46 | 10 | 315 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 7 | 100 | 195 | 50 | 0 | 115 | 70 | 17 | 1 | 106 | 34 | 22 |  | 909 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 0 | 1 | 24 | 179 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 16 | 0 | 21 | 7 | 8 | 71 | 0 | 269 | 0 | 0 | 196 | 0 | 0 | 0 | 51 | 0 | 198 | 0 | 414 | 73 | 0 | 113 | 104 | 105 | 0 | 4 |  | 6985 | 3351 | 10336 | 4199 | 909 | 2137 | 2373 | 340 | 202 | 17 | 146 | 13 | 0 | 0
17:00 | 70 | 0 | 194 | 110 | 0 | 93 | 66 | 392 | 255 |  | 0 | 300 | 240 | 0 | 0 | 36 | 329 | 0 | 0 | 0 | 0 | 101 | 16 | 10 | 72 | 0 | 19 | 53 | 55 | 35 | 22 | 25 | 26 | 33 | 33 | 43 | 0 | 112 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 51 | 0 | 22 | 15 | 0 | 0 | 100 | 335 | 0 | 141 | 68 | 0 | 30 | 49 | 0 | 10 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 140 | 150 | 95 | 22 | 0 | 60 | 42 | 45 | 48 | 163 | 232 | 60 | 10 | 5 | 47 | 0 | 20 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 100 | 0 | 100 | 100 | 10 | 0 | 115 | 70 | 17 | 0 | 106 | 17 | 50 |  | 906 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 22 | 23 | 24 | 168 | 25 | 0 | 12 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 16 | 0 | 22 | 7 | 8 | 71 | 0 | 269 | 0 | 0 | 187 | 0 | 0 | 0 | 53 | 0 | 200 | 0 | 414 | 105 | 0 | 94 | 104 | 100 | 0 | 1 |  | 6629 | 3399 | 10028 | 4170 | 906 | 1968 | 2228 | 340 | 202 | 73 | 140 | 1 | 0 | 0
18:00 | 70 | 0 | 200 | 110 | 0 | 52 | 66 | 338 | 254 |  | 0 | 300 | 240 | 1 | 2 | 42 | 332 | 0 | 0 | 0 | 1 | 101 | 26 | 18 | 72 | 0 | 20 | 53 | 55 | 35 | 22 | 25 | 22 | 33 | 33 | 43 | 0 | 119 | 90 | 95 | 120 | 25 | 177 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 88 | 35 | 22 | 18 | 0 | 0 | 100 | 260 | 0 | 143 | 68 | 0 | 30 | 51 | 0 | 10 | 0 | 0 | 52 | 21 | 11 | 33 | 0 | 144 | 152 | 95 | 22 | 0 | 60 | 42 | 8 | 10 | 130 | 233 | 67 | 10 | 5 | 48 | 0 | 18 | 10 | 290 | 24 | 11 | 0 | 2 | 0 | 0 | 100 | 0 | 105 | 0 | 100 | 50 | 10 | 0 | 115 | 70 | 17 | 0 | 107 | 17 | 50 |  | 905 | 0 | 270 | 0 | 42 | 0 | 0 | 0 | 31 | 36 | 8 | 167 | 23 | 16 | 0 | 0 | 55 | 14 | 10 | 90 | 12 | 42 | 14 | 16 | 9 | 22 | 7 | 8 | 71 | 0 | 270 | 0 | 0 | 168 | 0 | 0 | 0 | 52 | 0 | 187 | 0 | 270 | 50 | 0 | 113 | 103 | 105 | 0 | 0 |  | 6396 | 3186 | 9582 | 3841 | 905 | 1674 | 2238 | 341 | 209 | 230 | 144 | 0 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 70 | 0 | 200 | 110 | 0 | 93 | 67 | 331 | 323 |  | 0 | 330 | 235 | 57 | 70 | 42 | 333 | 0 | 0 | 0 | 65 | 101 | 125 | 83 | 72 | 0 | 19 | 53 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 43 | 0 | 121 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 68 | 50 | 97 | 28 | 22 | 23 | 0 | 0 | 100 | 345 | 90 | 144 | 68 | 0 | 30 | 52 | 0 | 28 | 0 | 50 | 52 | 21 | 11 | 33 | 20 | 184 | 153 | 95 | 22 | 0 | 60 | 42 | 50 | 33 | 100 | 242 | 67 | 72 | 45 | 47 | 0 | 45 | 10 | 300 | 24 | 11 | 30 | 193 | 103 | 25 | 168 | 27 | 135 | 0 | 100 | 132 | 100 | 0 | 115 | 70 | 17 | 0 | 107 | 17 | 50 |  | 905 | 0 | 395 | 0 | 100 | 0 | 0 | 0 | 24 | 72 | 33 | 167 | 34 | 110 | 0 | 0 | 55 | 50 | 43 | 94 | 35 | 42 | 18 | 42 | 22 | 22 | 7 | 11 | 71 | 0 | 270 | 0 | 0 | 172 | 0 | 0 | 0 | 91 | 56 | 193 | 0 | 370 | 105 | 0 | 113 | 104 | 98 | 0 | 0 |  | 8157 | 3924 | 12081 | 4207 | 905 | 2163 | 3504 | 341 | 211 | 566 | 184 | 0 | 0 | 0
19:30 | 70 | 0 | 200 | 110 | 0 | 93 | 67 | 342 | 305 |  | 0 | 330 | 260 | 100 | 100 | 42 | 333 | 0 | 0 | 0 | 80 | 101 | 133 | 100 | 72 | 0 | 21 | 53 | 55 | 35 | 22 | 25 | 30 | 33 | 33 | 43 | 0 | 121 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 2 | 68 | 50 | 97 | 28 | 22 | 28 | 0 | 0 | 100 | 345 | 120 | 142 | 68 | 0 | 30 | 51 | 0 | 43 | 0 | 50 | 52 | 21 | 11 | 33 | 20 | 184 | 153 | 95 | 22 | 0 | 60 | 42 | 51 | 48 | 100 | 242 | 67 | 72 | 45 | 48 | 0 | 45 | 10 | 300 | 24 | 11 | 10 | 300 | 27 | 10 | 180 | 10 | 135 | 0 | 100 | 200 | 80 | 0 | 115 | 70 | 17 | 0 | 107 | 17 | 50 |  | 905 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 24 | 65 | 33 | 176 | 38 | 110 | 0 | 0 | 55 | 50 | 43 | 94 | 50 | 42 | 23 | 43 | 21 | 22 | 10 | 11 | 71 | 0 | 270 | 0 | 0 | 185 | 0 | 0 | 0 | 96 | 100 | 195 | 0 | 330 | 105 | 0 | 113 | 103 | 98 | 0 | 0 |  | 8401 | 3936 | 12337 | 4222 | 905 | 2152 | 3749 | 341 | 211 | 573 | 184 | 0 | 0 | 0
20:00 | 70 | 0 | 200 | 110 | 0 | 97 | 68 | 342 | 303 |  | 0 | 330 | 275 | 100 | 98 | 42 | 333 | 0 | 0 | 0 | 100 | 101 | 135 | 100 | 72 | 0 | 40 | 53 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 43 | 0 | 121 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 3 | 68 | 50 | 97 | 39 | 22 | 30 | 0 | 0 | 100 | 345 | 200 | 142 | 68 | 0 | 30 | 51 | 0 | 43 | 0 | 50 | 52 | 21 | 11 | 33 | 20 | 188 | 153 | 95 | 22 | 0 | 60 | 42 | 51 | 48 | 100 | 242 | 65 | 72 | 46 | 48 | 0 | 46 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 200 | 50 | 0 | 115 | 70 | 17 | 0 | 106 | 17 | 50 |  | 906 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 24 | 63 | 40 | 179 | 39 | 110 | 0 | 0 | 55 | 50 | 43 | 94 | 50 | 42 | 31 | 51 | 21 | 22 | 10 | 11 | 71 | 0 | 270 | 0 | 0 | 186 | 0 | 0 | 0 | 96 | 100 | 196 | 0 | 330 | 105 | 0 | 113 | 103 | 91 | 0 | 0 |  | 8469 | 3957 | 12426 | 4306 | 906 | 2150 | 3742 | 341 | 211 | 582 | 188 | 0 | 0 | 0
21:00 | 70 | 0 | 210 | 110 | 0 | 96 | 40 | 345 | 300 |  | 0 | 330 | 276 | 100 | 98 | 42 | 334 | 0 | 0 | 0 | 95 | 101 | 135 | 100 | 72 | 0 | 47 | 53 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 43 | 0 | 122 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 68 | 50 | 97 | 50 | 22 | 34 | 0 | 0 | 100 | 335 | 235 | 142 | 68 | 0 | 30 | 53 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 186 | 152 | 95 | 22 | 0 | 60 | 42 | 51 | 48 | 100 | 242 | 66 | 72 | 46 | 48 | 0 | 46 | 10 | 305 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 200 | 10 | 0 | 115 | 70 | 17 | 0 | 106 | 17 | 50 |  | 905 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 24 | 62 | 40 | 178 | 40 | 110 | 0 | 0 | 55 | 50 | 42 | 94 | 50 | 42 | 29 | 43 | 21 | 22 | 11 | 11 | 71 | 0 | 262 | 0 | 0 | 192 | 0 | 0 | 0 | 96 | 100 | 196 | 0 | 330 | 105 | 0 | 113 | 103 | 91 | 0 | 0 |  | 8414 | 3943 | 12357 | 4347 | 905 | 2141 | 3708 | 333 | 212 | 525 | 186 | 0 | 0 | 0
22:00 | 70 | 0 | 210 | 110 | 0 | 97 | 40 | 347 | 300 |  | 0 | 330 | 275 | 100 | 97 | 42 | 333 | 0 | 0 | 0 | 50 | 101 | 135 | 100 | 72 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 43 | 0 | 122 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 68 | 50 | 97 | 46 | 22 | 38 | 0 | 0 | 100 | 260 | 235 | 142 | 68 | 0 | 30 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 190 | 153 | 95 | 22 | 0 | 60 | 42 | 52 | 48 | 100 | 242 | 65 | 72 | 46 | 47 | 0 | 46 | 10 | 310 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 133 | 0 | 100 | 200 | 10 | 0 | 115 | 70 | 17 | 0 | 107 | 17 | 50 |  | 905 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 24 | 60 | 40 | 179 | 40 | 110 | 0 | 0 | 55 | 50 | 42 | 93 | 12 | 42 | 29 | 43 | 21 | 22 | 11 | 11 | 70 | 0 | 261 | 0 | 0 | 191 | 0 | 0 | 0 | 97 | 100 | 197 | 0 | 330 | 105 | 0 | 113 | 103 | 98 | 0 | 0 |  | 8326 | 3909 | 12235 | 4276 | 905 | 2154 | 3645 | 331 | 212 | 522 | 190 | 0 | 0 | 105.41
23:00 | 70 | 0 | 210 | 110 | 0 | 97 | 40 | 349 | 300 |  | 0 | 330 | 130 | 100 | 97 | 42 | 333 | 0 | 0 | 0 | 50 | 101 | 135 | 100 | 72 | 0 | 47 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 43 | 0 | 122 | 90 | 95 | 120 | 25 | 215 | 0 | 130 | 0 |  | 0 | 0 | 68 | 10 | 97 | 46 | 22 | 38 | 0 | 0 | 100 | 295 | 235 | 142 | 68 | 0 | 30 | 51 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 186 | 151 | 95 | 22 | 0 | 60 | 42 | 52 | 48 | 100 | 247 | 65 | 76 | 45 | 48 | 0 | 46 | 10 | 315 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 133 | 0 | 100 | 200 | 10 | 0 | 115 | 70 | 17 | 0 | 107 | 17 | 50 |  | 905 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 24 | 60 | 40 | 179 | 40 | 110 | 0 | 0 | 55 | 50 | 42 | 93 | 12 | 42 | 29 | 43 | 21 | 22 | 11 | 11 | 71 | 0 | 260 | 0 | 0 | 190 | 0 | 0 | 0 | 95 | 100 | 191 | 0 | 330 | 105 | 0 | 113 | 103 | 98 | 0 | 0 |  | 8194 | 3900 | 12094 | 4321 | 905 | 2157 | 3460 | 331 | 212 | 522 | 186 | 0 | 0 | 105.41
24:00 | 70 | 0 | 210 | 110 | 0 | 97 | 50 | 367 | 300 |  | 0 | 330 | 140 | 100 | 98 | 42 | 336 | 0 | 0 | 0 | 50 | 101 | 135 | 100 | 72 | 0 | 46 | 53 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 43 | 0 | 122 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 68 | 10 | 51 | 47 | 22 | 38 | 0 | 0 | 100 | 260 | 155 | 143 | 68 | 0 | 26 | 54 | 0 | 43 | 0 | 0 | 52 | 21 | 11 | 33 | 20 | 184 | 155 | 95 | 22 | 0 | 58 | 42 | 49 | 49 | 130 | 240 | 67 | 76 | 46 | 0 | 0 | 46 | 10 | 300 | 24 | 11 | 0 | 300 | 0 | 0 | 192 | 0 | 136 | 0 | 100 | 200 | 10 | 0 | 115 | 70 | 17 | 0 | 107 | 17 | 17 |  | 905 | 0 | 390 | 0 | 115 | 0 | 0 | 0 | 24 | 60 | 40 | 178 | 39 | 110 | 0 | 0 | 55 | 50 | 42 | 93 | 12 | 42 | 29 | 43 | 21 | 22 | 7 | 11 | 71 | 0 | 260 | 0 | 0 | 196 | 0 | 0 | 0 | 95 | 100 | 200 | 0 | 380 | 105 | 0 | 113 | 103 | 100 | 0 | 0 |  | 7997 | 4011 | 12008 | 4226 | 905 | 2229 | 3399 | 331 | 212 | 522 | 184 | 0 | 0 | 0
KWH | 1588000 | 0 | 4849000 | 2583000 | 0 | 2212181 | 1445696 | 8292180 | 6947000 |  | 0 | 7668250 | 6136233 | 756480 | 657192 | 538016 | 5198420 | 0 | 0 | 0 | 447360 | 1558800 | 1360320 | 995290 | 1536000 | 0 | 517296 | 1196280 | 1160166 | 855822 | 465696 | 575000 | 662040 | 789500 | 803 | 976944 | 0 | 2369100 | 2156000 | 2200000 | 2900000 | 436862 | 4934907 | 0 | 2890630 | 0 |  | 0 | 8368 | 438518 | 415680 | 1358400 | 775680 | 519264 | 514080 | 0 | 0 | 2394302 | 7938600 | 5013500 | 3463000 | 1739636 | 0 | 487224 | 1252320 | 0 | 1002706 | 0 | 115360 | 930917 | 456372 | 236700 | 806700 | 460340 | 3797760 | 3597480 | 2100480 | 511596 | 12150 | 1418000 | 955920 | 978000 | 1122552 | 3083735 | 5462000 | 1570176 | 1510080 | 1014 | 1206170 | 297000 | 972000 | 250920 | 7361700 | 571320 | 249 | 23040 | 1962108 | 83201 | 21347 | 2601600 | 23598 | 2043360 | 128250 | 2190720 | 3621120 | 1309745 | 0 | 2737200 | 1600152 | 424870 | 30960 | 2160327 | 739750 | 694178 |  | 21741818 | 0 | 8696736 | 0 | 1533120 | 0 | 0 | 0 | 205920 | 456548 | 581125 | 4329000 | 624546 | 958272 | 11081 | 0 | 1330000 | 385616 | 274525 | 1169184 | 382060 | 887413 | 228900 | 465120 | 192425 | 508560 | 183456 | 225972 | 1656000 | 0 | 6466800 | 0 | 33000 | 4726455 | 0 | 0 | 0 | 1568735 | 633600 | 4779109 | 0 | 8572727 | 1668480 | 0 | 2436576 | 2345472 | 2232960 | 0 | 30591 |  | 169359959 | 82521902 | 251881861 | 99382361 | 21741818 | 49519894 | 59710412 | 8122800 | 4525100 | 4879765 | 3797760 | 201951 | 0
Fuel Cost | 1778560 | 0 | 5188430 | 2892960 | 0 | 2145815.57 | 2110716.16 | 5970369.6 | 5279720 |  | 0 | 6134600 | 5522609.7 | 7716096 | 7117389.36 | 5520044.16 | 6446040.8 | 0 | 0 | 0 | 4965696 | 15837408 | 13480771.2 | 10430639.2 | 13977600 | 0 | 4841890.56 | 11472325.2 | 11067983.64 | 8523987.12 | 349272 | 431250 | 0 | 0 | 0 | 9359123.52 | 0 | 615966 | 560560 | 3366000 | 4437000 | 4198243.82 | 5181652.35 | 0 | 3671100.1 | 0 |  | 0 | 88617.12 | 4600053.82 | 4277347.2 | 12918384 | 7260364.8 | 477722.88 | 1429142.4 | 0 | 0 | 2514017.1 | 5874564 | 4211340 | 3185960 | 1704843.28 | 0 | 399523.68 | 1289889.6 | 0 | 1433869.58 | 0 | 1352019.2 | 8750619.8 | 465499.44 | 177525 | 1524663 | 345255 | 26204544 | 2949933.6 | 19975564.8 | 521827.92 | 199260 | 1928480 | 1300051.2 | 1330080 | 1403190 | 3823831.4 | 5025040 | 2339562.24 | 2657740.8 | 1125.54 | 1833378.4 | 472230 | 1137240 | 589662 | 5226807 | 428490 | 189.24 | 387993.6 | 20543270.76 | 1422737.1 | 356494.9 | 25027392 | 394086.6 | 20617502.4 | 1480005 | 20417510.4 | 33966105.6 | 12272310.65 | 0 | 24005244 | 14257354.32 | 4015021.5 | 0 | 19918214.94 | 0 | 0 |  | 58702908.6 | 0 | 6783454.08 | 0 | 14779276.8 | 0 | 0 | 0 | 2388672 | 5980778.8 | 5747326.25 | 3463200 | 968046.3 | 10291841.28 | 367335.15 | 0 | 2500400 | 4295762.24 | 3362931.25 | 11574921.6 | 3961962.2 | 10391606.23 | 2758245 | 4632595.2 | 1895386.25 | 559416 | 302702.4 | 171060.804 | 10548720 | 0 | 26449212 | 0 | 931590 | 4159280.4 | 0 | 0 | 0 | 2494288.65 | 10707840 | 4205615.92 | 0 | 6258090.71 | 15783820.8 | 0 | 22367767.68 | 20898155.52 | 20855846.4 | 0 | 0 |  | 533302512.87 | 301540056.514 | 834842569.384 | 96970898.754 | 58702908.6 | 48280817.39 | 511752594.01 | 36997932 | 1176526 | 53077083.63 | 26204544 | 1679265 | 0
Yesterday Day Peak | 70 | 0 | 200 | 110 | 0 | 88 | 60 | 320 | 254 |  | 0 | 300 | 240 | 0 | 0 | 15 | 328 | 0 | 0 | 0 | 0 | 75 | 16 | 50 | 72 | 0 | 13 | 35 | 35 | 35 | 22 | 25 | 26 | 33 | 33 | 34 | 0 | 123 | 90 | 95 | 120 | 8 | 218 | 0 | 92 | 0 |  | 0 | 0 | 0 | 10 | 25 | 20 | 22 | 5 | 0 | 0 | 100 | 360 | 275 | 139 | 75 | 0 | 30 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 8 | 33 | 17 | 144 | 150 | 64 | 22 | 1.4 | 60 | 41 | 47 | 49 | 100 | 256 | 62 | 70 | 44 | 48 | 18 | 39 | 10 | 310 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 100 | 3.97 | 90 | 84 | 50 | 0 | 115 | 70 | 17 | 5.3 | 100 | 34 | 17 |  | 906 | 0 | 370 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 179 | 19 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 12 | 42 | 0 | 16 | 0 | 22 | 7 | 8 | 71 | 0 | 275 | 0 | 0 | 202 | 0 | 0 | 0 | 22 | 0 | 198 | 0 | 350 | 17 | 0 | 74 | 95 | 74 | 0 | 4.4 |  | 9782.07 | DayPeak
Yesterday Evening Peak | 70 | 0 | 200 | 110 | 0 | 97 | 68 | 342 | 303 | 0 | 0 | 330 | 275 | 100 | 98 | 42 | 333 | 0 | 0 | 0 | 100 | 101 | 135 | 100 | 72 | 0 | 40 | 53 | 55 | 35 | 22 | 25 | 31 | 33 | 33 | 43 | 0 | 121 | 90 | 95 | 120 | 25 | 204 | 0 | 130 | 0 | 0 | 0 | 3 | 68 | 50 | 97 | 39 | 22 | 30 | 0 | 0 | 100 | 345 | 200 | 142 | 68 | 0 | 30 | 51 | 0 | 43 | 0 | 50 | 52 | 21 | 11 | 33 | 20 | 188 | 153 | 95 | 22 | 0 | 60 | 42 | 51 | 48 | 100 | 242 | 65 | 72 | 46 | 48 | 0 | 46 | 10 | 290 | 24 | 11 | 0 | 300 | 0 | 0 | 190 | 0 | 135 | 0 | 100 | 200 | 50 | 0 | 115 | 70 | 17 | 0 | 106 | 17 | 50 |  | 906 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 24 | 63 | 40 | 179 | 39 | 110 | 0 | 0 | 55 | 50 | 43 | 94 | 50 | 42 | 31 | 51 | 21 | 22 | 10 | 11 | 71 | 0 | 270 | 0 | 0 | 186 | 0 | 0 | 0 | 96 | 100 | 196 | 0 | 330 | 105 | 0 | 113 | 103 | 91 | 0 | 0 |  | 12426 | EvPeak
Forecast for Evening | 70 | 0 | 200 | 110 | 0 | 97 | 70 | 395 | 290 | 0 | 0 | 330 | 150 | 100 | 100 | 42 | 335 | 0 | 0 | 0 | 100 | 100 | 133 | 100 | 72 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 125 | 90 | 100 | 120 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 80 | 100 | 90 | 50 | 22 | 30 | 0 | 0 | 100 | 360 | 360 | 225 | 68 | 0 | 30 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 191 | 150 | 95 | 22 | 0 | 60 | 42 | 51 | 50 | 163 | 259 | 66 | 77 | 46 | 0 | 18 | 46 | 10 | 320 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 0 | 115 | 70 | 100 | 0 | 260 | 54 | 113 |  | 925 | 30 | 410 | 0 | 115 | 200 | 0 | 0 | 40 | 70 | 40 | 180 | 35 | 110 | 30 | 0 | 60 | 50 | 43 | 100 | 50 | 42 | 31 | 52 | 35 | 22 | 10 | 11 | 71 | 0 | 280 | 0 | 18 | 215 | 0 | 0 | 0 | 95 | 100 | 215 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0
Forecast for Day | 70 | 0 | 200 | 110 | 0 | 94 | 70 | 350 | 290 | 0 | 0 | 330 | 150 | 100 | 100 | 41 | 335 | 0 | 0 | 0 | 100 | 100 | 133 | 100 | 72 | 0 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 43 | 0 | 125 | 90 | 100 | 120 | 25 | 215 | 0 | 130 | 0 | 0 | 0 | 0 | 50 | 100 | 90 | 50 | 22 | 10 | 0 | 0 | 100 | 360 | 360 | 225 | 68 | 0 | 30 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 149 | 150 | 95 | 22 | 1.6 | 60 | 42 | 51 | 50 | 163 | 259 | 66 | 77 | 45 | 0 | 18 | 46 | 10 | 315 | 24 | 11 | 0 | 200 | 0 | 0 | 200 | 0 | 149 | 20 | 100 | 200 | 150 | 0 | 115 | 70 | 50 | 4.4 | 230 | 54 | 113 |  | 925 | 0 | 380 | 0 | 115 | 200 | 0 | 0 | 0 | 0 | 40 | 180 | 25 | 70 | 0 | 0 | 60 | 50 | 0 | 80 | 40 | 42 | 30 | 52 | 0 | 22 | 10 | 11 | 71 | 0 | 280 | 0 | 0 | 215 | 0 | 0 | 0 | 95 | 80 | 205 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8
Generation at 08:00(Today) | 70 | 0 | 210 | 110 | 0 | 96 | 40 | 343 | 300 | 0 | 0 | 330 | 140 | 0 | 0 | 0 | 333 | 0 | 0 | 0 | 0 | 7 | 16 | 0 | 72 | 0 | 13 | 35 | 17 | 17 | 22 | 0 | 30 | 25 | 33 | 43 | 0 | 121 | 40 | 100 | 120 | 0 | 209 | 0 | 132 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 50 | 19 | 7 | 0 | 0 | 100 | 280 | 190 | 144 | 68 | 0 | 24 | 55 | 0 | 15 | 0 | 0 | 8 | 19 | 8 | 33 | 15 | 132 | 155 | 73 | 22 | 0.1 | 60 | 42 | 25 | 25 | 100 | 244 | 66 | 20 | 46 | 0 | 0 | 23 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 7 | 0 | 30 | 7.3 | 100 | 70 | 10 | 0 | 115 | 70 | 17 | 2.6 | 71 | 17 | 17 | 0 | 910 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 23 | 0 | 0 | 0 | 55 | 0 | 0 | 60 | 12 | 42 | 0 | 8 | 0 | 22 | 11 | 8 | 70 | 0 | 270 | 0 | 0 | 184 | 0 | 0 | 0 | 95 | 0 | 199 | 0 | 320 | 17 | 0 | 74 | 69 | 71 | 0 | 2 | 0
199
| Minimum Generation |  | 8940 | 8:00
| Highest Generation |  | 12426 | 20:00
| Day Peak Generation |  | 9782.07 | 12:00
| Evening Peak Generation |  | 12426 | 20:00
| HVDC Max Flow |  | 909 | 16:00
| HVDC EvPeak Flow |  | 906 | 20:00
| Load factor L.F |  | 84.46%

## P1
|  |  | POWER GRID COMPANY OF BANGLADESH LTD. |  |  |  | Revised
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2019-09-05
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2019-09-04 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9782.07 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8992 | MW
Evening Peak Generation : |  | 12426 | MW Hour : | 20:00 | Available Max Generation : |  | 14720 | MW
E.P. Demand (at gen end) : |  | 12426 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 12426 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1820 | MW
Total Gen. (MKWH) : |  | 251.8819 | System Load Factor : | 84.46% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -95 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2019-09-05
Actual : | 105.48 | Ft.(MSL) , | Rule curve : | 0 | Ft.( MSL )
Gas Consumed : | Total = | 1323.84 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 145251716.144
|  | Coal : | 36997932 | Oil : | 564829677.64 | Total : | 747079325.784
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4605.0868 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1570.7487 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1408.1877 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1272.7178 |  |  | 0 | 0%
) | 0 | 0:00 | 1149.9704 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 927.9975 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.7596 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.7721 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 715.7471 |  |  | 0 | 0%
Total | 0 |  | 12401.9876 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit- 2. | 7) Ghorashal Unit-3,7
|  |  |  | 2) Khulna ST 110 MW | 8) Sirajganj Unit-2
|  |  |  | 3) Sikalbaha ST 60 MW | 9) Ashuganj #3
|  |  |  | 4) Siddhirganj ST | 10) Chandpur 163 MW CCPP
|  |  |  | 5) Ashuganj #4 | 11) Sylhet-150 MW
6) Baghabari 100 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  |  | Comments on Power Interruption
a) Ashuganj(N)-Bhulta 400 kV Ckt-1 was under shut down from 10:03 to 16:10 for teleprotection testing.
b) Ramganj 132/33 kV T-1 transform was under shut down from 09:16 to 10:52 for C/M.
c) Rajshahi-Natore 132 kV Ckt-1 & 2 tripped at 12:48 showing dist.C-phase,Z1 and were switched on at |  |  |  |  | About 190 MW power interruption occurred under Rajshahi,Chapai &
12:58 & 13:08 respectively. |  |  |  |  | & Amnura S/S areas from 12:48 to 12:58.
d) Rajshahi-Amnura 132 kV Ckt tripped at 12:48 showing dist.Z1,Z2 and was switched on at 13:10.
e) Faridpur-Madaripur 132 kV Ckt-2 was under shut down at 09:30 for D/W.
f) Bagerhat-Mongla 132 kV Ckt tripped at 12:35 showing O/C relay and was switched on at 12:56. |  |  |  |  | About 30 MW power interruption occurred under Bagerhat S/S area
from 12:35 to 12:56.
g) Mongla 132/33 kV T-1 & T-2 transformers tripped from 33 kV end showing O/C relay as snake made short
circuit were switched on at 12:57 & 14:17 respectively.
h) Ashuganj(N)-Bhulta 400 kV Ckt-2 was under shut down from 16:11 to 17:45 for teleprotection testing.
i) Ashuganj(South)-360 MW CCPP ST & GT were shut down at 13:13 & 16:18 respectively due to vibration of
alternator high and GT was synchronized at 18:41.
j) Shahjadpur 132/33 kV T-2 transformer was under shut down from 10:10 to 17:20 for 132 kV breaker maint.
k) Mirpur 132 kV main Bus was under shut down from 07:55 to 17:44 for C/M.
l) Purbasadipur-Saidpur 132 kV Ckt-1 was shut down at 18:02 for replacing bypass isolator by line breaker |  |  |  |  | About 20 MW power interruption occurred under Purbasadipur, Thakurgaon
at Purbasadipur end and was switched on at 18:07. |  |  |  |  | & Panchaghar S/S areas from 18:02 to 18:07.
m) Thakurgaon-Panchaghar 132 kV Ckt tripped at 18:16 showing E/F relay and was switched on at 18:21 and |  |  |  |  | About 40 MW power interruption occurred under Panchaghar S/S area
again tripped at 18:28 & was switched on at 19:09 and again tripped at 19:21 & was switched on at 21:21. |  |  |  |  | from 18:16 to 18:21 & 18:28 to 19:09 & 19:21 to 21:21.
n) Gopalganj 132/33 kV T-1 & T-2 transformers tripped at 12:48 showing O/C relay as a snake made short |  |  |  |  | About 45 MW power interruption occurred under Gopalganj S/S area
circuit were switched on at 13:02 & 13:05 respectively. |  |  |  |  | from 12:48 to 13:02.
o) Summit Megnaghat GT-2 was shut down at 23:00 due to gas shortage.
p) Sylhet-150 MW was shut down at 00:01(5/9/19) due to air filter change.
q) Sirajganj-Shahjadpur 132 kV Ckt is under shut down at 06:04(5/9/19) for C/M.
r) Sikalbaha old 132 kV Bus-B is shut down since 07:15 due to TR-11 CB loop string cut.
s) Jamalpur 132/33 kV T-2 transformer is under shut down since 07:47(5/9/19) due to 33 kV Jumuna feeder |  |  |  |  | About 5 MW power interruption occurred under Jamalpur S/S area
red hot maintenance. |  |  |  |  | since 07:47 (05/09/2019).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2019-09-04 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal TPP (Unit-1&2) |  | PDB | 2*55 | 85 | 70 | 1588000
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 200 | 4849000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2583000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 68 | 1445696
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 2212181 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Machine problem
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 342 | 8292180 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 303 | 6947000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 7668250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 756480
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6136233 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 98 | 657192
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 42 | 538016 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 995290
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 465696
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Gas shortage
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
| Siddhirganj Desh |  | QRPP | 96*1.2 | 0 | 0 | 0 | Contract Expired
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 447360
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217 | 217 | 333 | 5198420
| Pagla (DPA ) |  | QRPP | 100*0.5 | 0 | 0 | 0 | Contract Expired
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 101 | 1558800
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 40 | 517296 | Engine problem
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1196280
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 135 | 1360320 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1160166
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 855822 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 72 | 1536000 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1237040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 789500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 43 | 976944 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 1962108
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 83201 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 21347 | Reserve
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 23598 | Reserve
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 135 | 2043360 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 1600152
| Dhaka area Total |  |  |  | 5693 | 3751 | 67702731
37 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 95 | 2200000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
38 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 436862
39 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 128250
40 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 39 | 775680 | Engine problem
41 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 211 | 4525100
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4934907 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2890630 | FGMO
| Sikalbaha 51 MW PP(Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 0 | 0 | 0 | Contract Expired
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 424870 | Transformer overload.
45 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 3 | 8368 | Under S/D
46 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 438518
47 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 415680 | Line O/L
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2190720
49 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 519264
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 514080
50 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1358400
51 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30960
52 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 106 | 2160327 | Transformer overload.
53 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 739750 | Transformer overload.
54 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 50 | 694178 | Transformer overload.
| Chattogram area Total |  |  |  | 2166 | 1384 | 28286544
55 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2394302 | Gas shortage
56 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 142 | 3463000 | ST U/M
57 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 345 | 7938600 | FGMO
58 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 200 | 5013500 | ST U/M
59 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 30 | 487224 | Engine problem
60 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1252320
61 | Ashuganj 53MW PP (United) |  | QRPP | 14*4 | 53 | 0 | 0 | Contract Expired
62 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1739636 | Gas shortage
63 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 1002706 | Engine problem
64 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1309745 | Transformer overload.
65 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 0 | 0 | Contract Expired
66 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 115360
67 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
68 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3621120
69 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 456372
70 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 188 | 3797760
71 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 806700
72 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 930917
73 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 460340 | Engine problem
74 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 23040 | Reserve
| Cumilla Area Total |  |  |  | 2891 | 1604 | 35049342
75 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 153 | 3597480 | Gas shortage
76 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 511596
77 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 95 | 2100480
78 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12150
79 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 2601600
80 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2737200
| Mymensingh Area Total |  |  |  | 637 | 575 | 11560506
81 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1418000
82 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 955920
83 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 100 | 3083735
84 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 242 | 5462000 | GT-2 under maint.
85 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 978000
86 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 48 | 1122552
87 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 249
88 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 65 | 1570176 | FGMO
89 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 72 | 1510080 | Engine problem
90 | Shahjibazar 50MW PP (EPL) |  | RPP | 27*2.0 | 50 | 46 | 1014
91 | Sylhet 150 MW CCPP |  | PDB | 1*142 | 142 | 48 | 1206170
92 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 297000
93 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 46 | 972000 | Engine problem
94 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 571320
95 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7361700 | FGMO
96 | Bibiyana-III 400 MW CCPP |  | PDB | 285 MW | 285 | 0 | 0 | Test
97 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 250920
| Sylhet Area Total |  |  |  | 1834 | 1155 | 26760836
98 | Bheramara GTPP Unit-1,2 & 3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 906 | 21741818
| Khulna 115 MW PP (KPCL-1 & 3) |  | IPP | 19*6.5 | 0 | 0 | 0 | Contract Expired
99 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1533120
100 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 205920
101 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
102 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 63 | 456548
103 | Bheramara 360 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8696736 | Frequency control
104 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 581125
| Khulna (Aggreeco) 55MW |  | QRPP | 71*0.85 | 0 | 0 | 0 | Contract Expired
105 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 633600
106 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1668480
107 | Madhumati 100 MW PP |  | IPP | 100 MW | 105 | 103 | 2345472
| Khulna Area Total |  |  |  | 2314 | 1796 | 37862819
108 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 958272
109 | Barisal GT PP Unit-1& 2 |  | PDB | 2*20 | 30 | 0 | 11081 | Reserve
110 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 39 | 624546
111 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 179 | 4329000
112 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1568735
| Barisal Area Total |  |  |  | 462 | 424 | 7491634
113 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 55 | 1330000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
114 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 385616
115 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 43 | 274525
116 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 50 | 382060
117 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 887413 | Engine problem
118 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 228900
119 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 186 | 4726455 | FGMO
120 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Gas shortage
121 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 196 | 4779109 | FGMO
122 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 330 | 8572727 | Frequency control
123 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 192425
124 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 508560
125 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 10 | 183456
126 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 225972
127 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 51 | 465120
128 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 1169184
129 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve
130 | Bagura 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2436576
| Rajshahi Area Total |  |  |  | 2070 | 1305 | 26748098
131 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 71 | 1656000
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
132 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 270 | 6466800
133 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
134 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 33000
135 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 91 | 2232960
136 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30591
| Rangpur Area Total |  |  |  | 605 | 432 | 10419351
| Total |  |  |  | 18672 | 12426 | 251881861
| Eastern Grid Total |  |  |  | 13221 | 8469 | 169359959
| Western Grid Total |  |  |  | 5451 | 3957 | 82521902
| National Grid Total |  |  |  | 18672 | 12426 | 251881861
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2019-09-04
(a) ENTIRE EASTERN GRID : |  | 8141 | MW | (b) ENTIRE WESTERN GRID : |  | 3797 | MW
i) Dhaka area |  | 4249 | MW | i) Khulna area |  | 1446 | MW
ii) Chittagong area |  | 1190 | MW | ii) Rajshahi area |  | 1277 | MW
iii) Comilla area |  | 1156 | MW | iii) Barisal area |  | 329 | MW
iv) Mymensingh area |  | 1013 | MW | iv) Rangpur area |  | 745 | MW
v) Sylhet area |  | 533 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11938 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 1600 | Sherpur | 108 | 2200 | Jhenida | 109 | 1900
Munsiganj | 126 | 2100 | Srimongal | 43 | 1930 | Bottail | 126 | 1930
Sonargaon | 88 | 2100 | Shahjibazar | 120 | 1930 | G.K Project | 59 | 2100
Shyampur | 200 | 1100 | Fenchuganj | 48 | 1930 | Faridpur | 182 | 2000
Bhulta | 183 | 100 | Kulawara | 46 | 2000 | Madaripur | 113 | 2100
Madanganj | 60 | 100 | Sylhet | 155 | 2000 | Sariatpur | 46 | 2300
Shitalakhya | 107 | 1600 | Chatak | 30 | 2000 | Gopalganj | 90 | 1930
Rahim steel | 14 | 1830 | Sunamganj | 47 | 1930 | Bagerhat | 85 | 1930
Matuail | 96 | 900 | Biani Bazar | 60 | 2100 | Mongla | 38 | 1700
Ghorasal | 85 | 2100 | Comilla (S) | 190 | 2200 | Satkhira | 98 | 2200
Narsingdi | 142 | 100 | Comilla(N) | 125 | 2000 | Gallamari | 49 | 1300
Haripur (SBU) | 99 | 1600 | Chandpur | 106 | 2000 | Magura | 52 | 1930
Ullon | 92 | 1800 | Feni | 137 | 2000 | Norail | 26 | 100
Hasnabad | 215 | 2100 | Chowmuhani | 182 | 2100 | Chuadanga | 89 | 2100
Magbazar | 146 | 1600 | Ashuganj | 61 | 2100 | Barisal(N) | 45 | 2200
Maniknagar | 116 | 1700 | Daudkandi | 136 | 2300 | Barisal (S) | 108 | 2200
Bangabhaban | 38 | 1200 | B.Baria | 144 | 2000 | Patuakhali | 113 | 2100
Narinda | 96 | 1600 | Ramganj | 96 | 2000 | Bhandaria | 52 | 1930
Dhanmondi | 183 | 1300 | Madunaghat | 57 | 1500 | Borhan Uddin | 39 | 100
Lalbag | 97 | 1300 | Hathazari | 103 | 1930 | Ishurdi | 67 | 2100
Madartek | 64 | 100 | Khulshi | 183 | 1600 | Ruppur Paromanobik | 1 | 100
Mirpur | 114 | 1830 | Halishahar | 146 | 1400 | Natore | 130 | 2000
Kalyanpur | 120 | 1830 | Baraulia | 62 | 1200 | Bogra | 252 | 1930
Gulshan | 166 | 1300 | Sikalbaha | 29 | 200 | Noagaon | 126 | 1930
Uttara | 81 | 1900 | Dohazari | 92 | 1900 | Rajshahi | 160 | 2100
Uttara New | 17 | 1500 | Cox'sbazar | 95 | 2100 | C.Nawabganj | 72 | 2100
Kamrangirchar | 78 | 1830 | Chandraghona | 28 | 1830 | Amnura | 37 | 2100
Savar | 140 | 1900 | Kaptai | 5 | 1930 | Pabna | 116 | 2100
Bhasantec | 174 | 1300 | A. Khaer Stl. | 0 | 0 | Shahjadpur | 112 | 2000
Agargaon | 66 | 1300 | Bakulia | 106 | 1500 | Serajganj | 109 | 2000
Satmosjid | 105 | 1830 | Julda | 20 | 900 | Niyamatpur | 61 | 2100
Tongi | 130 | 1500 | TK chemical | 18 | 700 | Joypurhat | 56 | 2100
Kabirpur | 206 | 1200 | Modern Steel | 14 | 400 | Mohastangor | 17 | 1930
Basundhara | 121 | 1600 | Shahmirpur | 33 | 1900 | Rangpur | 158 | 2000
Manikganj | 99 | 1930 | Khagrachhari | 20 | 1800 | Lalmonirhat | 67 | 1900
Joydevpur | 227 | 2100 | Matarbari | 29 | 2000 | Saidpur | 113 | 2100
New Tongi | 107 | 1500 | Baroiar Hat | 38 | 1900 | Purbasadipur | 106 | 2000
Korda | 262 | 1800 | Rangamati | 12 | 1830 | Thakurgaon | 82 | 1930
Dhamrai | 51 | 2100 | Abul Khair 230 | 149 | 600 | Palashbari | 123 | 2000
Valuka | 100 | 1900 | BSRM | 106 | 1000 | Barapukuria | 51 | 2000
Tangail | 196 | 2000 | Goalpara | 27 | 1900 | Panchagar | 42 | 500
Mymensing | 234 | 1930 | Central s/s | 96 | 1900 | Joldhaka | 28 | 1900
Kishorganj | 140 | 2100 | Noapara | 74 | 1900 | Kurigram | 40 | 1930
Netrokona | 104 | 2000 | Jessore | 108 | 1900
Jamalpur | 139 | 2000 | Benapol | 42 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  | (22) S.E. Consumer Affairs,PDB.

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2019-09-04 | [7 empty] | QF-LDC-10
Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | 126
Bibiyana | 387 | 7:00 | 377 | 12:00 | Kaliakoir | 367 | 6:00 | 353 | 15:00
Bheramara | 400 | 6:00 | 395 | 1:00 | Bhulta | 381 | 1:00 | 362 | 16:00
Ashuganj(N) | 387 | 7:00 | 370 | 16:00
230 KV | KV |  | KV |  | 230 KV | KV |  | 16:00
Ghorasal | 230 | 1:00 | 225 | 7:00 | Hathazari | 221 | 6:00 | 217 | 10:00
Ishurdi | 235 | 1:00 | 225 | 19:30 | Megnaghat | 221 | 1:00 | 212 | 11:00
Ashuganj | 236 | 6:00 | 223 | 18:30 | Fenchuganj | 235 | 6:00 | 229 | 16:00
Serajganj | 232 | 1:00 | 224 | 23:00 | Siddhirganj | 221 | 6:00 | 210 | 16:00
Baghabari | 233 | 11:00 | 228 | 20:00 | Maniknagar | 219 | 6:00 | 210 | 12:00
Barapukuria | 236 | 18:00 | 222 | 19:00 | Old Airport | 219 | 6:00 | 208 | 16:00
Bogra | 224 | 18:00 | 210 | 22:00 | Barisal | 232 | 6:00 | 218 | 14:00
Khulna South | 228 | 17:00 | 213 | 12:00 | AKSML | 218 | 6:00 | 212 | 16:00
Rampura | 220 | 1:00 | 210 | 15:00 | BSRM | 220 | 6:00 | 214 | 12:00
Haripur | 219 | 7:00 | 211 | 15:00 | Bibiyana | 232 | 7:00 | 202 | 13:00
Hasnabad | 220 | 4:00 | 210 | 10:00 | Bhulta | 221 | 4:00 | 212 | 12:00
Aminbazar | 220 | 1:00 | 210 | 15:00 | Ashuganj (S) | 234 | 1:00 | 223 | 17:00
Tongi | 222 | 1:00 | 208 | 15:00 | Kaliakoir | 223 | 8:00 | 213 | 15:00
Comilla (N) | 228 | 7:00 | 220 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 131 | 600 | 124 | 1600 | Khulshi | 129 | 500 | 126 | 700
Munsiganj | 135 | 100 | 124 | 1700 | Halishahar | 132 | 400 | 128 | 1200
Megnaghat | 130 | 2000 | 124 | 1700 | Baraulia | 131 | 500 | 126 | 800
Shyampur | 133 | 100 | 127 | 1200 | Sikalbaha | 132 | 700 | 129 | 1000
Bhulta | 126 | 500 | 118 | 1200 | Dohazari | 129 | 1300 | 126 | 1000
Madanganj | 136 | 100 | 127 | 1100 | Cox'sbazar | 124 | 700 | 116 | 1830
Shitalakhya | 139 | 1930 | 127 | 1000 | Chandraghona | 133 | 600 | 130 | 400
Rahim steal | 131 | 100 | 125 | 1200 | Kaptai | 132 | 700 | 130 | 300
Matuail | 130 | 600 | 123 | 1400 | A. Khaer Stl. | 129 | 1300 | 126 | 1200
Ghorasal | 135 | 100 | 132 | 1200 | Bakulia | 130 | 400 | 128 | 1600
Narsinghdi | 128 | 1800 | 123 | 2000 | Julda | 131 | 100 | 128 | 1100
Haripur (SBU) | 132 | 300 | 125 | 1700 | TK Chemical | 131 | 100 | 129 | 900
Ullon | 135 | 600 | 124 | 1700 | Modern Steel | 132 | 400 | 129 | 1000
Hasnabad | 136 | 1900 | 128 | 900 | Shahmirpur | 131 | 500 | 113 | 2000
Magbazar | 135 | 500 | 124 | 1600 | Khagrachhari | 132 | 600 | 129 | 900
Maniknagar | 134 | 600 | 126 | 1700 | Matarbari | 127 | 1700 | 120 | 200
Bangabhaban | 134 | 600 | 126 | 1700 | Baroiar Hat | 126 | 700 | 122 | 1830
Narinda | 134 | 600 | 126 | 1700 | Rangamati | 131 | 400 | 129 | 1000
Dhanmondi | 135 | 600 | 124 | 1700 | Goalpara | 138 | 600 | 128 | 1200
Lalbag | 134 | 1900 | 124 | 1000 | Central s/s | 138 | 1700 | 128 | 1200
Madartek | 135 | 700 | 124 | 1700 | Noapara | 134 | 1700 | 126 | 1200
Mirpur | 134 | 500 | 126 | 1200 | Jessore | 130 | 1700 | 122 | 1100
Kalyanpur | 137 | 500 | 131 | 1700 | Benapol | 134 | 1700 | 123 | 1900
Gulshan | 133 | 400 | 124 | 1700 | Jhenida | 131 | 1700 | 117 | 1930
Uttara | 134 | 600 | 124 | 1600 | Bottail | 135 | 700 | 126 | 1900
Uttara New | 133 | 1600 | 131 | 1900 | G.K Project | 142 | 800 | 135 | 2000
Kamrangirchar | 134 | 1800 | 124 | 1000 | Faridpur | 133 | 800 | 120 | 2000
Savar | 134 | 600 | 126 | 1600 | Madaripur | 134 | 900 | 125 | 1400
Bhasantec | 133 | 600 | 123 | 1200 | Sariatpur | 135 | 900 | 125 | 1400
Agargaon | 133 | 600 | 124 | 1600 | Gopalganj | 142 | 1800 | 129 | 1400
Satmosjid | 132 | 600 | 124 | 1500 | Bagerhat | 135 | 200 | 126 | 1100
Tongi | 133 | 800 | 127 | 1000 | Mongla | 134 | 600 | 124 | 1200
Kabirpur | 134 | 500 | 125 | 1900 | Satkhira | 138 | 1700 | 128 | 1100
Basundhara | 131 | 200 | 124 | 1500 | Gallamari | 138 | 600 | 127 | 1200
Manikganj | 135 | 700 | 128 | 2100 | Magura | 130 | 1700 | 115 | 1900
Joydevpur | 140 | 1300 | 134 | 900 | Norail | 127 | 1800 | 113 | 1930
New Tongi | 133 | 500 | 127 | 1500 | Chuadanga | 127 | 1700 | 109 | 2000
Kodda | 137 | 2400 | 132 | 800 | Barisal(N) | 137 | 600 | 128 | 1400
Dhamrai | 134 | 600 | 125 | 2100 | Barisal (S) | 136 | 100 | 127 | 1200
Valuka | 125 | 1800 | 110 | 2000 | Patuakhali | 134 | 900 | 125 | 1200
Tangail | 133 | 700 | 119 | 2200 | Bhandaria | 135 | 100 | 127 | 1200
Mymensing | 129 | 700 | 113 | 2000 | Ishurdi | 139 | 1800 | 132 | 2000
Kishorganj | 128 | 800 | 115 | 2100 | Ruppur Paromanobik | 138 | 1800 | 132 | 2000
Netrokona | 130 | 700 | 109 | 2200 | Natore | 137 | 1800 | 127 | 1900
Jamalpur | 138 | 300 | 128 | 1200 | Bogra | 136 | 1800 | 125 | 1900
Sherpur | 139 | 1700 | 127 | 2200 | Noagaon | 130 | 1800 | 117 | 1900
Srimongal | 134 | 900 | 130 | 1900 | Rajshahi | 132 | 1800 | 123 | 1830
Shahjibazar | 132 | 600 | 127 | 2200 | C.Nawabganj | 132 | 1800 | 120 | 1400
Fenchuganj | 135 | 600 | 129 | 2000 | Amnura | 133 | 600 | 120 | 1300
Khulawara | 132 | 100 | 129 | 1800 | Pabna | 137 | 900 | 128 | 1200
Sylhet | 134 | 500 | 128 | 1900 | Shahjadpur | 140 | 600 | 133 | 1930
Chatak | 132 | 400 | 126 | 1900 | Serajganj | 135 | 1800 | 126 | 2000
Sunamganj | 132 | 200 | 123 | 1900 | Niyamatpur | 130 | 1800 | 113 | 1900
Biani Bazar | 131 | 700 | 124 | 2000 | Joypurhat | 130 | 1800 | 114 | 2100
Comilla(s) | 125 | 1400 | 118 | 1830 | Mohastangor | 135 | 1800 | 122 | 2000
Comilla(n) | 134 | 1300 | 130 | 2200 | Rangpur | 131 | 1800 | 116 | 2000
Chandpur | 130 | 1300 | 125 | 2100 | Lalmonirhat | 126 | 1800 | 110 | 100
Feni | 127 | 1300 | 119 | 2300 | Saidpur | 131 | 1800 | 114 | 2100
Chowmuhani | 122 | 900 | 114 | 2100 | Purbasadipur | 126 | 1800 | 112 | 2100
Ashuganj | 134 | 700 | 129 | 2300 | Thakurgaon | 126 | 1800 | 106 | 2000
Daudkandi | 128 | 1900 | 122 | 1500 | Palashbari | 127 | 500 | 117 | 1900
B.Baria | 130 | 800 | 123 | 2200 | Barapukuria | 136 | 1800 | 122 | 1900
Ramganj | 122 | 1700 | 116 | 2200 | Panchagar | 124 | 1800 | 100 | 100
Madanhat | 132 | 100 | 130 | 1000 | Joldhaka | 133 | 1800 | 110 | 2000
Hathazari | 131 | 500 | 128 | 1100 | Kurigram | 126 | 900 | 108 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2019-09-04
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 95 | 7997 | 4011 | 12008 |  |  |  | QF-LDC-12
0:30 | 60 | 7834.5 | 3949.5 | 11784 | Date: | 2019-09-04
1:00 | 25 | 7672 | 3888 | 11560
1:30 | 25 | 7601.5 | 3802 | 11403.5
2:00 | 25 | 7531 | 3716 | 11247
2:30 | 37.5 | 7416.5 | 3659 | 11075.5 | [5 empty] | Gen. at Eve. Peak | 12426 | 12426 MW (20:00 )
3:00 | 50 | 7302 | 3602 | 10904 | [6 empty] | 20:00
3:30 | 52.5 | 7244 | 3541.5 | 10785.5 | [5 empty] | Gen. at Day Peak | 9782.07 | 9782.07 MW (12:00 )
4:00 | 55 | 7186 | 3481 | 10667 | [6 empty] | 12:00
4:30 | 55 | 7078 | 3438.5 | 10516.5 | [5 empty] | Highest Generation | 12426
5:00 | 55 | 6970 | 3396 | 10366 | [6 empty] | 20:00
5:30 | 32.5 | 6799.5 | 3294 | 10093.5
6:00 | 10 | 6629 | 3192 | 9821
6:30 | 25 | 6485.5 | 2995.5 | 9481
7:00 | 40 | 6342 | 2799 | 9141
7:30 | 65 | 6273.5 | 2767 | 9040.5
8:00 | 90 | 6205 | 2735 | 8940
8:30 | 180 | 6249.5 | 2769 | 9018.5
9:00 | 270 | 6294 | 2803 | 9097
9:30 | 307.5 | 6397 | 2843.5 | 9240.5
10:00 | 345 | 6500 | 2884 | 9384
10:30 | 357.5 | 6530 | 2911.5 | 9441.5
11:00 | 370 | 6560 | 2939 | 9499
11:30 | 387.5 | 6649 | 2990.5 | 9639.5
12:00 | 405 | 6738 | 3042 | 9780
12:30 | 382.5 | 6733 | 3011.5 | 9744.5
13:00 | 360 | 6728 | 2981 | 9709
13:30 | 370 | 6821 | 3084.5 | 9905.5
14:00 | 380 | 6914 | 3188 | 10102
14:30 | 415 | 6968.5 | 3254.5 | 10223
15:00 | 450 | 7023 | 3321 | 10344
15:30 | 480 | 7004 | 3336 | 10340
16:00 | 510 | 6985 | 3351 | 10336
16:30 | 575 | 6807 | 3375 | 10182
17:00 | 640 | 6629 | 3399 | 10028
17:30 | 604 | 6512.5 | 3292.5 | 9805
18:00 | 568 | 6396 | 3186 | 9582
18:30 | 294 | 7276.5 | 3555 | 10831.5
19:00 | 20 | 8157 | 3924 | 12081
19:30 | 45 | 8401 | 3936 | 12337
20:00 | 45 | 8469 | 3957 | 12426 |  |  |  | Executive Engineer
20:30 | 65 | 8441.5 | 3950 | 12391.5 |  |  |  | Network Operation Division
21:00 | 85 | 8414 | 3943 | 12357
21:30 | 90 | 8370 | 3926 | 12296
22:00 | 95 | 8326 | 3909 | 12235 |  |  |  |  | Page 6 of 7
22:30 | 60 | 8260 | 3904.5 | 12164.5
23:00 | 25 | 8194 | 3900 | 12094
23:30 | 60 | 8095.5 | 3955.5 | 12051
24:00 | 95 | 7997 | 4011 | 12008
12426 MW (20:00 )
9782.07 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2019-09-04 |  | Energy | 251881861
[10 empty] | 2019-09-04 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 4226 | 905 | 2229 | 3399 | 331 | 212 | 522 | 0 | 184
0:30 | 4240.5 | 905 | 2245.5 | 3175.5 | 331 | 211 | 496.5 | 0 | 179 | Date: | 2019-09-04
1:00 | 4255 | 905 | 2262 | 2952 | 331 | 210 | 471 | 0 | 174
1:30 | 4359 | 905.5 | 2270.5 | 2784 | 330 | 210 | 372.5 | 0 | 172 | [7 empty] | Total Energy | 251.8819 | Total Energy Gen 251.882 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 251.882 MKWHr
2:00 | 4463 | 906 | 2279 | 2616 | 329 | 210 | 274 | 0 | 170 | [7 empty] | Energy not Served | 0
2:30 | 4448 | 906 | 2287 | 2487.5 | 329.5 | 210 | 239.5 | 0 | 168 | [7 empty] | Energy Requirement | 251.8819
3:00 | 4433 | 906 | 2295 | 2359 | 330 | 210 | 205 | 0 | 166
3:30 | 4425.5 | 906 | 2289 | 2297 | 329.5 | 209 | 164.5 | 0 | 165 | [6 empty] | Shortage
4:00 | 4418 | 906 | 2283 | 2235 | 329 | 208 | 124 | 0 | 164
4:30 | 4419 | 906 | 2253.5 | 2127 | 329 | 208 | 116 | 0 | 158
5:00 | 4420 | 906 | 2224 | 2019 | 329 | 208 | 108 | 0 | 152
5:30 | 4317.5 | 906 | 2160 | 1922 | 329 | 208 | 106 | 0 | 145
6:00 | 4215 | 906 | 2096 | 1825 | 329 | 208 | 104 | 0 | 138
6:30 | 4194 | 906.5 | 2022.5 | 1619 | 329.5 | 209 | 64 | 0 | 133 |  |  |  |  | Coal
7:00 | 4173 | 907 | 1949 | 1413 | 330 | 210 | 24 | 0 | 128
7:30 | 4170 | 907 | 1857 | 1403.5 | 330 | 210 | 24 | 0 | 130 |  |  |  | Oil |  |  |  | ,
8:00 | 4167 | 907 | 1765 | 1394 | 330 | 210 | 24 | 0 | 132
8:30 | 4180 | 906.5 | 1781.5 | 1427 | 338 | 210.5 | 24 | 0 | 134
9:00 | 4193 | 906 | 1798 | 1460 | 346 | 211 | 24 | 0 | 136
9:30 | 4253 | 906 | 1851 | 1480.5 | 346 | 211.5 | 32 | 0 | 137
10:00 | 4313 | 906 | 1904 | 1501 | 346 | 212 | 40 | 0 | 138
10:30 | 4334.5 | 906 | 1913 | 1538.5 | 346 | 211.5 | 28 | 0 | 139
11:00 | 4356 | 906 | 1922 | 1576 | 346 | 211 | 16 | 0 | 140
11:30 | 4377.5 | 906 | 1944 | 1676.5 | 346 | 212 | 16 | 0 | 142
12:00 | 4399 | 906 | 1966 | 1777 | 346 | 213 | 16 | 0 | 144
12:30 | 4280.5 | 906 | 1949.5 | 1877 | 346 | 213.5 | 16 | 0 | 142
13:00 | 4162 | 906 | 1933 | 1977 | 346 | 214 | 16 | 0 | 140
13:30 | 4162 | 906 | 1933 | 1977 | 346 | 214 | 16 | 0 | 140
14:00 | 4162 | 906 | 1933 | 1977 | 346 | 214 | 16 | 0 | 140
14:30 | 4192 | 907 | 2014.5 | 2183 | 342.5 | 208 | 16 | 0 | 144
15:00 | 4222 | 908 | 2096 | 2389 | 339 | 202 | 16 | 0 | 148
15:30 | 4210.5 | 908.5 | 2116.5 | 2381 | 339.5 | 202 | 16.5 | 0 | 147
16:00 | 4199 | 909 | 2137 | 2373 | 340 | 202 | 17 | 0 | 146
16:30 | 4184.5 | 907.5 | 2052.5 | 2300.5 | 340 | 202 | 45 | 0 | 143
17:00 | 4170 | 906 | 1968 | 2228 | 340 | 202 | 73 | 0 | 140
17:30 | 4005.5 | 905.5 | 1821 | 2233 | 340.5 | 205.5 | 151.5 | 0 | 142
18:00 | 3841 | 905 | 1674 | 2238 | 341 | 209 | 230 | 0 | 144
18:30 | 4024 | 905 | 1918.5 | 2871 | 341 | 210 | 398 | 0 | 164
19:00 | 4207 | 905 | 2163 | 3504 | 341 | 211 | 566 | 0 | 184
19:30 | 4222 | 905 | 2152 | 3749 | 341 | 211 | 573 | 0 | 184
20:00 | 4306 | 906 | 2150 | 3742 | 341 | 211 | 582 | 0 | 188
20:30 | 4326.5 | 905.5 | 2145.5 | 3725 | 337 | 211.5 | 553.5 | 0 | 187
21:00 | 4347 | 905 | 2141 | 3708 | 333 | 212 | 525 | 0 | 186
21:30 | 4311.5 | 905 | 2147.5 | 3676.5 | 332 | 212 | 523.5 | 0 | 188
22:00 | 4276 | 905 | 2154 | 3645 | 331 | 212 | 522 | 0 | 190
22:30 | 4298.5 | 905 | 2155.5 | 3552.5 | 331 | 212 | 522 | 0 | 188
23:00 | 4321 | 905 | 2157 | 3460 | 331 | 212 | 522 | 0 | 186
23:30 | 4273.5 | 905 | 2193 | 3429.5 | 331 | 212 | 522 | 0 | 185 | Max Temp. in Dhaka |  | 33.5° C
24:00 | 4226 | 905 | 2229 | 3399 | 331 | 212 | 522 | 0 | 184
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 251.882 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 251.882 MKWHr
Note on W13: Author:

## Generation
2019-09-04
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 120 | 120 | 120 | 118 | 118 | 118 | 120 | 120 | 121 | 122 | 121 | 123 | 124 | 113 | 112 | 112 | 112 | 119 |  | 121 | 121 | 121 | 122 | 122 | 122 | 122 | 2369100
2 | Karnaphuli Hydro PP Unit-4 & 5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2156000
3 | Chattogram TPP-1 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 100 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2200000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 436862
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 7 | 10 | 17 | 18 | 20 | 3 | 5 | 11 | 16 | 7 | 0 | [9 empty] | 128250
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 213 | 203 | 204 | 203 | 203 | 205 | 205 | 230 | 216 | 212 | 218 | 205 | 204 | 217 | 206 | 204 | 177 |  | 204 | 204 | 204 | 204 | 204 | 215 | 204 | 4934907
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 135 | 130 | 90 | 90 | 90 | 91 | 93 | 96 | 92 | 100 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2890630
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 0 | [14 empty] | 0 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 438518
12 | Hathazari 100 MW peaking PP |  | 0 | [10 empty] | 0 | 5 | 0 | 0 |  |  |  | 0 | 2 | 3 | 0 |  |  |  | 8368
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 424870
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 0 |  | 30 | 10 | 0 |  |  |  |  | 23040
14 | Titas 50 MW Peaking PP | [17 empty] | 0 |  | 50 | 50 | 50 | 0 |  |  |  | 115360
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 336 | 331 | 334 | 333 | 332 | 340 | 338 | 338 | 338 | 331 | 331 | 328 | 331 | 329 | 326 | 328 | 329 | 332 |  | 333 | 333 | 333 | 334 | 333 | 333 | 336 | 5198420
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 0 | [14 empty] | 0 | 2 |  | 193 | 300 | 300 | 300 | 300 | 300 | 300 | 1962108
19 | Ashuganj 195MW PP (APSCL-United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 75 | 75 | 75 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1739636
20 | Ghorasal TPP (Unit-1&2) | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1588000
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 194 | 200 |  | 200 | 200 | 200 | 210 | 210 | 210 | 210 | 4849000
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2583000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2394302
32 | Ashuganj 50 MW PP | 26 | 26 | 0 |  |  | 0 | 20 | 27 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 487224
33 | Ashuganj 225 MW CCPP | 144 | 144 | 144 | 144 | 144 | 144 | 145 | 146 | 143 | 144 | 140 | 139 | 143 | 142 | 139 | 141 | 141 | 143 |  | 144 | 142 | 142 | 142 | 142 | 142 | 143 | 3463000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 275 | 275 | 275 | 275 | 315 | 305 | 295 | 290 | 285 | 275 | 145 | 70 | 70 | 25 | 0 |  |  | 90 | 120 | 200 | 235 | 235 | 235 | 155 | 5013500
| Ashuganj 450 MW CCPP(North) | 320 | 340 | 320 | 335 | 345 | 295 | 260 | 260 | 270 | 360 | 360 | 360 | 325 | 335 | 360 | 335 | 335 | 260 |  | 345 | 345 | 345 | 335 | 260 | 295 | 260 | 7938600
35 | Ashuganj 55 MW PP (Precision) | 53 | 55 | 55 | 54 | 54 | 54 | 54 | 50 | 50 | 51 | 53 | 52 | 51 | 50 | 48 | 48 | 49 | 51 |  | 52 | 51 | 51 | 53 | 54 | 51 | 54 | 1252320
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 185 | 375 | 395 | 360 | 356 | 350 | 342 | 343 | 352 | 368 | 363 | 320 | 280 | 280 | 300 | 375 | 392 | 338 |  | 331 | 342 | 342 | 345 | 347 | 349 | 367 | 8292180
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 7668250
41 | Haripur 360MW CCPP(HPL) | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 270 | 270 | 274 | 274 | 254 | 254 | 254 | 254 | 255 | 255 | 254 |  | 323 | 305 | 303 | 300 | 300 | 300 | 300 | 6947000
42 | RPCL 210MW CCPP | 155 | 154 | 154 | 156 | 156 | 159 | 158 | 158 | 155 | 153 | 151 | 150 | 151 | 154 | 150 | 151 | 150 | 152 |  | 153 | 153 | 153 | 152 | 153 | 151 | 155 | 3597480
43
44 | Fenchugonj CCPP Phase-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 60 | 59 | 59 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 1418000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 955920
46 | Shajibazar 330 MW CCPP | 243 | 241 | 241 | 240 | 243 | 240 | 240 | 240 | 240 | 247 | 243 | 256 | 240 | 238 | 246 | 240 | 232 | 233 |  | 242 | 242 | 242 | 242 | 242 | 247 | 240 | 5462000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 67 | 67 | 67 | 69 | 69 | 68 | 66 | 65 | 63 | 62 | 57 | 63 | 62 | 65 | 60 | 67 |  | 67 | 67 | 65 | 66 | 65 | 65 | 67 | 1570176
48 | Shahjibazar 86MW PP (Shahjibazar) | 73 | 73 | 73 | 73 | 73 | 71 | 71 | 40 | 40 | 40 | 60 | 70 | 70 | 70 | 70 | 70 | 10 | 10 |  | 72 | 72 | 72 | 72 | 72 | 76 | 76 | 1510080
49 | Shahjibazar 50MW PP (EPL) | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 45 | 5 | 5 |  | 45 | 45 | 46 | 46 | 46 | 45 | 46 | 1014
50 | Sylhet 150 MW CCPP | 48 | 48 | 49 | 49 | 48 | 48 | 48 | 48 | 47 | 48 | 48 | 48 | 48 | 47 | 48 | 48 | 47 | 48 |  | 47 | 48 | 48 | 48 | 47 | 48 | 0 | 1206170
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | [8 empty] | 297000
52 | Sylhet 50MW PP (EPL) | 42 | 41 | 41 | 41 | 42 | 42 | 43 | 42 | 41 | 39 | 39 | 39 | 38 | 41 | 41 | 46 | 20 | 18 |  | 45 | 45 | 46 | 46 | 46 | 46 | 46 | 972000
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 250920
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 4 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 52 | 53 | 53 | 50 | 50 | 50 | 11 | 11 | 11 | 14 | 47 | 47 | 50 | 50 | 50 | 45 | 8 |  | 50 | 51 | 51 | 51 | 52 | 52 | 49 | 978000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 571320
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 285 | 300 | 290 | 300 | 260 | 255 | 270 | 275 | 315 | 310 | 310 | 265 | 270 | 280 | 315 | 290 | 290 |  | 300 | 300 | 290 | 305 | 310 | 315 | 300 | 7361700
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 21 | 35 | 35 | 35 | 35 | 35 | 35 | 40 | 35 | 35 |  | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 855822
59 | Sikalbaha 51 MW PP(Energis)
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 519264
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 465696
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 511596
63 | Impoprt (Tripura) | 174 | 170 | 166 | 164 | 152 | 138 | 128 | 132 | 136 | 138 | 140 | 144 | 140 | 142 | 148 | 146 | 140 | 144 |  | 184 | 184 | 188 | 186 | 190 | 186 | 184 | 3797760
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 41 | 35 | 40 | 31 | 10 | 3 | 2 | 2 | 5 | 8 | 7 | 4 | 5 | 15 | 18 |  | 23 | 28 | 30 | 34 | 38 | 38 | 38 | 514080
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 19 | 19 | 18 | 18 | 18 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 456372
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 806700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 |  |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 460340
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 19 | 26 | 22 |  | 24 | 30 | 31 | 28 | 31 | 31 | 31 | 662040
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 789500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803
73 | Ghorashal 108MW PP (Regent) | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 96 | 93 | 90 | 87 | 88 | 94 | 94 | 94 | 93 | 93 | 52 |  | 93 | 93 | 97 | 96 | 97 | 97 | 97 | 2212181
76 | Siddhirganj Desh
77 | Siddhirganj 100 PP(Dutch Bangla) | [17 empty] | 1 |  | 65 | 80 | 100 | 95 | 50 | 50 | 50 | 447360
78 | Gazipur 52 MW PP | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 34 | 34 | 34 | 34 | 34 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 976944
79 | Kodda 150MW PP | 133 | 65 | 65 | 36 | 20 | 16 | 0 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 26 |  | 125 | 133 | 135 | 135 | 135 | 135 | 135 | 1360320
80 | Jamalpur 95 MW PP(Powerpac) | 95 | 95 | 95 | 95 | 75 | 64 | 64 | 65 | 64 | 64 | 64 | 64 | 83 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2100480
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 930917
| Gazipur 100 MW PP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1600152
| Kaptai 7 MW Solar PP |  |  |  |  | 0 | 0 | 0 | 1 | 4 | 3 | 2 | 5 | 5 | 5 | 3 | 1 | 0 | [9 empty] | 30960
| Jodiac Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 739750
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 17 | 694178
82 | Madanganj 102 PP(Summit) | 45 | 0 | [14 empty] | 0 | 2 |  | 70 | 100 | 98 | 98 | 97 | 97 | 98 | 657192
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 23 | 50 | 50 | 50 | 50 | 50 | 10 | 18 |  | 83 | 100 | 100 | 100 | 100 | 100 | 100 | 995290
86 | Meghnaghat CCPP(Summit) | 265 | 269 | 262 | 270 | 272 | 260 | 265 | 265 | 270 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 235 | 260 | 275 | 276 | 275 | 130 | 140 | 6136233
87 | Meghnaghat 100 MW(IEL) | 100 | 60 | 0 | [14 empty] | 1 |  | 57 | 100 | 100 | 100 | 100 | 100 | 100 | 756480
88 | Ghorashal 78.5 MW PP(MAX) | 69 | 69 | 70 | 69 | 70 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 67 | 66 | 66 | 65 | 66 | 66 |  | 67 | 67 | 68 | 40 | 40 | 40 | 50 | 1445696
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 415680
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 48 | 48 | 48 | 48 | 48 | 10 |  | 33 | 48 | 48 | 48 | 48 | 48 | 49 | 1122552
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 |  | 28 | 43 | 43 | 43 | 43 | 43 | 43 | 1002706
94 | Gagnagar 102 MW PP (Digital Power) | 64 | 40 | 16 | 16 | 0 |  | 0 | 3 | 7 | 24 | 50 | 75 | 93 | 101 | 101 | 101 | 101 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 1558800
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 47 | 44 | 17 |  |  | 1 | 17 | 20 | 40 | 48 | 50 | 0 |  | 35 |  | 28 | 28 | 39 | 50 | 46 | 46 | 47 | 775680
96 | Chattogram 108 MW PP (ECPV) | 51 | 51 | 51 | 51 | 51 | 51 | 25 | 25 | 25 | 25 | 25 | 25 | 43 | 51 | 51 | 51 | 51 | 88 |  | 97 | 97 | 97 | 97 | 97 | 97 | 51 | 1358400
97 | Katpotti 52 MW PP (Sinha) | 27 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 19 | 20 |  | 19 | 21 | 40 | 47 | 47 | 47 | 46 | 517296
98 | Bosila 108MW PP(CLC) | 72 | 72 | 72 | 72 | 72 | 69 | 40 | 40 | 40 | 40 | 40 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1536000
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [8 empty] | 0 | 15 | 32 | 42 | 42 | 26 | 36 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 538016
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1160166
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 163 | 163 | 163 | 130 |  | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 3083735
102 | Sarishabari 3 MW Solar Plant |  |  |  |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 0 | 1 | 0 | [9 empty] | 12150
103 | Kamalaghat 54 MW PP(Banco Energy) | 53 | 53 | 53 | 53 | 53 | 53 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1196280
104 | Keranigonj 300 MW PP (APR) | [17 empty] | 0 |  | 103 | 27 | 0 |  |  |  | 0 | 83201
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 0 |  | 25 | 10 | 0 |  |  |  | 0 | 21347
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 150 | 120 | 80 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 36 | 81 | 100 | 100 | 100 | 100 |  | 168 | 180 | 190 | 190 | 190 | 190 | 192 | 2601600
112 | Aurahati 100MW PP (Aggreko) | [17 empty] | 0 |  | 27 | 10 | 0 |  |  |  | 0 | 23598
114 | Kodda 149 MW PP Unit-1 (Summit) | 138 | 72 | 20 | 0 |  |  | 0 | 1 | 66 | 96 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 105 |  | 135 | 135 | 135 | 135 | 133 | 133 | 136 | 2043360
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2190720
116 | Chandpur 200MW (Desh energy) | 180 | 180 | 180 | 180 | 180 | 140 | 70 | 70 | 70 | 70 | 70 | 84 | 139 | 151 | 175 | 195 | 100 | 50 |  | 132 | 200 | 200 | 200 | 200 | 200 | 200 | 3621120
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10 | 10 |  | 100 | 80 | 50 | 10 | 10 | 10 | 10 | 1309745
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2737200
| Anwara 300 MW PP (United) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 68 | 69 | 69 | 100 | 105 | 106 | 106 | 106 | 106 | 107 |  | 107 | 107 | 106 | 106 | 107 | 107 | 107 | 2160327
120 | Eastern Zone Total | 7672 | 7531 | 7302 | 7186 | 6970 | 6629 | 6342 | 6205 | 6294 | 6500 | 6560 | 6738 | 6728 | 6914 | 7023 | 6985 | 6629 | 6396 |  | 8157 | 8401 | 8469 | 8414 | 8326 | 8194 | 7997 | 169359959
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 66 | 66 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 49 | 49 | 49 | 49 | 49 | 42 |  | 100 | 115 | 115 | 115 | 115 | 115 | 115 | 1533120
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 24 | 0 | [13 empty] | 0 | 22 | 31 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 205920
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 96 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 53 | 53 | 73 | 105 | 50 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1668480
130
131
132
133
| Barisal 110 MW PP (Summit ) | 110 | 96 | 32 | 0 | [12 empty] | 0 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 958272
136 | Barisal GT PP Unit-1& 2 | [15 empty] | 0 | 12 | 0 | [8 empty] | 11081
137 | Bhola 95 MW PP (Aggreko) | 95 | 97 | 97 | 95 | 94 | 97 | 62 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 52 | 51 | 53 | 52 |  | 91 | 96 | 96 | 96 | 97 | 95 | 95 | 1568735
| Bhola 225 MW CCPP | 180 | 180 | 179 | 179 | 179 | 167 | 167 | 166 | 180 | 180 | 180 | 179 | 166 | 166 | 180 | 179 | 168 | 167 |  | 167 | 176 | 179 | 178 | 179 | 179 | 178 | 4329000
140 | Bhola 33 MW PP (Venture) | 31 | 31 | 30 | 30 | 24 | 20 | 21 | 18 | 17 | 14 | 17 | 19 | 18 | 20 | 19 | 20 | 25 | 23 |  | 34 | 38 | 39 | 40 | 40 | 40 | 39 | 624546
141 | Noapara 100 MW PP (Bangla Trac) | 20 | 0 | [15 empty] | 0 |  | 56 | 100 | 100 | 100 | 100 | 100 | 100 | 633600
142 | Noapara 40 MW PP (Khanjahan Ali) | 40 | 40 | 40 | 40 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 8 |  | 33 | 33 | 40 | 40 | 40 | 40 | 40 | 581125
143 | Gopalganj 100 MW Peaking PP | 55 | 0 | [12 empty] | 0 | 1 | 23 | 36 |  | 72 | 65 | 63 | 62 | 60 | 60 | 60 | 456548
144 | Bheramara GTPP Unit-1,2 & 3
145 | Madhumati 100 MW PP | 104 | 104 | 104 | 104 | 104 | 103 | 100 | 105 | 97 | 87 | 93 | 95 | 0 | 59 | 104 | 104 | 104 | 103 |  | 104 | 103 | 103 | 103 | 103 | 103 | 103 | 2345472
146 | Bheramara HVDC | 905 | 906 | 906 | 906 | 906 | 906 | 907 | 907 | 906 | 906 | 906 | 906 | 906 | 906 | 908 | 909 | 906 | 905 |  | 905 | 905 | 906 | 905 | 905 | 905 | 905 | 21741818
147 | Bheramara 360 MW CCPP | 380 | 380 | 380 | 380 | 380 | 300 | 270 | 270 | 270 | 270 | 300 | 370 | 370 | 370 | 400 | 410 | 410 | 270 |  | 395 | 340 | 340 | 340 | 340 | 340 | 390 | 8696736
148
149
150 | Barapukuria TPP Unit-1 | 71 | 69 | 69 | 69 | 69 | 69 | 70 | 70 | 71 | 71 | 71 | 71 | 71 | 70 | 70 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 70 | 71 | 71 | 1656000
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 260 | 260 | 261 | 260 | 260 | 260 | 260 | 260 | 275 | 275 | 275 | 275 | 275 | 275 | 269 | 269 | 269 | 270 |  | 270 | 270 | 270 | 262 | 261 | 260 | 260 | 6466800
153 | Baghabari 71 MW GTPP | 55 | 55 | 55 | 55 | 55 | 55 | 60 | 60 | 60 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1330000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 0 | [15 empty] | 14 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 385616
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 186 | 185 | 187 | 186 | 187 | 180 | 160 | 165 | 166 | 170 | 205 | 202 | 193 | 195 | 197 | 196 | 187 | 168 |  | 172 | 185 | 186 | 192 | 191 | 190 | 196 | 4726455
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 191 | 189 | 190 | 190 | 190 | 181 | 159 | 161 | 167 | 173 | 177 | 198 | 206 | 199 | 198 | 198 | 200 | 187 |  | 193 | 195 | 196 | 196 | 197 | 191 | 200 | 4779109
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 415 | 415 | 415 | 360 | 320 | 270 | 240 | 280 | 350 | 350 | 350 | 350 | 418 | 414 | 414 | 414 | 270 |  | 370 | 330 | 330 | 330 | 330 | 330 | 380 | 8572727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 37 | 37 | [15 empty] | 10 |  | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 274525
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 508560
163 | Bogura 20 MW PP (Energyprima) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 10 | 10 | 11 | 11 | 11 | 7 | 183456
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 225972
165 | Amnura 50 MW PP(Sinha) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0 | 0 | 12 | 12 | 12 | 12 |  | 35 | 50 | 50 | 50 | 12 | 12 | 12 | 382060
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 24 | 24 | 24 | 42 | 42 | 42 | 0 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 887413
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 0 | [13 empty] | 14 |  | 18 | 23 | 31 | 29 | 29 | 29 | 29 | 228900
168 | Santahar 50 MW Peaking PP | 22 | 22 | 22 | 0 | [13 empty] | 9 |  | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 192425
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 42 | 43 | 51 | 43 | 43 | 43 | 43 | 465120
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 88 | 24 | 24 | 24 | 24 | 0 | 0 | [5 empty] | 90 |  | 94 | 94 | 94 | 94 | 93 | 93 | 93 | 1169184
171 | Baghabari 200 MW PP (Paramount)
172 | Bagura 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 113 | 74 | 74 | 74 | 74 | 74 | 74 | 94 | 107 | 113 | 113 | 94 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2436576
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 15 | 15 | 0 | [23 empty] | 33000
176 | Rangpur 113 MW PP (Confidence) | 105 | 98 | 98 | 98 | 98 | 98 | 73 | 70 | 70 | 70 | 70 | 74 | 95 | 102 | 105 | 105 | 100 | 105 |  | 98 | 98 | 91 | 91 | 98 | 98 | 100 | 2232960
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 5 | 4 | 1 | 0 | [8 empty] | 30591
178
178