## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:July 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-07-01 |  | 2023-06-01 |  | 2022-07-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15164 | 2023-07-26 | 14655 | 2023-06-08 | 14038 | 2022-06-08 | 15648 | 2023-04-19
|  |  | 21:00 |  | 20:00 |  | 23:00 |  | 21:00
2 | Minimum Generation (MW) | 8071 | 2023-07-01 | 7589 | 2023-06-28 | 8231 | 2022-06-17 | 8071 | 2023-07-01
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | 6:00
3 | Maximum Evening Peak Generation (MW) | 14655 | 2023-06-08 | 14655 | 2023-06-08 | 14004 | 2022-06-06 | 15648 | 2023-04-19
|  |  | 20:00 |  | 20:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13419 | 2023-07-24 | 12677 | 2023-06-08 | 12226 | 2022-06-08 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15700 | 2023-07-30 | 15800 | 2023-06-30 | 14038 | 2022-06-08 | 16096 | 2023-04-19
|  |  | 21:00 |  | 20:00 |  | 23:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14160.6129 |  | 13225.3 |  | 13051.7667 |  | - | -
7 | Average Generation (MW) at Day Peak | 12085.4516 |  | 11423.9667 |  | 11161.4333 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 927 | 2023-07-02 | 930 | 2023-06-25 | 933 | 2022-06-07 | 956 | 27/3/2019
|  |  | 21:00 |  | 7:30 |  | 2:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 182 | 2023-07-13 | 184 | 2023-06-13 | 188 | 2022-06-08 | 194 | 12/06/19
|  |  | 15:00 |  | 19:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1100 | 2023-07-19 | 1945 | 2023-06-06 | - | - | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | - |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14448 | 2023-07-19 | 13763 | 2023-06-06 | - | - | 13200 | 04/10/2022
|  |  | 21:00 | - | 21:00 | - | - |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-07-03 | 0 | 2023-06-09 | - | - | - | -
|  |  | 21:00 |  | - |  |  | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12454 | 2023-07-03 | 12699 | 2023-06-09 | - | - | - | -
|  |  | 21:00 |  | 21:00 |  |  | - | -
14 | Maximum Load Shed (MW) at Day Peak | 1806 | 2023-07-20 | 2675 | 2023-06-05 | - | - | - | -
|  |  | 12:00 |  | 12:00 |  |  | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12359 | 2023-07-20 | 12099 | 2023-06-05 | - | - | - | -
|  |  | 12:00 |  | 12:00 |  |  | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-07-03 | 0 | 2023-06-27 | - | - | - | -
|  |  | 21:00 |  | - |  |  | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 9951 | 2023-07-03 | 12099 | 2023-06-05 | - | - | - | -
|  |  | 21:00 |  | 12:00 |  |  | - | -
18 | Nos. of Days Load Shed at Evening Peak | 24 |  | 22 |  | - |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 24 |  | 26 |  | - |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1774.0473 |  | 1745.3811 |  | 1590.9771 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 45.3987 |  | 88.4927 |  | 84.3577 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1728.6486 |  | 1656.8884 |  | 1506.6194 |  | - | -
23 | Net Generation of IPP (MKWH) | 5418.6942 |  | 4513.7304 |  | 5289.635 |  | - | -
24 | Net Generation of REB (MKWH) | 119.8463 |  | 121.3394 |  | 122.8415 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 406.1896 |  | 364.0404 |  | 624.4748 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7673.3787 |  | 6655.9986 |  | 7543.5707 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4793.0721 |  | 4651.8044 |  | 4234.9012 |  | 493.07 | July-23
27 | Energy Generation by Diesel (MKWH) | 254.4028 |  | 299.6883 |  | 491.7382 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1645.587 |  | 1291.3754 |  | 2164.1587 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 45.1338 |  | 25.8407 |  | 52.8346 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 45.4439 |  | 34.6981 |  | 25.0967 |  | 40.67 | July-23
31 | Energy Generation by Coal (MKWH) | 935.1378 |  | 441.0844 |  | 659.199 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 773.3438 |  | 737.9119 |  | 738.4142 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 84.9553 |  | 78.4931 |  | 88.6952 |  | 92.62 | August-22

## QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 15164 | 2023-07-26 | 21:00
Generation Period
| Dhaka | MW | 5079.09
| Chattogram | MW | 1402
| Cumilla | MW | 1393
| Mymensingh | MW | 1101
| Sylhet | MW | 546
a) | Total supply in East zone | MW | 9521.09
| Khulna | MW | 1775.8
| Barisal | MW | 472
| Rajshahi | MW | 1588.4
| Rangpur | MW | 968
b) | Total supply in West zone | MW | 4804.2
c) | Total supply in both zone ( a+b) | MW | 14325.29
Ref: | 27.21.0000.603.16.087.20.697 | Date: 17/08/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:July 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 580 | 2023-07-31 | 23:00
| b) Ishurdi end | MW | 244 | 2023-07-13 | 9:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 980 | 2023-07-13 | 11:00
| b) Ishurdi end | MW | 108 | 2023-07-03 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.8611
| b) Ishurdi end | MKWH | 59.887
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 58.0904
| b) Ishurdi end | MKWH | 3.7487
23 | Transmission loss of EWI/ NO-1 | % | 3 |  |  | 5.91
24 | Daily Maximum power Export through EWI/ NO-2 |  |  |  |  | 2.955
| a) Ashuganj end | MW | 280 | 2023-07-09 | 6:00
| b)Serajganj end | MW | 490 | 2023-07-13 | 1:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 180 | 2023-07-05 | 15:00
| b)Sirajganj end | MW | 74 | 2023-07-10 | 7:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.2861
| b)Sirajganj end | MKWH | 173.102
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 171.4014
| b)Sirajganj end | MKWH | 0.288
30 | Transmission loss of EWI /NO-2 | % | 1.432
31 | Daily Maximum power Export through EWI/ NO-3
a) | Gopalganj end | AMPS | 2370 | 2023-07-26 | 13:00
|  | MW | 1550
b) | Aminbazar end | AMPS
MW
32 | Daily Maximum power Import through EWI/ NO-3
a) | Gopalganj end | AMPS | 948 | 2023-07-03 | 20:00
|  | MW | 660
b) | Aminbazar end | AMPS
MW
33 | Daily Maximum Energy Export through EWI/NO-3
a) | Gopalganj end | MWH | 33305.6 | 2023-07-25
b) | Aminbazar end | MWH
34 | Daily Maximum Energy Import through EWI/ NO-3
a) | Gopalganj end | MWH | 8272.25 | 2023-07-02
b) | Aminbazar end | MWH
35 | Total Energy Export through EWI/ NO-3
a) | Gopalganj end | MWH | 534511.376
b) | Aminbazar end | MWH | 15448.01
36 | Total Energy Import through EWI/ NO-3
a) | Gopalganj end | MWH | 15423.424
b) | Aminbazar end | MWH | 533851.502
37 | Transmission loss of EWI/ NO-3 | % | 0.12445
* ** Total energy export from Gopalganj end and import from Aminbazar end.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division | [10 empty] | 8801.6
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance | [11 empty] | 498.6333
Month: July 2023 | [11 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks |  |  | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-07-05 08:52 | 2023-07-05 09:20 | 0:28 | T | Trip due to df/dt | 29 | 13.5333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-07-13 22:26 | 2023-07-13 22:31 | 0:05 | T | df/dt Rely | 40 | 3.3333 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-07-05 08:52 | 2023-07-05 09:20 | 0:28 | T | Trip due to df/dt | 29 | 13.5333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-07-13 22:26 | 2023-07-13 22:31 | 0:05 | T | df/dt Rely | 40 | 3.3333 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-07-13 22:28 | 2023-07-13 22:36 | 0:08 | T | Under frequency | 120 | 16 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-07-16 13:22 | 2023-07-16 13:27 | 0:05 | T | Under frequency | 60 | 5 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-07-29 18:40 | 2023-07-29 18:51 | 0:11 | T | 33 kv pbs feeder trip | 64 | 11.7333 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-07-13 22:28 | 2023-07-13 22:36 | 0:08 | T | Under frequency | 120 | 16 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-07-16 13:22 | 2023-07-16 13:27 | 0:05 | T | Under frequency | 60 | 5 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-07-29 18:40 | 2023-07-29 18:51 | 0:11 | T | 33 kv pbs feeder trip | 64 | 11.7333 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-07-25 17:39 | 2023-07-25 18:28 | 0:49 | T | 33 Kv 9 number feeder jumper Out | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-07-25 17:39 | 2023-07-25 18:28 | 0:49 | T | 33 Kv 9 number feeder jumper Out | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) HT | 2023-07-29 11:51 | 2023-07-29 13:08 | 1:17 | T | When the Auxiliary drop out fuse is installed it bursts at 33kv LA. | 0 | 0 | No interruption
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) LT | 2023-07-29 11:51 | 2023-07-29 13:09 | 1:18 | T | When the Auxiliary drop out fuse is installed it bursts at 33kv LA. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I LT | 2023-07-05 19:18 | 2023-07-05 19:43 | 0:25 | T | T-1 33kV tripped due to Chandra 33kV feeder fault. | 60 | 25 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 LT | 2023-07-05 19:18 | 2023-07-05 19:43 | 0:25 | T | T-2 33kV tripped due to Chandra 33kV feeder fault. | 60 | 25 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) LT | 2023-07-16 04:22 | 2023-07-16 04:37 | 0:15 | T | Over Current (B,C Phase) | 45 | 11.25 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2023-07-16 04:22 | 2023-07-16 04:37 | 0:15 | T | Over Current (B Phase) | 45 | 11.25 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-07-08 16:38 | 2023-07-08 16:46 | 0:08 | T | PBS rowmari 33 Kv rips off the feeders skywire. | 30 | 4 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-07-08 16:38 | 2023-07-08 16:46 | 0:08 | T | PBS rowmari 33 Kv rips off the feeders skywire. | 30 | 4 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-07-18 06:20 | 2023-07-18 08:15 | 1:55 | E/O | Red hot maintenance | 15 | 28.75 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2023-07-18 06:20 | 2023-07-18 08:11 | 1:51 | E/O | Red hot maintenance | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-07-30 21:37 | 2023-07-30 22:43 | 1:06 | E/O | DCS Blade change (PBS) | 34 | 37.4 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-07-30 21:37 | 2023-07-30 22:43 | 1:06 | E/O | DCS blade change (PBS) | 34 | 37.4 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I HT | 2023-07-13 11:43 | 2023-07-13 13:37 | 1:54 | E/O | Shutdown taken by DPBS-1 due to 33kV Kabirpur feeder's bus DS maintenance work. | 40 | 76 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2023-07-22 21:32 | 2023-07-22 23:42 | 2:10 | E/O | 33 kv Bajitpur (PDB) feeder red hot, S/D Taken by PDB Kishoreganj | 70 | 151.6667 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | 33 kV T2 Bus | 2023-07-22 21:35 | 2023-07-22 23:35 | 2:00 | E/O | 33 kv Bajitpur (PDB) feeder red hot, S/D Taken by PDB Kishoreganj | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2023-07-08 03:31 | 2023-07-08 04:30 | 0:59 | E/O | 33 diggar kanda feedar red hot bus ds so T-3 X-F shut down by PDB. | 30 | 29.5 | Power interruption
|  |  | Total : | 20:44 |  | Unserved Energy: |  | 540.4167
Dhaka (South) Grid Circle :
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 HT | 2023-07-04 13:09 | 2023-07-04 13:29 | 0:20 | T | PRV-2 tripped. | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-02 14:09 | 2023-07-02 14:30 | 0:21 | T | 33kV Incoming 1&2 Tripped because 33kV Outgoing Feeder(Munshiganj Sadar Zonal) is not tripped | 45 | 16.5 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-07-02 14:09 | 2023-07-02 14:31 | 0:22 | T | 33kV Incoming 1&2 Tripped because 33kV Outgoing Feeder(Munshiganj Sadar Zonal) is not tripped | 45 | 16.5 | Power interruption
Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2023-07-06 17:19 | 2023-07-06 20:05 | 2:46 | E/O | S/D taken for Redhot Occures in Y -phase C.T (33 kv) | 20 | 55.3333 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-14 06:30 | 2023-07-14 09:05 | 2:35 | E/O | Due to Red Hot 33Kv Bus Coupler (Work Done By Pbs) Load Shead Will be Manage by pbs. | 43 | 111.0833 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-07-14 06:32 | 2023-07-14 09:07 | 2:35 | E/O | Due to Red Hot 33Kv Bus Coupler (Work Done By Pbs) Load Shead Will be Manage by pbs. | 44 | 113.6667 | Power interruption
|  |  | Total : | 8:59 |  | Unserved Energy: |  | 313.0833
Chattogram Grid Circle :
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-07-31 16:43 | 2023-07-31 18:26 | 1:43 | T | 33 kV Blue phase XLPE Cable Punchured | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | TR-2 LT | 2023-07-21 10:13 | 2023-07-21 10:52 | 0:39 | T | T-02 secondary tripped due to T-02 main tank PRD Trip. | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | 425T(BSRM) HT | 2023-07-03 12:12 | 2023-07-03 12:36 | 0:24 | E/O | Collect Transformer oil | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2023-07-30 07:15 | 2023-07-30 09:24 | 2:09 | E/O | PDB nd PBS 33 kv bus-01 S/D for emergency disk insuletor replacement work. | 33 | 70.95 | Power interruption
Khagrachori 132/33kV Grid Sub-Station | TR-1 HT | 2023-07-25 07:48 | 2023-07-25 09:14 | 1:26 | E/O | Prework Measurement for Transformer painting | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2023-07-14 05:52 | 2023-07-14 06:52 | 1:00 | E/O | R-phase RED HOT | 50 | 50 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2023-07-20 10:22 | 2023-07-20 11:30 | 1:08 | E/O | 33KV Bus shut down taken by Chokoria PDB for 33 KV bus isolator maintenance. | 6 | 6.8 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-07-31 20:14 | 2023-07-31 20:58 | 0:44 | E/O | For 33KV Bus DS high temperature maintenance. | 40 | 29.3333 | Power interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) LT | 2023-07-01 13:45 | 2023-07-01 18:39 | 4:54 | E/O | DS maintainance of PDB | 0 | 0 | No interruption
|  |  | Total : | 14:07 |  | Unserved Energy: |  | 157.0833
Cumilla Grid Circle :
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T LT | 2023-07-11 17:49 | 2023-07-11 17:54 | 0:05 | T | INST. Earth -Fault. 33KV LPBS -02 Feeder fault | 60 | 5 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR1-415T LT | 2023-07-15 10:35 | 2023-07-15 10:55 | 0:20 | T | T-1 VCB 33kv incoming tripping O/C (T)for CHO.33/11 T-4 Feeder . | 30 | 10 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 LT | 2023-07-12 14:44 | 2023-07-12 16:10 | 1:26 | T | 33 KV feeder fault | 10 | 14.3333 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 HT | 2023-07-04 21:39 | 2023-07-04 22:29 | 0:50 | T | Overload | 122 | 101.6667 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2023-07-04 21:39 | 2023-07-04 22:25 | 0:46 | T | Overload | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-07-16 12:20 | 2023-07-16 12:40 | 0:20 | T | 33KV PDB CT blast (R & Y phase) | 18 | 6 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-07-16 12:20 | 2023-07-16 12:45 | 0:25 | T | 33KV PDB CT blast (R & Y phase) | 18 | 7.5 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 HT | 2023-07-27 20:16 | 2023-07-27 20:42 | 0:26 | T | 67 HV Dir O/C Trip | 47 | 20.3667 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 LT | 2023-07-24 13:20 | 2023-07-24 14:59 | 1:39 | T | Due to 230kv side winding temperature trip alarm(Actual temperature was 54, Trip temperature -90. But meter temperature indications was HV-52, MV-54, LV-52) | 23 | 37.95 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-07-26 08:45 | 2023-07-26 08:57 | 0:12 | T | Over Load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-07-30 18:51 | 2023-07-30 19:12 | 0:21 | T | Over Load | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 HT | 2023-07-14 15:17 | 2023-07-14 16:20 | 1:03 | E/O | T-03 transformer 33KV Side Y-Phase Red hot Remove | 15 | 15.75 | Power interruption
Daudkandi 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-05 07:04 | 2023-07-05 09:50 | 2:46 | E/O | Red Hot removing work at 33KV bus of T-1 by PBS-3 Cumilla. | 30 | 83 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-07-21 06:25 | 2023-07-21 07:51 | 1:26 | E/O | Red hot maintenance work of BPDB 33KV bus isolator ofchowmohoni ckt-1. S/D taken by BPDB. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-07-31 06:21 | 2023-07-31 08:14 | 1:53 | E/O | BPDB 33KV T-1 Bus side isolator Red Hot maintenance. | 15 | 28.25 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 LT | 2023-07-01 11:12 | 2023-07-01 11:54 | 0:42 | E/O | 33kv breaker high temperature | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 401T LT | 2023-07-24 13:40 | 2023-07-24 13:57 | 0:17 | E/O | For safe power restoration. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-07-24 13:40 | 2023-07-24 14:20 | 0:40 | E/O | For safe power restoration. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-07-27 21:36 | 2023-07-28 00:05 | 2:29 | E/O | 33 kv Circuit Breaker Maintenance . | 40 | 99.3333 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-07-24 13:40 | 2023-07-24 13:58 | 0:18 | E/O | For safe power restoration. | 0 | 0 | No interruption
Beanibazar 132/33kV Grid Sub-Station | 132 KV Transformer TR-01 LT | 2023-07-08 12:42 | 2023-07-08 15:23 | 2:41 | E/O | Red hot 33kv feeder | 6 | 16.1 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132 KV Transformer TR-01 LT | 2023-07-24 13:29 | 2023-07-24 14:20 | 0:51 | E/O | Line trip | 60 | 51 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2023-07-13 00:54 | 2023-07-13 02:17 | 1:23 | E/O | 33 kv bus bar red hot | 30 | 41.5 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2023-07-22 18:38 | 2023-07-22 20:16 | 1:38 | E/O | 33 kv bus red hot | 44 | 71.8667 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2023-07-24 13:29 | 2023-07-24 14:20 | 0:51 | E/O | Line trip | 60 | 51 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2023-07-11 20:33 | 2023-07-12 11:44 | 15:11 | E/O | T-2 33kv incoming R phase Red hot | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2023-07-20 22:30 | 2023-07-21 08:30 | 10:00 | E/O | 33KV Bus loop Red Hot | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2023-07-11 20:32 | 2023-07-12 11:45 | 15:13 | E/O | T-2 33kv incoming R phase Red Hot | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2023-07-20 20:55 | 2023-07-21 08:31 | 11:36 | E/O | 33kv Bus Loop R phase | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2023-07-30 20:19 | 2023-07-31 08:46 | 12:27 | E/O | Red hot | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2023-07-24 14:05 | 2023-07-24 14:21 | 0:16 | E/O | Blackout, With permission of NLDC | 23 | 6.1333 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 HT | 2023-07-27 20:30 | 2023-07-27 21:11 | 0:41 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2023-07-24 14:05 | 2023-07-24 14:26 | 0:21 | E/O | Blackout, With permission of NLDC | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2023-07-27 20:30 | 2023-07-27 20:43 | 0:13 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 HT | 2023-07-10 15:16 | 2023-07-10 19:01 | 3:45 | E/O | Due to emergency PT maintenance | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 HT | 2023-07-24 23:45 | 2023-07-25 00:13 | 0:28 | E/O | Maintenance. | 20 | 9.3333 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 LT | 2023-07-10 15:17 | 2023-07-10 20:29 | 5:12 | E/O | due to PT emergency maintenance | 0 | 0 | No interruption
|  |  | Total : | 101:11 |  | Unserved Energy: |  | 676.0833
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-07-12 03:32 | 2023-07-12 03:47 | 0:15 | T | For WZPDCL 33kV Polashpur Fedder fault. | 52 | 13 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-07-12 03:32 | 2023-07-12 03:47 | 0:15 | T | For 33kV Polashpur feeder fault. | 33 | 8.25 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2023-07-14 07:14 | 2023-07-14 09:55 | 2:41 | T | Due to loos connection of relay panel. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-07-13 05:01 | 2023-07-13 14:04 | 9:03 | T | 33 kv cable fault. Only 132 kv CB Trip. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-07-21 10:24 | 2023-07-21 10:52 | 0:28 | T | Bagerhat pbs1&2 Faulty | 34 | 15.8667 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-07-21 10:24 | 2023-07-21 10:53 | 0:29 | T | Bagerhat pbs 1&2 Faulty | 34 | 16.4333 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-16 13:20 | 2023-07-16 13:27 | 0:07 | T | NLDC signal. | 25 | 2.9167 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-07-13 22:27 | 2023-07-13 22:35 | 0:08 | T | None | 36 | 4.8 | Power interruption
Rajbari 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-07-16 13:20 | 2023-07-16 13:28 | 0:08 | T | NLDC signal. | 25 | 3.3333 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-07-23 18:58 | 2023-07-23 19:47 | 0:49 | T | N/A | 11 | 8.9833 | Power interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-07-19 05:09 | 2023-07-19 08:18 | 3:09 | E/O | Maintenance for Red Hot | 0 | 0 | No interruption
Barguna 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-07-18 21:33 | 2023-07-19 08:18 | 10:45 | E/O | Red hot Occured at 33 kV Incomer 2 Bus D/S at B phase | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) LT | 2023-07-16 08:59 | 2023-07-16 12:58 | 3:59 | E/O | Due to sparking of 33 kV Y-phase Bushing shutdown was taken on emergency basis. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-07-13 05:45 | 2023-07-13 14:06 | 8:21 | E/O | 33 kv under ground fault (B- fase) | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-07-27 13:38 | 2023-07-27 15:21 | 1:43 | E/O | red hot at 33kv sharsha feeder Y phase | 20 | 34.3333 | Power interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2023-07-04 08:50 | 2023-07-04 10:16 | 1:26 | E/O | Redhot | 4 | 5.7333 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2023-07-25 14:21 | 2023-07-25 16:44 | 2:23 | E/O | TR 2 33kv Incomer Isolator R phase red hot maintenance. | 15 | 35.75 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-07-05 10:42 | 2023-07-05 13:53 | 3:11 | E/O | in between 436B(33kv incoming CB) & CT nut-bolt melted. (After 22 minutes of load interruption 33KV BUS Closed and at 11:06 AM NO LOAD INTRRUPTION) | 20 | 63.6667 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-07-11 09:09 | 2023-07-11 10:59 | 1:50 | E/O | Shutdown due to Mongla WZPDCL substation 33kv ds3 bus coupler red phase jumper out. | 4 | 7.3333 | Power interruption
Rampal 400/230kV Grid Sub-Station | Start-Up Transformer (SUT) HT | 2023-07-13 10:57 | 2023-07-13 20:04 | 9:07 | E/O | Energy meter cabling work. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-07-04 08:23 | 2023-07-04 09:49 | 1:26 | E/O | Station auxiliary transformer fuse connection work | 40 | 57.3333 | Power interruption
Satkhira 132/33kV Grid Sub-Station | 33 KV BUS | 2023-07-04 08:28 | 2023-07-04 09:39 | 1:11 | E/O | Station auxiliary transformer fuse connection work. | 40 | 47.3333 | Power interruption
|  |  | Total : | 62:54 |  | Unserved Energy: |  | 325.0667
HVDC Grid Circle :
Jashore 132/33kV Grid Sub-Station | T-3 HT | 2023-07-12 05:49 | 2023-07-12 06:12 | 0:23 | T | T3 both side triped by lockout relay due to earth fault of 33 kv PBS Hasimpur feeder fault. | 26 | 9.9667 | Power interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-07-21 09:43 | 2023-07-21 10:05 | 0:22 | T | Differential protection trip, wind. Temo. Trip. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 HT | 2023-07-27 14:55 | 2023-07-29 18:24 | 51:29 | T | PRD OPERATE | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-1 LT | 2023-07-09 16:11 | 2023-07-09 17:34 | 1:23 | E/O | Red hot at 132kv side(PDB) | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-1 HT | 2023-07-05 06:45 | 2023-07-05 10:20 | 3:35 | E/O | Red hot maintenance work. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | T-1 HT | 2023-07-21 20:30 | 2023-07-21 21:45 | 1:15 | E/O | Emergency red hot maintenece. | 38 | 47.5 | Power interruption
Pabna 132/33kV Grid Sub-Station | T-1 LT | 2023-07-05 06:42 | 2023-07-05 10:24 | 3:42 | E/O | Red hot maintenance work | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-07-31 21:27 | 2023-07-31 22:39 | 1:12 | E/O | 33 kV Incoming CT (B-phase) Red-hot maintenance work. | 15 | 18 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-3 HT | 2023-07-16 21:51 | 2023-07-17 14:48 | 16:57 | E/O | due to 132 kv T3 side air leakage from air compressor | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-3 LT | 2023-07-16 21:41 | 2023-07-17 14:49 | 17:08 | E/O | due to 132 kv T3 side air leakage from air compressor | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-07-01 21:19 | 2023-07-01 22:20 | 1:01 | E/O | Red Hot maintanance | 25 | 25.4167 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 HT | 2023-07-01 08:23 | 2023-07-01 09:40 | 1:17 | E/O | T2A incomer Y-Phase DS Red hot maintenance. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 LT | 2023-07-01 08:23 | 2023-07-01 09:41 | 1:18 | E/O | T2A incomer Y-Phase DS Red hot maintenance. | 35 | 45.5 | No interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-07-30 07:16 | 2023-07-30 08:35 | 1:19 | E/O | Redhot maintenance . | 30 | 39.5 | Power interruption
Magura 132/33kV Grid Sub-Station | T-3 HT | 2023-07-26 12:41 | 2023-07-26 14:52 | 2:11 | E/O | Buchholz Alarm. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 HT | 2023-07-27 11:16 | 2023-07-27 13:22 | 2:06 | E/O | Forced S/D for Buchholz alarm by annunciator | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 LT | 2023-07-26 12:39 | 2023-07-26 14:54 | 2:15 | E/O | Buchholz alarm. | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 LT | 2023-07-27 11:15 | 2023-07-27 13:22 | 2:07 | E/O | Forced S/D for Buchholz alarm by annunciator | 0 | 0 | No interruption
|  |  | Total : | 111:00 |  | Unserved Energy: |  | 185.8833
Bogura Grid Circle:
Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-31 20:56 | 2023-07-31 21:30 | 0:34 | T | O/C | 20 | 11.3333 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 LT | 2023-07-01 10:17 | 2023-07-01 10:45 | 0:28 | T | 33kv dupchacia pbs feeder | 19 | 8.8667 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-07-11 06:55 | 2023-07-11 07:26 | 0:31 | T | Heavy Thundering | 35 | 18.0833 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-07-11 06:55 | 2023-07-11 07:26 | 0:31 | T | Heavy Thundering | 15 | 7.75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2023-07-25 08:30 | 2023-07-25 23:31 | 15:01 | T | Problem of NESCO (Underground cables) | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-07-25 08:30 | 2023-07-25 23:33 | 15:03 | T | Gas pressure lpw | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2023-07-26 21:09 | 2023-07-26 21:11 | 0:02 | T | Over current relay | 37 | 1.2333 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-07-05 07:42 | 2023-07-05 09:31 | 1:49 | E/O | For Red-Hot Maintenance. | 10 | 18.1667 | Power interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2023-07-25 15:27 | 2023-07-25 17:40 | 2:13 | E/O | Red hot maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 HT | 2023-07-10 09:56 | 2023-07-10 14:48 | 4:52 | E/O | Red hot | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | T-02 LT | 2023-07-10 09:56 | 2023-07-10 14:49 | 4:53 | E/O | Red hot | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-07-17 05:30 | 2023-07-17 17:40 | 12:10 | E/O | None | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-07-20 11:05 | 2023-07-20 11:20 | 0:15 | E/O | After 132kv CB 432B emergency maintenance to power throw by CB 432B. Power flow to T-3 no forced load-shed | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-07-24 06:54 | 2023-07-24 08:58 | 2:04 | E/O | TR-04 33kV CT connector at R-phase P1 side Crack Found. | 25 | 51.6667 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2023-07-30 07:35 | 2023-07-30 16:09 | 8:34 | E/O | T-3 33 kv C.B Maintanance.(SF6 GAS Lekage) | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-07-30 07:28 | 2023-07-30 16:10 | 8:42 | E/O | T-3 33 kv C.B Maintanance.(SF6 GAS Lekage) | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-07-02 10:42 | 2023-07-02 11:51 | 1:09 | E/O | Deluabari 33 kV feeder Source DS Red hot Maintenance Work. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T LT | 2023-07-02 10:41 | 2023-07-02 11:51 | 1:10 | E/O | Deluabari 33 kV feeder Source DS Red hot Maintenance Work. | 15 | 17.5 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 426T LT | 2023-07-14 16:04 | 2023-07-14 16:33 | 0:29 | E/O | PBS 33/.4 kV Auxiliary transformer disconnect wire Maintenance work. | 23 | 11.1167 | Power interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) HT | 2023-07-25 12:12 | 2023-07-25 12:52 | 0:40 | E/O | TR-01 , Incomer-01 CT B-phase Connector red hot. | 0 | 0 | No interruption
Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) LT | 2023-07-25 12:11 | 2023-07-25 12:53 | 0:42 | E/O | Transformer- 01, Incomer-01 CT B-phase Connector Red Hot. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2023-07-28 07:04 | 2023-07-28 09:30 | 2:26 | E/O | Red hot | 60 | 146 | Power interruption | ok
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) HT | 2023-07-28 07:04 | 2023-07-28 09:30 | 2:26 | E/O | red hot | 60 | 146 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) HT | 2023-07-01 12:01 | 2023-07-01 12:55 | 0:54 | E/O | Due to Redhot T-4 Tr. LT Breaker pole connector (R-ph). | 0 | 0 | No interruption
|  |  | Total : | 87:38 |  | Unserved Energy: |  | 437.7167
Others :
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 HT | 2023-07-24 13:20 | 2023-07-24 13:54 | 0:34 | T | Over current | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 LT | 2023-07-24 13:20 | 2023-07-24 13:53 | 0:33 | T | Over current | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan HT | 2023-07-24 09:58 | 2023-07-24 12:14 | 2:16 | T | Over current, Earth fault | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan LT | 2023-07-24 09:58 | 2023-07-24 12:15 | 2:17 | T | Over current, earth fault | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan HT | 2023-07-11 10:18 | 2023-07-11 11:33 | 1:15 | E/O | "B" Phase CB connection point Temperature rise. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan LT | 2023-07-11 10:19 | 2023-07-11 11:35 | 1:16 | E/O | "B" Phase CB connection point Temperature rise. | 0 | 0 | No interruption
|  |  | Total : | 8:11 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 479:48 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [9 empty] | 498.6333
Month: July 2023 | [9 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 01 | 2023-07-19 17:20 | 2023-07-19 18:16 | 0:56 | T | O/C RYB Phase, O/C PU Only E.(PT operated at ckt1 sreepur s/s) | 80 | 74.6667 | Power interruption
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 02 | 2023-07-19 17:20 | 2023-07-19 17:58 | 0:38 | T | Sreepur ckt 2 tripped at sreepur s/s not Bhaluka s/s by O/C. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-1 | 2023-07-19 17:21 | 2023-07-19 17:56 | 0:35 | T | PD operate | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2023-07-19 17:20 | 2023-07-19 18:15 | 0:55 | T | Over Current | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-07-03 09:44 | 2023-07-03 09:53 | 0:09 | T | Distance relay Zone-4 operated only on Mirpur end. No tripping or signal received on Aminbazar ss end. | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-07-28 15:17 | 2023-07-28 15:36 | 0:19 | T | Earth fault | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-02 | 2023-07-14 15:54 | 2023-07-14 16:00 | 0:06 | T | Rain and Thundering | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-2 | 2023-07-14 15:55 | 2023-07-14 16:00 | 0:05 | T | 132kV Mymensingh-Jamalpur ckt-2 GCB(213B) Trip due Z1,Dist.-(A-phase), Aided Trip. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-07-02 14:01 | 2023-07-02 14:33 | 0:32 | T | Rain | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-07-07 16:02 | 2023-07-07 16:16 | 0:14 | T | Rainy weather | 114 | 26.6 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-07-31 13:46 | 2023-07-31 14:15 | 0:29 | E/O | work at Kabirpur end | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-07-19 14:21 | 2023-07-19 14:39 | 0:18 | E/O | emergency ROW | 0 | 0 | No interruption
|  |  | Total : | 5:16 |  | Unserved Energy: |  | 101.2667
Dhaka (South) Grid Circle :
Rampura 230/132kV Grid Sub-Station | Basundhara-02 | 2023-07-14 09:55 | 2023-07-14 10:03 | 0:08 | T | Tripped at Basundhara SS end | 0 | 0 | No interruption |  | 120.3333 | 251.2167
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-07-01 14:02 | 2023-07-01 14:31 | 0:29 | T | None | 0 | 0 | No interruption |  | 14.7833
Maniknagar 132/33kV Grid Sub-Station | Narinda Ckt-1 | 2023-07-03 11:15 | 2023-07-03 12:43 | 1:28 | E/O | Main & backup relay intertrip tested by protection Division, DPDC due to show "Protection abnormal"in control Panel of 132kv Narinda-1. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Kazla Ckt -1 | 2023-07-23 06:57 | 2023-07-23 09:05 | 2:08 | E/O | kazla-ckt 1 due to B-phase Tclamp red hot work. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-07-20 08:37 | 2023-07-20 09:11 | 0:34 | E/O | Basundhara S/S end Energy Meter check order by NLDC. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-07-06 14:45 | 2023-07-06 16:03 | 1:18 | E/O | Line fault at Banasree, Dhaka | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Comilla-02 | 2023-07-08 13:06 | 2023-07-08 14:43 | 1:37 | E/O | wave trap R phase red hot maintenance. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-07-13 11:10 | 2023-07-13 13:38 | 2:28 | E/O | Schedul Checking Unit-1 Transformer for EGCB ends. | 0 | 0 | No interruption
|  |  | Total : | 10:10 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2023-07-06 10:50 | 2023-07-06 11:13 | 0:23 | T | Due to E/F . | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2023-07-13 08:15 | 2023-07-13 09:19 | 1:04 | T | Distance trip | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2023-07-06 10:49 | 2023-07-06 11:12 | 0:23 | T | Fault | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | AKSML-02 | 2023-07-09 12:26 | 2023-07-10 14:07 | 25:41 | T | Tripping | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | PHP | 2023-07-09 08:15 | 2023-07-09 16:41 | 8:26 | E/O | PHP Substation work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | AKSML Ckt | 2023-07-10 09:01 | 2023-07-10 14:00 | 4:59 | E/O | AKSML SS End fault. | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-07-22 06:24 | 2023-07-22 08:53 | 2:29 | E/O | Emergency S/D due to Bus S/D of Dohazari. | 0 | 0 | No interruption
|  |  | Total : | 43:25 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-07-31 21:46 | 2023-07-31 22:19 | 0:33 | T | None | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-2 | 2023-07-13 09:40 | 2023-07-13 10:41 | 1:01 | T | Unknown | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-07-18 23:50 | 2023-07-19 00:06 | 0:16 | T | heavy rain and thundering | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-07-18 23:50 | 2023-07-19 00:06 | 0:16 | T | heavy rain and thundering | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-07-24 13:20 | 2023-07-24 14:23 | 1:03 | T | Black Out | 42 | 44.1 | Power interruption
Sylhet 132/33kV Grid Sub-Station | 150MW GT PS | 2023-07-03 15:22 | 2023-07-03 17:52 | 2:30 | T | transformer trotection fail | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-07-04 12:09 | 2023-07-04 16:35 | 4:26 | E/O | Red Hot Maintenance Of 01 No Tower R phase in Feni Line-02 | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2023-07-01 01:10 | 2023-07-01 05:28 | 4:18 | E/O | Ordered By NLDC. | 16 | 68.8 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2023-07-01 01:11 | 2023-07-01 01:15 | 0:04 | E/O | Ordered By NLDC | 16 | 1.0667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2023-07-08 13:04 | 2023-07-08 15:51 | 2:47 | E/O | Meghnaghat Grid SS end maintenance (wap tap redhot remove). | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-1 | 2023-07-27 19:50 | 2023-07-27 21:54 | 2:04 | E/O | 132 KV Line D/S R-Phase Contact Point Red hot maintenance work. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-07-24 14:04 | 2023-07-24 14:15 | 0:11 | E/O | Blackout, With permission of NLDC | 61 | 11.1833 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-07-27 20:29 | 2023-07-27 20:40 | 0:11 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-07-24 14:03 | 2023-07-24 14:11 | 0:08 | E/O | Blackout, With permission of NLDC | 61 | 8.1333 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-07-27 20:29 | 2023-07-27 21:01 | 0:32 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2023-07-24 14:05 | 2023-07-24 14:20 | 0:15 | E/O | Blackout, With permission of NLDC | 23 | 5.75 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-1 | 2023-07-27 20:31 | 2023-07-27 20:53 | 0:22 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-2 | 2023-07-24 14:05 | 2023-07-24 14:20 | 0:15 | E/O | Blackout, With permission of NLDC | 23 | 5.75 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Kulaura-2 | 2023-07-27 20:31 | 2023-07-27 21:03 | 0:32 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-07-24 14:05 | 2023-07-24 14:16 | 0:11 | E/O | Blackout, With permission of NLDC | 30 | 5.5 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-07-27 20:29 | 2023-07-27 20:45 | 0:16 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-1 | 2023-07-24 14:06 | 2023-07-24 14:17 | 0:11 | E/O | Blackout, With permission of NLDC | 50 | 9.1667 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-1 | 2023-07-27 20:32 | 2023-07-27 20:50 | 0:18 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2023-07-24 14:06 | 2023-07-24 14:17 | 0:11 | E/O | Blackout, With permission of NLDC | 50 | 9.1667 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-2 | 2023-07-27 20:32 | 2023-07-27 20:59 | 0:27 | E/O | Blackout. | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-3 | 2023-07-24 14:06 | 2023-07-24 14:17 | 0:11 | E/O | Blackout, With permission of NLDC | 50 | 9.1667 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-3 | 2023-07-27 20:32 | 2023-07-27 21:02 | 0:30 | E/O | Blackout. | 0 | 0 | No interruption
|  |  | Total : | 23:59 |  | Unserved Energy: |  | 177.7833
Khulna Grid Circle :
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Noapara-1 | 2023-07-27 06:43 | 2023-07-27 09:40 | 2:57 | E/O | High temperature at DS-101S ,Phase-B, A-Bus side. | 0 | 0 | No interruption
Gollamari 132/33kV Grid Sub-Station | E03 Gollamari-Khulna(S) Line-1 | 2023-07-05 10:56 | 2023-07-05 12:24 | 1:28 | E/O | Maintenance Work at Rampal Power Plant End. | 0 | 0 | No interruption
|  |  | Total : | 4:25 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2023-07-07 20:31 | 2023-07-08 10:25 | 13:54 | T | None | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Bghabari-2 | 2023-07-07 08:30 | 2023-07-08 00:52 | 16:22 | T | Power station DS flashing | 35 | 572.8333 | No interruption
|  |  | Total : | 30:16 |  | Unserved Energy: |  | 572.8333
Bogura Grid Circle:
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-07-07 20:32 | 2023-07-07 22:58 | 2:26 | T | Control Panel Signal: 1. Distance Relay Z1 2. Distance Relay SOTF. & Relay panel Signal: 1. (21 Distance Relay) SOTF +A phase 2. (79 AR relay) CB1 AR fail | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-1 | 2023-07-10 21:37 | 2023-07-10 22:00 | 0:23 | T | Heavy Thundaring | 8 | 3.0667 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | Thakurgaon Line-2 | 2023-07-10 21:39 | 2023-07-10 21:59 | 0:20 | T | Heavy thundering | 8 | 2.6667 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | Purbasadipur-Thakurgaon Ckt-1 | 2023-07-10 21:35 | 2023-07-10 21:58 | 0:23 | T | N/A | 60 | 23 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | Purbasadipur-Thakurgaon Ckt-2 | 2023-07-10 21:35 | 2023-07-10 21:58 | 0:23 | T | N/A | 58 | 22.2333 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2023-07-28 09:37 | 2023-07-28 10:00 | 0:23 | T | Fault | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | Saidpur-Rangpur CKT-02 | 2023-07-28 09:37 | 2023-07-28 10:09 | 0:32 | T | Carrier received, and Zone -4 | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-07-26 08:28 | 2023-07-26 18:24 | 9:56 | E/O | Control Panel Signal: 1. Distance Relay Z1 2. Distance Relay SOTF. & Relay panel Signal: 1. (21 Distance Relay) SOTF +A phase 2. (79 AR relay) CB1 AR fail | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-07-29 20:30 | 2023-07-29 21:26 | 0:56 | E/O | NLDC Instruction | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-2 | 2023-07-29 20:31 | 2023-07-30 09:52 | 13:21 | E/O | recommendation by ALDC | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 1 | 2023-07-25 15:27 | 2023-07-25 17:40 | 2:13 | E/O | recommendation by ALDC | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2023-07-12 19:12 | 2023-07-13 07:05 | 11:53 | E/O | Red hot maintenance | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2023-07-12 19:13 | 2023-07-13 07:08 | 11:55 | E/O | Instruction from NLDC (X-Former over load) | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Shahjadpur | 2023-07-07 20:57 | 2023-07-08 10:49 | 13:52 | E/O | Instruction from NLDC (X-Former over load) | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-07-08 00:37 | 2023-07-08 10:50 | 10:13 | E/O | by the instruction of NLDC | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2023-07-23 11:15 | 2023-07-23 15:10 | 3:55 | E/O | by the instruction of NLDC | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-01 | 2023-07-23 11:15 | 2023-07-23 15:07 | 3:52 | E/O | To remove kite from 132 Kv Tr. Line. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2023-07-05 20:33 | 2023-07-05 23:23 | 2:50 | E/O | à¦°à¦¾à¦œà¦¶à¦¾à¦¹à§€ à§§à§©à§¨ à¦•à§‡à¦œà¦¿ à¦¸à¦¾à¦°à§à¦•à¦¿à¦Ÿ à§¦à§§, à¦Ÿà¦¾à¦“à¦¯à¦¼à¦¾à¦° à¦¨à¦®à§à¦¬à¦° à§§à§®- -à§§à§¯ à¦à¦¬à¦‚ à§©à§«-à§©à§¬ à¦à¦° à¦®à¦¾à¦à§‡ à¦¸à¦žà§à¦šà¦¾à¦²à¦¨ à¦²à¦¾à¦‡à¦¨à§‡à¦° à¦˜à§à¦¡à¦¼à¦¿ à¦…à¦ªà¦¸à¦¾à¦°à¦£ à¦•à¦¾à¦œà¥¤ | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Barapukuria-2 | 2023-07-20 11:20 | 2023-07-20 13:49 | 2:29 | E/O | Confidence Line-01 was open by order of XEN NLDC Sir to avoid overloading of Mohastan-Palashbari line. | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Confidence-1 | 2023-07-07 09:35 | 2023-07-07 16:17 | 6:42 | E/O | Red hot | 0 | 0 | No interruption
|  |  | Total : | 98:57 |  | Unserved Energy: |  | 50.9667
Others :
Ashuganj 230/132/33kV Sub-Station | B.Baria 132 kV Ckt-1 | 2023-07-24 13:49 | 2023-07-24 13:55 | 0:06 | E/O | 132kv busbar-2 is dead. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | B.Baria 132 kV Ckt-2 | 2023-07-24 13:50 | 2023-07-24 13:56 | 0:06 | E/O | 132kv busbar-2 is dead. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Shahajibazar 132 kV Ckt-3 | 2023-07-24 13:51 | 2023-07-24 13:57 | 0:06 | E/O | 132kv busbar-2 is dead. | 0 | 0 | No interruption
|  |  | Total : | 0:18 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 211:38 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: July 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-07-04 05:51 | 2023-07-04 16:50 | 10:59 | S/O | GT-2 Transformer oil centrifuge | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-07-05 05:37 | 2023-07-05 15:50 | 10:13 | S/O | GT-2 132/33kV X-Former oil Centrifuging. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-07-06 05:40 | 2023-07-06 16:58 | 11:18 | S/O | GT-2 Transformer oil centrifuge work | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) HT | 2023-07-07 05:44 | 2023-07-07 16:55 | 11:11 | S/O | GT-2 132/33 kV X-Former Oil centrifuging. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-07-04 05:51 | 2023-07-04 17:15 | 11:24 | S/O | GT-2 Transformer oil centrifuge | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-07-05 05:37 | 2023-07-05 16:14 | 10:37 | S/O | GT-2 132/33kV X-Former oil Centrifuging. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-07-07 05:44 | 2023-07-07 17:06 | 11:22 | S/O | GT-2 132/33 kV X-Former Oil centrifuging. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-07-05 17:01 | 2023-07-05 18:29 | 1:28 | S/O | GT-3 33 kV side Redhot Maintenance. | 25 | 36.6667 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-07-09 07:42 | 2023-07-09 10:09 | 2:27 | S/O | Works by pbs | 44 | 107.8 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-07-09 07:42 | 2023-07-09 10:09 | 2:27 | S/O | Works by pbs | 44 | 107.8 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) HT | 2023-07-22 06:45 | 2023-07-22 17:10 | 10:25 | S/O | Line DS change | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2023-07-10 06:11 | 2023-07-10 07:48 | 1:37 | S/O | 33kv Incoming DS maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2023-07-22 06:45 | 2023-07-22 17:12 | 10:27 | S/O | Line DS change | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2023-07-03 10:50 | 2023-07-03 13:02 | 2:12 | S/O | High Temperature Maintenance Work. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2023-07-04 14:34 | 2023-07-04 15:01 | 0:27 | S/O | For NIPS system inactive | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2023-07-17 08:52 | 2023-07-17 12:36 | 3:44 | S/O | None | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-07-07 08:17 | 2023-07-07 16:42 | 8:25 | S/O | Red Hot Maintenance Work . | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-I LT | 2023-07-24 07:35 | 2023-07-24 09:31 | 1:56 | S/O | 33 kv bus maintenance, Shutdown is taken by DPBS-1 | 80 | 154.6667 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2023-07-04 11:04 | 2023-07-04 12:01 | 0:57 | S/O | PBS working | 60 | 57 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 LT | 2023-07-24 11:05 | 2023-07-24 13:41 | 2:17 | S/O | T-2 33 KV bus, S/D is taken by DPBS-1 | 140 | 319.6667 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-07-03 21:07 | 2023-07-03 22:30 | 1:23 | S/O | Bus coupler connector maintenance work of 33kv Tr-02 extension bus. | 40 | 55.3333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2023-07-21 12:13 | 2023-07-21 12:20 | 0:07 | S/O | 132/33kV TR-3 Transformer shift 132kV A-Bus(Kaliakoire side) To 132kV B-Bus(Ash-Sreepur side) by instruction NLDC(XEN) and XEN, GMD, Mymensingh | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-07-11 11:29 | 2023-07-11 14:23 | 2:54 | S/O | Roumari 33 Kv Feeder C.T & D/S Loop Change. | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 04 HT | 2023-07-09 13:04 | 2023-07-09 14:02 | 0:58 | S/O | 132 KV CT Numbering | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-07-10 07:14 | 2023-07-10 09:54 | 2:40 | S/O | Oil Leakage | 0 | 0 | No interruption
|  |  | Total : | 133:55 |  | Unserved Energy: |  | 838.9333
Dhaka (South) Grid Circle : | [11 empty] | 39.3333
Maniknagar 132/33kV Grid Sub-Station | Transformer GT-1 HT | 2023-07-08 07:12 | 2023-07-08 07:49 | 0:37 | S/O | Maintenance work by DPDC. | 0 | 0 | No interruption |  |  | 39.3333
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 LT | 2023-07-04 13:30 | 2023-07-04 17:02 | 3:32 | S/O | To do the maintenance of 230/132/33 kV ATR 01. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 LT | 2023-07-02 08:02 | 2023-07-02 09:52 | 1:50 | S/O | Red hot maintenance by pbs feeder2 and 33 kv bussection -1 | 29 | 53.1667 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2023-07-21 07:09 | 2023-07-21 08:43 | 1:34 | S/O | Red hot remedy & Nut-bolt tightening and abnormal maintenance | 15 | 23.5 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2023-07-15 07:55 | 2023-07-15 10:26 | 2:31 | S/O | Red Hot Maintenance | 20 | 50.3333 | Power interruption
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2023-07-21 08:50 | 2023-07-21 10:29 | 1:39 | S/O | Red hot remedy & Nut-bolt tightening and abnormal maint. | 15 | 24.75 | Power interruption
|  |  | Total : | 11:43 |  | Unserved Energy: |  | 151.75
Chattogram Grid Circle :
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2023-07-12 09:56 | 2023-07-12 11:47 | 1:51 | S/O | 132/33 kV, Tr-02 Shutdown due to Over current relay replace by Ctg SPMD | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) LT | 2023-07-12 09:55 | 2023-07-12 11:54 | 1:59 | S/O | 132/33 kV, Tr-02 Shutdown due to Over current relay replace by Ctg SPMD | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2023-07-12 12:13 | 2023-07-12 13:17 | 1:04 | S/O | Emergency Red Hot Maintenance work By BPDB. | 5 | 5.3333 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2023-07-26 10:17 | 2023-07-26 16:12 | 5:55 | S/O | Maintainance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-03 LT | 2023-07-20 09:30 | 2023-07-20 14:10 | 4:40 | S/O | HT side R Ph. Loop Repair | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2023-07-11 08:30 | 2023-07-11 12:37 | 4:07 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2023-07-11 08:29 | 2023-07-11 12:37 | 4:08 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-2(517T) LT | 2023-07-16 18:14 | 2023-07-16 19:04 | 0:50 | S/O | shutdown for red hot maintenance by bpdb . | 10 | 8.3333 | Power interruption
|  |  | Total : | 24:34 |  | Unserved Energy: |  | 13.6667
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 402T LT | 2023-07-31 07:03 | 2023-07-31 09:16 | 2:13 | S/O | High temperature removing | 12 | 26.6 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 422T LT | 2023-07-30 06:17 | 2023-07-30 08:26 | 2:09 | S/O | For 33 KV T-5 Bus section red Hot maintenance | 33 | 70.95 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 200KVA Aux. T-1 LT | 2023-07-31 07:01 | 2023-07-31 09:19 | 2:18 | S/O | Bus section-1 T-1 Incoming DS maintenance works. | 0 | 0 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 HT | 2023-07-22 07:56 | 2023-07-22 08:56 | 1:00 | S/O | LT Side Red hot Remove | 0 | 0 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-1 LT | 2023-07-22 07:56 | 2023-07-22 08:57 | 1:01 | S/O | LT side Red Hot Remove | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 402T LT | 2023-07-27 06:07 | 2023-07-27 08:54 | 2:47 | S/O | red hot maintenance | 10 | 27.8333 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-07-04 16:02 | 2023-07-04 16:43 | 0:41 | S/O | Redhot maintenance. | 14 | 9.5667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-07-25 21:37 | 2023-07-25 22:39 | 1:02 | S/O | Pbs red hot maintenance | 16 | 16.5333 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-07-04 16:04 | 2023-07-04 16:42 | 0:38 | S/O | Redhot maintenance. | 14 | 8.8667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-07-16 14:23 | 2023-07-16 15:34 | 1:11 | S/O | Due to PDB maintenance. | 10 | 11.8333 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2023-07-04 16:02 | 2023-07-04 16:43 | 0:41 | S/O | Redhot maintenance. | 14 | 9.5667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2023-07-16 14:22 | 2023-07-16 15:35 | 1:13 | S/O | Due to PDB maintenance. | 10 | 12.1667 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2023-07-13 08:51 | 2023-07-13 10:48 | 1:57 | S/O | Hot spot maintennace by BPDB | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 HT | 2023-07-27 08:13 | 2023-07-27 14:59 | 6:46 | S/O | 33 KV Habiganj New Feeder Isolator Hot Spot Maiintenece Work By BPDB Habigonj. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-07-27 08:13 | 2023-07-27 16:34 | 8:21 | S/O | 33 KV Habiganj New Feeder Isolator Hot Spot Maiintenece Work By BPDB. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-07-02 08:24 | 2023-07-02 10:30 | 2:06 | S/O | 33kv Madhanpur feeder red hot maintenance by PBS. | 25 | 52.5 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-07-28 09:01 | 2023-07-28 10:08 | 1:07 | S/O | madhobpur-01 33 kv, D/S maintenance by PBS | 45 | 50.25 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-07-31 08:18 | 2023-07-31 09:10 | 0:52 | S/O | Red hot Maintenece work by Habiganj Pbs | 40 | 34.6667 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2023-07-31 07:07 | 2023-07-31 08:45 | 1:38 | S/O | 33kv Bus loop Redhot | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-3 LT | 2023-07-01 09:38 | 2023-07-01 10:51 | 1:13 | S/O | 33kv T3 incoming shutdown for red hot | 7 | 8.5167 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-01 LT | 2023-07-29 08:35 | 2023-07-29 09:24 | 0:49 | S/O | OLTC Silica Gel changing | 0 | 0 | No interruption
|  |  | Total : | 41:43 |  | Unserved Energy: |  | 339.85
Khulna Grid Circle :
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-07-03 08:44 | 2023-07-03 10:02 | 1:18 | S/O | Auxiliary transformer bus ds redhot maintenance | 14 | 18.2 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-12 06:26 | 2023-07-12 08:29 | 2:03 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-07-16 06:30 | 2023-07-16 08:14 | 1:44 | S/O | à¦°à§‡à¦¡ à¦¹à¦Ÿ à¦¸à¦®à¦¸à§à¦¯à¦¾ à¦¸à¦®à¦¾à¦§à¦¾à¦¨ à¥¤ | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2023-07-14 07:10 | 2023-07-14 08:36 | 1:26 | S/O | Red hot maintenance of 33kv khospur feeder. | 20 | 28.6667 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | T1-406T LT | 2023-07-25 08:41 | 2023-07-25 11:38 | 2:57 | S/O | Red Hot maintenance by PBS. | 10 | 29.5 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) HT | 2023-07-12 09:34 | 2023-07-12 11:52 | 2:18 | S/O | NIFPS Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-07-12 09:33 | 2023-07-12 11:53 | 2:20 | S/O | NIFPS Maintenance | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2023-07-21 07:11 | 2023-07-21 11:30 | 4:19 | S/O | Rectification work by khulna pbs. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 HT | 2023-07-21 07:20 | 2023-07-21 11:27 | 4:07 | S/O | Rectification work by khulna pbs. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 HT | 2023-07-31 07:20 | 2023-07-31 08:16 | 0:56 | S/O | red hot | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2023-07-21 07:11 | 2023-07-21 11:28 | 4:17 | S/O | Rectification work by khulna pbs. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | T-6 LT | 2023-07-31 07:19 | 2023-07-31 08:17 | 0:58 | S/O | Red hot | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2023-07-05 16:19 | 2023-07-05 19:08 | 2:49 | S/O | 33 kv bus section-1 s/D by wzpdcl | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-2 415 T LT | 2023-07-28 06:47 | 2023-07-28 09:59 | 3:12 | S/O | High temperature maintenance | 5 | 16 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-07-28 06:47 | 2023-07-28 09:59 | 3:12 | S/O | High temperature maintenance | 5 | 16 | Power interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-07-25 16:06 | 2023-07-25 17:59 | 1:53 | S/O | 33 kV feeder No-02 Bus DS Mechanical Switching Operation Problem Maintenance by JPBS-02 | 20 | 37.6667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 HT | 2023-07-28 07:04 | 2023-07-28 09:36 | 2:32 | S/O | 33 KV BUS-1 Shut-Down . | 11 | 27.8667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2023-07-04 07:25 | 2023-07-04 10:08 | 2:43 | S/O | 33Kv Bus Shutdown for REB-1 (33kv Feeder) Redhot Maintenance | 14 | 38.0333 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-2 LT | 2023-07-28 07:02 | 2023-07-28 09:37 | 2:35 | S/O | 33 KV BUS-1 Shut-Down . | 11 | 28.4167 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-07-16 07:28 | 2023-07-16 09:51 | 2:23 | S/O | REB-5 Feeder D/S Point Maintenance. | 22 | 52.4333 | Power interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 LT | 2023-07-30 13:05 | 2023-07-30 15:09 | 2:04 | S/O | Remotely switching operation checked from NLDC. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-2 LT | 2023-07-30 15:30 | 2023-07-30 17:33 | 2:03 | S/O | Remotely switching operation checked from NLDC. | 0 | 0 | No interruption
|  |  | Total : | 54:09 |  | Unserved Energy : |  | 292.7833
HVDC Grid Circle
Pabna 132/33kV Grid Sub-Station | T-1 HT | 2023-07-21 08:27 | 2023-07-21 11:55 | 3:28 | S/O | 33KV university Feeder shifting | 30 | 104 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-07-06 07:35 | 2023-07-06 17:35 | 10:00 | S/O | 33 kV Bus Conductor Upgrade . | 5 | 50 | Power interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-3 LT | 2023-07-24 07:15 | 2023-07-24 08:53 | 1:38 | S/O | PBS 33kV feeder red hot maintenance | 13 | 21.2333 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-07-26 07:07 | 2023-07-26 08:35 | 1:28 | S/O | 33 kv isolator installation | 35 | 51.3333 | Power interruption
|  |  | Total : | 16:34 |  | Unserved Energy : |  | 226.5667
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-07-03 07:38 | 2023-07-03 09:04 | 1:26 | S/O | Red-hot maintenance. | 30 | 43 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-07-28 08:08 | 2023-07-28 10:08 | 2:00 | S/O | 33kv Red hot to bus connector | 22 | 44 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T HT | 2023-07-25 10:47 | 2023-07-25 14:43 | 3:56 | S/O | RED HOT MAINTENANCE WORK | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T LT | 2023-07-25 10:46 | 2023-07-25 14:45 | 3:59 | S/O | RED HOT MAINTENANCE WORK | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-07-08 07:37 | 2023-07-08 19:03 | 11:26 | S/O | 33kv bus Upgradation works | 50 | 571.6667 | Power interruption | ok
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-07-10 07:26 | 2023-07-10 12:57 | 5:31 | S/O | 33kv bus upgradation work | 60 | 331 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-07-07 07:08 | 2023-07-07 08:30 | 1:22 | S/O | 33kv Bus conductor replacement by PBS&NESCO | 24 | 32.8 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | 412T LT | 2023-07-28 06:20 | 2023-07-28 08:31 | 2:11 | S/O | T-2 132 kV Bus Primary Bay Bus DS Clamp & T-2 Incoming Bus DS Clamp Red Hot. | 20 | 43.6667 | Power interruption
Amnura 132/33kV Grid Sub-Station | T-1 (406T) HT | 2023-07-25 07:16 | 2023-07-25 18:19 | 11:03 | S/O | Maintenance of B-Phase CT of T-1 | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-07-11 06:46 | 2023-07-11 09:05 | 2:19 | S/O | T1 R phase ct to ds loop change. | 8 | 18.5333 | Power interruption |  | 2:19
Natore 132/33kV Grid Sub-Station | TR-2 (415 T) HT | 2023-07-28 07:05 | 2023-07-28 09:59 | 2:54 | S/O | Bus maintanance | 70 | 205.3333 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-1 425T LT | 2023-07-29 06:10 | 2023-07-29 13:30 | 7:20 | S/O | 33 kv bus maintenance | 0 | 0 | No interruption
Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-2 415T LT | 2023-07-02 10:45 | 2023-07-02 11:15 | 0:30 | S/O | Red Hot Maintenance on 33kV Isolator. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-07-14 08:23 | 2023-07-14 11:32 | 3:09 | S/O | Aux-01 DS, Bus section DS Maintenance work. | 34 | 47.25 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-07-14 08:25 | 2023-07-14 20:48 | 12:23 | S/O | Aux-01 DS, Bus section DS Maintenance work. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) HT | 2023-07-08 09:23 | 2023-07-08 11:24 | 2:01 | S/O | To remove redhot at 33kv old feeder of Nilphamari nesco. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-07-08 09:22 | 2023-07-08 11:24 | 2:02 | S/O | To remove redhot at DS of 33kv oid feeder of Nilphamari nesco. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-07-07 07:04 | 2023-07-07 10:57 | 3:53 | S/O | 33 KV Bus coupler Red hot | 10 | 38.8333 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2023-07-28 06:45 | 2023-07-28 15:20 | 8:35 | S/O | 33 kV bus section isolator replacement works under saidpur NESCO. | 0 | 0 | No interruption
|  |  | Total : | 88:00 |  | Unserved Energy : |  | 1376.0833
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 370:38 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-07-02 05:40 | 2023-07-02 17:24 | 11:44 | S/O | GT-2 Transformer oil centrifuzing | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-07-03 05:24 | 2023-07-03 17:16 | 11:52 | S/O | gt2 Transformer oil centrifuging work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-1 | 2023-07-13 09:37 | 2023-07-13 10:45 | 1:08 | S/O | Energymeter change at raj ss | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-2 | 2023-07-13 11:24 | 2023-07-13 12:51 | 1:27 | S/O | Energymeter change at Rajendrapur ss | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2023-07-10 06:06 | 2023-07-10 08:04 | 1:58 | S/O | Shutdown taken from Kabirpur End via NLDC. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Meghnaghat-02 | 2023-07-09 15:01 | 2023-07-09 18:03 | 3:02 | S/O | Red hot maintenance | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | Tongi-2 | 2023-07-10 06:02 | 2023-07-10 08:04 | 2:02 | S/O | B-phase conductor armoring of Tongi ckt-2. | 40 | 81.3333 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2023-07-29 06:31 | 2023-07-29 09:51 | 3:20 | S/O | Red Hot maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2023-07-25 08:16 | 2023-07-26 00:21 | 16:05 | S/O | To Change Relay | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2023-07-26 08:30 | 2023-07-26 15:52 | 7:22 | S/O | Distance Relay Change work | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2023-07-25 08:15 | 2023-07-26 00:20 | 16:05 | S/O | 132kV Mym-Kish ckt-1 shut down due to Distance Relay Change work purposes in Kish. Grid S/S | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2023-07-26 08:27 | 2023-07-26 15:51 | 7:24 | S/O | Relay test kishorganj grid | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-07-28 15:36 | 2023-07-28 16:44 | 1:08 | S/O | SD due to Relay testing at RPCL end | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-07-28 09:12 | 2023-07-28 15:30 | 6:18 | S/O | Relay test | 0 | 0 | No interruption
|  |  | Total : | 90:55 |  | Unserved Energy: |  | 81.3333
Dhaka (South) Grid Circle :
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2023-07-14 09:59 | 2023-07-14 12:24 | 2:25 | S/O | DS temperature is high | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-1 | 2023-07-24 06:53 | 2023-07-27 13:30 | 78:37 | S/O | Shutdown complete according to NLDC instruction. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Shyampur old-2(E10) | 2023-07-04 10:35 | 2023-07-04 12:58 | 2:23 | S/O | Maintenance at 132kV Shyampur old ss end | 0 | 0 | No interruption
Bhulta 132/33kV Grid Sub-Station | Narsingdi | 2023-07-21 06:40 | 2023-07-21 09:57 | 3:17 | S/O | Red hot remedy & Nut-bolt tightening and abnormal maint. | 0 | 0 | No interruption
|  |  | Total : | 86:42 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Khulshi 132/33kV Grid Sub-Station | Khulshi-AKSPL Line | 2023-07-10 08:25 | 2023-07-12 13:25 | 53:00 | S/O | 132 KV CB Change AKSPL End | 0 | 0 | No interruption
AKS 132/33kV Grid Sub-Station | Khulshi | 2023-07-10 08:30 | 2023-07-12 13:15 | 52:45 | S/O | CT Replace of Bus coupler and Incoming CT of Radial Feeder aks 132/33kv ss | 0 | 0 | No interruption
AKS 132/33kV Grid Sub-Station | Bar Aulia | 2023-07-10 08:33 | 2023-07-12 13:21 | 52:48 | S/O | AKSPL want to replace Radial feeder CT & Bus Coupler CT. | 0 | 0 | No interruption
|  |  | Total : | 158:33 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2023-07-09 08:12 | 2023-07-09 16:36 | 8:24 | S/O | Half yearly maintenance | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowmuhani Ckt-2 | 2023-07-04 12:09 | 2023-07-04 16:35 | 4:26 | S/O | Due to Red-hot maintenance(R-Phase, T-Connector) of Tower No. -01 | 48 | 212.8 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-07-11 08:07 | 2023-07-11 16:45 | 8:38 | S/O | Sag adjust and conductor armering | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-01 | 2023-07-24 13:25 | 2023-07-24 14:10 | 0:45 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-07-24 13:25 | 2023-07-24 14:10 | 0:45 | S/O | Instructed by NLDC | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 02 | 2023-07-15 07:25 | 2023-07-15 09:20 | 1:55 | S/O | 132KV Sylhet-Chhatak Circuit-2 Shutdown for BUS DS(202S) R-ph Loop Change. | 5 | 9.5833 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Power Station-1 | 2023-07-08 10:54 | 2023-07-08 17:43 | 6:49 | S/O | Breaker oil leakage maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-2 | 2023-07-15 07:27 | 2023-07-15 09:22 | 1:55 | S/O | maintenance work by chattak grid | 0 | 0 | No interruption
|  |  | Total : | 33:37 |  | Unserved Energy: |  | 222.3833
Khulna Grid Circle :
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-2 | 2023-07-23 06:39 | 2023-07-23 20:07 | 13:28 | S/O | Installation of TCSR | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-07-28 08:36 | 2023-07-28 18:40 | 10:04 | S/O | Ct change B phase. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-1 | 2023-07-24 09:02 | 2023-07-24 20:58 | 11:56 | S/O | Faridpur ss side relay test | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-1 | 2023-07-28 08:27 | 2023-07-28 18:39 | 10:12 | S/O | Faridpur end teleprotection work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-03 | 2023-07-20 07:10 | 2023-07-20 21:20 | 14:10 | S/O | TCS Relay Installation and Maintenance Works | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur - 2 | 2023-07-23 06:38 | 2023-07-23 20:07 | 13:29 | S/O | SPMD work on Faridpur grid. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-1 | 2023-07-28 06:55 | 2023-07-28 10:02 | 3:07 | S/O | Maintenence Works at Khulna central Grid Substation 132 KV Bus. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-2 | 2023-07-28 06:57 | 2023-07-28 13:02 | 6:05 | S/O | Maintenence Works at Khulna central Grid Substation 132 KV Bus. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Goalpara-1 | 2023-07-28 06:56 | 2023-07-28 10:01 | 3:05 | S/O | High temperature maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | 132kV Central-Goalpara-2 | 2023-07-28 07:08 | 2023-07-28 13:02 | 5:54 | S/O | High temperature maintenance | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 1 | 2023-07-27 06:42 | 2023-07-27 09:42 | 3:00 | S/O | High temperature at DS-101S ,Phase-B, A-Bus side. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2023-07-03 10:03 | 2023-07-03 17:08 | 7:05 | S/O | Maintenance Work at Rampal Power Plant End. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2023-07-15 10:31 | 2023-07-15 11:26 | 0:55 | S/O | Distance Relay Update Rampal End. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-1 | 2023-07-31 11:18 | 2023-07-31 16:53 | 5:35 | S/O | Due to protection test on Rample end | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2023-07-03 10:05 | 2023-07-03 17:12 | 7:07 | S/O | Maintenance Work at Rampal Power Plant End. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Rampal Ckt-2 | 2023-07-15 11:28 | 2023-07-15 13:53 | 2:25 | S/O | Distance Relay Update Rampal End. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Satkhira Ckt-2 | 2023-07-05 07:58 | 2023-07-05 10:52 | 2:54 | S/O | Red Hot Removed Work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | Gallamari Ckt-1 | 2023-07-05 10:57 | 2023-07-05 12:23 | 1:26 | S/O | Red Hot Removed Work | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Khulna Line-1 | 2023-07-31 11:18 | 2023-07-31 16:55 | 5:37 | S/O | Remotely switching operation Check from NlDC. | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-2 (L-2) | 2023-07-05 07:58 | 2023-07-05 10:53 | 2:55 | S/O | Maintenance work | 0 | 0 | No interruption
|  |  | Total : | 130:29 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2023-07-19 07:01 | 2023-07-19 18:04 | 11:03 | S/O | Ruppur project development work à¦à¦° à¦œà¦¨à§à¦¯ Baghabari-Ishurdi ckt-1& ckt-2 schedule shutdown à¦à¦° à¦‰à¦¦à§à¦¦à§‡à¦¶à§à¦¯à§‡ à¦œà¦¨à¦¾à¦¬ à¦¶à§à¦­à¦¾à¦¶à¦¿à¦¸ SDE,NLDC à¦¸à§à¦¯à¦¾à¦°à§‡à¦° à¦¨à¦¿à¦°à§à¦¦à§‡à¦¶à§‡ â€à¦‰à¦•à§à¦¤ à¦²à¦¾à¦‡à¦¨à¦¦à§à¦¬à§Ÿ shutdown à¦¨à§‡à§Ÿà¦¾ à¦¹à§Ÿà¥¤ | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2023-07-20 07:04 | 2023-07-20 17:50 | 10:46 | S/O | Project development work at Ishurdi SS end. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2023-07-21 06:40 | 2023-07-21 18:45 | 12:05 | S/O | Project development work at Ishurdi SS end. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi -1 | 2023-07-22 07:06 | 2023-07-22 18:26 | 11:20 | S/O | Project development work at Ishurdi SS end. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi-2 | 2023-07-19 07:04 | 2023-07-19 19:11 | 12:07 | S/O | Rooppur project development work | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi-2 | 2023-07-20 07:06 | 2023-07-20 17:51 | 10:45 | S/O | Project development work at Ishurdi SS end. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi-2 | 2023-07-21 06:41 | 2023-07-21 18:45 | 12:04 | S/O | Project development work at Ishurdi SS end. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi-2 | 2023-07-22 07:07 | 2023-07-22 18:27 | 11:20 | S/O | Project development work at Ishurdi SS end. | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Baghabari 1 | 2023-07-19 07:14 | 2023-07-19 18:03 | 10:49 | S/O | For conductor crossing | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Baghabari 1 | 2023-07-21 06:42 | 2023-07-21 18:41 | 11:59 | S/O | 230 kv Ruppur Dhamrai line stringing | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Baghabari 2 | 2023-07-19 07:14 | 2023-07-19 19:07 | 11:53 | S/O | For conductor crossing | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230 kV Baghabari 2 | 2023-07-21 06:42 | 2023-07-21 18:43 | 12:01 | S/O | 230 kv Ruppur Dhamrai line stringing | 0 | 0 | No interruption
|  |  | Total : | 138:12 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 132/33kV Grid Sub-Station | Natore-1 | 2023-07-27 09:09 | 2023-07-27 17:41 | 8:32 | S/O | Rooppur-Bogura 400KV line work. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Natore-2 | 2023-07-27 09:09 | 2023-07-27 17:42 | 8:33 | S/O | Rooppur-Bogura 400KV line work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-07-09 10:18 | 2023-07-09 12:38 | 2:20 | S/O |  | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-07-09 12:40 | 2023-07-09 16:48 | 4:08 | S/O |  | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt2 | 2023-07-20 11:21 | 2023-07-20 13:40 | 2:19 | S/O | Red hot Maintenance | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - Chapai Nawabganj | 2023-07-07 06:14 | 2023-07-07 08:35 | 2:21 | S/O | Shut down taken from Chapainawabganj grid substation | 0 | 0 | No interruption
Amnura 132/33kV Grid Sub-Station | Amnura - Chapai Nawabganj | 2023-07-07 17:08 | 2023-07-07 18:05 | 0:57 | S/O | Shutdown taken from Chapainawabganj Grid. | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2023-07-07 06:09 | 2023-07-07 08:40 | 2:31 | S/O | Chapai- Rohanpur line 2 connect to main bus | 58 | 145.9667 | Power interruption | ok
Chapai 132/33kV Grid Sub-Station | Chapai-Amnura | 2023-07-07 17:03 | 2023-07-07 18:10 | 1:07 | S/O | Chapai - Rohanpur 132 KV line connect with main Bus | 60 | 67 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-2 | 2023-07-06 07:12 | 2023-07-06 08:56 | 1:44 | S/O | Red Hotspot maintenance at CT connector at 230/132 Kv S/S. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2023-07-24 08:36 | 2023-07-24 14:26 | 5:50 | S/O | Y phase CVT change. | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132 kV Rajshahi ckt-02 | 2023-07-06 07:11 | 2023-07-06 08:57 | 1:46 | S/O | CT connector hotspot maintenance. | 0 | 0 | No interruption
|  |  | Total : | 42:08 |  | Unserved Energy: |  | 212.9667
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 680:36 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:July 2023
| Area | Previous Month (June' 2023) |  |  |  | Current Month (July '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 43 | 29 | 50 | 122 | 30 | 10 | 39 | 79
2 | Dhaka (South) Grid Circle. | 13 | 15 | 37 | 65 | 5 | 9 | 10 | 24
3 | Chattogram Grid Circle. | 19 | 14 | 34 | 67 | 6 | 10 | 11 | 27
4 | Cumilla Grid Circle. | 44 | 30 | 35 | 109 | 19 | 46 | 29 | 94
5 | Khulna Grid Circle. | 28 | 35 | 73 | 136 | 10 | 14 | 42 | 66
6 | HVDC Grid Circle | 11 | 31 | 8 | 50 | 7 | 15 | 16 | 38
7 | Bogura Grid Circle. | 36 | 42 | 44 | 122 | 14 | 30 | 31 | 75
8 | Others | 0 | 2 | 1 | 3 | 4 | 5 |  | 9
9 | Total | 196 | 221 | 223 | 674 | 95 | 139 | 178 | 412
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:July 2023
| Area | Previous Month (June' 2023) |  |  |  | Current Month (July '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 458.57 | 345.43 | 0 | 804 | 280.97 | 360.7 | 920.26 | 1561.93
2 | Dhaka (South) Grid Circle. | 179.77 | 203.77 | 310.25 | 693.79 | 33 | 280.1 | 151.75 | 464.85
3 | Chattogram Grid Circle. | 54.74 | 41.28 | 75.65 | 171.67 | 0 | 157.08 | 13.67 | 170.75
4 | Cumilla Grid Circle. | 201.94 | 224.4 | 274.15 | 700.49 | 246.9 | 606.98 | 562.23 | 1416.11
5 | Khulna Grid Circle. | 662.49 | 161.05 | 54.88 | 878.42 | 73.6 | 251.5 | 292.78 | 617.88
6 | HVDC Grid Circle | 295.25 | 516.79 | 55 | 867.04 | 582.83 | 175.92 | 226.57 | 985.32
7 | Bogura Grid Circle. | 550.45 | 174.25 | 433.02 | 1157.72 | 98.3 | 390.5 | 1589.05 | 2077.85
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 2460.09 | 2375.79 | 2460.3967 | 5273.13 | 1315.6 | 2222.78 | 3756.31 | 7294.69
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:July 2023
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 22 | 7 | 29 | 16 | 2 | 11 | 1379.35
2 | Dhaka (South) | 5031.6 | 5 | 4 | 9 | 1 |  | 8 | 464.83
3 | Chattogram | 2042 | 4 | 2 | 6 | - | 3 | 3 | 170.75
4 | Khulna | 2434 | 15 | 11 | 26 | 7 |  | 19 | 617.85
5 | HVDC | 5954.3 | 6 | 3 | 9 | 1 |  | 8 | 412.45
6 | Bogura | 3145.6 | 11 | 10 | 21 | 3 | 2 | 16 | 1813.8
7 | Cumilla | 2981 | 19 | 14 | 34 | 7 | 7 | 19 | 1015.87
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 5874.9
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.93%
3 | Chattogram | 99.97%
4 | Khulna | 99.95%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.87% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:July 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 | 1 | 3 | 1 | 1 | 1 | 182.6
2 | Dhaka (South) | 990.29 | - | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | 1 | - | 1 | - | - | 1 | 572.83
6 | Bogura | 1803.3 | - | 4 | 2 | 6 | 4 | - | 2 | 263.94
7 | Cumilla | 1648.16 | - | 11 | 2 | 13 | 1 | 8 | 4 | 400.2
8 | Others | - | - | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 1419.57
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 100%
3 | Chattogram | 100%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.99%
6 | Bogura | 99.99%
7 | Cumilla | 99.99%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:July 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-07-01 | 15 | - | 6 | 07hr18 min |  |  | - | - | 1 | 0:40 | - | - | Sylhet zone blackout at 13:20 initiated from Fenchuganj 230/132kV ATR-1 (Only ATR of the S/S) Trip. Around 630MW loadshed due to trip and forced shutdown.
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:July2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Manikganj 132/33kV Grid Sub-Station | 4 | 1:06 | 33.7
Bhaluka 132/33kV Grid Sub-Station | 6 | 0:48 | 65.5
Kabirpur 132/33kV Grid Sub-Station | 2 | 0:50 | 50
Kishoreganj 132/33kV Grid Sub-Station | 2 | 0:30 | 22.5
Sherpur 132/33kV Grid Sub-Station | 2 | 0:16 | 8
Kodda 132/33kV Grid Sub-Station | 1 | 1:55 | 28.75
Sreepur 230/132/33kV Grid Sub-Station | 2 | 2:12 | 74.8
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:54 | 76
Kishoreganj 132/33kV Grid Sub-Station | 2 | 2:10 | 151.6667
Mymensingh 132/33kV Grid Sub-Station | 1 | 0:59 | 29.5
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:56 | 74.6667
Tangail 132/33kV Grid Sub-Station | 1 | 0:14 | 26.6
Manikganj 132/33kV Grid Sub-Station | 1 | 1:28 | 36.6667
Kodda 132/33kV Grid Sub-Station | 2 | 4:54 | 215.6
Kabirpur 132/33kV Grid Sub-Station | 3 | 5:10 | 531.3
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:23 | 55.3333
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:02 | 81.3333
Munshiganj 132/33kV Grid Sub-Station | 2 | 0:43 | 33
Sonargaon 132/33kV Grid Sub-Station | 1 | 2:46 | 55.3
Munshiganj 132/33kV Grid Sub-Station | 2 | 5:10 | 224.8
Srinagar 132/33kV Grid Sub-Station | 1 | 1:50 | 53.1667
Bhulta 132/33kV Grid Sub-Station | 3 | 5:44 | 98.6
Hathazari 230/132/33kV Grid Sub-Station | 1 | 2:09 | 70.95
Coxsbazar 132/33kV Grid Sub-Station | 1 | 1:00 | 50
Dohazari 132/33kV Grid Sub-Station | 2 | 1:52 | 36.1
Halishahar 132/33kV Grid Sub-Station | 1 | 1:04 | 5.3333
Madunaghat 132/33kV Grid Sub-Station | 1 | 0:50 | 8.3333
Chowmuhani 132/33kV Grid Sub-Station | 2 | 0:25 | 15
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 1:26 | 14.3333
Ramganj 132/33kV Grid Sub-Station | 1 | 0:50 | 101.6667
Kulaura 132/33kV Grid Sub-Station | 2 | 0:45 | 13.5
Fenchuganj 230/132/33kV Grid Sub-Station | 2 | 2:05 | 58.3
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 1:03 | 15.75
Daudkandi 132/33kV Grid Sub-Station | 1 | 2:46 | 83
Feni 132/33kV Grid Sub-Station | 1 | 1:53 | 28.25
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 2:29 | 99.3333
Beanibazar 132/33kV Grid Sub-Station | 5 | 7:24 | 231.5
Sunamganj 132/33kV Grid Sub-Station | 1 | 1:03 | 44.1
Chowmuhani 132/33kV Grid Sub-Station | 2 | 4:22 | 69.9
Fenchuganj 230/132/33kV Grid Sub-Station | 10 | 2:17 | 79.3
Chandpur 132/33kV Grid Sub-Station | 2 | 4:22 | 97.6
Brahmanbaria 132/33kV Grid Sub-Station | 1 | 2:47 | 27.8
Kulaura 132/33kV Grid Sub-Station | 6 | 5:26 | 68.5
Shahjibazar 132/33kV Grid Sub-Station | 3 | 4:05 | 137.4
Chhatak 132/33kV Grid Sub-Station | 1 | 1:13 | 8.5167
Feni 132/33kV Grid Sub-Station | 1 | 4:26 | 212.8
Chhatak 132/33kV Grid Sub-Station | 1 | 1:55 | 9.5833
Barishal 132/33kV Grid Sub-Station | 2 | 0:30 | 21.3
Gopalganj 132/33kV Grid Sub-Station | 2 | 0:57 | 32.3
Rajbari 132/33kV Grid Sub-Station | 3 | 0:23 | 11.1
Mongla 132/33kV Grid Sub-Station | 1 | 0:49 | 8.9833
Benapole 132/33kV Grid Sub-Station | 1 | 1:43 | 34.3333
Goalpara 132/33kV Grid Sub-Station | 1 | 1:26 | 5.7333
Khulna (C) 132/33kV Grid Sub-Station | 1 | 2:23 | 35.75
Noapara 132/33kV Grid Sub-Station | 1 | 3:11 | 63.6667
Mongla 132/33kV Grid Sub-Station | 1 | 1:50 | 7.3333
Satkhira 132/33kV Grid Sub-Station | 2 | 2:37 | 104.7
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:18 | 18.2
Madaripur 132/33kV Grid Sub-Station | 1 | 1:26 | 28.6667
Shariatpur 132/33kV Grid Sub-Station | 1 | 2:57 | 29.5
Khulna (C) 132/33kV Grid Sub-Station | 2 | 6:24 | 32
Narail 132/33kV Grid Sub-Station | 1 | 1:53 | 37.6667
Noapara 132/33kV Grid Sub-Station | 4 | 10:13 | 146.8
Jashore 132/33kV Grid Sub-Station | 1 | 0:23 | 9.9667
Pabna 132/33kV Grid Sub-Station | 1 | 1:15 | 47.5
Jashore 132/33kV Grid Sub-Station | 1 | 1:12 | 18
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:01 | 25.4167
Kushtia 132/33kV Grid Sub-Station | 2 | 2:37 | 85
Shahjadpur 132/33kV Grid Sub-Station | 1 | 16:22 | 572.8333
Pabna 132/33kV Grid Sub-Station | 1 | 3:28 | 104
Shahjadpur 132/33kV Grid Sub-Station | 1 | 10:00 | 50
Bheramara(GK) 132/33kV Grid Sub-Station | 1 | 1:38 | 21.2333
Kushtia 132/33kV Grid Sub-Station | 1 | 1:28 | 51.3333
Bogura 132/33kV Grid Sub-Station | 2 | 1:02 | 20.2
Purbasadipur 132/33kV Grid Sub-Station | 2 | 1:02 | 25.8
Saidpur 132/33kV Grid Sub-Station | 1 | 0:02 | 1.2333
Bog-Sherpur 132/33kV Grid Sub-Station | 1 | 1:49 | 18.1667
Sirajganj 132/33kV Grid Sub-Station | 1 | 2:04 | 51.6667
Niamatpur 132/33kV Grid Sub-Station | 2 | 1:39 | 28.6
Rangpur 132/33kV Grid Sub-Station | 2 | 4:52 | 292
Purbasadipur 132/33kV Grid Sub-Station | 2 | 0:43 | 5.7
Thakurgaon 132/33kV Grid Sub-Station | 2 | 0:46 | 45.2
Bog-Sherpur 132/33kV Grid Sub-Station | 2 | 3:26 | 87
Purbasadipur 132/33kV Grid Sub-Station | 3 | 18:19 | 935.5
Thakurgaon 132/33kV Grid Sub-Station | 1 | 2:11 | 43.6667
Natore 132/33kV Grid Sub-Station | 2 | 5:13 | 223.9
Mithapukur 132/33kV Grid Sub-Station | 1 | 3:09 | 47.25
Saidpur 132/33kV Grid Sub-Station | 1 | 3:53 | 38.8333
Chapai 132/33kV Grid Sub-Station | 2 | 3:38 | 212.97
Total Unserved energy : | 156 | 238:09 | 7294.6
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:July 2023
Sl. No | Sub-station | Load (MW) | Time
1 | AKS | 21 | 2023-07-29 15:00
2 | AKSML | 113 | 2023-07-20 16:00
3 | Aftabnagar | 42 | 2023-07-25 00:00
4 | Agargaon | 112 | 2023-07-20 03:00
5 | Agrabad | 86 | 2023-07-25 12:00
6 | Amnura | 86 | 2023-07-22 20:00
7 | Ashuganj | 87 | 2023-07-17 01:00
8 | BIPTC | N/A | N/A
9 | BSRM | 174 | 2023-07-18 18:00
10 | Bagerhat | 98 | 2023-07-04 00:00
11 | Bakulia | 113 | 2023-07-23 19:30
12 | Banani | 56 | 2023-07-25 13:00
13 | Bangabhaban | 23 | 2023-07-25 10:00
14 | Barapukuria | 70 | 2023-07-31 19:30
15 | Barguna | 26 | 2023-07-03 23:00
16 | Barishal | 118 | 2023-07-03 21:00
17 | Barishal-230 | 116 | 2023-07-04 23:00
18 | Baroaulia | 77 | 2023-07-12 00:00
19 | Baroirhat | 79 | 2023-07-24 19:30
20 | Bashundhara | 184 | 2023-07-24 15:00
21 | BashundharaCement | 7 | 2023-07-04 15:00
22 | Beanibazar | 90 | 2023-07-18 19:00
23 | Benapole | 78 | 2023-07-31 21:00
24 | Bhaluka | 164 | 2023-07-10 19:30
25 | Bhandaria | 58 | 2023-07-04 23:00
26 | Bhangura | 46 | 2023-07-04 20:00
27 | Bheramara(GK) | 69 | 2023-07-31 22:00
28 | Bhulta | 269 | 2023-07-17 22:00
29 | Bog-Sherpur | 82 | 2023-07-31 23:00
30 | Bogura | 201 | 2023-07-20 22:00
31 | Borhanuddin | 83 | 2023-07-03 00:00
32 | Brahmanbaria | 192 | 2023-07-20 21:00
33 | Cantonment | 168 | 2023-07-31 13:00
34 | Chandpur | 82 | 2023-07-20 22:00
35 | Chandraghona | 36 | 2023-07-02 19:30
36 | Chapai | 94 | 2023-07-25 13:00
37 | Charsaidpur | 49.5 | 2023-07-19 15:00
38 | Chauddagram | 71 | 2023-07-04 22:00
39 | Chhatak | 38 | 2023-07-31 21:00
40 | Chowmuhani | 244 | 2023-07-26 22:00
41 | Chuadanga | 127 | 2023-07-18 20:00
42 | Coxsbazar | 140 | 2023-07-24 19:30
43 | Cumilla(N) | 211 | 2023-07-26 22:00
44 | Cumilla(S) | 182 | 2023-07-13 15:00
45 | Daudkandi | 163 | 2023-07-31 20:00
46 | Dhaka | 36 | 2023-07-31 13:00
47 | Dhamrai | 132 | 2023-07-27 10:00
48 | Dhanmondi | 182 | 2023-07-31 13:00
49 | Dohazari | 144 | 2023-07-22 23:00
50 | Faridpur | 176 | 2023-07-31 22:00
51 | Fatullah | 72 | 2023-07-20 10:00
52 | Fenchuganj | 55 | 2023-07-18 19:00
53 | Feni | 128 | 2023-07-20 21:00
54 | GPH | 93 | 2023-07-20 05:00
55 | Ghorashal | 76 | 2023-07-29 21:00
56 | Goalpara | 38 | 2023-07-04 23:00
57 | Gollamari | 65 | 2023-07-09 12:00
58 | Gopalganj | 116 | 2023-07-30 19:30
59 | Gulshan | 156 | 2023-07-31 13:00
60 | Halishahar | 92.5 | 2023-07-18 10:00
61 | HaripurSBU | 174 | 2023-07-17 16:00
62 | Hasnabad | 102 | 2023-07-23 23:00
63 | Hathazari | 89 | 2023-07-24 19:30
64 | Ishurdi | 85 | 2023-07-24 21:00
65 | Jaldhaka | 90 | 2023-07-26 19:30
66 | Jamalpur | 172 | 2023-07-26 20:00
67 | Jashore | 153 | 2023-07-30 21:00
68 | Jhenaidah | 151 | 2023-07-18 20:00
69 | Joydebpur | 191 | 2023-07-25 19:00
70 | Joypurhat | 74 | 2023-07-25 19:30
71 | Juldah | 29 | 2023-07-12 12:00
72 | KSRM | 45 | 2023-07-23 18:30
73 | Kabirpur | 312 | 2023-07-13 19:00
74 | Kachua | 97 | 2023-07-04 22:00
75 | Kallyanpur | 123 | 2023-07-30 23:00
76 | Kalurghat | 40 | 2023-07-19 15:00
77 | Kamrangirchar | 58.8 | 2023-07-25 13:00
78 | Kaptai | N/A | N/A
79 | Kazla | 108 | 2023-07-31 17:00
80 | Keranigonj | 88 | 2023-07-26 11:00
81 | Khagrachori | 40 | 2023-07-30 19:00
82 | Khulna | 106 | 2023-07-19 20:00
83 | Khulshi | 202 | 2023-07-24 18:00
84 | Kishoreganj | 170 | 2023-07-28 21:00
85 | Kodda | 311 | 2023-07-26 19:00
86 | Kulaura | 62 | 2023-07-30 19:00
87 | Kurigram | 70 | 2023-07-31 20:00
88 | Kushtia | 158 | 2023-07-18 20:00
89 | Lalbag | 100 | 2023-07-25 13:00
90 | Lalmonirhat | 56 | 2023-07-29 21:00
91 | Madanganj | 48 | 2023-07-26 12:00
92 | Madaripur | 121 | 2023-07-03 23:00
93 | Madartek | 102.33 | 2023-07-31 00:00
94 | Madunaghat | 63 | 2023-07-30 19:00
95 | Magura | 74 | 2023-07-24 20:00
96 | Mahasthangarh | 88 | 2023-07-31 23:00
97 | Manikganj | 126 | 2023-07-23 21:00
98 | Maniknagar | 114 | 2023-07-12 13:00
99 | Matarbari | 52 | 2023-07-18 19:30
100 | Matuail | 72 | 2023-07-23 10:00
101 | Millgate | 110 | 2023-07-19 16:00
102 | Mirpur | 149 | 2023-07-25 15:00
103 | Mirsorai | 6 | 2023-07-09 21:00
104 | Mithapukur | 48 | 2023-07-31 20:00
105 | Modern | 0 | 2023-07-01 00:00
106 | Mogbazar | 154.9 | 2023-07-31 15:00
107 | Mongla | 36 | 2023-07-11 20:00
108 | Motijheel | 46 | 2023-07-31 16:00
109 | Munshiganj | 118 | 2023-07-04 00:00
110 | Mymensingh | 250 | 2023-07-17 22:00
111 | Naogaon | 157 | 2023-07-27 21:00
112 | Narail | 63 | 2023-07-24 20:00
113 | Narinda | 100 | 2023-07-15 13:00
114 | Narshingdi | 184 | 2023-07-29 00:00
115 | Natore | 167 | 2023-07-24 21:00
116 | Nawabganj | 64 | 2023-07-19 22:00
117 | Netrakona | 157 | 2023-07-21 19:30
118 | New | 168 | 2023-07-18 09:00
119 | Niamatpur | 114 | 2023-07-25 19:30
120 | Noapara | 67 | 2023-07-05 22:00
121 | PHP | 11 | 2023-07-08 10:00
122 | Pabna | 135 | 2023-07-24 21:00
123 | Palashbari | 151 | 2023-07-23 19:30
124 | Panchagarh | 69 | 2023-07-30 19:30
125 | Patuakhali | 123 | 2023-07-04 23:00
126 | Payra | 34 | 2023-07-05 00:00
127 | Postogola | 66 | 2023-07-31 00:00
128 | Purbachal | 24 | 2023-07-31 00:00
129 | Purbasadipur | 149 | 2023-07-25 20:00
130 | Rahim | 50 | 2023-07-17 09:00
131 | Rajbari | 82 | 2023-07-31 20:00
132 | Rajendrapur | 106 | 2023-07-25 19:30
133 | Rajshahi | 190 | 2023-07-31 21:00
134 | Rajshahi-230 | 47 | 2023-07-24 23:00
135 | Ramganj | 134 | 2023-07-03 22:00
136 | Rampur | 34 | 2023-07-24 19:00
137 | Rangamati | 20 | 2023-07-03 19:30
138 | Rangpur | 172 | 2023-07-31 20:00
139 | Ruppur | 6.2 | 2023-07-13 10:00
140 | SSM | 16 | 2023-07-30 15:00
141 | Saidpur | 117 | 2023-07-15 19:30
142 | Satkhira | 143 | 2023-07-04 00:00
143 | Satmasjid | 115 | 2023-07-31 00:00
144 | Savar | 210 | 2023-07-25 15:00
145 | Shahjadpur | 118 | 2023-07-30 21:00
146 | Shahjibazar | 136 | 2023-07-23 22:00
147 | Shahmirpur | 58 | 2023-07-26 00:00
148 | Shariatpur | 94 | 2023-07-04 23:00
149 | Sherpur | 150 | 2023-07-29 21:00
150 | Shikalbaha | 36 | 2023-07-19 19:30
151 | Shikalbaha-230 | N/A | N/A
152 | Shitalakhya | 114.6 | 2023-07-12 12:00
153 | Sholosohor | 41 | 2023-07-31 19:30
154 | Shyampur | 172 | 2023-07-13 13:00
155 | Siddhirganj | 151 | 2023-07-30 17:00
156 | Sirajganj | 141 | 2023-07-30 21:00
157 | Sonargaon | 122 | 2023-07-13 21:00
158 | Sreemongol | 73 | 2023-07-07 19:00
159 | Sreepur | 83 | 2023-07-26 11:00
160 | Srinagar | 51.1 | 2023-07-30 22:00
161 | Sunamganj | 64 | 2023-07-30 22:00
162 | Sylhet | 180 | 2023-07-25 19:00
163 | TK | 35 | 2023-07-25 23:00
164 | Tangail | 242 | 2023-07-20 19:30
165 | Thakurgaon | 114 | 2023-07-25 20:00
166 | Tongi | 121 | 2023-07-24 11:00
167 | Ullon | 48 | 2023-07-25 00:00
168 | Uttara | 89 | 2023-07-31 16:00
169 | UttaraNew | 76 | 2023-07-31 15:00
170 | Zigatola | 101 | 2023-07-25 16:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:July 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5346.47 | 2023-07-25 | 19:30
Chattogram | 1589.5 | 2023-07-24 | 19:30
Cumilla | 1447 | 2023-07-12 | 22:00
Mymensingh | 1176 | 2023-07-29 | 22:00
Sylhet | 650 | 2023-07-23 | 22:00
Khulna | 1862.2 | 2023-07-04 | 23:00
Barishal | 535 | 2023-07-04 | 23:00
Rajshahi | 1718.8 | 2023-07-24 | 21:00
Rangpur | 1012 | 2023-07-29 | 19:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:July 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 412 | 2023-07-04 18:30 | 364 | 2023-07-27 19:30
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 407 | 2023-07-01 16:00 | 386 | 2023-07-12 10:00
3 | Bibiana 400/230kV Sub-Station | 400 | 415 | 2023-07-17 18:30 | 395 | 2023-07-22 12:00
4 | BIPTC | 400 | 403 | 2023-07-26 06:00 | 386 | 2023-07-19 15:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 416 | 2023-07-02 18:30 | 389 | 2023-07-03 22:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 402 | 2023-07-11 18:30 | 345 | 2023-07-25 19:30
7 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 420 | 2023-07-19 20:00 | 359 | 2023-07-25 17:00
8 | Payra 400kV Sub-Station | 400 | 420 | 2023-07-06 18:30 | 398 | 2023-07-03 22:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 417 | 2023-07-07 18:30 | 385 | 2023-07-03 22:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 242 | 2023-07-01 16:00 | 220 | 2023-07-25 16:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 242 | 2023-07-20 17:00 | 203 | 2023-07-21 02:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 232 | 2023-07-02 18:00 | 217 | 2023-07-12 19:30
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 222 | 2023-07-11 11:00 | 200 | 2023-07-12 19:30
5 | Barishal 230/132kV Grid Sub-Station | 230 | 248 | 2023-07-04 18:30 | 227 | 2023-07-07 15:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 234 | 2023-07-02 18:00 | 222 | 2023-07-08 21:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 229 | 2023-07-26 | 203 | 2023-07-12 19:30
8 | BSRM 230/33kV Grid Sub-Station | 230 | 240 | 2023-07-04 18:30 | 214 | 2023-07-24 08:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-07-04 18:30 | 221 | 2023-07-22 11:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 248 | 2023-07-10 14:00 | 228 | 2023-07-31 15:00
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 240 | 2023-07-10 15:00 | 230 | 2023-07-12 10:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 239 | 2023-07-01 18:30 | 214 | 2023-07-24 08:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 245 | 2023-07-02 22:00 | 224 | 2023-07-25 12:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 241 | 2023-07-01 16:00 | 219 | 2023-07-26 23:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-07-01 18:30 | 215 | 2023-07-22 11:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 238 | 2023-07-15 15:00 | 223 | 2023-07-12 19:30
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 229 | 2023-07-02 18:30 | 211 | 2023-07-03 22:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-07-01 16:00 | 220 | 2023-07-25 16:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 238 | 2023-07-02 18:30 | 211 | 2023-07-03 15:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 241 | 2023-07-01 16:00 | 221 | 2023-07-25 15:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 245 | 2023-07-01 17:00 | 229 | 2023-07-22 11:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 241 | 2023-07-10 19:30 | 212 | 2023-07-24 09:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 235 | 2023-07-06 18:30 | 216 | 2023-07-07 13:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 240 | 2023-07-01 16:00 | 223 | 2023-07-25 15:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 238 | 2023-07-05 20:00 | 215 | 2023-07-23 09:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 240 | 2023-07-01 16:00 | 222 | 2023-07-25 15:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 242 | 2023-07-01 16:00 | 223 | 2023-07-18 01:00
28 | Sirajgonj 230 kV Switching Station | 230 | 239 | 2023-07-01 18:30 | 224 | 2023-07-12 19:30
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 235 | 2023-07-01 09:00 | 222 | 2023-07-27 14:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-07-01 16:00 | 217 | 2023-07-16 12:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-14 17:00 | 124 | 2023-07-12 10:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-30 19:30 | 122 | 2023-07-08 15:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-05 18:30 | 123 | 2023-07-02 12:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-10 18:30 | 120 | 2023-07-07 13:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 141 | 2023-07-01 16:00 | 134 | 2023-07-12 13:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-17 13:00 | 117 | 2023-07-03 13:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-25 19:30 | 124 | 2023-07-08 15:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-14 07:00 | 125 | 2023-07-12 11:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-01 16:00 | 121 | 2023-07-25 16:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-05 18:00 | 126 | 2023-07-03 22:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-05 18:00 | 122 | 2023-07-03 22:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-10 17:00 | 124 | 2023-07-08 14:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-19 20:00 | 119 | 2023-07-08 15:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-05 05:00 | 123 | 2023-07-12 10:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 140 | 2023-07-04 20:00 | 126 | 2023-07-22 11:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-24 15:00 | 120 | 2023-07-26 19:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-27 18:00 | 118 | 2023-07-02 13:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 133 | 2023-07-01 10:00 | 118 | 2023-07-12 16:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-31 22:00 | 117 | 2023-07-01 01:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 05:00 | 128 | 2023-07-12 22:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-02 18:00 | 126 | 2023-07-07 21:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 135 | 2023-07-01 15:00 | 116 | 2023-07-25 15:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-07-16 18:00 | 120 | 2023-07-07 22:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-24 08:00 | 121 | 2023-07-12 22:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 17:00 | 120 | 2023-07-22 15:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 140 | 2023-07-01 16:00 | 124 | 2023-07-25 16:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-09 18:00 | 115 | 2023-07-01
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-01 18:30 | 123 | 2023-07-08 15:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-03 10:00 | 120 | 2023-07-07 11:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 141 | 2023-07-04 20:00 | 128 | 2023-07-22 10:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-09 22:00 | 121 | 2023-07-01 13:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-24 15:00 | 120 | 2023-07-31 21:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-09 18:00 | 113 | 2023-07-03 13:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-19 23:00 | 116 | 2023-07-02 21:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 129 | 2023-07-10 16:00 | 113 | 2023-07-01 05:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-10 | 121 | 2023-07-08 19:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-01 16:00 | 124 | 2023-07-26 13:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-14 08:00 | 125 | 2023-07-12 11:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 16:00 | 121 | 2023-07-22 11:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-01 16:00 | 126.6 | 2023-07-26 13:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-05 18:00 | 120 | 2023-07-22 10:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-07-06 18:00 | 123 | 2023-07-20 22:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-01 16:00 | 124 | 2023-07-22 10:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-09 22:00 | 120 | 2023-07-08 15:00
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-04 18:30 | 123 | 2023-07-02 13:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-04 18:30 | 124 | 2023-07-03 13:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-26 18:00 | 123 | 2023-07-02 13:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-14 08:00 | 125 | 2023-07-12 11:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-22 23:00 | 122 | 2023-07-08 15:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 140 | 2023-07-01 16:00 | 123 | 2023-07-15 09:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 141 | 2023-07-02 18:30 | 129 | 2023-07-22 10:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-02 18:30 | 128 | 2023-07-07 21:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-19 15:00 | 113 | 2023-07-08 22:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-15 18:30 | 113 | 2023-07-08 01:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-28 05:00 | 120 | 2023-07-02 13:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-04 18:30 | 125 | 2023-07-02 13:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-07-06 18:00 | 129 | 2023-07-31 16:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 131 | 2023-07-11 16:00 | 113 | 2023-07-07
59 | Juldah 132/33kV Grid Sub-Station | 132 | 142 | 2023-07-05 19:00 | 125 | 2023-07-01 09:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-05 23:00 | 120 | 2023-07-12 10:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-09 18:00 | 116 | 2023-07-01 01:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-07-01 16:00 | 122 | 2023-07-25 15:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-05 18:00 | 124 | 2023-07-08 13:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-28 18:00 | 120 | 2023-07-25 12:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-02 20:00 | 121 | 2023-07-25 13:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 18:30 | 121 | 2023-07-08 15:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-11 18:30 | 121 | 2023-07-03 14:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 18:30 | 121 | 2023-07-08 15:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-02 17:00 | 122 | 2023-07-08 21:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-03 19:30 | 119 | 2023-07-22 12:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-10 17:00 | 123 | 2023-07-08 15:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-08 18:00 | 127 | 2023-07-25 12:00
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-19 15:00 | 113 | 2023-07-05 21:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-02 18:00 | 125 | 2023-07-07 21:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-28 16:00 | 122 | 2023-07-07 11:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 132 | 2023-07-03 02:00 | 113 | 2023-07-31 22:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-04 20:00 | 126 | 2023-07-22 11:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 07:00 | 123 | 2023-07-03 22:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-14 06:00 | 125 | 2023-07-12 10:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-05 19:00 | 124 | 2023-07-08 15:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-27 18:00 | 123 | 2023-07-07 22:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-16 18:30 | 119 | 2023-07-12 19:30
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-06 17:00 | 118 | 2023-07-22 12:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 16:00 | 122 | 2023-07-25 12:00
85 | Matarbari 132/33kV Sub-Station | 132 | 139 | 2023-07-10 02:00 | 113 | 2023-07-01 10:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 140.3 | 2023-07-02 19:00 | 127.7 | 2023-07-25 15:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-01 16:00 | 123 | 2023-07-12 11:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-01 16:00 | 124 | 2023-07-25 16:00
89 | Mithapukur 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-11 11:00 | 116 | 2023-07-12 22:00
90 | Modern Steel 132/11kV Grid Sub-Station | 132 | 140 | 2023-07-05 19:00 | 124 | 2023-07-08 14:00
91 | Mogbazar 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-14 18:00 | 125 | 2023-07-12 10:00
92 | Mongla 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-17 13:00 | 118 | 2023-07-02 13:00
93 | Motijheel 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-01 16:00 | 121 | 2023-07-25 16:00
94 | Munshiganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-04 20:00 | 128 | 2023-07-22 09:00
95 | Mymensingh 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-02 15:00 | 114 | 2023-07-28 18:00
96 | Naogaon 132/33kV Grid Sub-Station | 132 | 131 | 2023-07-01 18:30 | 113 | 2023-07-12 19:30
97 | Narail 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-03 18:00 | 122 | 2023-07-07 21:00
98 | Narshingdi 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-02 18:00 | 119 | 2023-07-26 13:00
99 | Natore 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-16 18:30 | 124 | 2023-07-12 21:00
100 | Nawabganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-28 17:00 | 124 | 2023-07-22 11:00
101 | Netrakona 132/33kV Grid Sub-Station | 132 | 135 | 2023-07-01 09:00 | 113 | 2023-07-05 21:00
102 | New Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-01 16:00 | 124 | 2023-07-12 11:00
103 | Niamatpur 132/33kV Grid Sub-Station | 132 | 131 | 2023-07-11 17:00 | 113 | 2023-07-02 21:00
104 | Noapara 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-04 18:30 | 121 | 2023-07-03 14:00
105 | Pabna 132/33kV Grid Sub-Station | 132 | 135 | 2023-07-01 08:00 | 125 | 2023-07-07 21:00
106 | Palashbari 132/33kV Grid Sub-Station | 132 | 131 | 2023-07-16 16:00 | 113 | 2023-07-12 22:00
107 | Panchagarh 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-09 18:30 | 113 | 2023-07-06 01:00
108 | Patuakhali 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-06 18:30 | 128 | 2023-07-03 22:00
109 | PHP 132/33kV Sub-Station | 132 | 137 | 2023-07-09 18:00 | 118 | 2023-07-08 15:00
110 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2023-07-02 18:30 | 129 | 2023-07-22 10:00
111 | Purbachal 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-01 16:00 | 123 | 2023-07-11 10:00
112 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 135 | 2023-07-19 15:00 | 113 | 2023-07-06 04:00
113 | Rahim Steel 132/33kV Sub-Station | 132 | 140 | 2023-07-01 16:00 | 128 | 2023-07-01 15:00
114 | Rajbari 132/33kV Grid Sub-Station | 132 | 132 | 2023-07-02 18:30 | 122 | 2023-07-03 22:00
115 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-05 01:00 | 119 | 2023-07-22 12:00
116 | Rajshahi 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-13 08:00 | 124 | 2023-07-01
117 | Ramganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-09 18:00 | 113 | 2023-07-01
118 | Rangamati 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-01 18:30 | 122 | 2023-07-08 15:00
119 | Rangpur 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-19 15:00 | 113 | 2023-07-31 19:00
120 | Ruppur 132/11kV Grid Sub-Station | 132 | 137 | 2023-07-06 18:00 | 128 | 2023-07-07 22:00
121 | Saidpur 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-19 15:00 | 113 | 2023-07-26 06:00
122 | Satkhira 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-16 18:00 | 117 | 2023-07-03 14:00
123 | Satmasjid 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-01 16:00 | 124 | 2023-07-25 16:00
124 | Savar 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-02 18:30 | 124 | 2023-07-25 16:00
125 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-01 08:00 | 127 | 2023-07-07 21:00
126 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-02 10:00 | 122 | 2023-07-31 12:00
127 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-05 19:00 | 125 | 2023-07-01 07:00
128 | Shariatpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-07-02 18:30 | 121 | 2023-07-03 22:00
129 | Sherpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-07-08 18:30 | 113 | 2023-07-03 23:00
130 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 140.4 | 2023-07-04 20:00 | 127 | 2023-07-22 10:00
131 | Sholosohor 132/33kV Grid Sub-Station | 132 | 139 | 2023-07-10 17:00 | 122 | 2023-07-08 15:00
132 | Shyampur 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-01 16:00 | 123 | 2023-07-25 12:00
133 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-02 18:30 | 129 | 2023-07-22 10:00
134 | Sirajganj 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-02 18:30 | 114 | 2023-07-07 22:00
135 | Sonargaon 132/33kV Grid Sub-Station | 132 | 138 | 2023-07-05 22:00 | 126 | 2023-07-27 13:00
136 | Sreemongol 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-10 03:00 | 124 | 2023-07-22 15:00
137 | Srinagar 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-28 16:00 | 124 | 2023-07-22 11:00
138 | SSM 132/33kV Grid Sub-Station | 132 | 142 | 2023-07-05 19:00 | 126 | 2023-07-02 12:00
139 | Sunamganj 132/33kV Grid Sub-Station | 132 | 134 | 2023-07-24 15:00 | 117 | 2023-07-26 22:00
140 | Sylhet 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-24 15:00 | 124 | 2023-07-31 15:00
141 | Tangail 132/33kV Grid Sub-Station | 132 | 136 | 2023-07-01 09:00 | 117 | 2023-07-22 12:00
142 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-03 01:00 | 113 | 2023-07-06
143 | TK chemical 132kV Grid Sub-Station | 132 | 140 | 2023-07-10 17:00 | 124 | 2023-07-08 15:00
144 | Ullon 132/33kV Grid Sub-Station | 132 | 137 | 2023-07-14 04:00 | 126 | 2023-07-12 09:00
145 | Uttara 132/33kV Grid Sub-Station | 132 | 141 | 2023-07-04 18:00 | 124 | 2023-07-23 12:00
146 | UttaraNew 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-01 16:00 | 121 | 2023-07-22 08:00
147 | Zigatola 132/33kV Grid Sub-Station | 132 | 140 | 2023-07-28 07:00 | 124 | 2023-07-22 12:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:July 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 471 | 504.2232 | 2023-07-18 11:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 471 | 504.2232 | 2023-07-18 11:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -256 | 301.3586 | 2023-07-12 11:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -256 | 301.3586 | 2023-07-12 11:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | 241 | 282.2942 | 2023-07-09 06:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -205 | 209.2582 | 2023-07-07 01:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 303 | 318.1478 | 2023-07-15 13:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 402 | 402.0199 | 2023-07-05 07:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 421 | 424.0778 | 2023-07-03 16:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -276.63 | 280.0277 | 2023-07-28 23:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -273.53 | 277.0941 | 2023-07-28 23:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -143 | 143.3492 | 2023-07-21 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -143 | 143.3492 | 2023-07-21 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -335 | 335.6576 | 2023-07-20 13:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 311 | 318.5624 | 2023-07-16 05:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 311 | 318.5624 | 2023-07-16 05:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -91 | 102.8834 | 2023-07-02
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -91 | 102.8834 | 2023-07-02
Rahanpur_I 400/132kV Grid Sub-Station | AT-1 -Gen | 400/132 | 162 | 167.869 | 2023-07-07 05:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 238 | 242.4046 | 2023-07-15 18:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 290 | 312.7123 | 2023-07-29 13:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 175 | 179.5132 | 2023-07-20 17:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 175 | 179.5132 | 2023-07-20 17:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 145 | 149.6462 | 2023-07-25 15:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 110 | 125.2996 | 2023-07-25 18:30
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 150 | 159.7655 | 2023-07-08 21:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 205 | 223.8861 | 2023-07-08 03:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 142 | 162.9847 | 2023-07-24 21:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 189 | 196.563 | 2023-07-29 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 180 | 197.7979 | 2023-07-25 22:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 234 | 245.1224 | 2023-07-25 21:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 172 | 174.5967 | 2023-07-19 16:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 172 | 174.5967 | 2023-07-19 16:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -108 | 120.7477 | 2023-07-27 22:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -1147 | 1147.0039 | 2023-07-07 22:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 192 | 201.1567 | 2023-07-30 23:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 192 | 201.1567 | 2023-07-30 23:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 214 | 308.3504 | 2023-07-25 18:30
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 201 | 213.5064 | 2023-07-06 15:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 197 | 209.067 | 2023-07-06 15:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 250 | 264.3785 | 2023-07-24 16:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 100 | 141.4214 | 2023-07-31 02:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 105 | 105 | 2023-07-15 22:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 44 | 226.3184 | 2023-07-18 15:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 64 | 102.45 | 2023-07-31 06:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 64 | 102.45 | 2023-07-31 06:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 0.5 | 99.0013 | 2023-07-07
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 0.5 | 99.0013 | 2023-07-07
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 0.5 | 99.0013 | 2023-07-07
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 115 | 115.9741 | 2023-07-26 14:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 115 | 115.9741 | 2023-07-26 14:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 115 | 115.9741 | 2023-07-26 14:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 115 | 115.9741 | 2023-07-26 14:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 122 | 135.0852 | 2023-07-07 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 65 | 210.2974 | 2023-07-13 15:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 122 | 135.0852 | 2023-07-07 22:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -210 | 237.5311 | 2023-07-31 20:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -210 | 237.5311 | 2023-07-31 20:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 176 | 186.6012 | 2023-07-31 19:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 2 | 2 | 2023-07-16 03:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 234 | 245.1224 | 2023-07-04 14:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -121 | 129.4488 | 2023-07-04 22:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -121 | 129.4488 | 2023-07-04 22:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -1150 | 1151.1303 | 2023-07-05 04:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 175 | 190.3943 | 2023-07-19 13:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 232 | 237.9769 | 2023-07-16 11:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-01 (704T) | 230/132 | -122 | 127.7811 | 2023-07-10 06:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-02 (714T) | 230/132 | -122 | 127.7811 | 2023-07-10 06:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2023-07-01
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1.4142 | 2023-07-15 06:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 217 | 219.9659 | 2023-07-31 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 217 | 219.9659 | 2023-07-31 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 217 | 219.9659 | 2023-07-31 13:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 228 | 272.3692 | 2023-07-25
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 228 | 272.3692 | 2023-07-25
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 118 | 127.7693 | 2023-07-13 12:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 118 | 127.7693 | 2023-07-13 12:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 103 | 108.4666 | 2023-07-22 07:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 103 | 108.4666 | 2023-07-22 07:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 174 | 184.3828 | 2023-07-27 19:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 174 | 184.3828 | 2023-07-27 19:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 210 | 213.7756 | 2023-07-17 11:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 210 | 213.7756 | 2023-07-17 11:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 210 | 213.7756 | 2023-07-17 11:00
423
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: July 2023 | [5 empty] | (For Evening Peak) | [8 empty] | Month: July 2023 |  |  |  |  | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-07-01 | 11031 | 11031 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-01 | 8701 | 8701 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-02 | 11720 | 11720 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-02 | 9606 | 9606 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-03 | 12454 | 12454 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-03 | 9951 | 9951 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-04 | 13402 | 13440 | 36 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | - | 2023-07-04 | 11051 | 11051 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-05 | 13555 | 13555 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-05 | 11456 | 11510 | 52 | 12:00 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | -
2023-07-06 | 13087 | 13087 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-06 | 11699 | 11699 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-07 | 12899 | 13049 | 143 | 21:00 | 0 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-07 | 10746 | 10746 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-08 | 14085 | 14085 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-08 | 11681 | 11800 | 114 | 12:00 | 0 | 0 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | -
2023-07-09 | 14210 | 14850 | 611 | 21:00 | 0 | 0 | 160 | 80 | 80 | 120 | 71 | 0 | 100 | - | 2023-07-09 | 12030 | 12600 | 544 | 12:00 | 0 | 84 | 115 | 60 | 100 | 35 | 50 | 15 | 85 | -
2023-07-10 | 14459 | 14765 | 292 | 21:00 | 35 | 0 | 2 | 0 | 10 | 80 | 0 | 0 | 165 | - | 2023-07-10 | 12062 | 13200 | 1086 | 12:00 | 200 | 100 | 108 | 100 | 250 | 133 | 70 | 25 | 100 | -
2023-07-11 | 14691 | 14921 | 220 | 21:00 | 12 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 111 | - | 2023-07-11 | 12178 | 13400 | 1167 | 12:00 | 220 | 135 | 190 | 140 | 105 | 135 | 75 | 35 | 132 | -
2023-07-12 | 14601 | 14780 | 171 | 21:00 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0 | 55 | - | 2023-07-12 | 12805 | 13350 | 520 | 12:00 | 260 | 0 | 0 | 0 | 155 | 80 | 25 | 0 | 0 | -
2023-07-13 | 14709 | 14870 | 154 | 21:00 | 0 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | - | 2023-07-13 | 12004 | 13500 | 1429 | 12:00 | 265 | 225 | 82 | 193 | 172 | 125 | 82 | 55 | 230 | -
2023-07-14 | 13730 | 13870 | 134 | 21:00 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 79 | - | 2023-07-14 | 11879 | 11879 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-07-15 | 14545 | 14545 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-07-15 | 12219 | 12339 | 115 | 12:00 | 53 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | -
2023-07-16 | 14316 | 14485 | 161 | 21:00 | 22 | 0 | 0 | 0 | 15 | 73 | 0 | 0 | 51 | - | 2023-07-16 | 12457 | 12680 | 213 | 12:00 | 73 | 0 | 0 | 0 | 30 | 110 | 0 | 0 | 0 | -
2023-07-17 | 14701 | 15066 | 349 | 21:00 | 37 | 0 | 58 | 0 | 0 | 144 | 0 | 0 | 110 | - | 2023-07-17 | 12432 | 13000 | 542 | 12:00 | 116 | 0 | 100 | 38 | 140 | 105 | 0 | 10 | 33 | -
2023-07-18 | 14518 | 15200 | 651 | 21:00 | 100 | 0 | 0 | 56 | 157 | 150 | 0 | 0 | 188 | - | 2023-07-18 | 12428 | 13500 | 1024 | 12:00 | 270 | 150 | 50 | 115 | 140 | 95 | 64 | 0 | 140 | -
2023-07-19 | 14448 | 15600 | 1100 | 21:00 | 138 | 0 | 172 | 100 | 180 | 200 | 90 | 40 | 180 | - | 2023-07-19 | 12586 | 14200 | 1541 | 12:00 | 350 | 181 | 180 | 150 | 220 | 175 | 80 | 50 | 155 | -
2023-07-20 | 15059 | 15499 | 420 | 21:00 | 82 | 0 | 0 | 0 | 85 | 177 | 0 | 0 | 76 | - | 2023-07-20 | 12359 | 14250 | 1806 | 12:00 | 435 | 100 | 200 | 170 | 300 | 216 | 120 | 35 | 230 | -
2023-07-21 | 14218 | 14344 | 120 | 21:00 | 0 | 0 | 0 | 0 | 105 | 15 | 0 | 0 | 0 | - | 2023-07-21 | 12290 | 12491 | 192 | 12:00 | 0 | 0 | 0 | 0 | 82 | 110 | 0 | 0 | 0 | -
2023-07-22 | 14909 | 15300 | 373 | 21:00 | 0 | 0 | 0 | 0 | 145 | 120 | 0 | 0 | 108 | - | 2023-07-22 | 12607 | 12800 | 184 | 12:00 | 60 | 0 | 0 | 0 | 116 | 8 | 0 | 0 | 0 | -
2023-07-23 | 14476 | 15300 | 786 | 21:00 | 52 | 132 | 142 | 100 | 140 | 105 | 0 | 0 | 115 | - | 2023-07-23 | 13242 | 14100 | 819 | 12:00 | 118 | 267 | 0 | 0 | 158 | 123 | 0 | 0 | 153 | -
2023-07-24 | 15018 | 15550 | 508 | 21:00 | 45 | 0 | 77 | 0 | 122 | 107 | 65 | 0 | 92 | - | 2023-07-24 | 13419 | 14200 | 746 | 12:00 | 105 | 131 | 0 | 0 | 195 | 190 | 0 | 0 | 125 | -
2023-07-25 | 15118 | 15520 | 384 | 21:00 | 0 | 0 | 0 | 25 | 64 | 210 | 35 | 0 | 50 | - | 2023-07-25 | 13129 | 14200 | 1023 | 12:00 | 150 | 200 | 0 | 80 | 170 | 180 | 53 | 0 | 190 | -
2023-07-26 | 15164 | 15420 | 244 | 21:00 | 0 | 0 | 0 | 30 | 40 | 100 | 0 | 0 | 74 | - | 2023-07-26 | 13334 | 13900 | 541 | 12:00 | 101 | 80 | 0 | 0 | 50 | 230 | 0 | 0 | 80 | -
2023-07-27 | 14804 | 15160 | 340 | 20:00 | 0 | 0 | 0 | 0 | 25 | 193 | 0 | 0 | 122 | - | 2023-07-27 | 13417 | 13800 | 366 | 12:00 | 128 | 0 | 0 | 0 | 22 | 124 | 0 | 0 | 92 | -
2023-07-28 | 14098 | 14300 | 193 | 21:00 | 0 | 0 | 0 | 0 | 22 | 23 | 140 | 0 | 8 | - | 2023-07-28 | 11909 | 12118 | 200 | 12:00 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 67 | -
2023-07-29 | 15049 | 15175 | 120 | 21:00 | 25 | 0 | 0 | 0 | 32 | 52 | 11 | 0 | 0 |  | 2023-07-29 | 12587 | 12656 | 83 | 12:00 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 47
2023-07-30 | 15104 | 15700 | 569 | 21:00 | 40 | 0 | 89 | 20 | 105 | 100 | 20 | 70 | 125 |  | 2023-07-30 | 13187 | 14150 | 920 | 12:00 | 125 | 135 | 100 | 90 | 145 | 145 | 30 | 15 | 135
2023-07-31 | 14801 | 15220 | 400 | 21:00 | 40 | 0 | 0 | 60 | 40 | 170 | 0 | 0 | 90 |  | 2023-07-31 | 13198 | 14550 | 1291 | 12:00 | 271 | 205 | 145 | 135 | 145 | 160 | 65 | 25 | 140
|  |  | 1100 | [14 empty] | 1806
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:July 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15164 | 2023-07-26 | 21:00
2 | Maximum Day Peak Genaration | MW | 13419 | 2023-07-24 | 12:00
3 | Maximum Evening Peak Demand | MW | 15700 | 2023-07-30 | 21:00
4 | Minimum Generation | MW | 8071 | 2023-07-01 | 6:00
5 | Average of the daily evening peak Genaration | MW | 14160.6129 | - | -
6 | Average of the daily day peak Genaration | MW | 12085.4516 | - | -
7 | Maximum load shed (Evening Peak) | MW | 1100 | 2023-07-19 | 21:00
8 | Minimum load shed | MW | 0 | 2023-07-03 | 21:00
9 | Total nos. of load shed days | Day | 24 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 273.5161 | - | -
11 | Total Generation | MkWh | 8492.1212 | - | -
12 | Total Generation by BPDB | MkWh | 1774.0473 | % of total Gen. | 20.89%
13 | Total Generation by IPP | MkWh | 2504.1596 | '' | 29.49%
14 | A) Total Generation by Generation Companies | MkWh | 2914.5346 | '' | 34.32%
| B) Total Generation by REB | MkWh | 119.8463 | " | 1.411%
| C) Total Generation by RENTAL | MkWh | 406.1896 | " | 4.783%
| D) Total Imported from India (BIPTC) | MkWh | 671.7413 | " | 7.91%
| E) Total Imported from Tripura, India (A.C) | MkWh | 101.6025 | " | 1.196%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4793.0721 | % of total Gen. | 56.44%
| B) Oil | MkWh | 1899.9898 | '' | 22.37%
| C) Hydro | MkWh | 45.1338 | '' | 0.5315%
| D) Solar | MkWh | 45.4439 | '' | 0.5351%
| E) Coal | MkWh | 935.1378 | '' | 11.01%
| F) BIPTC (Import from India) | MkWh | 671.7413 | '' | 7.91%
| G) A.C (Import from Tripura, India) | MkWh | 101.6025 | '' | 1.196%
16 | Maximun of the daily total Generation . | MkWh | 325.3274 | 2023-07-26
17 | Monthly Load factor | % | 84.9553 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 37994.3805 | - | -
| A) Gas | M.Taka | 5315.1621 | - | -
| B) Liquid fuel | M.Taka | 22536.5402 | - | -
| C) Coal | M.Taka | 6347.9999 | - | -
| D) BIPTC (Import from India) | M.Taka | 3063.1404 | - | -
| E) Tripura(Import from India) | M.Taka | 731.5378 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1453.9633 | 2023-07-23
| A) Gas | M.Taka | 186.26 | 2023-07-01
| B) Liquid fuel | M.Taka | 1081.0704 | 2023-07-03
| C) Coal | M.Taka | 312.6394 | 2023-07-17
| D) BIPTC (Import from India) | M.Taka | 101.5338 | 2023-07-21
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.4867
| B) Excluding Hydro & Solar | Taka/kWhR | 6.5546
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.83 | 31/07/2023 | 06:00
b) | Actual | FT (MSL) | 80.3 | 31/07/2023 | 6:00
22 | Peak Genaration of July 2022 | MW | 13765 | 17/07/2022 | 21:00
23 | Peak Demand of July 2022 | MW | 13765 | 17/07/2022 | 21:00
24 | Maximum peak Generation recorded upto 31/07/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/07/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/06/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:July 2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | bar: FGMO Status 1 to FGMO Status 4; FGMO Status 6 to FGMO Status 31
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | bar: FGMO Status 12 to FGMO Status 31
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | bar: FGMO Status 1 to FGMO Status 12
8 | Ashuganj 225 MW CCPP | APSCL | 221
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | bar: FGMO Status 1 to FGMO Status 18
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage