## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:May 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-05-01 |  | 2021-04-01 |  | 2020-05-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13417 | 2021-05-22 | 13792 | 2021-04-27 | 11977 | 18/05/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 20:00 |  | 22:00 |  | 20:00
2 | Minimum Generation (MW) | 6470 | 2021-05-14 | 4853 | 2021-04-17 | 2679.2 | 21/05/20 | - | -
|  |  | 9:00 |  | 7:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13417 | 2021-05-22 | 13792 | 2021-04-27 | 11941 | 18/05/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 20:00 |  | 21:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 12021 | 2021-05-23 | 11773 | 2021-04-28 | 9490.1 | 18/05/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13417 | 2021-05-22 | 14097 | 2021-04-27 | 11941 | 18/05/20 | 14097 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 21:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 11615.0323 |  | 12676.7 |  | 9477.5161 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 9675.8387 |  | 10379.6667 |  | 7427.4674 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 933 | 2021-04-29 18:00 | 933 | 2021-04-29 18:00 | 949 | 10/05/2020 | 956 | 27/3/2019
|  |  | 18:00 |  | 18:00 |  | 1:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 187 | 2021-04-18 | 187 | 2021-04-18 | 190 | 17/05/2020 | 194 | 12/06/19
|  |  | 18:00 |  | 18:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 275 | 2021-04-27 | 275 | 2021-04-27 | - | - | 1459 | 04/05/2010
|  |  | 20:00 |  | 20:00 |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13792 | 2021-04-27 | 13792 | 2021-04-27 | - | - | 13792 | 2021-04-27
|  |  | 20:00 |  | 20:00 |  |  |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 0 |  | 1 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1736.8634 |  | 1830.3371 |  | 3143.7123 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 108.694 |  | 184.6566 |  | 69.8388
22 | Net Generation of BPDB (MKWH) | 1628.1694 |  | 1645.6805 |  | 3073.8735
23 | Net Generation of IPP (MKWH) | 4485.1096 |  | 4706.4414 |  | 124.5045
24 | Net Generation of REB (MKWH) | 122.6176 |  | 133.246 |  | 118.008
24 | Net Generation of Rental Power Plant (MKWH) | 487.59 |  | 587.4025 |  | 375.5825
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6723.4866 |  | 7072.7704 |  | 3691.9684 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 4753.881 |  | 4613.3508 |  | 4152.6276 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 247.9394 |  | 295.1848 |  | 175.8613 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1303.8078 |  | 1657.9757 |  | 644.461 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 16.1091 |  | 41.547 |  | 38.7155 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 21.292 |  | 21.9287 |  | 15.7592 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 489.1513 |  | 627.4399 |  | 325.8707 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 716.5811 |  | 658.1569 |  | 568.5998 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 75.6219 |  | 77.1406 |  | 66.4568 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:May 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13417 | 2021-05-22 | 21:00
Generation Period
| Dhaka | MW | 4259
| Chattogram | MW | 1308
| Cumilla | MW | 1325
| Mymensingh | MW | 1046
| Sylhet | MW | 566
a) | Total supply in East zone | MW | 8504
| Khulna | MW | 1656
| Barisal | MW | 427
| Rajshahi | MW | 1346
| Rangpur | MW | 777
b) | Total supply in West zone | MW | 4206
c) | Total supply in both zone ( a+b) | MW | 12710
Ref: | 27.21.0000.603.16.087.20.407 | Date: 18/06/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 550 | 2021-05-04 | 1:00
| b) Ishurdi end | MW | 288 | 2021-05-04 | 0:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 700 | 2021-05-04 | 0:00
| b) Ishurdi end | MW | 208 | 2021-05-03 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 9.17
| b) Ishurdi end | MKWH | 40.36
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 39.15
| b) Ishurdi end | MKWH | 8.9
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 510 | 2021-05-14 | 21:00
| b)Serajganj end | MW | 580 | 2021-05-04 | 0:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 570 | 2021-05-04 | 0:00
| b)Sirajganj end | MW | 410 | 2021-05-14 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.6 | 2021-05-15
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 4.4 | 2021-05-15
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 28.22
| b)Sirajganj end | MKWH | 77.65
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 76.68
| b)Sirajganj end | MKWH | 28.03
30 | Transmission loss of EWI /NO-2 | % | 1.101
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Sreenagar | 132/33 kV Transformers-T1 | 2021-05-01 01:12 | 2021-05-01 01:41 | 0:29 | T | Tripped showing REF relay | 0 | 0 | No interruption
Sreenagar | 132/33 kV Transformers- T-2 | 2021-05-01 01:12 | 2021-05-01 01:52 | 0:40 | T | Tripped showing REF relay | 38 | 25.3333 | Power interruption
Bhulta | 132/33 kV Transformers- T-1 | 2021-05-03 00:44 | 2021-05-03 06:24 | 5:40 | E/O | Due to red-hot maint at 132 kV Y-phase CT connector. | 0 | 0 | No interruption
Sreenagar | 132/33 kV Transformers- T-2 | 2021-05-01 17:45 | 2021-05-01 18:03 | 0:18 | T | Tripped operating differential relay | 0 | 0 | No interruption
Lalbag | 132/33 kV Transformers- T-2 | 2021-05-06 16:20 | 2021-05-07 01:38 | 9:18 | T | Tripped operating buchholz relay | 0 | 0 | No interruption
Lalbag | 132/33 kV Transformers- T-1 | 2021-05-06 16:20 | 2021-05-06 17:03 | 0:43 | T | Tripped showing O/C relay | 80 | 57.3333 | Power interruption
Aminbazar | 230/132 kV transformer T-01 | 2021-05-07 10:34 | 2021-05-07 17:44 | 7:10 | E/O | Due to red-hot maint at 132 kV end | 0 | 0 | No interruption
Keraniganj | 230/132 kV transformer ATR1 | 2021-05-08 10:34 | 2021-05-08 17:44 | 7:10 | E/O | Due to oil leakage maintenance. | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers- T1,T-2 | 2021-05-10 20:06 | 2021-05-10 20:23 | 0:17 | E/O | Due to flashing at 33 kV feeder | 10 | 2.8333 | Power interruption
Joydevpur | 132/33 kV Transformers- T-2 | 2021-05-11 10:46 | 2021-05-11 11:41 | 0:55 | T | Due to showing PRD at HT side | 25 | 22.9167 | Power interruption
Savar | 33 kV Bus-A | 2021-05-11 09:00 | 2021-05-11 11:41 | 2:41 | T | Due to red hot maintenance at 33 kV PBS feeder | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformers- T-1 with 33 kV Bus | 2021-05-13 12:08 | 2021-05-13 13:45 | 1:37 | E/O | Due to red hot maintenance | 5 | 8.0833 | Power interruption
Kishoreganj | 132/33 kV Transformers- T1,T-2 | 2021-05-15 21:45 | 2021-05-15 21:55 | 0:10 | T | Due to 33 kV feeder fault | 82 | 13.6667 | Power interruption
Tongi | 132/33 kV Transformers- T1,T-2 | 2021-05-16 11:11 | 2021-05-16 11:16 | 0:05 | T | Due to 33 kV feeder fault | 40 | 3.3333 | Power interruption
Hasnabad | 230/132 kV transformer T1 | 2021-05-16 14:09 | 2021-05-16 17:45 | 3:36 | E/O | Due to flashing from ground wire | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers- T-3 with 33 kV Bus | 2021-05-17 12:39 | 2021-05-17 14:29 | 1:50 | E/O | Due to 33 kV EPZ feeder fault | 20 | 36.6667 | Power interruption
Tangail | 132/33 kV Transformers- T1,T2 with 33 kV Bus | 2021-05-17 18:30 | 2021-05-17 18:30 | 0:00 | T | Due to Kechuadanga feeder CT blast | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers- T1,T2 | 2021-05-19 16:26 | 2021-05-19 16:40 | 0:14 | T | Due to 33 kV feeder fault showing O/C relay | 119 | 27.7667 | Power interruption
Kodda | 132/33 kV full S/S | 2021-05-20 21:45 | 2021-05-21 23:00 | 25:15 | T | Due to fire at 33 kV laltir feeder | 220 | 5555 | Power interruption
Mymensingh | 132/33 kV Transformers- T-3 | 2021-05-23 09:17 | 2021-05-23 12:38 | 3:21 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers- T-1 | 2021-05-23 15:35 | 2021-05-23 16:37 | 1:02 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers- T1,T2 | 2021-05-24 00:30 | 2021-05-24 00:42 | 0:12 | T | Due to 33 kV feeder fault showing O/C relay | 90 | 18 | Power interruption
Cantonment | 132/33 kV Transformer-T1 | 2021-05-24 13:47 | 2021-05-24 14:20 | 0:33 | T | Tripped showing master trip relay | 23 | 12.65 | Power interruption
Mymensing | 132/33 kV all Transformer- | 2021-05-24 20:54 | 2021-05-24 21:05 | 0:11 | T | Tripped showing SPS operated at Mymensing S/S | 0 | 0 | No interruption
Sreenagar | 132/33 kV Transformer-T1 | 2021-05-26 13:10 | 2021-05-26 14:30 | 1:20 | E/O | Due to red hot maintenance | 15 | 20 | Power interruption
Nawabganj | 132/33 kV Transformer-T1 | 2021-05-26 13:40 | 2021-05-26 15:29 | 1:49 | E/O | Due to LT CT joint sparking. | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T2 | 2021-05-27 10:34 | 2021-05-27 18:18 | 7:44 | T | Tripped showing Diff. protection | 0 | 0 | No interruption
Keraniganj GIS | 132/33 kV Transformer-T1 | 2021-05-27 13:58 | 2021-05-27 16:41 | 2:43 | T | Tripped showing 51N,86T,87 relay | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2021-05-28 11:17 | 2021-05-28 12:56 | 1:39 | E/O | Due to red-hot maint | 70 | 115.5 | Power interruption
Sreenagar | 132/33 kV Transformer-T1,T2 | 2021-05-29 17:00 | 2021-05-29 17:55 | 0:55 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2021-05-29 19:18 | 2021-05-29 19:23 | 0:05 | T | Tripped showing O/C relay | 40 | 3.3333 | Power interruption
Kishoreganj | 132/33 kV Transformer-T3,T4 | 2021-05-30 22:06 | 2021-05-30 22:36 | 0:30 | T | Tripped showing O/C relay | 60 | 30 | Power interruption
Hasnabad | 230/132 kV transformer T1 | 2021-05-31 19:25 | 2021-05-31 20:32 | 1:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 91:19 |  | Unserved Energy: |  | 5952.4167
Dhaka (South) Grid Circle :
Haripur | 230/132 kV transformer T1 | 2021-05-05 14:02 | 2021-05-05 14:28 | 0:26 | T | Tripped showing L/O relay | 0 | 0 | No interruption
Narshingdi | 132 kV Bus-2 | 2021-05-09 17:06 | 2021-05-09 18:22 | 1:16 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Narshingdi | 132/33 kv transformers T-2 | 2021-05-11 18:54 | 2021-05-11 19:22 | 0:28 | T | Tripped showing mechanical protection | 25 | 11.6667 | Power interruption
Narshingdi | 132/33 kv transformers T-3 | 2021-05-11 19:22 | 2021-05-11 20:16 | 0:54 | T | Tripped showing mechanical protection | 0 | 0 | No interruption
Haripur | 230 kV CB 845 B(mid CB) | 2021-05-15 00:28 | 2021-05-15 00:28 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sonargaon | 132/33 kv transformers T-1 | 2021-05-18 20:21 | 2021-05-18 20:21 | 0:00 | T | Due to 33 kV feeder fault. | 0 | 0 | No interruption
Aftabnagar | 132/33 kv transformers T-2 | 2021-05-19 05:06 | 2021-05-19 05:06 | 0:00 | T | Due to High winding temperature. | 0 | 0 | No interruption
|  |  | Total : | 3:04 |  | Unserved Energy: |  | 11.6667
Chattogram Grid Circle :
Hathazari | 132/33 kV Transformer-T2 | 2021-05-04 01:57 | 2021-05-04 11:41 | 9:44 | T | Due to 33 kV cable burst | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1,T2 | 2021-05-05 14:17 | 2021-05-05 14:26 | 0:09 | T | Due to 33 kV CB burst of PBS feeder | 120 | 18 | Power interruption
Cox's Bazar | 132/33 kV Transformer-T3 | 2021-05-18 18:40 | 2021-05-18 18:54 | 0:14 | T | Due to 33 kV feeder fault | 40 | 9.3333 | Power interruption
Chowmuhani | 132/33 kV Transformer-T2 | 2021-05-21 08:15 | 2021-05-21 09:42 | 1:27 | E/O | Due to red hot maint | 40 | 58 | Power interruption
Sikalbaha | Sikalbaha 230 kV bus | 2021-05-24 16:57 | 2021-05-24 17:06 | 0:09 | T | Due to tripping of Sikalbaha 230 kV bus | 244 | 36.6 | Power interruption at Chattogram Zone
|  |  | Total : | 11:43 |  | Unserved Energy: |  | 121.9333
Cumilla Grid Circle :
Cumilla(S) | 132/33 kV Transformer-T2 with 33 kV bus | 2021-05-01 08:28 | 2021-05-01 10:10 | 1:42 | E/O | Due to red-hot maint at 33 kV Laksham feeder | 30 | 51 | Power interruption
Feni | 132/33 kV Transformer-T2 | 2021-05-02 09:45 | 2021-05-02 11:45 | 2:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sreemangal | 132/33 kV Transformer- T1 & T2 | 2021-05-03 12:54 | 2021-05-03 13:08 | 0:14 | T | Due to 33 kV REB feeder fault | 18 | 4.2 | Power interruption
B.Baria | 132/33 kV Transformer- T1,T2 & T3 | 2021-05-04 02:12 | 2021-05-04 02:53 | 0:41 | T | Due to 33 kV Norsingdi feeder fault | 116 | 79.2667 | Power interruption
Sylhet | 132/33 kV Transformer-T2 | 2021-05-04 10:01 | 2021-05-04 10:28 | 0:27 | T | Tripped showing O/C relay | 56 | 25.2 | Power interruption
Shahjibazar | 132/33 kV Transformer-T2 | 2021-05-11 07:04 | 2021-05-11 07:29 | 0:25 | T | Tripped showing lockout, O/C, E/F relay | 0 | 0 | No interruption
Chatak | 132/33 kV Transformer-T3 | 2021-05-18 05:00 | 2021-05-18 05:30 | 0:30 | T | Tripped showing O/C, E/F relay | 5 | 2.5 | Power interruption
Chatak | 132/33 kV Transformer-T2 | 2021-05-18 15:06 | 2021-05-18 15:20 | 0:14 | T | Tripped showing O/C relay | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer- T1,T2 & T3 | 2021-05-19 03:20 | 2021-05-19 04:12 | 0:52 | T | Tripped due to 33 kV CT burst | 120 | 104 | Power interruption
Daudkandi | 132/33 kV Transformer- T1,T2 | 2021-05-23 01:38 | 2021-05-23 01:50 | 0:12 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Ashuganj | 230/132 kV transformer OAT-12 | 2021-05-23 17:54 | 2021-05-23 20:30 | 2:36 | T | Due to Ashuganj U-5 OAT-3 R-phase CT burst | 250 | 650 | Power interruption
Ashuganj | Ashuganj 230 kV bus-1,2 | 2021-05-24 15:49 | 2021-05-24 17:18 | 1:29 | T | Tripped showing gen trip differential trip | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2021-05-25 07:09 | 2021-05-25 07:09 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T1,T2 | 2021-05-30 00:26 | 2021-05-30 00:50 | 0:24 | T | Due to 33 kV tin lac pir feeder CT burst | 145 | 58 | Power interruption
|  |  | Total : | 11:46 |  |  |  | 974.1667
Khulna Grid Circle :
Gopalganj | 400/132 kV transformers T-1 & T-2 | 2021-05-02 21:15 | 2021-05-02 22:59 | 1:44 | T | Tripped showing PRD | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T-1 | 2021-05-03 11:00 | 2021-05-03 12:54 | 1:54 | E/O | Due to oil leakage from bottom of radiator | 0 | 0 | No interruption
Goalpara | 132/33 kV Transformer-T-6 | 2021-05-04 11:25 | 2021-05-04 22:21 | 10:56 | T | Tripped showing differential relay | 0 | 0 | No interruption
Gopalganj | 400/132 kV transformers T-1 | 2021-05-05 17:49 | 2021-05-06 01:22 | 7:33 | T | Tripped showing PRD | 0 | 0 | No interruption
Gopalganj | 400/132 kV transformers T-2 | 2021-05-05 17:49 | 2021-05-05 18:09 | 0:20 | T | Tripped showing PRD | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T | 2021-05-06 09:13 | 2021-05-06 09:28 | 0:15 | T | Due to 33 kV PBS feeder fault showing O/C,E/F | 40 | 10 | Power interruption
Bagerhat | 400/132 kV transformers T-3 | 2021-05-08 07:23 | 2021-05-08 07:23 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T-1 & T-2 | 2021-05-11 12:27 | 2021-05-11 12:56 | 0:29 | E/O | Due to to 33 kV REB-1 feeder DS flashing | 6 | 2.9 | Power interruption
Bagerhat | 132/33 kV transformer T-1 & T-2 | 2021-05-12 08:29 | 2021-05-12 08:45 | 0:16 | T | Due to 33 kV PBS feeder fault | 43 | 11.4667 | Power interruption
Gopalganj (Old) | 132/33 kV transformer T-1 with 33 kV Bus | 2021-05-12 09:15 | 2021-05-12 10:15 | 1:00 | E/O | Due to red-hot maintenance | 18 | 18 | Power interruption
Bheramara | 230/132 kV transformer T-2 | 2021-05-14 10:47 | 2021-05-14 12:50 | 2:03 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Bheramara | 230/132 kV transformer T-2 | 2021-05-14 21:13 | 2021-05-15 04:48 | 7:35 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Bheramara | 230/132 kV transformer T2 | 2021-05-18 12:15 | 2021-05-18 17:45 | 5:30 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T-1 | 2021-05-19 07:09 | 2021-05-19 07:09 | 0:00 | E/O | Due to 33 kV feeder red-hot maintenance | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T-1 | 2021-05-20 17:55 | 2021-05-20 18:43 | 0:48 | E/O | Due to red-hot maintenance | 8 | 6.4 | Power interruption
Bheramara | 132/33 kV transformer T-3 | 2021-05-22 15:35 | 2021-05-22 15:45 | 0:10 | E/O | Due to winding temperature high | 25 | 4.1667 | Power interruption
Gopalganj (Old) | 132/33 kV transformer T-1 with 33 kV Bus-1 | 2021-05-26 09:15 | 2021-05-26 09:33 | 0:18 | E/O | Due to red-hot maintenance | 10 | 3 | Power interruption
Goalpara | 132/33 kV transformer T-6 | 2021-05-27 08:46 | 2021-05-27 09:58 | 1:12 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Goalpara | 33 kV bus was | 2021-05-28 11:07 | 2021-05-28 12:50 | 1:43 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T-2 | 2021-05-29 09:40 | 2021-05-29 13:06 | 3:26 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformer-T4 | 2021-05-28 20:25 | 2021-05-28 20:36 | 0:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barisal(N) | 132/33 kV Transformer-T5 | 2021-05-28 20:25 | 2021-05-28 23:52 | 3:27 | E/O | Due to red-hot maintenance | 46 | 158.7 | Power interruption
|  |  | Total : | 50:50 |  | Unserved Energy: |  | 214.6333
HVDC Grid Circle : Nil
Nil
|  |  | Total : | 0:00 |  |  |  | 0
Bogura Grid Circle:
Sherpur (Bogura) | 132/33 kV Transformer-T-2 | 2021-05-02 12:31 | 2021-05-02 13:41 | 1:10 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Thakurgaon | 132/33 kV Transformer-T-2 | 2021-05-02 18:12 | 2021-05-02 18:34 | 0:22 | T | Due to 33 kV Capacitor Bank burst | 0 | 0 | No interruption
Niamatpur | 132/33 kV Transformer-T-2 | 2021-05-02 19:57 | 2021-05-03 17:15 | 21:18 | T | Due to 33 kV CT burst showing Diff. protection | 0 | 0 | No interruption
Joypurhat | 132/33 kV Transformer-T-4 | 2021-05-04 08:45 | 2021-05-04 09:30 | 0:45 | T | Tripped showing no relay | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T1 | 2021-05-08 09:25 | 2021-05-08 09:45 | 0:20 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T-3 | 2021-05-11 08:03 | 2021-05-11 08:27 | 0:24 | T | Tripped showing no relay | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer T-2 & Bus-2 | 2021-05-11 10:42 | 2021-05-11 11:57 | 1:15 | E/O | Due to red-hot maint at 33 kV Vabanipur PBS feeder | 10 | 12.5 | Power interruption
Rangpur | 33 kV full Bus | 2021-05-12 06:32 | 2021-05-12 07:40 | 1:08 | E/O | Due to red-hot maintenance | 50 | 56.6667 | Power interruption
Barapukuria | 132/33 kV Transformer-T-4 | 2021-05-12 10:23 | 2021-05-12 15:03 | 4:40 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Shajadpur | 132/33 kV Transformer-T-1 | 2021-05-14 20:43 | 2021-05-18 21:31 | 96:48 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T-3 | 2021-05-18 12:05 | 2021-05-18 12:25 | 0:20 | T | Due to 33 kV PBS feeder fault | 40 | 13.3333 | Power interruption
Ishurdi | 132/33 kV Transformer-T-2 | 2021-05-19 10:13 | 2021-05-19 11:17 | 1:04 | E/O | Due to red hot maint at 33 kV NESCO feeder | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer-T1,T-2 | 2021-05-20 09:01 | 2021-05-20 10:30 | 1:29 | E/O | Due to red-hot maint at 33 kV Bus sectionalizer | 35 | 51.9167 | Power interruption
C.Nawanganj | 132/33 kV Transformer-T1 | 2021-05-21 11:06 | 2021-05-21 11:06 | 0:00 | E/O | Due to oil leakage of 132 kV bushing. | 0 | 0 | No interruption
Shajadpur | 132/33 kV transformer T3 | 2021-05-21 10:15 | 2021-05-21 10:32 | 0:17 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Pabna | 132/33 kV transformer T3 & 33 kV Bus-4 | 2021-05-22 17:51 | 2021-05-22 18:14 | 0:23 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T4 | 2021-05-23 08:09 | 2021-05-23 10:57 | 2:48 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T-1 | 2021-05-23 21:10 | 2021-05-23 22:11 | 1:01 | T | Due to 3 kV BPS feeder fault | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T-2 | 2021-05-26 07:44 | 2021-05-26 08:50 | 1:06 | E/O | Due to red-hot maintenance | 5 | 5.5 | Power interruption
Ishurdi | 132/33 kV Transformer-T1 | 2021-05-27 11:20 | 2021-05-27 11:20 | 0:00 | T | Tripped showing self protection | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T1 | 2021-05-27 20:29 | 2021-05-27 21:41 | 1:12 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T4 | 2021-05-31 09:42 | 2021-05-31 10:12 | 0:30 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 138:20 |  |  |  | 139.9167
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 307:02 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2021-05-02 15:30 | 2021-05-02 15:44 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishwardi 230 kV line-2 | 2021-05-04 00:26 | 2021-05-04 01:08 | 0:42 | T | Tripped showing PTAW,PTB and dist. relay | 0 | 0 | No interruption
B.Baria | B.Baria-Norsingdi 132 kV line-2 | 2021-05-04 01:08 | 2021-05-04 01:18 | 0:10 | T | Tripped showing dist relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2021-05-04 00:49 | 2021-05-04 01:25 | 0:36 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV line-1 | 2021-05-04 01:20 | 2021-05-04 01:49 | 0:29 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2021-05-06 10:06 | 2021-05-06 12:08 | 2:02 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Lalbag | Lalbag-Kamrangirchar 132 kV line | 2021-05-07 11:20 | 2021-05-07 14:33 | 3:13 | E/O | Due to red-hot maintenance at 33 kV end. | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorasal 230 kV line-1 | 2021-05-07 15:02 | 2021-05-08 11:37 | 20:35 | T | Tripped showing dist relay | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV line-1 | 2021-05-07 20:23 | 2021-05-07 20:38 | 0:15 | T | Tripped showing dist relay | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd 132 kV line | 2021-05-10 18:22 | 2021-05-10 18:31 | 0:09 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-2 | 2021-05-11 17:30 | 2021-05-11 17:45 | 0:15 | T | Tripped showing dist relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Bangabhaban 132 kV line-2 | 2021-05-13 23:38 | 2021-05-14 02:32 | 2:54 | T | Tripped showing Backup protection,O/C relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-2 | 2021-05-14 20:50 | 2021-05-15 12:34 | 15:44 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2021-05-18 17:26 | 2021-05-18 18:07 | 0:41 | T | Tripped showing dist relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-1 | 2021-05-22 15:30 | 2021-05-22 17:46 | 2:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishwardi 230 kV line-2 | 2021-05-23 14:46 | 2021-05-23 17:18 | 2:32 | E/O | Due to fire at Tongi area. | 0 | 0 | No interruption
Ghorashal | Ghorasal(1)-Ishurdi(2) 230 kV line | 2021-05-24 15:54 | 2021-05-24 17:14 | 1:20 | T | Tripped showing dist relay | 0 | 0 | No interruption
Mymensing S/S | Mymensing S/S-Mymensing RPCL 132 kV line-1,2 | 2021-05-24 20:54 | 2021-05-24 21:12 | 0:18 | T | Due to SPS operated Mymensing S/S | 0 | 0 | No interruption
Mymensing S/S | Mymensing RPCL-Tangail 132 kV line-1 | 2021-05-24 23:58 | 2021-05-25 00:10 | 0:12 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2021-05-27 14:59 | 2021-05-28 10:05 | 19:06 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 230 kV line-2 | 2021-05-27 16:12 | 2021-05-27 16:51 | 0:39 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-1 | 2021-05-28 06:06 | 2021-05-28 11:42 | 5:36 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 79:58 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Shyampur | APR P.P.-Shyampur 230 kV line | 2021-05-02 22:04 | 2021-05-02 22:56 | 0:52 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV line-1 | 2021-05-02 22:05 | 2021-05-02 22:38 | 0:33 | T | Tripped showing dist relay | 40 | 22 | Power interruption
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV line-2 | 2021-05-02 22:05 | 2021-05-02 22:57 | 0:52 | T | Tripped showing dist relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV line-1 | 2021-05-02 22:07 | 2021-05-02 22:43 | 0:36 | T | Tripped showing dist relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2021-05-09 11:20 | 2021-05-09 11:33 | 0:13 | T | Tripped showing dist relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2021-05-11 05:30 | 2021-05-11 05:58 | 0:28 | T | Tripped showing dist relay | 0 | 0 | No interruption
APR | APR-Shyampur 230 kV line | 2021-05-11 10:19 | 2021-05-11 10:28 | 0:09 | T | Tripped showing O/C & E/F relays | 0 | 0 | No interruption
APR | APR-Hasnabad 230 kV line | 2021-05-11 10:19 | 2021-05-11 11:43 | 1:24 | T | Tripped showing O/C & E/F relays | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV line-1 | 2021-05-13 15:36 | 2021-05-13 19:47 | 4:11 | E/O | Due to GIS problem at Shyampur end. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV line-1 | 2021-05-13 22:50 | 2021-05-15 11:55 | 37:05 | E/O | Due to GIS problem at Shyampur end. | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2021-05-15 09:48 | 2021-05-15 10:50 | 1:02 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
APR | APR-Hasnabad 230 kV line | 2021-05-15 12:12 | 2021-05-15 15:22 | 3:10 | E/O | Due to problem with PT at Hasnabad end. | 0 | 0 | No interruption
Fatulla | Fatulla-Shyampur 132 kV line-2 | 2021-05-18 16:27 | 2021-05-18 17:01 | 0:34 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV line-2 | 2021-05-22 04:20 | 2021-05-22 05:16 | 0:56 | T | Tripped showing dist, E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2021-05-22 04:20 | 2021-05-22 04:20 | 0:00 | T | Due to Y-phase PT burst at Haripur end. | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2021-05-24 21:45 | 2021-05-24 22:26 | 0:41 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 52:46 |  | Unserved Energy: |  | 22
Chattogram Grid Circle :
Halishahar | Halishahar-Rampur 132 kV line-1 | 2021-05-03 02:05 | 2021-05-03 02:33 | 0:28 | T | Tripped showing dist. relay | 0 | 0 | No interruption
AKSML | AKSML-BSRM 230 kV line-1 | 2021-05-10 08:55 | 2021-05-10 09:20 | 0:25 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-2 | 2021-05-23 18:06 | 2021-05-23 18:25 | 0:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroirhat 132 kV line-2 | 2021-05-23 17:28 | 2021-05-23 17:44 | 0:16 | T | Tripped showing dist. O/C relay | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV line-1 | 2021-05-24 12:35 | 2021-05-24 13:28 | 0:53 | T | Tripped showing dist. Directional O/C relay | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV line-2 | 2021-05-24 12:35 | 2021-05-24 17:19 | 4:44 | T | Tripped showing dist. Directional O/C relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV line | 2021-05-24 12:35 | 2021-05-24 12:55 | 0:20 | T | Tripped showing O/C relay | 364 | 121.3333 | Power interruption under Chattogram zone
Sikalbaha | Sikalbaha-TK 132 kV Ckt | 2021-05-24 12:38 | 2021-05-24 13:30 | 0:52 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chowmuhuni | Chowmuhuni S/S-Chandpur P/S 132 kV line | 2021-05-30 13:38 | 2021-05-30 15:02 | 1:24 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 9:41 |  | Unserved Energy: |  | 121.3333
Cumilla Grid Circle :
Cumilla(N) | Comilla(N)-Daudkandi 132 kV line-2 | 2021-05-01 02:47 | 2021-05-01 02:55 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2021-05-02 22:46 | 2021-05-02 23:08 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cumilla(N) | Comilla(N)-Daudkandi 132 kV line-2 | 2021-05-03 00:26 | 2021-05-03 01:08 | 0:42 | T | Tripped showing dist and O/C relay | 0 | 0 | No interruption
B.Baria | B.Baria-Ashuganj 132 kV line-1 | 2021-05-04 02:18 | 2021-05-04 02:31 | 0:13 | T | Tripped showing dist relay | 0 | 0 | No interruption
B.Baria | B.Baria-Ashuganj 132 kV line-2 | 2021-05-04 02:18 | 2021-05-04 02:32 | 0:14 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1,2 | 2021-05-07 15:20 | 2021-05-07 15:59 | 0:39 | T | Tripped showing dist relay | 0 | 0 | No interruption
Feni | Feni-Choumohani 132 kV line-2 | 2021-05-07 16:41 | 2021-05-07 16:49 | 0:08 | T | Tripped showing dist relay | 0 | 0 | No interruption
Comilla(N) | Comilla(N)-Daudkandi 132 kV line-2 | 2021-05-09 16:04 | 2021-05-09 16:09 | 0:05 | T | Tripped showing dist , O/C relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Beanibazar-Sylhet 132 kV line | 2021-05-18 06:20 | 2021-05-18 06:34 | 0:14 | T | Tripped showing dist relay | 7 | 1.6333 | Power interruption
Fenchuganj | Fenchuganj S/S-Fenchuganj P/P 132 kV line-1 | 2021-05-18 06:42 | 2021-05-18 07:15 | 0:33 | T | Tripped showing dist relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj S/S-Fenchuganj P/P 132 kV line-2 | 2021-05-18 06:42 | 2021-05-18 07:15 | 0:33 | T | Tripped showing dist relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-2 | 2021-05-18 16:32 | 2021-05-18 17:11 | 0:39 | T | Tripped showing dist relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-1 | 2021-05-18 17:15 | 2021-05-18 17:49 | 0:34 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-1 | 2021-05-18 17:33 | 2021-05-18 18:30 | 0:57 | T | Tripped showing dist relay | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV both line-1,2 | 2021-05-19 12:30 | 2021-05-19 13:48 | 1:18 | T | Due to Voltage fluctuation | 170 | 221 | Power interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1 | 2021-05-19 03:23 | 2021-05-19 03:40 | 0:17 | T | Tripped showing dist relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV line-2 | 2021-05-20 14:23 | 2021-05-20 14:31 | 0:08 | T | Tripped showing dist ,O/C relay | 0 | 0 | No interruption
Chattak | Sylhet-Chattak 132 kV line-1 | 2021-05-21 10:01 | 2021-05-21 15:02 | 5:01 | T | Tripped showing no relay | 9 | 45.15 | Power interruption
Sunamganj | Chattak-Sunamganj 132 kV line | 2021-05-21 11:40 | 2021-05-21 12:19 | 0:39 | T | Due to flashing at bus coupler DS | 23 | 14.95 | Power interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1,2 | 2021-05-23 17:54 | 2021-05-23 18:40 | 0:46 | T | Due to Ashuganj U-5 OAT-3 R-phase CT burst | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1,2 | 2021-05-23 17:54 | 2021-05-23 18:40 | 0:46 | T | Due to Ashuganj U-5 OAT-3 R-phase CT burst | 0 | 0 | No interruption
Ashuganj | Ashuganj network-Ashuganj (S) 230 kV line-2 | 2021-05-24 15:49 | 2021-05-24 15:49 | 0:00 | T | Due to Y-phase CT burst | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj line-1 | 2021-05-24 15:49 | 2021-05-24 17:31 | 1:42 | T | Due to differential trip | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj line-2 | 2021-05-24 15:49 | 2021-05-24 17:33 | 1:44 | T | Due to differential trip | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) line-1 | 2021-05-24 15:49 | 2021-05-24 17:18 | 1:29 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) line-2 | 2021-05-24 15:49 | 2021-05-24 17:48 | 1:59 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2021-05-24 23:41 | 2021-05-25 11:54 | 12:13 | T | Tripped showing dist relay | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur Desh P/S 132 kV line-2 | 2021-05-27 06:04 | 2021-05-28 20:48 | 38:44 | T | Tripped showing differential relay due to LA burst. | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-1 | 2021-05-27 14:42 | 2021-05-28 09:48 | 19:06 | T | Tripped showing O/C,E/F,Dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-1 | 2021-05-30 00:26 | 2021-05-30 01:12 | 0:46 | T | Tripped showing Dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-2 | 2021-05-30 00:26 | 2021-05-30 01:13 | 0:47 | T | Tripped showing Dist relay | 0 | 0 | No interruption
Feni | Feni-Chauddagram 132 kV line-2 | 2021-05-31 11:40 | 2021-05-31 11:57 | 0:17 | T | Tripped showing Auto reclosure relay | 0 | 0 | No interruption
|  |  | Total : | 93:43 |  | Unserved Energy: |  | 282.7333
Khulna Grid Circle :
Gopalganj | Payra-Gopalganj 400 kV line | 2021-05-02 21:15 | 2021-05-02 23:00 | 1:45 | T | Tripped showing O/V | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-05-06 11:01 | 2021-05-06 12:20 | 1:19 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bagerhat | Bagerhat-Orion Rupsha 132 kV line | 2021-05-06 18:30 | 2021-05-06 19:40 | 1:10 | T | Tripped showing dist relay | 30 | 35 | Power interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-2 | 2021-05-09 15:40 | 2021-05-09 16:24 | 0:44 | T | Tripped showing dist relay | 0 | 0 | No interruption
Jhenida | Jhenida-Joshore 132 kV line -1 | 2021-05-11 11:43 | 2021-05-11 12:38 | 0:55 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV line | 2021-05-11 16:47 | 2021-05-11 17:06 | 0:19 | T | Tripped showing dist relay | 40 | 12.6667 | Power interruption
Goalpara | Goalpara-Rupsha P/S 132 kV line | 2021-05-11 16:47 | 2021-05-11 17:16 | 0:29 | T | Tripped showing dist relay | 0 | 0 | No interruption
Madaripur | Madaripur-Barishal(N) 132 kV line-2 | 2021-05-12 09:41 | 2021-05-13 18:30 | 32:49 | T | Tripped showing dist relay | 0 | 0 | No interruption
Gopalganj(Old) | Gopalganj(Old)-Madaripur 132 kV line | 2021-05-12 12:45 | 2021-05-12 12:59 | 0:14 | T | Tripped showing dist protection | 0 | 0 | No interruption
Gopalganj(Old) | Gopalganj(Old)-Gopalganj P/S 132 kV line | 2021-05-13 12:45 | 2021-05-13 13:04 | 0:19 | T | Due to LA burst at P/S end | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line -1 | 2021-05-13 14:24 | 2021-05-13 14:45 | 0:21 | T | Tripped showing dist. Z1, O/C relay | 0 | 0 | No interruption
Gopalganj(Old) | Gopalganj(Old)-Madaripur 132 kV line | 2021-05-16 10:17 | 2021-05-16 10:45 | 0:28 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bheramara | Bheramara-Faridpur 132 kV line-2 | 2021-05-17 15:35 | 2021-05-17 19:07 | 3:32 | T | Tripped showing dist relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line -2 | 2021-05-18 07:14 | 2021-05-18 07:14 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj(N) 132 kV line | 2021-05-26 10:45 | 2021-05-26 13:13 | 2:28 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bheramara | Bheramara-Ishurdi 132 kV line -1 | 2021-05-26 15:13 | 2021-05-26 20:50 | 5:37 | T | Tripped showing dist relay | 0 | 0 | No interruption
Barisal | Barisal-Bhola 230 kV line -1 | 2021-05-29 10:04 | 2021-05-29 10:58 | 0:54 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 53:23 |  | Unserved Energy: |  | 47.6667
HVDC Grid Circle :
Bheramara HVDC | Bheramara HVDC-Khulna(S) 230 kV line-1 | 2021-05-20 10:51 | 2021-05-20 14:33 | 3:42 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 3:42 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Chapai nawabganj | Chapai nawabganj-Rajshahia(New) 132 kV line | 2021-05-03 21:12 | 2021-05-03 21:28 | 0:16 | T | Tripped showing dist relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Saidpur 132 kV line-1 | 2021-05-07 15:44 | 2021-05-07 16:51 | 1:07 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur(Bogura) 132 kV line-1 | 2021-05-07 18:18 | 2021-05-07 18:51 | 0:33 | T | Tripped showing dist ,O/C relay | 0 | 0 | No interruption
Bogura | Bogura-Bogura Confidance-1 132 kV line | 2021-05-07 18:18 | 2021-05-07 18:36 | 0:18 | T | Tripped showing dist ,O/C relay | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV line | 2021-05-08 06:23 | 2021-05-08 06:30 | 0:07 | T | Tripped showing dist relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line-2 | 2021-05-09 00:02 | 2021-05-09 02:48 | 2:46 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur(Bogura) 132 kV line-1 | 2021-05-09 13:02 | 2021-05-09 14:16 | 1:14 | T | Tripped showing dist relay | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV line | 2021-05-11 00:15 | 2021-05-11 00:58 | 0:43 | T | Tripped showing dist relay | 0 | 0 | No interruption
Naogaon | Naogaon-Niyamatpur 132 kV line | 2021-05-11 07:10 | 2021-05-11 07:39 | 0:29 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Shahjadpur | Shahjadpur-Pabna 132 kV line | 2021-05-11 08:03 | 2021-05-11 08:38 | 0:35 | T | Tripped showing dist relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura(Sherpur) 132 kV line-1 | 2021-05-17 15:35 | 2021-05-17 16:28 | 0:53 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ishwardi | Ishwardi-Ghorasal 230 kV line-1 | 2021-05-17 15:35 | 2021-05-17 16:12 | 0:37 | T | Tripped showing dist relay | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Confidence 132 kV line-1 | 2021-05-20 05:40 | 2021-05-20 07:35 | 1:55 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV line-1 | 2021-05-20 14:48 | 2021-05-20 15:02 | 0:14 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Confidence 132 kV line-2 | 2021-05-20 14:58 | 2021-05-20 15:55 | 0:57 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Confidence 132 kV line-1 | 2021-05-20 14:50 | 2021-05-20 16:36 | 1:46 | T | Tripped showing A/R block, SOTF relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line -1 | 2021-05-22 00:35 | 2021-05-22 00:48 | 0:13 | T | Tripped showing dist relay | 115 | 24.9167 | Power interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line -2 | 2021-05-22 00:35 | 2021-05-22 00:57 | 0:22 | T | Tripped showing dist relay | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Saidpur 132 kV line -1 | 2021-05-22 01:10 | 2021-05-22 01:22 | 0:12 | T | Tripped showing dist relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV line -1 | 2021-05-22 14:19 | 2021-05-22 15:06 | 0:47 | E/O | Due to CT meter connection problem | 0 | 0 | No interruption
Ishwardi | Ishwardi-Bheramara 132 kV line -1 | 2021-05-23 21:10 | 2021-05-23 21:37 | 0:27 | T | Tripped showing dist O/C relay | 0 | 0 | No interruption
Ishwardi | Ishurdi-Ghorasal 230 kV line -1 | 2021-05-26 13:12 | 2021-05-26 13:48 | 0:36 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ishwardi | Ishurdi-Natore 132 kV line -1 | 2021-05-26 15:12 | 2021-05-26 16:12 | 1:00 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ishwardi | Ishurdi-Ghorasal 230 kV line -1 | 2021-05-27 12:28 | 2021-05-27 13:44 | 1:16 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line -1 | 2021-05-30 10:52 | 2021-05-30 11:06 | 0:14 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 19:37 |  | Unserved Energy: |  | 24.9167
Others :Nil
Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 312:50 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:May 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhulta | Bhulta 132 kV Bus | 2021-05-01 07:02 | 2021-05-01 08:51 | 1:49 | S/O | Due to project work | 137 | 248.8833 | Power interruption
Mirpur | 132/33 kV Transformer-T1 | 2021-05-02 09:35 | 2021-05-02 14:45 | 5:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230/132 Transformer-T3 | 2021-05-03 11:01 | 2021-05-03 11:01 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | 230/132 Transformer-T3 |  | 2021-05-07 12:08 |  | S/O | After maintenance | 0 | 0 | No interruption
Joydebpur | 132/33 kV Transformer-GT2 | 2021-05-11 07:23 | 2021-05-11 07:23 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydebpur | 132/33 kV Transformer-GT2 | 2021-05-13 10:12 | 2021-05-13 11:06 | 0:54 | S/O | Due to PRD replacement. | 5 | 4.5 | Power interruption
Kabirpur | 132 kV reserve bus | 2021-05-19 10:23 | 2021-05-19 11:31 | 1:08 | S/O | Due to 132 kV bus coupler replacement | 0 | 0 | No interruption
Rajendrapur | 230/132 Transformer-T1 | 2021-05-20 08:37 | 2021-05-20 14:34 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve bus | 2021-05-21 06:49 | 2021-05-21 09:18 | 2:29 | S/O | Due to changing the loop of bus coupler breaker | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-05-21 08:39 | 2021-05-21 16:17 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2021-05-22 06:40 | 2021-05-22 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-05-22 08:38 | 2021-05-22 16:53 | 8:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T1 |  | 2021-05-22 19:43 |  | S/O | After maintenance | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T2 |  | 2021-05-22 19:48 |  | S/O | After maintenance | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-05-23 08:32 | 2021-05-23 17:07 | 8:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T4 |  | 2021-05-23 11:58 |  | S/O | After maintenance | 0 | 0 | No interruption
Dhamrai | 132/33 kV Transformer-T1 | 2021-05-24 06:05 | 2021-05-24 07:11 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformers- T1, with 33 kV Bus-1 | 2021-05-24 06:40 | 2021-05-24 09:25 | 2:45 | S/O | Due to C/M work | 15 | 41.25 | Power interruption
Dhamrai | 132/33 kV Transformer-T2 | 2021-05-24 07:14 | 2021-05-24 09:23 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T2 | 2021-05-26 08:09 | 2021-05-26 09:29 | 1:20 | S/O | Due to C/M work | 13 | 17.3333 | Power interruption
Kodda | 132/33 kV Transformer-T1 ,T2 with 33 kV Bus | 2021-05-28 07:40 | 2021-05-28 18:45 | 11:05 | S/O | Due to replacing 33 kV Bus isolator. | 60 | 665 | Power interruption
Savar | 132/33 kV Transformer-T3 | 2021-05-28 08:42 | 2021-05-28 17:40 | 8:58 | S/O | Due to D/W work | 61 | 546.9667 | Power interruption
Tangail | 132/33 kV Transformer-T2 | 2021-05-28 08:34 | 2021-05-28 11:48 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2021-05-29 07:13 | 2021-05-29 20:20 | 13:07 | S/O | Due to D/W work | 35 | 459.0833 | Power interruption
Sherpur | 132/33 kV Transformer-T1 with 33 kV bus | 2021-05-29 07:04 | 2021-05-29 14:12 | 7:08 | S/O | Due to D/W by PBS | 20 | 142.6667 | Power interruption
Kabirpur | 132/33 kV Transformer-T3 | 2021-05-29 07:07 | 2021-05-29 09:47 | 2:40 | S/O | Due to D/W work | 30 | 80 | Power interruption
Kodda | 132/33 kV Transformer-T3,T4 | 2021-05-29 08:27 | 2021-05-29 18:51 | 10:24 | S/O | Due to C/M work | 105 | 1092 | Power interruption
Savar | 132/33 kV Transformer-T3 | 2021-05-29 08:34 | 2021-05-29 16:36 | 8:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | 132/33 kV Transformer-T1 | 2021-05-29 09:48 | 2021-05-29 16:40 | 6:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV Transformer-T2 | 2021-05-30 09:20 | 2021-05-30 16:42 | 7:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2021-05-30 15:05 | 2021-05-30 19:07 | 4:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-05-31 08:52 | 2021-05-31 15:15 | 6:23 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 138:32 |  | Unserved Energy: |  | 3297.6833
Dhaka (South) Grid Circle :
Kaliakoir | 230 kV Bus-2 | 2021-05-06 10:37 | 2021-05-06 11:57 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV Transformer-T1 along with 33 kV Bus-1 | 2021-05-06 08:04 | 2021-05-06 09:24 | 1:20 | S/O | Due to 33 kV Bus isolator nut tight. | 26 | 34.6667 | Power interruption
Nawabganj | 132/33 kV Transformer-T1 along with 33 kV Bus-2 | 2021-05-06 08:21 | 2021-05-06 09:24 | 1:03 | S/O | Due to PBS work | 0 | 0 | No interruption
Rampura | 132 kV Bus-2 | 2021-05-06 10:41 | 2021-05-06 16:45 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 133 kV Bus-1 | 2021-05-08 10:07 | 2021-05-08 10:07 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sitalakha | 132/33 kV Transformer-GT1 | 2021-05-08 09:38 | 2021-05-08 09:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Norsingdi | 132/33 kV Transformer-T1 | 2021-05-15 19:49 | 2021-05-15 21:11 | 1:22 | S/O | Due to 33 kV DS incoming maintenance | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T-3 | 2021-05-20 09:20 | 2021-05-20 13:30 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 132 kV bus-1 | 2021-05-21 07:04 | 2021-05-21 08:20 | 1:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV T1 transformer | 2021-05-21 07:04 | 2021-05-21 08:22 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 132 kV reserve bus section-2 | 2021-05-24 09:04 | 2021-05-24 09:04 | 0:00 | S/O | Due to bus coupler loop changing. | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2021-05-24 11:02 | 2021-05-24 12:04 | 1:02 | S/O | Due to C/M work | 23 | 23.7667 | Power interruption
Hasnabad | 230/132 kV transformer T-2 | 2021-05-29 08:31 | 2021-05-29 08:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T-1 | 2021-05-30 08:47 | 2021-05-30 08:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | 230 kV Bus-2 | 2021-05-30 08:27 | 2021-05-30 08:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 18:55 |  | Unserved Energy: |  | 58.4333
Chattogram Grid Circle :
BSRM | 230/132 kV Transformer-T-1 | 2021-05-01 09:32 | 2021-05-01 13:32 | 4:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus-2 | 2021-05-02 09:29 | 2021-05-02 14:43 | 5:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus-2 | 2021-05-03 09:51 | 2021-05-03 14:43 | 4:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus-2 | 2021-05-04 09:44 | 2021-05-04 14:02 | 4:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus-1 | 2021-05-06 09:44 | 2021-05-06 12:45 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Agrabad | 132/33 kV Transformer-T1 | 2021-05-06 11:25 | 2021-05-06 15:00 | 3:35 | S/O | Due to 33 kV cable work | 0 | 0 | No interruption
Chowmuhuni | 132/33 kV Transformer-T2 | 2021-05-08 08:48 | 2021-05-08 10:48 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | 132 kV Bus-1 | 2021-05-22 08:23 | 2021-05-22 13:34 | 5:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | 132/33 kV Transformer-T2 | 2021-05-24 07:26 | 2021-05-24 07:36 | 0:10 | S/O | Due to BPDB work | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T3 | 2021-05-31 09:40 | 2021-05-31 09:40 | 0:00 | S/O | Due to Shitalpur steal mill work | 0 | 0 | No interruption
|  |  | Total : | 32:21 |  | Unserved Energy : |  | 0
Cumilla Grid Circle :
Fenchuganj | 132 kV Bus-1 | 2021-05-01 08:36 | 2021-05-01 16:55 | 8:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrokona | 132/33 kV transformer T-2 | 2021-05-01 11:58 | 2021-05-01 13:42 | 1:44 | S/O | Due to PDB-2 feeder maint | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-1 | 2021-05-02 09:09 | 2021-05-02 18:22 | 9:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T-4 | 2021-05-03 09:02 | 2021-05-03 14:15 | 5:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | 132 kV Bus-2 | 2021-05-04 09:02 | 2021-05-04 17:46 | 8:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-2 | 2021-05-05 08:24 | 2021-05-05 23:13 | 14:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | 132 kV Bus-2 | 2021-05-06 09:03 | 2021-05-06 19:45 | 10:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-2 | 2021-05-07 08:15 | 2021-05-07 18:41 | 10:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T1 | 2021-05-07 08:14 | 2021-05-07 18:41 | 10:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Fenchuganj | 132 kV Bus-1 | 2021-05-08 08:40 | 2021-05-08 22:25 | 13:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrokona | 132/33 kV transformer T1 | 2021-05-09 07:16 | 2021-05-09 07:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T2 | 2021-05-10 06:48 | 2021-05-10 06:48 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 132 kV Bus-1 | 2021-05-16 07:00 | 2021-05-16 07:00 | 0:00 | S/O | Due to jumper maintenance | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T1 | 2021-05-22 11:21 | 2021-05-22 12:38 | 1:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T-4 | 2021-05-24 09:06 | 2021-05-24 15:10 | 6:04 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 100:43 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
Gollamari | 132/33 kV Transformer-T2 | 2021-05-02 08:16 | 2021-05-02 15:41 | 7:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Gollamari | 132 kV Bus-1 | 2021-05-03 08:15 | 2021-05-03 08:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Gollamari | 132/33 kV Transformer-T2 | 2021-05-03 08:07 | 2021-05-03 17:01 | 8:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Gollamari | 132/33 kV Transformer-T2 | 2021-05-04 08:06 | 2021-05-04 17:40 | 9:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Gollamari | 132 kV Bus-2 | 2021-05-04 08:09 | 2021-05-04 17:40 | 9:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 |  | 2021-05-06 08:08 |  | S/O | After maintenance work | 0 | 0 | No interruption
GK project | 132/33 kV Transformer-T3 | 2021-05-06 12:50 | 2021-05-06 12:50 | 0:00 | S/O | Due to 33 kV Bay connection | 0 | 0 | No interruption
Narail | 132/33 kV Transformer-T2 | 2021-05-08 14:15 | 2021-05-08 15:38 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | 230/132 kV transformer T-01 | 2021-05-18 09:42 | 2021-05-18 11:35 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | 230/132 kV transformer T-01 | 2021-05-19 07:20 | 2021-05-19 07:20 | 0:00 | S/O | Due to PRD maintenance | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2021-05-22 07:48 | 2021-05-22 07:48 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 33 kV Bus section-1 | 2021-05-22 07:50 | 2021-05-22 07:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 & 33 kV Bus-1 | 2021-05-22 14:58 | 2021-05-22 16:02 | 1:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Magura | 132/33 kV Transformer-T2 | 2021-05-29 07:40 | 2021-05-29 12:38 | 4:58 | S/O | Due to C/M work | 18 | 89.4 | Power interruption
|  |  | Total : | 44:42 |  | Unserved Energy : |  | 89.4
Page: 4/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :Nil
Bheramara | Bheramara HVDC 20DF21 filter | 2021-05-06 09:59 | 2021-05-06 14:37 | 4:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 400 kV Bus-1 | 2021-05-20 09:32 | 2021-05-20 12:53 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 7:59 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Barapukuria | 132/33 kV transformer T6 | 2021-05-01 07:24 | 2021-05-01 07:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132 kV Bus-2 | 2021-05-01 10:10 | 2021-05-01 12:16 | 2:06 | S/O | Due to conductor replacement | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV transformer T3 | 2021-05-02 08:10 | 2021-05-02 10:43 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | 132/33 kV transformer T2 | 2021-05-03 09:46 | 2021-05-03 13:58 | 4:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T2 | 2021-05-05 08:17 | 2021-05-05 12:04 | 3:47 | S/O | Due to C/M work | 10 | 37.8333 | Power interruption
Sherpur | 132/33 kV transformer T1 | 2021-05-05 09:34 | 2021-05-05 11:13 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T3 |  | 2021-05-06 19:36 |  | S/O | After maintenance | 0 | 0 | No interruption
Bogura(new) | 132 kV all Bus | 2021-05-07 06:36 | 2021-05-07 08:56 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T3 | 2021-05-08 10:20 | 2021-05-08 10:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformer T3 | 2021-05-08 12:05 | 2021-05-08 16:20 | 4:15 | S/O | Due to protection test | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 | 2021-05-09 07:01 | 2021-05-09 08:15 | 1:14 | S/O | Due to C/M work | 52 | 64.1333 | Power interruption
Shahjadpur | 132/33 kV transformer T2 | 2021-05-09 12:09 | 2021-05-09 12:58 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 along with 33 kV Bus | 2021-05-10 07:04 | 2021-05-10 08:07 | 1:03 | S/O | Due to PBS work | 45 | 47.25 | Power interruption
Bogura | 132/33 kV transformer T3 along with 33 kV Bus | 2021-05-11 23:10 | 2021-05-11 23:10 | 0:00 | S/O | Due to tear of conductor string of 33 kV DS | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T3 | 2021-05-12 10:24 | 2021-05-12 12:44 | 2:20 | S/O | Due to C/M work | 25 | 58.3333 | Power interruption
Natore | 132/33 kV transformer T3 | 2021-05-16 11:30 | 2021-05-16 12:35 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132 kV full bus | 2021-05-19 08:30 | 2021-05-19 09:58 | 1:28 | S/O | Due to C/M work | 90 | 132 | Power interruption
Shajadpur | 132/33 kV transformer T2 | 2021-05-19 10:29 | 2021-05-19 11:49 | 1:20 | S/O | Due to C/M work | 12 | 16 | Power interruption
Barapukuria | 132 kV Bus-2 | 2021-05-21 07:53 | 2021-05-21 11:26 | 3:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohastanghor | 132/33 kV transformer T1,T2& 33 kV Bus | 2021-05-21 08:25 | 2021-05-21 10:04 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T1 & 33 kV Bus-1 | 2021-05-21 08:30 | 2021-05-21 18:42 | 10:12 | S/O | Due to D/W work | 25 | 255 | Power interruption
Rangpur | 132/33 kV transformer T1 | 2021-05-21 19:12 | 2021-05-21 19:29 | 0:17 | S/O | Due to project Work | 20 | 5.6667 | Power interruption
Bogura | 132/33 kV transformer T3 | 2021-05-22 09:17 | 2021-05-22 21:44 | 12:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T4 | 2021-05-23 14:50 | 2021-05-23 16:02 | 1:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T3 | 2021-05-24 08:16 | 2021-05-24 09:56 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T2 | 2021-05-24 10:22 | 2021-05-24 11:29 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T3 | 2021-05-24 10:34 | 2021-05-24 11:39 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132 kV Bus-2 | 2021-05-26 16:08 | 2021-05-26 19:29 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV transformer T2 | 2021-05-28 09:58 | 2021-05-28 14:03 | 4:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishwardi | 132/33 kV transformer T1 | 2021-05-30 10:32 | 2021-05-30 13:15 | 2:43 | S/O | Due to Oil filling. | 0 | 0 | No interruption
Rajshahi | 230/132 kV transformer T1 | 2021-05-31 09:51 | 2021-05-31 18:10 | 8:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T1 | 2021-05-31 12:05 | 2021-05-31 14:30 | 2:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T1 | 2021-05-31 15:09 | 2021-05-31 16:19 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T2 | 2021-05-31 16:24 | 2021-05-31 16:47 | 0:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformer T2 | 2021-05-31 14:30 | 2021-05-31 19:02 | 4:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 90:21 |  | Unserved Energy : |  | 616.2167
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 433:33 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:May 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Hasnabad | Hasnabad-Lalbagh 132 kV line | 2021-05-07 04:30 | 2021-05-07 07:23 | 2:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2021-05-07 04:31 | 2021-05-07 07:24 | 2:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2021-05-08 09:52 | 2021-05-08 12:13 | 2:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Ghorasal 230 kV line-1 | 2021-05-09 11:34 | 2021-05-09 14:54 | 3:20 | S/O | Due to kite removing | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV line | 2021-05-09 11:40 | 2021-05-09 13:18 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-2 | 2021-05-09 13:52 | 2021-05-09 15:31 | 1:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2021-05-10 10:05 | 2021-05-10 11:24 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-05-10 11:28 | 2021-05-10 14:46 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalakhya | Sitalakhya-Digital P/P 132 kV line | 2021-05-15 09:01 | 2021-05-15 12:14 | 3:13 | S/O | Due to CT,PT connection checking | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-05-16 07:17 | 2021-05-16 15:11 | 7:54 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132 kV line-1 | 2021-05-16 15:24 | 2021-05-16 15:53 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-1 | 2021-05-18 07:32 | 2021-05-18 20:47 | 13:15 | S/O | Due to OPGW replacing work. | 0 | 0 | No interruption
Mymensing | Mymensing-Kishoreganj 132 kV line-1 | 2021-05-18 07:28 | 2021-05-18 19:50 | 12:22 | S/O | Due to CT replacing work. | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-2 | 2021-05-18 08:25 | 2021-05-18 08:25 | 0:00 | S/O | Due to OPGW replacing work. | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2021-05-18 12:21 | 2021-05-18 13:24 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Joydevpur 132 kV line-1,2 | 2021-05-19 06:50 | 2021-05-19 06:50 | 0:00 | S/O | Due to OPGW replacing work. | 0 | 0 | No interruption
Mymensingh | Mymensing-Kishoreganj 132 kV line-2 | 2021-05-19 07:19 | 2021-05-19 07:19 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensing-Kishoreganj 132 kV line-1 | 2021-05-20 07:29 | 2021-05-20 17:32 | 10:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV line-1 & 2 | 2021-05-21 09:43 | 2021-05-21 12:36 | 2:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV line-1 & 2 | 2021-05-22 07:29 | 2021-05-22 07:29 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Tangail-Kabirpur 132 kV line-1 | 2021-05-22 07:30 | 2021-05-22 08:25 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 | 2021-05-22 08:36 | 2021-05-22 10:32 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 |  | 2021-05-22 15:28 |  | S/O | After maintenance work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensing 132 kV line-1 | 2021-05-23 07:37 | 2021-05-23 19:04 | 11:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensing 132 kV line-2 | 2021-05-24 07:40 | 2021-05-24 07:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-1 | 2021-05-26 18:31 | 2021-05-26 20:52 | 2:21 | S/O | Due to removing kite. | 0 | 0 | No interruption
New Tongi | New Tongi-old Tongi 132 kV line-2 | 2021-05-27 09:55 | 2021-05-27 16:26 | 6:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2021-05-27 14:13 | 2021-05-27 16:22 | 2:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2021-05-28 07:09 | 2021-05-28 18:04 | 10:55 | S/O | Due to cross-arm painting. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2021-05-28 08:15 | 2021-05-28 08:15 | 0:00 | S/O | Due to cross-arm painting. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2021-05-28 08:06 | 2021-05-28 18:13 | 10:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2021-05-28 08:38 | 2021-05-28 20:31 | 11:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2021-05-29 08:52 | 2021-05-29 18:22 | 9:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal(O) | Ghorashal(O)-Ghorashal GIS 230 kV line-1 |  | 2021-05-31 22:00 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 138:17 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Shyampur GIS | Shyampur GIS-Shyampur old 132 kV line-2 | 2021-05-01 09:02 | 2021-05-01 15:53 | 6:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 230 kV line-1 | 2021-05-11 13:33 | 2021-05-11 15:39 | 2:06 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | Rampura-Mogbazar 132 kV line-1 & 2 | 2021-05-15 08:52 | 2021-05-15 17:02 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.Baria 132 kV line-2 | 2021-05-16 14:14 | 2021-05-16 15:19 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-1 | 2021-05-19 11:06 | 2021-05-19 12:20 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV line-2 | 2021-05-19 12:21 | 2021-05-19 13:52 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur P.P.-Haripur 230 kV S/S 132 kV line-2 | 2021-05-19 10:42 | 2021-05-19 11:48 | 1:06 | S/O | Due to loop maintenance. | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2021-05-19 14:00 | 2021-05-19 15:03 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Meghan 230 kV line -1 | 2021-05-19 12:20 | 2021-05-19 14:50 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon S/S | Sonargaon S/S-Sonargaon P/S 132 kV line | 2021-05-21 09:38 | 2021-05-21 17:15 | 7:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbagh 132 kV line -1 | 2021-05-29 07:44 | 2021-05-29 16:55 | 9:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur 412 MW CCPP 230 kV line | 2021-05-30 12:33 | 2021-05-30 14:42 | 2:09 | S/O | Due to unit transformer of P/P maint | 0 | 0 | No interruption
|  |  | Total : | 44:33 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Madunaghat 132 kV line-2 | 2021-05-02 09:26 | 2021-05-02 16:39 | 7:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-2 | 2021-05-08 09:24 | 2021-05-08 15:21 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroaulia | Baroaulia-KSRM 132 kV Ckt | 2021-05-10 12:35 | 2021-05-10 13:18 | 0:43 | S/O | Due to R-phase loop change | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-05-18 07:23 | 2021-05-18 16:24 | 9:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Julda | Julda-Shahmirpur 132 kV line-2 | 2021-05-18 13:47 | 2021-05-18 14:41 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-2 | 2021-05-19 08:18 | 2021-05-19 15:06 | 6:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-TK Chemical 132 kV line | 2021-05-20 09:46 | 2021-05-20 11:52 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK Chemical 132 kV line | 2021-05-20 12:04 | 2021-05-20 13:53 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha-225 MW | Sikalbaha-225 MW GT bay-Sikalbaha 230 kV S/S 132 kV line | 2021-05-21 11:26 | 2021-05-21 16:23 | 4:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-2 | 2021-05-22 06:08 | 2021-05-22 12:08 | 6:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Julda S/S | Julda S/S-Julda P/S 132 kV line | 2021-05-22 07:03 | 2021-05-22 08:52 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-1 | 2021-05-22 08:42 | 2021-05-22 11:27 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV line-2 | 2021-05-22 11:31 | 2021-05-22 12:53 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroiarhat 132 kV line-2 | 2021-05-22 08:29 | 2021-05-22 14:30 | 6:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Anwara united 300 MW P/P 230 kV line-2 | 2021-05-23 06:21 | 2021-05-23 17:46 | 11:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line | 2021-05-23 08:34 | 2021-05-23 10:13 | 1:39 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV line-3 | 2021-05-23 10:35 | 2021-05-23 10:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Julda 132 kV line | 2021-05-24 06:45 | 2021-05-24 06:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Anwara united 300 MW P/P 230 kV line-1 | 2021-05-24 07:12 | 2021-05-24 07:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-2 | 2021-05-25 06:34 | 2021-05-25 06:34 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-2 |  | 2021-05-30 20:27 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 70:29 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Fenchuganj | Fenchuganj-Srimongal 132 kV 132 kV line-2 | 2021-05-01 12:03 | 2021-05-01 17:09 | 5:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2021-05-03 13:13 | 2021-05-03 17:38 | 4:25 | S/O | Due to tele-protection test. | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-1 | 2021-05-04 10:01 | 2021-05-04 14:28 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Srimongal 132 kV line-2 | 2021-05-05 08:17 | 2021-05-05 12:04 | 3:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Chaddogram line-1 | 2021-05-06 10:59 | 2021-05-06 14:17 | 3:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Srimongal 132 kV line | 2021-05-07 12:09 | 2021-05-07 19:44 | 7:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemangal | Fenchuganj-Srimongal 132 kV line-1 | 2021-05-08 08:29 | 2021-05-08 18:17 | 9:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | Halishahar-Julda 132 kV line | 2021-05-20 07:07 | 2021-05-20 09:19 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet- | Sylhet-Fenchuganj 132 kV line | 2021-05-22 07:21 | 2021-05-22 07:21 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj S/S-Fenchuganj P/P 132 kV line-2 |  | 2021-05-22 17:50 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 |  | 2021-05-23 19:52 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 |  | 2021-05-23 20:04 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV line-2 |  | 2021-05-23 20:01 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV line-2 |  | 2021-05-24 07:08 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj(S)- Ashuganj 230 kV line-1 |  | 2021-05-24 13:46 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132 kV line-1 |  | 2021-05-28 10:08 |  | S/O | After maintenance | 0 | 0 | No interruption
Chandpur S/S | Chandpur S/S-Chandpur desh 132 kV |  | 2021-05-28 20:48 |  | S/O | After maintenance | 0 | 0 | No interruption
|  |  | Total : | 40:38 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Jashore | Jashore-Jhenaidah 132 kV line-1 | 2021-05-01 07:17 | 2021-05-01 07:17 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV line-2 | 2021-05-02 07:19 | 2021-05-02 07:19 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | Payra-Gopalganj 400 kV line | 2021-05-02 10:23 | 2021-05-02 12:39 | 2:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | Gopalganj(N)-Madaripur 132 kV line-1 | 2021-05-08 08:15 | 2021-05-08 11:14 | 2:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj(N)-Madaripur 132 kV line-2 | 2021-05-09 07:19 | 2021-05-09 07:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | Goalpara-Khulna 225 MW 132 kV line | 2021-05-19 11:02 | 2021-05-19 12:55 | 1:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna(s) | Khulna(s)-Satkhira 132 kV line-1 | 2021-05-19 10:36 | 2021-05-19 12:43 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal | Barishal-Madaripur 132 kV line-1 | 2021-05-26 09:03 | 2021-05-26 10:07 | 1:04 | S/O | Due to OPGW shifting work. | 0 | 0 | No interruption
Benapole | Benapole-Jashore 132 kV line-2 | 2021-05-27 08:15 | 2021-05-27 15:23 | 7:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | Benapole-Jashore 132 kV line-1 | 2021-05-28 08:57 | 2021-05-28 16:37 | 7:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line-1 | 2021-05-28 10:45 | 2021-05-28 16:19 | 5:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line-1 | 2021-05-29 11:44 | 2021-05-29 11:53 | 0:09 | S/O | Due to protection test. | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line-2 | 2021-05-29 13:14 | 2021-05-29 13:17 | 0:03 | S/O | Due to protection test. | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-1 | 2021-05-30 15:30 | 2021-05-30 16:16 | 0:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-2 | 2021-05-30 16:27 | 2021-05-30 17:06 | 0:39 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 32:18 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0:00
Bogura Grid Circle :
Bagura | Bagura-Sherpur 132 kV line -2 | 2021-05-01 08:01 | 2021-05-01 17:52 | 9:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -2 | 2021-05-02 09:10 | 2021-05-02 16:19 | 7:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -2 | 2021-05-02 09:01 | 2021-05-02 18:10 | 9:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -1 | 2021-05-05 08:20 | 2021-05-05 18:09 | 9:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -2 | 2021-05-05 08:30 | 2021-05-05 18:14 | 9:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(New) | Rajshahi(New)-Rajshahi(Old) 132 kV line -2 |  | 2021-05-05 18:14 |  | S/O | After maintenance | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -1,2 | 2021-05-06 09:13 | 2021-05-06 17:58 | 8:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Sirajganj 230 kV S/S | Sirajganj unit-4 P/P-Sirajganj 230 kV S/S 230 kV line | 2021-05-07 08:47 | 2021-05-07 13:20 | 4:33 | S/O | Due to bay maintenance | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura 230 kV line -2 | 2021-05-09 09:48 | 2021-05-09 11:28 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | B.Pukuria-Saidpur 132 kV line -2 | 2021-05-22 07:44 | 2021-05-22 07:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur-Thakurgaon 132 kV line-1 | 2021-05-24 05:56 | 2021-05-24 05:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Rajlanka 132 kV line -1 | 2021-05-24 12:03 | 2021-05-24 13:50 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Purbasadipur 132 kV line -1 | 2021-05-27 05:21 | 2021-05-27 05:21 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | Thakurgaon-Purbasadipur 132 kV line -2 |  | 2021-05-27 22:48 |  | S/O | After maintenance | 0 | 0 | No interruption
Thakurgaon | Thakurgaon PP-Thakurgaon S/S 132 kV line -2 |  | 2021-05-27 22:48 |  | S/O | After maintenance | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi(old) 132 kV line -1 | 2021-05-31 12:53 | 2021-05-31 13:08 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi(old) 132 kV line -2 | 2021-05-31 13:11 | 2021-05-31 13:39 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Amnura 132 kV line | 2021-05-31 14:38 | 2021-05-31 14:54 | 0:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Chapainawabganj 132 kV line | 2021-05-31 14:57 | 2021-05-31 15:28 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 63:57 |  | Unserved Energy: |  | 0
Others :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 390:12 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May 2021
| Area | Previous Month (April' 2021) |  |  |  | Current Month (May' 2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 26 | 9 | 82 | 117 | 36 | 19 | 66 | 121
2 | Dhaka (South) Grid Circle. | 10 | 3 | 13 | 26 | 17 | 6 | 27 | 50
3 | Chattogram Grid Circle. | 12 | 3 | 43 | 58 | 12 | 2 | 31 | 45
4 | Cumilla Grid Circle. | 28 | 13 | 49 | 90 | 44 | 3 | 32 | 79
5 | Khulna Grid Circle. | 6 | 6 | 45 | 57 | 23 | 16 | 29 | 68
6 | HVDC Grid Circle | 2 | 0 | 10 | 12 | 1 | 0 | 2 | 3
7 | Bogura Grid Circle. | 28 | 24 | 52 | 104 | 31 | 16 | 54 | 101
8 | Others |  |  |  | 0 |  |  |  | 0
9 | Total | 112 | 58 | 294 | 464 | 164 | 62 | 241 | 467
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May 2021
| Area | Previous Month (April 2021) |  |  |  | Current Month (May' 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 116.97 | 112.83 | 1016.2333 | 1246.0333 | 5769.34 | 183.08 | 3297.68 | 9250.1
2 | Dhaka (South) Grid Circle. | 46.33 | 56.1667 | 0 | 102.4967 | 33.67 | 0 | 58.43 | 92.1
3 | Chattogram Grid Circle. | 23.42 | 16 | 191.74 | 231.16 | 185.26 | 58 | 0 | 243.26
4 | Cumilla Grid Circle. | 182.87 | 164.83 | 21 | 368.7 | 1205.9 | 51 | 0 | 1256.9
5 | Khulna Grid Circle. | 37.9 | 321.28 | 111.15 | 470.33 | 69.14 | 193.17 | 89.4 | 351.71
6 | HVDC Grid Circle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Bogura Grid Circle. | 147.09 | 359.48 | 651.2822 | 1157.8522 | 38.25 | 126.59 | 616.22 | 781.06
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 554.58 | 1030.5867 | 1991.4056 | 3576.5722 | 7301.56 | 611.84 | 4061.73 | 11975.13
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 16 | 10 | 26 | 7 | 5 | 14 | 9250.1
2 | Dhaka (South) | 5031.6 | 1 | 2 | 3 | 1 | 0 | 2 | 70.1
3 | Chattogram | 2042 | 4 | 0 | 4 | 3 | 0 | 1 | 121.93
4 | Khulna | 2434 | 8 | 1 | 9 | 5 | 2 | 2 | 304.03
5 | HVDC | 5954.3 | - | - | - | - | - | - | 0
6 | Bogura | 3145.6 | 5 | 8 | 13 | 2 | - | 11 | 756.14
7 | Cumilla | 2981 | 8 | 0 | 8 | 4 | 2 | 2 | 974.17
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 11476.47
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.66%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.91%
4 | Khulna | 99.51%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.59% | [6 empty] | Information Management Division
7 | Cumilla | 99.95% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | - | - | - | - | - | - | -
2 | Dhaka (South) | 990.29 |  | 1 | - | 1 | - | 1 | - | 22
3 | Chattogram | 917 | - | 1 | - | 1 | 1 | - | - | 121.34
4 | Khulna | 1238.4 | - | 2 | - | 2 | 1 | - | 1 | 47.6667 | -
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | - | 1 | 1 | - | - | 24.92
7 | Cumilla | 1648.16 | - | 4 | - | 4 | 1 | 1 | 2 | 282.7333
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 498.66
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.6%
2 | Dhaka (South) | 99.87%
3 | Chattogram | 99.97%
4 | Khulna | 99.85%
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 99.81% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-05-18 | 46 | - | 17 | 18hr22 min |  |  | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Sreenagar | 2 | 0:40 | 38 | 25.3333 | Due to tripping of 132/33 kV Transformers- T2
|  | 1:20 | 15 | 20 | Due to red-hot maintenance of 132/33 kV Trasformer T1
Lalbag | 1 | 0:43 | 80 | 57.3333 | Due to tripping of 132/33 kV Transformers- T1
Kishoreganj | 4 | 0:17 | 10 | 2.8333 | Due to flashing at 33 kV feeder
|  | 0:10 | 82 | 13.6667 | Due to 33 kV feeder fault
|  | 0:12 | 90 | 18 | Due to tripping of 132/33 kV Transformers-T1, T2
|  | 0:30 | 60 | 30 | Due to tripping of 132/33 kV Transformers-T3, T4
Joydevpur | 3 | 0:55 | 25 | 22.9167 | Due to tripping of 132/33 kV Transformers- T2
|  | 0:54 | 5 | 4.5 | Due to S/D of 132/33 kV Transformer GT2
|  | 1:20 | 13 | 17.3333 | Due to S/D of 132/33 kV Transformer T2
Jamalpur | 1 | 1:37 | 5 | 8.0833 | Due to red-hot maintenance of 132/33 kV Trasformer T1 with 33 kV bus
Tongi | 1 | 0:05 | 40 | 3.3333 | Due to 33 kV feeder fault
Kabirpur | 3 | 1:50 | 20 | 36.6667 | Due to 33 kV EPZ feeder fault
|  | 1:39 | 70 | 115.5 | Due to red-hot maintenance of 132/33 kV Trasformer T2
|  | 2:40 | 30 | 80 | Due to S/D of 132/33 kV Transformer T3
Tangail | 3 | 0:14 | 119 | 27.7667 | Due to tripping of 132/33 kV Transformers-T1, T2
|  | 0:05 | 40 | 3.3333 | Due to tripping of 132/33 kV Transformers-T2
|  | 13:07 | 35 | 459.0833 | Due to S/D of 132/33 kV Transformer T1
Kodda | 3 | 25:15 | 220 | 5555 | Due to fire at 33 kV laltir feeder
|  | 11:05 | 60 | 665 | Due to replacing 33 kV Bus isolator.
|  | 10:24 | 105 | 1092 | Due to S/D of 132/33 kV Transformer T3, T4
Cantonment | 1 | 0:33 | 23 | 12.65 | Due to tripping of 132/33 kV Transformers- T1
Bhulta | 1 | 1:49 | 137 | 248.8833 | Due to S/D of 132 kV Bus
Munshiganj | 1 | 2:45 | 15 | 41.25 | Due to S/D of 132/33 kV Transformer T1 and 33 kV Bus -1
Savar | 1 | 8:58 | 61 | 546.9667 | Due to S/D of 132/33 kV Transformer T3
Sherpur | 1 | 7:08 | 20 | 142.6667 | Due to S/D of 132/33 kV Transformer T1 with 33 kV bus
Narshingdi | 1 | 0:28 | 25 | 11.6667 | Due to tripping of 132/33 kV Transformers-T2
Shyampur(N) | 1 | 0:33 | 40 | 22 | Due to tripping of Shyampur(N)-Shyampur(O) 132 kV line-1
Nawabganj | 1 | 1:20 | 26 | 34.6667 | Due to 132/33 kV Transformer-T1 along with 33 kV Bus-1
Sonargaon | 1 | 1:02 | 23 | 23.7667 | Due to S/D of 132/33 kV Transformer T2
Chowmuhani | 2 | 0:09 | 120 | 18 | Due to 33 kV CB burst of PBS feeder
|  | 1:27 | 40 | 58 | Due to red-hot maintenance of 132/33 kV Transformer T2
Cox's Bazar | 1 | 0:14 | 40 | 9.3333 | Due to 33 kV feeder fault
Sikalbaha | 2 | 0:09 | 244 | 36.6 | Due to tripping of Sikalbaha 230 kV bus
|  | 0:20 | 364 | 121.3333 | Due to tripping of Sikalbaha-Madunaghat 132 kV line
Cumilla(S) | 2 | 1:42 | 30 | 51 | Due to red-hot maint at 33 kV Laksham feeder
|  | 1:18 | 170 | 221 | Due to Cumilla(S)-Tripura 132 kV both line-1,2
Sreemangal | 1 | 0:14 | 18 | 4.2 | Due to tripping of 132/33 kV transformers T-1 & T-2
B.Baria | 3 | 0:41 | 116 | 79.2667 | Due to tripping of 132/33 kV transformers T-1, T2 & T-3
|  | 0:52 | 120 | 104 | Due to tripping of 132/33 kV transformers T-1, T2 & T-3
|  | 0:24 | 145 | 58 | Due to tripping of 132/33 kV transformers T-1, T2
Sylhet | 1 | 0:27 | 56 | 25.2 | Due to tripping of 132/33 kV transformers T-2
Ashuganj | 1 | 2:36 | 250 | 650 | Due to Ashuganj U-5 OAT-3 R-phase CT burst
Sunamganj | 1 | 0:39 | 23 | 14.95 | Due to tripping of Chattak-Sunamganj 132 kV line
Chatak | 2 | 0:30 | 5 | 2.5 | Due to tripping of 132/33 kV transformers T-3
|  | 5:01 | 9 | 45.15 | Due to tripping of Sylhet-Chattak 132 kV line-1
Fenchuganj | 1 | 0:14 | 7 | 1.6333 | Due to tripping of Fenchuganj-Beanibazar-Sylhet 132 kV line
Bottail | 1 | 0:15 | 40 | 10 | Due to 33 kV PBS feeder fault showing O/C,E/F
Noapara | 1 | 0:29 | 6 | 2.9 | Due to to 33 kV REB-1 feeder DS flashing
Bagerhat | 3 | 0:16 | 43 | 11.4667 | Due to tripping of 132/33 kV transformers T-1 & T-2
|  | 1:10 | 30 | 35 | Due to tripping of Bagerhat-Orion Rupsha 132 kV line
|  | 0:19 | 40 | 12.6667 | Due to tripping of Bagerhat-Goalpara 132 kV line
Gopalganj (Old) | 2 | 1:00 | 18 | 18 | Due to red-hot maintenance of transformers T-1
|  | 0:18 | 10 | 3 | Due to red-hot maintenance of transformers T-1
Patuakhali | 1 | 0:48 | 8 | 6.4 | Due to red-hot maintenance of transformers T-1
Bheramara | 1 | 0:10 | 25 | 4.1667 | Due to winding temperature high of transformers T-3
Barisal(N) | 1 | 3:27 | 46 | 158.7 | Due to red-hot maintenance of transformers T-5
Magura | 1 | 4:58 | 18 | 89.4 | Due to S/D of 132/33 kV Transformers-T2
Sherpur(Bogura) | 2 | 1:15 | 10 | 12.5 | Due to red-hot maint at 33 kV Vabanipur PBS feeder
|  | 1:29 | 35 | 51.9167 | Due to red-hot maint at 33 kV Bus sectionalizer
Rangpur | 3 | 1:08 | 50 | 56.6667 | Due to red-hot maintenance
|  | 10:12 | 25 | 255.01 | Due to S/D of 132/33 kV Transformers-T1 and 33 kV Bus-1
|  | 0:17 | 20 | 5.6667 | Due to S/D of 132/33 kV Transformers-T1
Naogaon | 1 | 0:20 | 40 | 13.34 | Due to 33 kV PBS feeder fault
Saidpur | 1 | 1:06 | 5 | 5.5 | Due to red-hot maintenance of transformers T2
Purbasadipur | 1 | 0:13 | 115 | 24.9167 | Due to tripping of Purbasadipur-Thakurgaon 132 kV line -1
Jaldhaka | 1 | 3:47 | 10 | 37.8333 | Due to S/D of 132/33 kV transformers T-2
Bogura | 2 | 1:14 | 52 | 64.1333 | Due to S/D of 132/33 kV transformers T-1
|  | 1:03 | 45 | 47.25 | Due to S/D of 132/33 kV Transformers-T1 and its 33 kV Bus
Barapukuria | 1 | 2:20 | 25 | 58.3333 | Due to S/D of 132/33 kV Transformers-T3
Rajshahi | 1 | 1:28 | 90 | 132 | Due to S/D of 132 kV full Bus
Shahjadpur | 1 | 1:20 | 12 | 16 | Due to S/D of 132/33 kV transformers T-2
| Total Unserved energy : |  |  | 11975.1333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:May'2021
Sl. No | Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 128 | 2 | 2021-05-01 | 12:00
2 | Munsiganj | 120 | 5 | 2021-05-01 | 21:00
3 | Sonargaon | 82 | 29 | 2021-05-01 | 12:00
4 | Shyampur | 228 | 4 | 2021-05-01 | 10:00
5 | Bhulta | 213 | 30 | 2021-05-01 | 16:00
6 | Madanganj | 62 | 6 | 2021-05-01 | 0:00
7 | Shitalakhya | 123 | 3 | 2021-05-01 | 15:00
8 | Rahim steel | 36 | 9 | 2021-05-01 | 13:00
9 | Matuail | 92 | 28 | 2021-05-01 | 1:00
10 | Ghorasal | 82 | 22 | 2021-05-01 | 22:00
11 | Narsingdi | 183 | 30 | 2021-05-01 | 19:30
12 | Haripur (SBU) | 122 | 27 | 2021-05-01 | 11:00
13 | Sreenagar | 48 | 22 | 2021-05-01 | 22:00
14 | Ullon | 82 | 23 | 2021-05-01 | 24:00
15 | Hasnabad | 89 | 22 | 2021-05-01 | 22:00
16 | Magbazar | 114 | 23 | 2021-05-01 | 15:00
17 | Maniknagar | 90 | 1 | 2021-05-01 | 1:00
18 | Bangabhaban | 188 | 16 | 2021-05-01 | 11:00
19 | Motijheel | 26 | 30 | 2021-05-01 | 11:00
20 | Narinda | 80 | 2 | 2021-05-01 | 13:00
21 | Kazla | 79 | 30 | 2021-05-01 | 15:00
22 | Dhanmondi | 232 | 24 | 2021-05-01 | 13:00
23 | Lalbag | 93 | 30 | 2021-05-01 | 13:00
24 | Madartek | 86 | 23 | 2021-05-01 | 23:00
25 | Dhaka University | 52 | 24 | 2021-05-01 | 13:00
26 | Aftabnagar | 12 | 22 | 2021-05-01 | 23:00
27 | Fatullah | 66 | 31 | 2021-05-01 | 10:00
28 | Nawabganj | 58 | 2 | 2021-05-01 | 21:00
29 | Keraniganj | 76 | 2 | 2021-05-01 | 21:00
30 | Mirpur | 134 | 24 | 2021-05-01 | 19:00
31 | Kalyanpur | 137 | 19 | 2021-05-01 | 20:00
32 | Gulshan | 174 | 24 | 2021-05-01 | 15:00
33 | Uttara | 109 | 23 | 2021-05-01 | 11:00
34 | Uttara(new) | 36 | 24 | 2021-05-01 | 13:00
35 | Kamrangirchar | 93 | 30 | 2021-05-01 | 19:00
36 | Savar | 191 | 29 | 2021-05-01 | 19:00
37 | Bhasantec | 184 | 24 | 2021-05-01 | 13:00
38 | Agargaon | 93 | 24 | 2021-05-01 | 13:00
39 | Satmosjid | 112 | 24 | 2021-05-01 | 19:30
40 | Tongi | 134 | 25 | 2021-05-01 | 12:00
41 | Kabirpur | 293 | 22 | 2021-05-01 | 19:00
42 | Basundhara | 202 | 24 | 2021-05-01 | 17:00
43 | Manikganj | 88 | 22 | 2021-05-01 | 21:00
44 | Joydevpur | 198 | 23 | 2021-05-01 | 15:00
45 | New Tongi | 113 | 29 | 2021-05-01 | 15:00
46 | Kodda | 295 | 25 | 2021-05-01 | 16:00
47 | Dhamrai | 128 | 29 | 2021-05-01 | 15:00
48 | Rajendrapur | 114 | 29 | 2021-05-01 | 16:00
49 | Valuka | 134 | 30 | 2021-05-01 | 17:00
50 | Tangail | 233 | 29 | 2021-05-01 | 21:00
51 | Mymensing | 232 | 24 | 2021-05-01 | 23:00
52 | Kishorganj | 140 | 12 | 2021-05-01 | 21:00
53 | Netrokona | 130 | 24 | 2021-05-01 | 20:00
54 | Jamalpur | 163 | 23 | 2021-05-01 | 19:30
55 | Sherpur | 140 | 23 | 2021-05-01 | 22:00
56 | Srimongal | 65 | 23 | 2021-05-01 | 21:00
57 | Shahjibazar | 135 | 23 | 2021-05-01 | 22:00
58 | Fenchuganj | 53 | 23 | 2021-05-01 | 19:30
59 | Kulawara | 50 | 23 | 2021-05-01 | 20:00
60 | Sylhet | 140 | 25 | 2021-05-01 | 20:00
61 | Chatak | 34 | 29 | 2021-05-01 | 20:00
62 | Sunamganj | 55 | 30 | 2021-05-01 | 22:00
63 | Bianibazar | 80 | 23 | 2021-05-01 | 22:00
64 | Cumilla (S) | 178 | 22 | 2021-05-01 | 19:00
65 | Cumilla(N) | 157 | 23 | 2021-05-01 | 19:30
66 | Chandpur | 91 | 21 | 2021-05-01 | 22:00
67 | Feni | 148 | 22 | 2021-05-01 | 22:00
68 | Chowmuhani | 212 | 30 | 2021-05-01 | 22:00
69 | Ashuganj | 52 | 24 | 2021-05-01 | 11:00
70 | Daudkandi | 172 | 23 | 2021-05-01 | 21:00
71 | B.Baria | 168 | 21 | 2021-05-01 | 22:00
72 | Ramganj | 116 | 22 | 2021-05-01 | 22:00
73 | Chaddagram | 54 | 23 | 2021-05-01 | 19:00
74 | PHP | 11 | 5 | 2021-05-01 | 19:00
75 | Kochua | 78 | 23 | 2021-05-01 | 21:00
76 | Madanhat | 84 | 29 | 2021-05-01 | 1:00
77 | Hathazari | 100 | 22 | 2021-05-01 | 21:00
78 | Khulshi | 222 | 19 | 2021-05-01 | 16:00
79 | Halishahar | 155 | 23 | 2021-05-01 | 14:00
80 | Baraulia | 167 | 30 | 2021-05-01 | 0:00
81 | Sikalbaha | 41 | 30 | 2021-05-01 | 16:00
82 | Dohazari | 110 | 27 | 2021-05-01 | 22:00
83 | Cox'sbazar | 111 | 3 | 2021-05-01 | 21:00
84 | Chandraghona | 34 | 2 | 2021-05-01 | 20:00
85 | Kaptai | 5 | 21 | 2021-05-01 | 6:00
86 | A. Khaer Stl. | 0 | 1 | 2021-05-01 | 1:00
87 | Bakulia | 118 | 24 | 2021-05-01 | 19:30
88 | Julda | 24 | 3 | 2021-05-01 | 3:00
89 | TK chemical | 31.5 | 2 | 2021-05-01 | 22:00
90 | Modern Steel | 0 | 1 | 2021-05-01 | #N/A
91 | Shahmirpur | 28 | 8 | 2021-05-01 | 0:00
92 | Khagrachhari | 30 | 22 | 2021-05-01 | 21:00
93 | Matarbari | 46 | 22 | 2021-05-01 | 20:00
94 | Baroiar Hat | 50 | 19 | 2021-05-01 | 22:00
95 | Rangamati | 14 | 22 | 2021-05-01 | 19:30
96 | Abul Khair 230 | 165 | 1 | 2021-05-01 | 22:00
97 | BSRM | 159 | 8 | 2021-05-01 | 19:00
98 | GPH Ispat | 95 | 23 | 2021-05-01 | 17:00
99 | Agrabad | 0 | 0 | 2021-05-01 | 0:00
100 | Goalpara | 36 | 3 | 2021-05-01 | 22:00
101 | Khulna Central s/s | 105 | 1 | 2021-05-01 | 20:00
102 | Noapara | 68 | 6 | 2021-05-01 | 20:00
103 | Jashore | 131 | 23 | 2021-05-01 | 22:00
104 | Benapol | 70 | 23 | 2021-05-01 | 22:00
105 | Jhenidah | 119 | 23 | 2021-05-01 | 20:00
106 | Bottail | 148 | 19 | 2021-05-01 | 19:30
107 | G.K Project | 64 | 23 | 2021-05-01 | 21:00
108 | Faridpur | 220 | 23 | 2021-05-01 | 22:00
109 | Madaripur | 129 | 23 | 2021-05-01 | 22:00
110 | Sariatpur | 84 | 23 | 2021-05-01 | 22:00
111 | Gopalganj | 108 | 23 | 2021-05-01 | 22:00
112 | Bagerhat | 119 | 22 | 2021-05-01 | 22:00
113 | Mongla | 44 | 29 | 2021-05-01 | 16:00
114 | Satkhira | 132 | 18 | 2021-05-01 | 22:00
115 | Gallamari | 46 | 23 | 2021-05-01 | 13:00
116 | Magura | 125 | 22 | 2021-05-01 | 19:00
117 | Norail | 49 | 20 | 2021-05-01 | 20:00
118 | Chuadanga | 97 | 23 | 2021-05-01 | 19:30
119 | Borguna | 22 | 19 | 2021-05-01 | 22:00
120 | Barsal(N) | 56 | 23 | 2021-05-01 | 23:00
121 | Barsal(S) | 128 | 23 | 2021-05-01 | 22:00
122 | Patuakhali | 137 | 19 | 2021-05-01 | 22:00
123 | Bhandaria | 62 | 17 | 2021-05-01 | 22:00
124 | Borhan Uddin | 49 | 29 | 2021-05-01 | 0:00
125 | Ishurdi | 71 | 22 | 2021-05-01 | 21:00
126 | Ruppur Paromanobik | 4 | 4 | 2021-05-01 | 10:00
127 | Natore | 160 | 23 | 2021-05-01 | 21:00
128 | Bogura | 167 | 3 | 2021-05-01 | 21:00
129 | Naogaon | 133 | 3 | 2021-05-01 | 21:00
130 | Rajshahi | 166 | 19 | 2021-05-01 | 21:00
131 | Rajshahi New | 24 | 29 | 2021-05-01 | 21:00
132 | C.Nawabganj | 80 | 19 | 2021-05-01 | 21:00
133 | Amnura | 54 | 19 | 2021-05-01 | 21:00
134 | Pabna | 112 | 29 | 2021-05-01 | 20:00
135 | Shahjadpur | 107 | 23 | 2021-05-01 | 21:00
136 | Serajganj | 102 | 23 | 2021-05-01 | 21:00
137 | Niyamatpur | 86 | 24 | 2021-05-01 | 1:00
138 | Joypurhat | 66 | 23 | 2021-05-01 | 21:00
139 | Sherpur(Bogura) | 64 | 23 | 2021-05-01 | 21:00
140 | Mohastangar | 78 | 22 | 2021-05-01 | 21:00
141 | Bangura | 40 | 23 | 2021-05-01 | 20:00
142 | Rangpur | 144 | 25 | 2021-05-01 | 20:00
143 | Lalmonirhat | 46 | 19 | 2021-05-01 | 19:30
144 | Saidpur | 110 | 24 | 2021-05-01 | 21:00
145 | Purbasadipur | 117 | 23 | 2021-05-01 | 19:30
146 | Thakurgaon | 86 | 18 | 2021-05-01 | 21:00
147 | Palshbari | 124 | 25 | 2021-05-01 | 20:00
148 | Barapukuria | 59 | 23 | 2021-05-01 | 21:00
149 | Panchugar | 56 | 30 | 2021-05-01 | 20:00
150 | Joldhaka | 66 | 19 | 2021-05-01 | 20:00
151 | Kurigram | 62 | 23 | 2021-05-01 | 19:00
152 | Mitha Pukur | 48 | 29 | 2021-05-01 | 21:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:May 2021
Area | MW | Date | Hour | Remarks
Dhaka | 4747 | 23.05.2021 | 15:00
Chattogram | 1474 | 08.05.2021 | 23:00
Khulna | 1800 | 26.05.2021 | 18:00
Rajshahi | 1403 | 23.05.2021 | 21:00
Cumilla | 1354 | 22.05.2021 | 24:00
Mymensingh | 1063 | 03.05.2021 | 21:00
Sylhet | 580 | 23.05.2021 | 22:00
Barisal | 435 | 19.05.2021 | 22:00
Rangpur | 845 | 24.05.2021 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May'2021
SL. | Substation Name | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 409 | 18 | 2021-05-01 | 17:00 | 393 | 30 | 2021-05-01 | 12:00
2 | Bheramara | 400 | 407 | 4 | 2021-05-01 | 4:00 | 383 | 23 | 2021-05-01 | 24:00
3 | Ashuganj(N) | 400 | 394 | 18 | 2021-05-01 | 17:00 | 367 | 5 | 2021-05-01 | 10:00
4 | Payra | 400 | 416 | 3 | 2021-05-01 | 19:00 | 0 | 2 | 2021-05-01 | 1:00
5 | Kaliakoir | 400 | 403 | 15 | 2021-05-01 | 18:30 | 283 | 11 | 2021-05-01 | 1:00
6 | Bhulta | 400 | 389 | 15 | 2021-05-01 | 15:00 | 357 | 6 | 2021-05-01 | 11:00
7 | Gopalganj | 400 | 411 | 11 | 2021-05-01 | 15:00 | 0 | 2 | 2021-05-01 | 22:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 235 | 26 | 2021-05-01 | 21:00 | 220 | 8 | 2021-05-01 | 9:00
2 | Ishurdi | 230 | 236 | 15 | 2021-05-01 | 4:00 | 220 | 17 | 2021-05-01 | 19:00
3 | Ashuganj | 230 | 240 | 2 | 2021-05-01 | 22:00 | 0 | 23 | 2021-05-01 | 19:30
4 | Serajganj | 230 | 235 | 1 | 2021-05-01 | 7:00 | 0 | 23 | 2021-05-01 | 19:30
5 | Baghabari | 230 | 235 | 12 | 2021-05-01 | 6:00 | 224 | 23 | 2021-05-01 | 1:00
6 | Barapukuria | 230 | 239 | 25 | 2021-05-01 | 5:00 | 222 | 19 | 2021-05-01 | 19:30
7 | Bogura | 230 | 232 | 7 | 2021-05-01 | 7:00 | 25 | 7 | 2021-05-01 | 10:00
8 | Rajshahi | 230 | 237 | 2 | 2021-05-01 | 18:30 | 218 | 2 | 2021-05-01 | 13:00
9 | Khulna South | 230 | 233 | 27 | 2021-05-01 | 4:00 | 203 | 20 | 2021-05-01 | 14:00
10 | Rampura | 230 | 233 | 16 | 2021-05-01 | 14:00 | 214 | 5 | 2021-05-01 | 11:00
11 | Haripur | 230 | 232 | 24 | 2021-05-01 | 22:00 | 210 | 31 | 2021-05-01 | 10:00
12 | Hasnabad | 230 | 232 | 14 | 2021-05-01 | 6:00 | 210 | 5 | 2021-05-01 | 9:00
13 | Shyampur | 230 | 229 | 4 | 2021-05-01 | 21:00 | 220 | 1 | 2021-05-01 | 11:00
14 | Aminbazar | 230 | 231 | 24 | 2021-05-01 | 1:00 | 209 | 2 | 2021-05-01 | 2:00
15 | Tongi | 230 | 228 | 2 | 2021-05-01 | 23:00 | 207 | 2 | 2021-05-01 | 9:00
16 | Comilla (N) | 230 | 230 | 31 | 2021-05-01 | 22:00 | 214 | 5 | 2021-05-01 | 11:00
17 | Hathazari | 230 | 224 | 24 | 2021-05-01 | 19:00 | 190 | 24 | 2021-05-01 | 13:00
18 | Megnaghat | 230 | 236 | 15 | 2021-05-01 | 14:00 | 30 | 13 | 2021-05-01 | 17:00
19 | Fenchuganj | 230 | 242 | 18 | 2021-05-01 | 17:00 | 232 | 7 | 2021-05-01 | 17:00
20 | Siddhirganj | 230 | 233 | 15 | 2021-05-01 | 15:00 | 213 | 31 | 2021-05-01 | 10:00
21 | Maniknagar | 230 | 232 | 24 | 2021-05-01 | 22:00 | 212 | 5 | 2021-05-01 | 11:00
22 | Old Airport | 230 | 234 | 18 | 2021-05-01 | 18:00 | 207 | 2 | 2021-05-01 | 9:00
23 | Barisal | 230 | 251 | 23 | 2021-05-01 | 2:00 | 229 | 2 | 2021-05-01 | 22:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-05-01 | 3:00 | 230 | 5 | 2021-05-01 | 18:00
25 | AKSML | 230 | 226 | 24 | 2021-05-01 | 21:00 | 200 | 24 | 2021-05-01 | 14:00
26 | BSRM | 230 | 226 | 24 | 2021-05-01 | 19:30 | 204 | 24 | 2021-05-01 | 15:00
27 | Bibiyana | 230 | 242 | 18 | 2021-05-01 | 17:00 | 231 | 15 | 2021-05-01 | 12:00
28 | Bhulta | 230 | 235 | 2 | 2021-05-01 | 21:00 | 214 | 5 | 2021-05-01 | 11:00
29 | Ashuganj (S) | 230 | 232 | 9 | 2021-05-01 | 3:00 | 222 | 2 | 2021-05-01 | 9:00
30 | Kaliakoir | 230 | 232 | 18 | 2021-05-01 | 17:00 | 209 | 6 | 2021-05-01 | 11:00
31 | GPH | 230 | 231 | 6 | 2021-05-01 | 13:00 | 198 | 24 | 2021-05-01 | 15:00
132 kV Substations
1 | Siddhirganj | 132 | 140 | 24 | 2021-05-01 | 0.91667 | 122 | 30 | 2021-05-01 | 0.45833
2 | Munsiganj | 132 | 142 | 24 | 2021-05-01 | 0.91667 | 121 | 30 | 2021-05-01 | 0.45833
3 | Sonargaon | 132 | 140 | 2 | 2021-05-01 | 0.95833 | 122 | 31 | 2021-05-01 | 0.41667
4 | Shyampur | 132 | 139 | 2 | 2021-05-01 | 0.95833 | 129 | 10 | 2021-05-01 | 0.41667
5 | Bhulta | 132 | 136 | 2 | 2021-05-01 | 0.95833 | 114 | 30 | 2021-05-01 | 0.45833
6 | Madanganj | 132 | 140 | 24 | 2021-05-01 | 0.91667 | 119 | 31 | 2021-05-01 | 0.41667
7 | Shitalakhya | 132 | 143 | 24 | 2021-05-01 | 0.91667 | 102 | 4 | 2021-05-01 | 0.70833
8 | Rahim Steal | 132 | 140 | 24 | 2021-05-01 | 0.91667 | 120 | 31 | 2021-05-01 | 0.41667
9 | Matuail | 132 | 140 | 24 | 2021-05-01 | 0.91667 | 122 | 30 | 2021-05-01 | 0.45833
10 | Ghorasal | 132 | 142 | 18 | 2021-05-01 | 0.70833 | 130 | 8 | 2021-05-01 | 0.54167
11 | Narsinghdi | 132 | 139 | 18 | 2021-05-01 | 0.66667 | 123 | 21 | 2021-05-01 | 0.91667
12 | Haripur (SBU) | 132 | 140 | 24 | 2021-05-01 | 0.91667 | 121 | 31 | 2021-05-01 | 0.41667
13 | Sreenagar | 132 | 0 | 0 | 2021-05-01 | 0 | 0 | 0 | 2021-05-01 | 0
14 | Ullon | 132 | 137 | 11 | 2021-05-01 | 0.25 | 123 | 8 | 2021-05-01 | 0.58333
15 | Hasnabad | 132 | 140 | 15 | 2021-05-01 | 0.625 | 124 | 5 | 2021-05-01 | 0.45833
16 | Magbazar | 132 | 137 | 24 | 2021-05-01 | 0.91667 | 121 | 24 | 2021-05-01 | 0.45833
17 | Maniknagar | 132 | 139 | 2 | 2021-05-01 | 0.91667 | 125 | 2 | 2021-05-01 | 0.5
18 | Bangabhaban | 132 | 139 | 2 | 2021-05-01 | 0.91667 | 125 | 2 | 2021-05-01 | 0.5
19 | Motijheel | 132 | 0 | 0 | 2021-05-01 | 0 | 0 | 0 | 2021-05-01 | 0
20 | Narinda | 132 | 139 | 2 | 2021-05-01 | 0.91667 | 125 | 2 | 2021-05-01 | 0.5
21 | Kazla | 132 | 0 | 0 | 2021-05-01 | 0 | 0 | 0 | 2021-05-01 | 0
22 | Dhanmondi | 132 | 138 | 18 | 2021-05-01 | 0.70833 | 120 | 30 | 2021-05-01 | 0.45833
23 | Lalbag | 132 | 142 | 11 | 2021-05-01 | 0.25 | 121 | 5 | 2021-05-01 | 0.45833
24 | Madartek | 132 | 138 | 24 | 2021-05-01 | 0.91667 | 122 | 24 | 2021-05-01 | 0.45833
25 | Dhaka University | 132 | 137 | 2 | 2021-05-01 | 0.91667 | 123 | 6 | 2021-05-01 | 0.45833
26 | Aftabnagar | 132 | 137 | 11 | 2021-05-01 | 0.25 | 123 | 23 | 2021-05-01 | 0.625
27 | Fatullah | 132 | 139 | 2 | 2021-05-01 | 0.95833 | 121 | 4 | 2021-05-01 | 0.25
28 | Nawabganj | 132 | 134 | 15 | 2021-05-01 | 0.77083 | 119 | 5 | 2021-05-01 | 0.5
29 | Keraniganj | 132 | 0 | 0 | 2021-05-01 | 0 | 0 | 0 | 2021-05-01 | 0
30 | Mirpur | 132 | 139 | 24 | 2021-05-01 | 0.91667 | 123 | 2 | 2021-05-01 | 0.375
31 | Kalyanpur | 132 | 139 | 15 | 2021-05-01 | 0.75 | 123 | 2 | 2021-05-01 | 0.375
32 | Gulshan | 132 | 137 | 24 | 2021-05-01 | 0.91667 | 122 | 24 | 2021-05-01 | 0.45833
33 | Uttara | 132 | 138 | 24 | 2021-05-01 | 0.91667 | 121 | 2 | 2021-05-01 | 0.375
34 | Uttara(New) | 132 | 139 | 2 | 2021-05-01 | 0.91667 | 120 | 2 | 2021-05-01 | 0.375
35 | Kamrangirchar | 132 | 140 | 11 | 2021-05-01 | 0.77083 | 121 | 31 | 2021-05-01 | 0.41667
36 | Savar | 132 | 140 | 15 | 2021-05-01 | 0.625 | 120 | 2 | 2021-05-01 | 0.375
37 | Bhasantec | 132 | 137 | 14 | 2021-05-01 | 0.33333 | 120 | 30 | 2021-05-01 | 0.45833
38 | Agargaon | 132 | 138 | 15 | 2021-05-01 | 0.20833 | 122 | 4 | 2021-05-01 | 0.41667
39 | Satmosjid | 132 | 137 | 11 | 2021-05-01 | 0.041667 | 122 | 4 | 2021-05-01 | 0.41667
40 | Tongi | 132 | 142 | 18 | 2021-05-01 | 0.70833 | 125 | 8 | 2021-05-01 | 0.5
41 | Kabirpur | 132 | 140 | 15 | 2021-05-01 | 0.70833 | 124 | 24 | 2021-05-01 | 0.625
42 | Basundhara | 132 | 139 | 15 | 2021-05-01 | 0.75 | 123 | 2 | 2021-05-01 | 0.375
43 | Manikganj | 132 | 144 | 15 | 2021-05-01 | 0.75 | 124 | 21 | 2021-05-01 | 0.75
44 | Joydevpur | 132 | 140 | 1 | 2021-05-01 | 0.77083 | 127 | 2 | 2021-05-01 | 0.375
45 | New Tongi | 132 | 142 | 18 | 2021-05-01 | 0.70833 | 124 | 8 | 2021-05-01 | 0.45833
46 | Kodda | 132 | 141 | 31 | 2021-05-01 | 0.20833 | 0 | 0 | 2021-05-01 | 1900-05-03
47 | Dhamrai | 132 | 139 | 17 | 2021-05-01 | 0.77083 | 124 | 23 | 2021-05-01 | 0.45833
48 | Rajendrapur | 132 | 140 | 4 | 2021-05-01 | 2:00 | 0 | 0 | 2021-05-01 | 0
49 | Valuka | 132 | 137 | 10 | 2021-05-01 | 0.79167 | 107 | 21 | 2021-05-01 | 0.91667
50 | Tangail | 132 | 140 | 10 | 2021-05-01 | 0.77083 | 120 | 24 | 2021-05-01 | 0.79167
51 | Mymensing | 132 | 139 | 24 | 2021-05-01 | 0 | 112 | 21 | 2021-05-01 | 0.91667
52 | Kishorganj | 132 | 138 | 10 | 2021-05-01 | 0.8125 | 111 | 23 | 2021-05-01 | 0.77083
53 | Netrokona | 132 | 139 | 24 | 2021-05-01 | 0 | 106 | 24 | 2021-05-01 | 0.875
54 | Jamalpur | 132 | 143 | 25 | 2021-05-01 | 0.8125 | 116 | 29 | 2021-05-01 | 0.875
55 | Sherpur | 132 | 140 | 7 | 2021-05-01 | 20:0 | 113 | 14 | 2021-05-01 | 0.45833
56 | Srimongal | 132 | 142 | 18 | 2021-05-01 | 0.66667 | 123 | 23 | 2021-05-01 | 0.79167
57 | Shahjibazar | 132 | 140 | 18 | 2021-05-01 | 0.625 | 120 | 23 | 2021-05-01 | 0.77083
58 | Fenchuganj | 132 | 140 | 18 | 2021-05-01 | 0.625 | 130 | 7 | 2021-05-01 | 0.70833
59 | Khulawara | 132 | 139 | 18 | 2021-05-01 | 0.66667 | 129 | 7 | 2021-05-01 | 0.70833
60 | Sylhet | 132 | 136 | 3 | 2021-05-01 | 0.25 | 116 | 7 | 2021-05-01 | 0.77083
61 | Chattak | 132 | 136 | 8 | 2021-05-01 | 0.29167 | 114 | 7 | 2021-05-01 | 0.70833
62 | Sunamganj | 132 | 136 | 3 | 2021-05-01 | 5;00 | 112 | 7 | 2021-05-01 | 0.77083
63 | Biani Bazar | 132 | 138 | 18 | 2021-05-01 | 0.29167 | 110 | 7 | 2021-05-01 | 0.79167
64 | Comilla(South) | 132 | 134 | 24 | 2021-05-01 | 0.875 | 120 | 25 | 2021-05-01 | 0.625
65 | Comilla (North) | 132 | 139 | 24 | 2021-05-01 | 0.875 | 128 | 5 | 2021-05-01 | 0.45833
66 | Chandpur | 132 | 141 | 26 | 2021-05-01 | 0.25 | 124 | 13 | 2021-05-01 | 0.54167
67 | Feni | 132 | 137 | 24 | 2021-05-01 | 0.875 | 120 | 12 | 2021-05-01 | 0.54167
68 | Chowmuhani | 132 | 137 | 4 | 2021-05-01 | 0.54167 | 112 | 14 | 2021-05-01 | 0
69 | Ashuganj | 132 | 142 | 18 | 2021-05-01 | 0.625 | 120 | 23 | 2021-05-01 | 0.77083
70 | Daudkandi | 132 | 140 | 24 | 2021-05-01 | 0.91667 | 122 | 31 | 2021-05-01 | 0.41667
71 | Brahminbaria | 132 | 139 | 18 | 2021-05-01 | 0.625 | 113 | 23 | 2021-05-01 | 0.77083
72 | Ramganj | 132 | 142 | 24 | 2021-05-01 | 0.875 | 117 | 13 | 2021-05-01 | 0.58333
73 | Chaddagram | 132 | 139 | 24 | 2021-05-01 | 0.875 | 123 | 8 | 2021-05-01 | 0.45833
74 | PHP | 132 | 136 | 24 | 2021-05-01 | 0.8125 | 118 | 20 | 2021-05-01 | 0.79167
75 | Kochua | 132 | 139 | 24 | 2021-05-01 | 0.875 | 124 | 13 | 2021-05-01 | 0.16667
76 | Madanhat | 132 | 139 | 25 | 2021-05-01 | 0.25 | 116 | 24 | 2021-05-01 | 0.58333
77 | Hathazari | 132 | 137 | 24 | 2021-05-01 | 0.79167 | 115 | 24 | 2021-05-01 | 0.54167
78 | Khulshi | 132 | 132 | 24 | 2021-05-01 | 0.8125 | 111 | 24 | 2021-05-01 | 0.58333
79 | Halishahar | 132 | 133 | 23 | 2021-05-01 | 0.875 | 110 | 24 | 2021-05-01 | 0.58333
80 | Baraulia | 132 | 134 | 24 | 2021-05-01 | 0.8125 | 106 | 22 | 2021-05-01 | 0.875
81 | Sikalbaha | 132 | 136 | 24 | 2021-05-01 | 0.75 | 118 | 24 | 2021-05-01 | 0.54167
82 | Dohazari | 132 | 135 | 23 | 2021-05-01 | 0.77083 | 112 | 24 | 2021-05-01 | 0.58333
83 | Cox'sbazar | 132 | 131 | 23 | 2021-05-01 | 0.875 | 0 | 24 | 2021-05-01 | 0.54167
84 | Chandraghona | 132 | 134 | 24 | 2021-05-01 | 0.77083 | 117 | 24 | 2021-05-01 | 0.58333
85 | Kaptai | 132 | 132 | 2 | 2021-05-01 | 0.16667 | 124 | 26 | 2021-05-01 | 0.041667
86 | A. Khaer Stl. | 132 | 131 | 1 | 2021-05-01 | 0.20833 | 116 | 24 | 2021-05-01 | 0.70833
87 | Bakulia | 132 | 137 | 24 | 2021-05-01 | 0.8125 | 103 | 30 | 2021-05-01 | 0.95833
88 | Julda | 132 | 138 | 24 | 2021-05-01 | 0.79167 | 117 | 24 | 2021-05-01 | 0.58333
89 | TK Chemical | 132 | 136 | 24 | 2021-05-01 | 0.79167 | 117 | 3 | 2021-05-01 | 0.125
90 | Modern Steel | 132 | #N/A | #N/A | 2021-05-01 | #N/A | 0 | #VALUE! | 2021-05-01 | #N/A
91 | Shahmirpur | 132 | 138 | 24 | 2021-05-01 | 0.8125 | 116 | 24 | 2021-05-01 | 0.58333
92 | Khagrachhari | 132 | 132 | 1 | 2021-05-01 | 0.16667 | 118 | 24 | 2021-05-01 | 0.8125
93 | Matarbari | 132 | 137 | 23 | 2021-05-01 | 0.875 | 105 | 20 | 2021-05-01 | 0.58333
94 | Baroiar Hat | 132 | 135 | 24 | 2021-05-01 | 0.875 | 120 | 20 | 2021-05-01 | 0.79167
95 | Rangamati | 132 | 134 | 24 | 2021-05-01 | 0.8125 | 117 | 24 | 2021-05-01 | 0.58333
96 | Agrabad | 132 | 0 | 0 | 2021-05-01 | 0 | 0 | 0 | 2021-05-01 | 0
97 | Goalpara | 132 | 140 | 9 | 2021-05-01 | 0.77083 | 120 | 6 | 2021-05-01 | 0.83333
98 | Khulna Central | 132 | 141 | 4 | 2021-05-01 | 0.77083 | 118 | 6 | 2021-05-01 | 0.83333
99 | Noapara | 132 | 138 | 4 | 2021-05-01 | 0.375 | 117 | 2 | 2021-05-01 | 0.54167
100 | Jessore | 132 | 137 | 11 | 2021-05-01 | 0.70833 | 110 | 2 | 2021-05-01 | 0.54167
101 | Benapol | 132 | 136 | 4 | 2021-05-01 | 0.375 | 109 | 2 | 2021-05-01 | 0.54167
102 | Jhenida | 132 | 134 | 3 | 2021-05-01 | 0.95833 | 104 | 23 | 2021-05-01 | 0.91667
103 | Bottail | 132 | 135 | 3 | 2021-05-01 | 0.95833 | 118 | 6 | 2021-05-01 | 0.875
104 | G.K Project | 132 | 140 | 5 | 2021-05-01 | 0.875 | 131 | 1 | 2021-05-01 | 0.875
105 | Faridpur | 132 | 140 | 15 | 2021-05-01 | 0.75 | 120 | 2 | 2021-05-01 | 0.91667
106 | Madaripur | 132 | 146 | 29 | 2021-05-01 | 0.45833 | 127 | 12 | 2021-05-01 | 0.875
107 | Sariatpur | 132 | 144 | 26 | 2021-05-01 | 0.375 | 122 | 5 | 2021-05-01 | 0.75
108 | Gopalganj | 132 | 147 | 26 | 2021-05-01 | 0.41667 | 121 | 2 | 2021-05-01 | 0.91667
109 | Bagerhat | 132 | 137 | 2 | 2021-05-01 | 0.75 | 108 | 6 | 2021-05-01 | 0.79167
110 | Mongla | 132 | 137 | 9 | 2021-05-01 | 0.77083 | 105 | 6 | 2021-05-01 | 0.79167
111 | Satkhira | 132 | 140 | 27 | 2021-05-01 | 0.16667 | 113 | 6 | 2021-05-01 | 0.83333
112 | Gallamari | 132 | 142 | 4 | 2021-05-01 | 0.77083 | 121 | 6 | 2021-05-01 | 0.79167
113 | Magura | 132 | 135 | 11 | 2021-05-01 | 0.70833 | 101 | 23 | 2021-05-01 | 0.95833
114 | Norail | 132 | 133 | 11 | 2021-05-01 | 0.70833 | 102 | 1 | 2021-05-01 | 0.875
115 | Chuadanga | 132 | 135 | 3 | 2021-05-01 | 0.95833 | 92 | 23 | 2021-05-01 | 0.91667
116 | Borguna | 132 | 142 | 26 | 2021-05-01 | 0.125 | 124 | 7 | 2021-05-01 | 0.875
117 | Barisal(N) | 132 | 142 | 9 | 2021-05-01 | 0.54167 | 127 | 20 | 2021-05-01 | 0.5
118 | Barisal(S) | 132 | 142 | 26 | 2021-05-01 | 0.20833 | 124 | 11 | 2021-05-01 | 0.083333
119 | Patuakhali | 132 | 141 | 3 | 2021-05-01 | 0.29167 | 124 | 1 | 2021-05-01 | 0.625
120 | Bhandaria | 132 | 143 | 9 | 2021-05-01 | 0.58333 | 119 | 6 | 2021-05-01 | 0.5
121 | Ishurdi | 132 | 138 | 5 | 2021-05-01 | 0.875 | 129 | 1 | 2021-05-01 | 0.875
122 | Ruppur paromanobik | 132 | 138 | 15 | 2021-05-01 | 0.70833 | 130 | 1 | 2021-05-01 | 0.54167
123 | Natore | 132 | 138 | 24 | 2021-05-01 | 0.75 | 127 | 1 | 2021-05-01 | 0.125
124 | Bogra | 132 | 139 | 20 | 2021-05-01 | 0.625 | 123 | 7 | 2021-05-01 | 0.33333
125 | Noagaon | 132 | 136 | 3 | 2021-05-01 | 0.91667 | 116 | 24 | 2021-05-01 | 0.91667
126 | Rajshahi | 132 | 136 | 5 | 2021-05-01 | 0.875 | 125 | 16 | 2021-05-01 | 0.875
127 | Rajshahi New | 132 | 138 | 2 | 2021-05-01 | 0.77083 | 125 | 2 | 2021-05-01 | 0.54167
128 | C.Nawabganj | 132 | 138 | 27 | 2021-05-01 | 0.83333 | 122 | 1 | 2021-05-01 | 1899-12-31
129 | Amnura | 132 | 141 | 24 | 2021-05-01 | 0.75 | 121 | 19 | 2021-05-01 | 0.041667
130 | Pabna | 132 | 138 | 24 | 2021-05-01 | 0.75 | 127 | 1 | 2021-05-01 | 0.91667
131 | Shahjadpur | 132 | 142 | 24 | 2021-05-01 | 0.75 | 131 | 2 | 2021-05-01 | 0.5
132 | Serajganj | 132 | 137 | 28 | 2021-05-01 | 0.625 | 125 | 2 | 2021-05-01 | 0.5
133 | Niyamatpur | 132 | 138 | 11 | 2021-05-01 | 0.25 | 113 | 23 | 2021-05-01 | 0.375
134 | Joypurhat | 132 | 140 | 11 | 2021-05-01 | 0.25 | 115 | 23 | 2021-05-01 | 0.875
135 | Sherpur(Bogura) | 132 | 138 | 2 | 2021-05-01 | 0.77083 | 124 | 5 | 2021-05-01 | 0.54167
136 | Mohastangor | 132 | 138 | 20 | 2021-05-01 | 0.625 | 123 | 19 | 2021-05-01 | 0.875
137 | Bangura | 132 | 138 | 12 | 2021-05-01 | 0.25 | 130 | 1 | 2021-05-01 | 0.54167
138 | Rangpur | 132 | 137 | 4 | 2021-05-01 | 0.041667 | 114 | 24 | 2021-05-01 | 0.91667
139 | Lalmonirhat | 132 | 137 | 7 | 2021-05-01 | 0.75 | 115 | 24 | 2021-05-01 | 0
140 | Saidpur | 132 | 136 | 3 | 2021-05-01 | 1899-12-31 | 111 | 18 | 2021-05-01 | 0.83333
141 | Purbasadipur | 132 | 136 | 22 | 2021-05-01 | 0.125 | 107 | 19 | 2021-05-01 | 0.8125
142 | Thakurgaon | 132 | 135 | 3 | 2021-05-01 | 1899-12-31 | 104 | 24 | 2021-05-01 | 0.91667
143 | Palashbari | 132 | 136 | 7 | 2021-05-01 | 0.75 | 118 | 25 | 2021-05-01 | 0.54167
144 | Barapukuria | 132 | 139 | 25 | 2021-05-01 | 0.20833 | 122 | 19 | 2021-05-01 | 0.8125
145 | Panchagar | 132 | 136 | 3 | 2021-05-01 | 1899-12-31 | 100 | 24 | 2021-05-01 | 0.95833
146 | Joldhaka | 132 | 136 | 7 | 2021-05-01 | 0.25 | 107 | 24 | 2021-05-01 | 0.91667
147 | Kurigram | 132 | 136 | 7 | 2021-05-01 | 0.75 | 110 | 22 | 2021-05-01 | 0.8125
148 | Mithapukur | 132 | 137 | 7 | 2021-05-01 | 0.75 | 118 | 24 | 2021-05-01 | 0.95833
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-36
| Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:May' 2021
Sl | Name of the sub-station | Auto transformer |  | Recorded maximum load
|  | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
1 | Keraniganj | TR1 | 300 | 77 | 219 | 2021-06-05 | 22:00
|  | TR2 | 300 | 77 | 219 | 2021-06-05 | 22:00
|  | TR3 | 300 | 55 | 158 | 2021-07-05 | 21:00
2 | Maniknagar | TR1 | 300 | 123 | 360 | 30.05.2021 | 16:00
|  | TR2 | 300 | 123 | 360 | 30.05.2021 | 16:00
3 | Ranpura | TR1 | 225 | 201 | 560 | 23/05/2021 | 15:00
|  | TR2 | 225 | 201 | 560 | 23/05/2021 | 15:00
|  | TR3 | 225 | 201 | 560 | 23/05/2021 | 15:00
4 | Haripur | TR1 | 225 | 111 | 280 | 04.05.2021 | 10:00
|  | TR2 | 225 | 111 | 280 | 04.05.2021 | 10:00
|  | TR3 | 225 | 111 | 280 | 04.05.2021 | 10:00
5 | Siddhirganj | ATR1 | 300 | 139 | 420 | 2021-05-05 | 13:00
|  | ATR2 | 300 | 139 | 420
6 | Hasnabad | TR1 | 225 | 100 | 320A | 03.05.2021 | 11:00
|  | TR2 | 225 | 100 | 320A | 03.05.2021 | 11:00
|  | TR3 | 225 | 100 | 320A | 03.05.2021 | 11:00
7 | Tongi | TR1 | 225 | 180 | 500 | 30/05/2021 | 17:00 | Parallel Operation
|  | TR2 | 225 | 180 | 500 | 30/05/2021 | 17:00
|  | TR3 | 225 | 180 | 500 | 30/05/2021 | 17:00
8 | Agargaon | TR1 | 300 | 190 | 562 | 24.05.2021 | 13:00
|  | TR2 | 300 | 190 | 562 | 24.05.2021 | 13:00
9 | Aminbazar | TR1 | 225 | 142 | 408 | 28.05.21 | 12:00 | Parallelly connected
|  | TR2 | 225 | 142 | 408 | 28.05.21 | 12:00
|  | TR3 | 225 | 151 | 428 | 28.05.21 | 12:00
10 | Rampur | TR1 | 225 | - | - | - | - | 230 KV side is not connected
|  | TR2 | 225 | - | - | - | -
11 | Hathazari | MT1 | 150 | 73 | 205 | 02.05.21 | 23:00
|  | MT2 | 150 | 73 | 205 | 02.05.21 | 23:00
|  | MT3 | 150 | 73 | 205 | 02.05.21 | 23:00
|  | MT4 | 150 | 73 | 205 | 02.05.21 | 23:00
12 | Shikalbaha | TR1 | 300 | 257 | 681 | 22.5.21 | 22:00
|  | TR2 | 300 | 257 | 681 | 22.5.21 | 22:00
13 | Cumilla(N) | TR1 | 225 | 191 | 568 | 14/05/2021 | 19:00
|  | TR2 | 225 | 189 | 564
14 | Fenchuganj | AT-1 | 225/300 | - | - | - | - | Under Maintenance
|  | AT-2 | 225/300 | 287 | 762 | 23.05.2021 | 23:00
15 | Barishal(N) | TR1 | 300 | 150 | 382 | 10.05.2021 | 12:00
|  | TR2 | 300 | 150 | 382 | 10.05.2021 | 12:00
16 | Khulna(S) | TR1 | 225 | 121 | 343 | 23.05.2021 | 6:00
|  | TR2 | 225 | 121 | 343 | 23.05.2021 | 6:00
|  | TR3 | 300 | 155 | 441 | 23.05.2021 | 6:00
| Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:May' 2021
Sl | Name of the sub-station | Auto transformer |  | Recorded maximum load |  | Date | Time | Remarks
|  | Name | Capacity ( MVA ) | MW | Amps ( 230kV side )
18 | Bogura | TR1 | 225 | 135 | 388 | 2.5.21 | 0:00
|  | TR2 | 225 | 135 | 388 | 2.5.21 | 0:00
|  | TR3 | 225 | 184 | 512 | 2.5.21 | 0:00
19 | Barapukuria | TR1 | 225 | 148 | 458 | 19.5.2021 | 21:00 | Due to unavailability of 230 kV side meters 132 kV current is being provided
|  | TR2 | 225 | 164 | 515
|  | TR6 | 300 | 211 | 659
20 | Rajshahi(N) | ATR-01 | 300 | 125 | 336 | 24.05.2021 | 23:00
|  | ATR-02 | 300 | 125 | 336 | 24.05.2021 | 23:00
21 | Baghabari | TR1 | 300 | 167 | 460 | 2021-01-05 | 20:00
|  | TR2 | 225 | 118 | 320
22 | Ishurdi | TR1 | 225 | 129 | 336 | 2021-02-05 | 23:00
|  | TR2 | 225 | 129 | 336
|  | TR3 | 225 | 129 | 336
23 | Bheramara | TR1 | 225 | 63 | 160 | 29/05/21 | 21:00
|  | TR2 | 225 | 63 | 160
Maximum load of 400/230kV and 400/132 kV Transformer
Month:May' 2021
| Name of the | Transformer |  | Recorded maximum load |  | Date | Time | Remarks
Sl | sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side)
| Kaliakoir | TR1(400/230 kV) | 520 | 281.3 | 432 | 31.5.21 | 14:30
|  | TR2(400/230 kV) | 520 | 284.2 | 432
|  | TR1(400/132 kV) | 325 | 280.6 | 478 | 24.5.21 | 19:30
|  | TR2(400/132 kV) | 325 | 280.5 | 478
| Bibiyana | ICT1(400/230 kV) | 520 | 155 | 228 | 26/05/21 | 20:00
|  | ICT2(400/230kV) | 520 | 151 | 222
| Bhulta | ATR1(400/230 kV) | 520 | 208 | 402 | 2021-05-05 | 13:30
|  | ATR2(400/230kV) | 520 | 208 | 402
| Ashuganj(N) | GSUT1 | 567 | 366.5 | 624 | 2021-05-05 | 9:00
| Gopalganj | ATR1(400/138 kV) | 325 | 302 | 441 | 02.05.21 | 21:00
|  | ATR2(400/138kV) | 325 | 302 | 441 | 02.05.21 | 21:00
| Payra | GSUT1 | 270 | 207 | 933 | 19/05/21 | 22:00
|  | GSUT2 | 270 | 207 | 933
|  | GSUT3 | 270 | 207 | 933
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:May 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-05-01 | 11665 | 11665 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-01 | 8860 | 8860 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-02 | 12738 | 12738 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-02 | 11158 | 11158 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-03 | 12943 | 12943 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-03 | 10219 | 10219 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-04 | 11394 | 11394 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-04 | 9490 | 9490 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-05 | 11620 | 11620 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-05 | 9733 | 9733 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-06 | 12527 | 12527 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-06 | 9841 | 9841 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-07 | 11125 | 11125 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-07 | 9641 | 9641 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-08 | 12734 | 12734 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-08 | 9510 | 9510 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-09 | 10978 | 10978 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-09 | 10714 | 10714 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-10 | 10812 | 10812 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-10 | 9904 | 9904 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-11 | 9453 | 9453 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-11 | 8443 | 8443 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-12 | 10111 | 10111 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-12 | 8111 | 8111 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-13 | 9099 | 9099 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-13 | 7235 | 7235 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-14 | 9780 | 9780 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-14 | 6995 | 6995 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-15 | 8766 | 8766 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-15 | 7607 | 7607 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-16 | 10787 | 10787 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-16 | 8466 | 8466 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-17 | 11192 | 11192 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-17 | 9442 | 9442 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-18 | 10978 | 10978 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-18 | 10113 | 10113 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-19 | 12768 | 12768 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-19 | 10283 | 10283 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-20 | 11980 | 11980 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-20 | 10760 | 10760 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-21 | 12519 | 12519 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-21 | 9546 | 9546 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-22 | 13417 | 13417 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-22 | 10561 | 10561 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-23 | 13357 | 13357 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-23 | 12021 | 12021 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-24 | 12353 | 12353 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-24 | 11835 | 11835 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-25 | 11907 | 11907 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-25 | 10365 | 10365 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-26 | 11529 | 11529 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-26 | 8780 | 8780 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-27 | 11749 | 11749 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-27 | 9506 | 9506 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-28 | 11780 | 11780 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-28 | 9064 | 9064 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-29 | 13171 | 13171 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-29 | 10341 | 10341 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-30 | 12994 | 12994 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-30 | 11332 | 11332 | - | - | - | - | - | - | - | - | - | - | - | -
2021-05-31 | 11840 | 11840 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-05-31 | 10075 | 10075 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:May 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13417 | 2021-05-22 | 21:00
2 | Maximum Day Peak Genaration | MW | 12021 | 2021-05-23 | 12:00
3 | Maximum Evening Peak Demand | MW | 13417 | 44338 | 19:00
4 | Minimum Generation | MW | 6470 | 2021-05-14 | 9:00
5 | Average of the daily evening peak Genaration | MW | 11615.0323
6 | Average of the daily day peak Genaration | MW | 9675.8387
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 1
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 9.1667
11 | Total Generation | MkWh | 7548.7616
12 | Total Generation by BPDB | MkWh | 1736.8634 | % of total Gen. | 23.01%
13 | Total Generation by IPP | MkWh | 2069.738 | '' | 27.42%
14 | A) Total Generation by Generation Companies | MkWh | 2415.3716 | '' | 32%
| B) Total Generation by REB | MkWh | 122.6176 | " | 1.624%
| C) Total Generation by RENTAL | MkWh | 487.59 | " | 6.459%
| D) Total Imported from India (BIPTC) | MkWh | 619.3053 | " | 8.204%
| E) Total Imported from Tripura, India (A.C) | MkWh | 97.2758 | " | 1.289%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4753.881 | % of total Gen. | 62.98%
| B) Oil | MkWh | 1551.7472 | '' | 20.56%
| C) Hydro | MkWh | 16.1091 | '' | 0.2134%
| D) Solar | MkWh | 21.292 | '' | 0.2821%
| E) Coal | MkWh | 489.1513 | '' | 6.48%
| F) BIPTC (Import from India) | MkWh | 619.3053 | '' | 8.204%
| G) A.C (Import from Tripura, India) | MkWh | 97.2758 | '' | 1.289%
16 | Maximun of the daily total Generation . | MkWh | 292.5282 | 2021-05-23
17 | Monthly Load factor | % | 75.6219
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 23372.1181
| A) Gas | M.Taka | 5040.3988
| B) Liquid fuel | M.Taka | 12262.5583
| C) Coal | M.Taka | 2293.0461
| D) BIPTC (Import from India) | M.Taka | 3071.0262
| E) Tripura(Import from India) | M.Taka | 705.0888
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1032 | 2021-05-30
| A) Gas | M.Taka | 178.6089 | 2021-05-10
| B) Liquid fuel | M.Taka | 791.7617 | 2021-05-30
| C) Coal | M.Taka | 90.4344 | 2021-05-01
| D) BIPTC (Import from India) | M.Taka | 113.2895 | 2021-05-27
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 2.5958
| B) Excluding Hydro & Solar | Taka/kWhR | 2.6014
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/5/2021 | 06:00
b) | Actual | FT (MSL) | 72.69 | 31/5/2021 | 06:00
22 | Peak Genaration of May 2020 | MW | 11977 | 18/05/20 | 22:00
23 | Peak Demand of May 2020 | MW | 11977 | 18/05/20 | 22:00
24 | Maximum peak Generation recorded upto 31/05/2021 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 31/05/2021 | MW | 14097 | 27/04/21 | 20:00
26 | Maximum load shed recorded upto 31/05/2021 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.