## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-07-09 | Monday
|  | Date (day): | 2018-07-09 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11191 | MW |  |  | (b) At Evening Peak Hour : |  | 12540 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-07-08 | 2018-07-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 65 | 65 | 65 | 65
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 300 | 365 | 0
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 30 | 35 | 40 | 77 | 18
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 89 | 88 | 88 | 88 | 20 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 365 | 350 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 98 | 50 | 98 |  | 12 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 261 | 272 | 320 | 340 | 60 |  | Gas shortage
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 390 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 200 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 65 | 95 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 74 | 87 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 35 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 89 | 93 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 139 | 116 | 100 | 140
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 11 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 34 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 140 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 82 | 40 | 88 | 88
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 55 | 57 | 57 |  | 23 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 50 | 50 | 50
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 273 | 301 | 200 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 52 | 50 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 0 | 0 | 150 | 150 | 150 | 150
| Dhaka area Total |  |  |  |  | 5635 | 5399 | 3397 | 3772 | 3924 | 4446 | 513 | 528
37 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
39 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 26 | 38 | 50 | 50 |  | 24
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 164 | 165 | 168 | 168 |  | 62 | # 2 & 3 under maint
41 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
42 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 189 | 196 | 225 | 225
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 60 | 135 | 100 | 135
44 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 50 | 50 | 51 | 51
45 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 56 | 73 | 73
46 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 15 | 60 | 75 | 75
47 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 80 | 90 | 90 |  | 10 | Engine problem
48 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19 |  | 3 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 22 | 10 | 22
49 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 92 | 105 | 105 | 105 |  | 3
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 698 | 942 | 982 | 1029 | 360 | 151
50 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 120 | 100 | 120 | 120 | 15 |  | Gas shortage
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Under shut down
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34 |  | Gas shortage
51 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 170 | 144 | 200 | 225 |  |  | FGMO
52 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 372 | 330 | 360 | 360 |  |  | FGMO
53 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 331 | 360 | 360
54 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 42 | 43 | 43 |  | 5 | Engine problem
55 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
56 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 53 | 53
57 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 110 | 125 | 125 | 70 |  | Gas shortage
58 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 45 | 51 | 51
59 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
60 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 42 | 0 | 50
61 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST under maint.
62 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
63 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 126 | 124 | 105 | 164
64 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
65 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 30 | 16 | 52 | 52
66 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 22 | 21 | 22 |  | 4 | Engine problem
67 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 150 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1570 | 1809 | 1838 | 2173 | 248 | 127
68 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 47 | 64 | 100 | 100 | 102 |  | Gas shortage
69 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
70 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
71 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.8 | 0 | 2 | 0
72 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 180 | 185 | 150 | 192
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 279.8 | 364 | 367 | 407 | 102 | 0
73 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 54 | 57 | 57
74 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 74 | 74 | 75 | 75
75 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
76 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 240 | 240 |  | 330
77 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 53 | 53
78 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
79 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
80 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 57 | 60 | 60 | 60
81 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
82 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 46 | 46 | 50 | 50
83 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 0 | 0 | 0 |  | 142 | Under maint. |  | 2018-10-07
84 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
85 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 44 | 47 | 45 | 45 |  | 5 | Engine problem
86 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 23 | 23 | 23 |  | 9 | Engine problem
87 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 341 | 341 |  |  | FGMO
88 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 948 | 957 | 1264 | 1264 | 0 | 506
89 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 48 | 0 | 48
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 462 | 462 | 467 | 467
90 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 78 | 73 | 51 | 90 |  | 20 | Engine problem
91 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 115 | 115 | 115 |  | 16
92 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 49 | 36 | 50
93 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 239 | 225 | 225 |  |  | FGMO
94 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 66 | 70 | 80
95 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 294 | 275 | 400 | 400 | 10
96 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
97 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 55 | 0 | 54
98 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 97 | 97 | 97
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 1060 | 1519 | 1501 | 1666 | 10 | 36
99 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 110 | 110 | 110
100 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 12 | 0 | 30
101 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 37 | 33 | 33
102 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 191 | 194 | 194
103 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 98 | 98 | 98
| Barisal Area Total |  |  |  |  | 472 | 462 | 366 | 448 | 435 | 465 | 0 | 0
104 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
105 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 51
106 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 0 | 36
107 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50 |  | 0
108 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 35 | 43 | 43 | 43 |  | 7 | Engine problem
109 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 43 | 43
110 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 165 | 171 | 214 | 214
111 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 178 | 166 | 180 | 180
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
112 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 42
113 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
114 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 9 | 9 | 10 | 10
115 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 10 | 11 | 11
116 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 52 | 43 | 43 |  | 9 | Engine problem
117 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 59 | 100 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 541 | 736 | 712 | 841 | 71 | 120
118 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
119 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 215 | 150 | 215
120 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 11 | 0 | 16
121 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 150 | 244 | 168 | 249 | 0 | 170
| Total |  |  |  |  | 15953 | 15410 | 9009.8 | 10791 | 11191 | 12540 | 1304 | 1638
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8636.5834 | 10344 | 10727.4306 | 12020.5505
A. |  | 2018-07-08 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 10791 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8007.3 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10791 | MW
3 | Day peak Generation : |  |  | 9009.8 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10344 | MW
4 | Evening peak Generation : |  |  | 10791 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 231.5403 | MKWHr | By Solar | 0.0141 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 127.5141 | MKWHr |  | By Oil: | 82.2855 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.8433 | MKWHr |  | By Hydro: | 3.8358 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1304 | MW | Dhaka | 3825 | 3825 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1638 | MW | Chittagong | 1032 | 1032 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2942 | MW | Khulna | 1336 | 1336 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 963.78 | MMCFD |  |  | Rajshahi | 1120 | 1120 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 91534531.004 | ii) Oil : | Taka | 762549937.24 | Comilla | 966 | 966 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14835138 | Total | Taka | 868919606.244 | Mymensingh | 758 | 758 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.216 | MKWHr. | Sylhet | 435 | 435 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -640 | MW at | 21:00 | hrs | Barisal | 276 | 276 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -760 | MW at | 20:00 | hrs | Rangpur | 596 | 596 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33° C |  |  | Total | 10344 | 10344 |  | 0
B. |  | 2018-07-09 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.5° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12540 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 1540 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 236.0247 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7794.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.9687 | MKWHr. | ii) HVDC Flow at Peak Time |  | 462 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0787 | MKWHr. | iii) Maximum HVDC Flow : |  | 462 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.36 |  | (b) Today: | 105.24 |  | (c) Rule Curve: |  | 85.28
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-07-08
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 69 | 120 | 0 | 0 | 365 | 88 | 35 | 412 | 334 | 105 | 0 | 440 | 200 | 100 | 97 | 55 | 120 | 0 | 0 | 0 | 93 | 50 | 80 | 88 | 80 | 10 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 63 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 70 | 0 | 50 | 72 | 56 | 80 | 99 | 26 | 19 | 39 | 100 | 0 | 100 | 275 | 276 | 188 | 72 | 100 | 41 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 22 | 132 | 83 | 95 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 47 | 0 | 0 | 45 | 10 | 280 | 23 | 11 | 0 | 301 | 0 | 0 | 165 | 0 | 150 |  | 456 | 0 | 385 | 54 | 83 | 233 | 0 | 0 | 42 | 0 | 40 | 191 | 36 | 96 | 0 | 0 | 0 | 51 | 36 | 100 | 50 | 43 | 44 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 148 | 0 | 0 | 0 | 162 | 0 | 162 | 96 | 0 | 0 | 0 |  | 7505 | 2597 | 10102 | 3330 | 456 | 2042 | 2556 | 148 | 143 | 1295 | 132 | 0 | 0 | 105.36
2:00 | 69 | 120 | 0 | 0 | 365 | 88 | 35 | 413 | 342 | 25 | 0 | 450 | 200 | 100 | 97 | 55 | 115 | 0 | 0 | 0 | 93 | 24 | 16 | 50 | 80 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 63 | 80 | 0 | 0 | 16 | 0 | 188 | 0 | 70 | 0 | 50 | 72 | 56 | 68 | 99 | 26 | 19 | 39 | 100 | 0 | 100 | 270 | 272 | 184 | 72 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 22 | 132 | 83 | 95 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 47 | 0 | 0 | 45 | 10 | 290 | 23 | 11 | 0 | 301 | 0 | 0 | 175 | 0 | 150 |  | 462 | 0 | 383 | 48 | 97 | 160 | 0 | 0 | 42 | 0 | 40 | 192 | 32 | 96 | 0 | 0 | 0 | 51 | 36 | 100 | 50 | 43 | 44 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 167 | 0 | 159 | 95 | 0 | 0 | 0 |  | 7271 | 2536 | 9807 | 3311 | 462 | 2065 | 2383 | 150 | 143 | 1161 | 132 | 0 | 0 | 105.36
3:00 | 69 | 120 | 0 | 0 | 365 | 88 | 35 | 414 | 352 | 0 | 0 | 450 | 200 | 92 | 97 | 55 | 110 | 0 | 0 | 0 | 50 | 7 | 16 | 10 | 80 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 188 | 0 | 70 | 0 | 51 | 72 | 56 | 80 | 99 | 26 | 19 | 38 | 100 | 0 | 100 | 270 | 272 | 184 | 72 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 22 | 148 | 83 | 48 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 47 | 0 | 0 | 45 | 10 | 300 | 23 | 11 | 0 | 301 | 0 | 0 | 180 | 0 | 150 |  | 462 | 0 | 383 | 48 | 97 | 120 | 0 | 0 | 42 | 0 | 40 | 192 | 31 | 96 | 0 | 0 | 0 | 51 | 25 | 100 | 50 | 43 | 44 | 52 | 0 | 18 | 9 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 168 | 0 | 167 | 95 | 0 | 0 | 0 |  | 7161 | 2497 | 9658 | 3308 | 462 | 2083 | 2221 | 153 | 164 | 1119 | 148 | 0 | 0 | 105.36
4:00 | 69 | 120 | 0 | 0 | 365 | 86 | 35 | 421 | 352 | 0 | 0 | 450 | 200 | 56 | 97 | 55 | 110 | 0 | 0 | 0 | 50 | 7 | 16 | 10 | 81 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 188 | 0 | 70 | 0 | 51 | 48 | 49 | 80 | 94 | 26 | 19 | 38 | 100 | 0 | 100 | 270 | 272 | 183 | 72 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 22 | 144 | 83 | 24 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 47 | 0 | 0 | 45 | 10 | 280 | 23 | 11 | 0 | 301 | 0 | 0 | 180 | 0 | 150 |  | 462 | 0 | 383 | 48 | 97 | 120 | 0 | 0 | 42 | 0 | 40 | 191 | 32 | 96 | 0 | 0 | 0 | 51 | 0 | 100 | 50 | 43 | 44 | 0 | 0 | 18 | 9 | 11 | 0 | 0 | 146 | 0 | 0 | 0 | 167 | 0 | 165 | 96 | 0 | 0 | 0 |  | 7046 | 2411 | 9457 | 3313 | 462 | 2063 | 2105 | 146 | 164 | 1060 | 144 | 0 | 0 | 105.36
5:00 | 69 | 120 | 0 | 0 | 365 | 86 | 35 | 420 | 352 | 0 | 0 | 450 | 200 | 28 | 48 | 55 | 71 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 81 | 0 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 192 | 0 | 70 | 0 | 50 | 0 | 15 | 80 | 92 | 24 | 19 | 42 | 100 | 0 | 100 | 292 | 290 | 191 | 72 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 136 | 84 | 8 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 61 | 50 | 47 | 0 | 0 | 45 | 10 | 270 | 23 | 11 | 0 | 301 | 0 | 0 | 187 | 0 | 150 |  | 462 | 0 | 380 | 48 | 81 | 120 | 0 | 0 | 42 | 0 | 40 | 190 | 25 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 44 | 0 | 0 | 18 | 9 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 174 | 0 | 173 | 96 | 0 | 0 | 0 |  | 6756 | 2356 | 9112 | 3319 | 462 | 2014 | 1913 | 154 | 168 | 946 | 136 | 0 | 0 | 105.36
6:00 | 69 | 120 | 0 | 0 | 365 | 86 | 35 | 415 | 352 | 0 | 0 | 410 | 200 | 7 | 15 | 15 | 71 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 32 | 0 | 39 | 18 | 18 | 36 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 191 | 0 | 50 | 0 | 50 | 0 | 15 | 80 | 92 | 21 | 19 | 42 | 100 | 0 | 100 | 270 | 272 | 183 | 72 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 122 | 86 | 8 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 61 | 50 | 47 | 0 | 0 | 45 | 10 | 280 | 23 | 11 | 0 | 243 | 0 | 0 | 150 | 0 | 150 |  | 462 | 0 | 375 | 10 | 16 | 120 | 0 | 0 | 42 | 0 | 40 | 188 | 21 | 96 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 0 | 0 | 0 | 18 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 175 | 0 | 163 | 95 | 0 | 0 | 0 |  | 6307 | 2181 | 8488 | 3258 | 462 | 1979 | 1477 | 150 | 168 | 872 | 122 | 0 | 0 | 105.36
7:00 | 69 | 120 | 0 | 0 | 365 | 86 | 35 | 350 | 352 | 0 | 0 | 410 | 200 | 7 | 15 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 6 | 18 | 18 | 36 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 188 | 0 | 50 | 0 | 50 | 0 | 15 | 80 | 92 | 22 | 19 | 32 | 100 | 0 | 100 | 270 | 272 | 182 | 72 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 112 | 82 | 8 | 20 | 0 | 58 | 74 | 53 | 50 | 163 | 0 | 61 | 58 | 47 | 0 | 0 | 44 | 10 | 280 | 8 | 11 | 0 | 110 | 0 | 0 | 100 | 0 | 150 |  | 462 | 0 | 368 | 10 | 16 | 120 | 0 | 0 | 18 | 0 | 40 | 190 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 50 | 43 | 0 | 8 | 0 | 18 | 9 | 8 | 0 | 0 | 152 | 0 | 0 | 0 | 168 | 0 | 170 | 95 | 0 | 0 | 0 |  | 5966 | 2090 | 8056 | 3167 | 462 | 1977 | 1214 | 152 | 168 | 804 | 112 | 0 | 0 | 105.36
8:00 | 69 | 120 | 0 | 0 | 365 | 85 | 35 | 345 | 331 | 0 | 0 | 410 | 200 | 7 | 15 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 6 | 18 | 18 | 36 | 22 | 25 | 32 | 33 | 33 | 8 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 50 | 0 | 15 | 80 | 90 | 22 | 19 | 2 | 100 | 0 | 100 | 368 | 265 | 165 | 73 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 110 | 65 | 8 | 20 | 0.3 | 58 | 74 | 53 | 50 | 163 | 0 | 60 | 50 | 46 | 0 | 0 | 44 | 10 | 295 | 8 | 11 | 0 | 102 | 0 | 0 | 100 | 0 | 150 |  | 462 | 0 | 345 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 13 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 50 | 43 | 0 | 8 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 164 | 0 | 166 | 96 | 0 | 0 | 0 |  | 5974.3 | 2033 | 8007.3 | 3197 | 462 | 1924 | 1204 | 150 | 168 | 792 | 110 | 0.3 | 0 | 105.36
9:00 | 69 | 120 | 0 | 0 | 365 | 88 | 35 | 390 | 306 | 0 | 0 | 420 | 305 | 7 | 15 | 25 | 70 | 0 | 0 | 0 | 7 | 10 | 16 | 36 | 83 | 10 | 21 | 54 | 18 | 55 | 22 | 25 | 32 | 33 | 33 | 10 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 196 | 0 | 135 | 0 | 50 | 0 | 15 | 80 | 90 | 22 | 19 | 2 | 100 | 0 | 90 | 366 | 255 | 202 | 8 | 100 | 20 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 106 | 64 | 8 | 20 | 0.3 | 58 | 74 | 51 | 50 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 44 | 10 | 330 | 15 | 11 | 0 | 105 | 0 | 0 | 186 | 0 | 150 |  | 462 | 0 | 329 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 40 | 191 | 12 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 50 | 35 | 0 | 8 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 181 | 0 | 184 | 94 | 0 | 0 | 0 |  | 6477.3 | 2043 | 8520.3 | 3229 | 462 | 1913 | 1586 | 150 | 168 | 906 | 106 | 0.3 | 0 | 105.36
10:00 | 69 | 120 | 0 | 0 | 365 | 88 | 35 | 355 | 296 | 0 | 0 | 420 | 240 | 40 | 28 | 55 | 84 | 0 | 0 | 0 | 30 | 32 | 32 | 50 | 83 | 21 | 39 | 54 | 32 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 135 | 0 | 50 | 0 | 15 | 80 | 92 | 26 | 16 | 2 | 120 | 0 | 100 | 372 | 272 | 170 | 8 | 100 | 20 | 0 | 5 | 51 | 85 | 0 | 10 | 19 | 11 | 33 | 15 | 124 | 64 | 8 | 20 | 1.2 | 58 | 74 | 47 | 47 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 44 | 10 | 300 | 22 | 11 | 0 | 155 | 0 | 0 | 185 | 0 | 150 |  | 462 | 0 | 320 | 10 | 50 | 120 | 0 | 0 | 0 | 0 | 33 | 189 | 15 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 40 | 35 | 0 | 8 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 171 | 0 | 174 | 94 | 0 | 0 | 0 |  | 6644.2 | 2032 | 8676.2 | 3215 | 462 | 1869 | 1796 | 150 | 164 | 895 | 124 | 1.2 | 0 | 105.36
11:00 | 69 | 120 | 0 | 0 | 365 | 88 | 30 | 345 | 265 | 0 | 0 | 420 | 200 | 88 | 60 | 55 | 128 | 0 | 0 | 0 | 80 | 50 | 32 | 50 | 82 | 21 | 33 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 130 | 0 | 50 | 0 | 15 | 80 | 92 | 26 | 17 | 2 | 120 | 0 | 100 | 372 | 295 | 171 | 8 | 100 | 20 | 0 | 5 | 51 | 85 | 0 | 24 | 19 | 11 | 33 | 20 | 120 | 65 | 8 | 20 | 1 | 58 | 74 | 47 | 47 | 130 | 0 | 58 | 86 | 46 | 0 | 0 | 44 | 10 | 280 | 22 | 11 | 0 | 253 | 0 | 0 | 166 | 0 | 150 |  | 462 | 0 | 310 | 10 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 188 | 17 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 40 | 35 | 0 | 8 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 158 | 0 | 164 | 94 | 0 | 0 | 0 |  | 6826 | 2023 | 8849 | 3267 | 462 | 1782 | 2036 | 150 | 164 | 867 | 120 | 1 | 0 | 105.35
12:00 | 65 | 120 | 0 | 0 | 365 | 89 | 30 | 345 | 261 | 0 | 0 | 400 | 200 | 90 | 65 | 55 | 139 | 0 | 0 | 0 | 89 | 84 | 32 | 74 | 82 | 21 | 34 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 60 | 0 | 50 | 0 | 15 | 68 | 92 | 26 | 16 | 2 | 120 | 0 | 100 | 372 | 300 | 170 | 8 | 100 | 20 | 0 | 5 | 51 | 85 | 0 | 30 | 19 | 11 | 33 | 20 | 126 | 47 | 32 | 20 | 0.8 | 58 | 74 | 47 | 50 | 163 | 0 | 57 | 86 | 46 | 0 | 0 | 44 | 10 | 280 | 22 | 11 | 0 | 273 | 0 | 0 | 180 | 0 | 150 |  | 462 | 0 | 294 | 78 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 50 | 35 | 0 | 16 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 165 | 0 | 178 | 95 | 0 | 0 | 0 |  | 6892.8 | 2117 | 9009.8 | 3243 | 462 | 1797 | 2249 | 150 | 164 | 818 | 126 | 0.8 | 0 | 105.35
13:00 | 65 | 120 | 0 | 0 | 365 | 88 | 30 | 345 | 251 | 13 | 0 | 400 | 250 | 90 | 70 | 55 | 141 | 0 | 0 | 0 | 91 | 102 | 64 | 74 | 90 | 21 | 34 | 54 | 55 | 55 | 10 | 25 | 30 | 33 | 33 | 44 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 60 | 0 | 50 | 0 | 15 | 68 | 92 | 26 | 17 | 2 | 120 | 0 | 100 | 383 | 300 | 170 | 8 | 100 | 40 | 0 | 5 | 51 | 86 | 0 | 34 | 19 | 11 | 33 | 16 | 122 | 38 | 64 | 20 | 0.7 | 58 | 74 | 53 | 50 | 163 | 0 | 50 | 86 | 20 | 0 | 0 | 46 | 10 | 290 | 22 | 11 | 0 | 286 | 0 | 0 | 172 | 0 | 150 |  | 462 | 0 | 280 | 82 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 186 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 50 | 25 | 0 | 25 | 0 | 18 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 160 | 0 | 163 | 96 | 0 | 0 | 0 |  | 7059.7 | 2082 | 9141.7 | 3226 | 462 | 1778 | 2408 | 150 | 165 | 830 | 122 | 0.7 | 0 | 105.35
14:00 | 65 | 120 | 0 | 0 | 365 | 88 | 30 | 344 | 252 | 13 | 0 | 360 | 200 | 90 | 85 | 55 | 70 | 0 | 0 | 0 | 93 | 102 | 64 | 87 | 89 | 21 | 39 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 60 | 0 | 50 | 0 | 15 | 80 | 93 | 26 | 17 | 2 | 120 | 0 | 100 | 377 | 301 | 184 | 8 | 100 | 39 | 0 | 5 | 51 | 50 | 0 | 34 | 16 | 11 | 33 | 16 | 138 | 35 | 64 | 20 | 2.3 | 58 | 74 | 53 | 50 | 100 | 0 | 52 | 86 | 20 | 0 | 0 | 21 | 10 | 265 | 22 | 11 | 0 | 288 | 0 | 0 | 174 | 0 | 150 |  | 462 | 0 | 250 | 77 | 66 | 120 | 0 | 0 | 0 | 2 | 40 | 179 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 58 | 50 | 25 | 0 | 25 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 161 | 0 | 162 | 96 | 0 | 0 | 0 |  | 6840.3 | 2042 | 8882.3 | 3132 | 462 | 1592 | 2410 | 150 | 165 | 831 | 138 | 2.3 | 0 | 105.34
15:00 | 65 | 120 | 0 | 0 | 365 | 88 | 30 | 375 | 252 | 40 | 0 | 390 | 305 | 90 | 97 | 55 | 70 | 0 | 0 | 0 | 85 | 102 | 98 | 87 | 88 | 51 | 39 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 135 | 0 | 50 | 0 | 15 | 80 | 94 | 26 | 17 | 2 | 120 | 0 | 100 | 372 | 250 | 165 | 8 | 100 | 39 | 0 | 5 | 51 | 84 | 0 | 34 | 16 | 11 | 33 | 22 | 152 | 37 | 90 | 20 | 1.8 | 50 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 44 | 0 | 0 | 44 | 10 | 290 | 22 | 11 | 0 | 301 | 0 | 0 | 174 | 0 | 150 |  | 424 | 0 | 275 | 73 | 66 | 120 | 0 | 0 | 0 | 3 | 40 | 187 | 20 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 35 | 0 | 43 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 181 | 0 | 181 | 12 | 0 | 0 | 0 |  | 7329.8 | 2108 | 9437.8 | 3130 | 424 | 1709 | 2685 | 150 | 164 | 1022 | 152 | 1.8 | 0 | 105.34
16:00 | 65 | 120 | 0 | 0 | 365 | 87 | 30 | 345 | 252 | 80 | 0 | 390 | 200 | 90 | 97 | 55 | 70 | 0 | 0 | 0 | 90 | 102 | 115 | 87 | 88 | 51 | 39 | 36 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 75 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 135 | 0 | 50 | 0 | 15 | 80 | 94 | 26 | 17 | 5 | 120 | 0 | 100 | 378 | 250 | 170 | 8 | 100 | 39 | 0 | 5 | 51 | 85 | 0 | 43 | 19 | 11 | 33 | 22 | 138 | 38 | 95 | 20 | 0.8 | 56 | 74 | 53 | 50 | 163 | 0 | 50 | 86 | 44 | 0 | 0 | 44 | 10 | 270 | 22 | 11 | 0 | 300 | 0 | 0 | 170 | 0 | 150 |  | 424 | 0 | 275 | 76 | 76 | 145 | 0 | 0 | 0 | 6 | 33 | 180 | 19 | 110 | 0 | 0 | 0 | 0 | 0 | 92 | 50 | 35 | 0 | 43 | 0 | 17 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 162 | 0 | 162 | 12 | 0 | 0 | 0 |  | 7215.8 | 2087 | 9302.8 | 3104 | 424 | 1690 | 2622 | 150 | 155 | 1019 | 138 | 0.8 | 0 | 105.33
17:00 | 65 | 120 | 0 | 0 | 365 | 87 | 35 | 345 | 252 | 95 | 0 | 390 | 200 | 50 | 75 | 55 | 70 | 0 | 0 | 0 | 50 | 8 | 115 | 50 | 57 | 51 | 39 | 36 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 75 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 60 | 0 | 50 | 33 | 29 | 80 | 95 | 25 | 19 | 5 | 120 | 0 | 100 | 300 | 279 | 170 | 8 | 100 | 36 | 0 | 5 | 40 | 40 | 0 | 52 | 19 | 11 | 0 | 22 | 128 | 38 | 95 | 20 | 0.2 | 52 | 74 | 53 | 50 | 130 | 0 | 40 | 40 | 46 | 0 | 0 | 44 | 10 | 270 | 22 | 11 | 0 | 300 | 0 | 0 | 170 | 0 | 150 |  | 424 | 0 | 275 | 75 | 115 | 120 | 0 | 0 | 0 | 22 | 40 | 183 | 21 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 0 | 43 | 0 | 16 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 163 | 0 | 161 | 12 | 0 | 0 | 0 |  | 6712.2 | 2143 | 8855.2 | 3010 | 424 | 1563 | 2435 | 150 | 155 | 990 | 128 | 0.2 | 0 | 105.33
18:00 | 65 | 120 | 0 | 0 | 300 | 47 | 35 | 340 | 251 | 98 | 0 | 390 | 200 | 30 | 16 | 15 | 128 | 0 | 0 | 0 | 7 | 14 | 82 | 10 | 57 | 51 | 12 | 18 | 55 | 36 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 75 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 60 | 0 | 50 | 56 | 29 | 80 | 92 | 25 | 19 | 3 | 120 | 0 | 100 | 300 | 279 | 184 | 8 | 100 | 42 | 0 | 5 | 14 | 10 | 0 | 52 | 19 | 0 | 0 | 0 | 112 | 53 | 24 | 20 | 0.1 | 54 | 74 | 11 | 47 | 130 | 0 | 60 | 10 | 10 | 0 | 0 | 12 | 10 | 295 | 23 | 11 | 0 | 301 | 0 | 0 | 180 | 0 | 150 |  | 461 | 0 | 275 | 62 | 115 | 120 | 0 | 0 | 15 | 40 | 40 | 186 | 22 | 110 | 0 | 0 | 0 | 0 | 10 | 100 | 50 | 43 | 0 | 43 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 0 | 0 | 0 | 162 | 0 | 159 | 12 | 0 | 0 | 0 |  | 6162.1 | 2212 | 8374.1 | 3025 | 461 | 1349 | 2102 | 150 | 155 | 1020 | 112 | 0.1 | 0 | 105.32
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 65 | 120 | 0 | 0 | 365 | 87 | 35 | 350 | 272 | 100 | 0 | 390 | 250 | 30 | 15 | 15 | 140 | 0 | 0 | 15 | 7 | 16 | 82 | 50 | 89 | 51 | 12 | 47 | 55 | 50 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 75 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 120 | 0 | 50 | 61 | 45 | 80 | 97 | 25 | 19 | 8 | 120 | 0 | 100 | 320 | 320 | 199 | 50 | 100 | 42 | 0 | 5 | 15 | 10 | 36 | 52 | 19 | 11 | 0 | 22 | 96 | 65 | 24 | 20 | 0 | 54 | 74 | 11 | 16 | 100 | 0 | 60 | 10 | 10 | 0 | 0 | 41 | 10 | 295 | 23 | 11 | 95 | 302 | 0 | 33 | 175 | 7 | 150 |  | 462 | 32 | 275 | 80 | 115 | 145 | 0 | 22 | 49 | 60 | 40 | 191 | 27 | 110 | 10 | 0 | 0 | 40 | 30 | 100 | 0 | 43 | 45 | 51 | 0 | 18 | 9 | 10 | 0 | 0 | 150 | 15 | 0 | 0 | 167 | 0 | 164 | 54 | 26 | 0 | 0 |  | 6869 | 2540 | 9409 | 3238 | 462 | 1473 | 2445 | 150 | 155 | 1390 | 96 | 0 | 0 | 105.32
19:30 | 65 | 120 | 0 | 0 | 365 | 87 | 35 | 345 | 271 | 100 | 0 | 390 | 250 | 100 | 15 | 55 | 140 | 0 | 0 | 20 | 10 | 50 | 149 | 87 | 89 | 51 | 20 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 135 | 0 | 50 | 85 | 62 | 80 | 105 | 31 | 19 | 7 | 120 | 0 | 100 | 300 | 300 | 184 | 89 | 100 | 42 | 0 | 5 | 18 | 85 | 42 | 52 | 19 | 11 | 33 | 22 | 110 | 65 | 95 | 20 | 0 | 54 | 74 | 11 | 50 | 163 | 0 | 60 | 86 | 45 | 0 | 0 | 44 | 10 | 310 | 23 | 11 | 200 | 301 | 0 | 50 | 180 | 50 | 150 |  | 461 | 49 | 275 | 75 | 115 | 170 | 0 | 54 | 50 | 60 | 40 | 190 | 34 | 110 | 12 | 0 | 0 | 43 | 30 | 100 | 0 | 43 | 45 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 167 | 12 | 18 | 0 | 176 | 0 | 172 | 75 | 97 | 0 | 0 |  | 7797 | 2762 | 10559 | 3210 | 461 | 1842 | 3007 | 167 | 165 | 1597 | 110 | 0 | 0 | 0
20:00 | 65 | 120 | 0 | 0 | 365 | 87 | 35 | 350 | 272 | 104 | 0 | 390 | 200 | 79 | 35 | 46 | 138 | 0 | 0 | 35 | 50 | 84 | 149 | 87 | 57 | 11 | 34 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 135 | 0 | 50 | 56 | 61 | 80 | 105 | 30 | 19 | 10 | 120 | 0 | 100 | 300 | 298 | 183 | 125 | 100 | 42 | 0 | 5 | 24 | 85 | 42 | 52 | 19 | 11 | 33 | 22 | 108 | 67 | 95 | 20 | 0 | 54 | 74 | 53 | 49 | 163 | 0 | 61 | 86 | 46 | 0 | 0 | 46 | 10 | 275 | 23 | 11 | 200 | 301 | 0 | 52 | 185 | 51 | 150 |  | 462 | 48 | 275 | 75 | 115 | 190 | 0 | 54 | 50 | 56 | 40 | 172 | 37 | 110 | 12 | 0 | 0 | 43 | 30 | 100 | 35 | 43 | 45 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 201 | 13 | 18 | 0 | 168 | 0 | 165 | 75 | 97 | 0 | 0 |  | 7805 | 2818 | 10623 | 3195 | 462 | 1900 | 3024 | 201 | 165 | 1568 | 108 | 0 | 0 | 105.31
21:00 | 65 | 120 | 0 | 0 | 365 | 88 | 35 | 365 | 272 | 98 | 0 | 390 | 200 | 100 | 95 | 55 | 116 | 0 | 0 | 35 | 93 | 102 | 140 | 87 | 40 | 11 | 40 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 196 | 0 | 135 | 0 | 50 | 56 | 60 | 80 | 105 | 38 | 19 | 22 | 100 | 0 | 100 | 330 | 331 | 144 | 110 | 100 | 42 | 0 | 5 | 45 | 85 | 42 | 16 | 19 | 11 | 33 | 22 | 124 | 64 | 95 | 20 | 0 | 54 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 47 | 10 | 280 | 23 | 11 | 150 | 301 | 0 | 52 | 185 | 0 | 150 |  | 462 | 48 | 275 | 73 | 115 | 239 | 0 | 55 | 49 | 66 | 40 | 191 | 37 | 110 | 12 | 0 | 0 | 43 | 30 | 100 | 50 | 43 | 44 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 215 | 11 | 18 | 0 | 171 | 0 | 166 | 98 | 97 | 0 | 0 |  | 7844 | 2947 | 10791 | 3207 | 462 | 1949 | 3043 | 215 | 165 | 1626 | 124 | 0 | 0 | 105.31
22:00 | 65 | 120 | 0 | 0 | 365 | 88 | 35 | 405 | 273 | 98 | 0 | 390 | 200 | 100 | 101 | 55 | 115 | 0 | 0 | 35 | 93 | 102 | 133 | 87 | 40 | 11 | 40 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 187 | 0 | 135 | 0 | 50 | 56 | 60 | 80 | 105 | 45 | 19 | 21 | 100 | 0 | 100 | 300 | 309 | 164 | 72 | 100 | 42 | 0 | 5 | 51 | 85 | 40 | 16 | 19 | 11 | 33 | 22 | 134 | 38 | 95 | 20 | 0 | 56 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 47 | 10 | 320 | 23 | 11 | 150 | 301 | 0 | 52 | 185 | 0 | 150 |  | 462 | 48 | 275 | 69 | 115 | 239 | 0 | 55 | 50 | 66 | 40 | 191 | 37 | 110 | 12 | 0 | 0 | 43 | 30 | 100 | 50 | 43 | 42 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 210 | 10 | 16 | 0 | 179 | 0 | 165 | 98 | 96 | 0 | 0 |  | 7840 | 2940 | 10780 | 3190 | 462 | 1957 | 3051 | 210 | 165 | 1611 | 134 | 0 | 0 | 0
23:00 | 65 | 120 | 0 | 0 | 365 | 88 | 35 | 405 | 272 | 98 | 0 | 390 | 240 | 100 | 100 | 55 | 115 | 0 | 0 | 30 | 93 | 102 | 133 | 87 | 40 | 10 | 40 | 54 | 55 | 55 | 22 | 25 | 31 | 33 | 33 | 50 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 188 | 0 | 135 | 0 | 50 | 48 | 59 | 80 | 105 | 45 | 19 | 21 | 100 | 0 | 100 | 275 | 305 | 190 | 72 | 100 | 42 | 0 | 5 | 51 | 85 | 40 | 16 | 19 | 11 | 33 | 22 | 130 | 42 | 95 | 20 | 0 | 60 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 47 | 0 | 0 | 46 | 10 | 305 | 23 | 11 | 150 | 300 | 0 | 51 | 185 | 0 | 150 |  | 462 | 32 | 275 | 70 | 64 | 239 | 0 | 52 | 49 | 58 | 40 | 191 | 37 | 110 | 0 | 0 | 0 | 43 | 30 | 100 | 50 | 43 | 42 | 51 | 0 | 18 | 9 | 10 | 0 | 0 | 149 | 12 | 16 | 0 | 167 | 0 | 136 | 96 | 97 | 0 | 0 |  | 7848 | 2748 | 10596 | 3196 | 462 | 1939 | 3029 | 149 | 164 | 1527 | 130 | 0 | 0 | 0
24:00 | 65 | 120 | 0 | 0 | 365 | 85 | 35 | 405 | 273 | 98 | 0 | 390 | 200 | 100 | 97 | 55 | 110 | 0 | 0 | 17 | 93 | 102 | 110 | 87 | 40 | 11 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 120 | 0 | 50 | 48 | 59 | 80 | 105 | 51 | 19 | 24 | 100 | 0 | 100 | 305 | 316 | 167 | 81 | 100 | 42 | 0 | 5 | 51 | 85 | 40 | 16 | 19 | 11 | 33 | 22 | 134 | 69 | 95 | 20 | 0 | 60 | 73 | 53 | 50 | 163 | 0 | 60 | 86 | 47 | 0 | 0 | 46 | 10 | 290 | 23 | 11 | 50 | 301 | 0 | 51 | 185 | 0 | 150 |  | 462 | 0 | 275 | 68 | 64 | 200 | 0 | 55 | 49 | 55 | 40 | 192 | 36 | 110 | 0 | 0 | 0 | 43 | 30 | 101 | 50 | 43 | 41 | 51 | 0 | 18 | 9 | 10 | 0 | 0 | 149 | 12 | 16 | 0 | 158 | 0 | 131 | 98 | 50 | 0 | 0 |  | 7712 | 2616 | 10328 | 3237 | 462 | 1935 | 2834 | 149 | 164 | 1413 | 134 | 0 | 0 | 0
KWH | 1448000 | 2766960 | 0 | 0 | 8689027 | 2021386 | 848288 | 9097190 | 7015000 | 1056800 | 0 | 9239376 | 5468480 | 1629120 | 1601040 | 1105397 | 2500728 | 0 | 0 | 239040 | 1487040 | 1325808 | 1637760 | 1344056 | 1578240 | 405980 | 835248 | 1131120 | 1087580 | 1248008 | 489168 | 600000 | 712980 | 771829 | 826800 | 872076 | 0 | 1928218 | 1907600 | 0 | 0 | 386100 | 0 | 4519219 | 0 | 2150187 | 0 | 1187040 | 703240 | 787395 | 1804920 | 2277120 | 692160 | 439632 | 401280 | 2698878 | 0 | 2394302 | 8033200 | 6921000 | 4327000 | 1187636 | 2390600 | 869400 | 0 | 120000 | 1043263 | 1601040 | 237656 | 607090 | 444888 | 236700 | 723700 | 471320 | 3078720 | 1442740 | 1286572 | 458064 | 14100 | 1319000 | 1776000 | 1162800 | 1119000 | 3658254 | 0 | 1371000 | 1776000 | 989280 | 0 | 0 | 1857831 | 5468480 | 7485300 | 474112 | 261168 | 835200 | 6363052 | 0 | 258031 | 4070400 | 58900 | 3697344 |  | 10968727 | 193700 | 7682112 | 1199040 | 1792320 | 3681600 | 0 | 383970 | 557280 | 401152 | 940500 | 4565000 | 596156 | 2181120 | 42745 | 0 | 0 | 430752 | 288884 | 2015790 | 1080960 | 893696 | 467421 | 723840 | 0 | 413520 | 209232 | 219442 | 0 | 0 | 3843300 | 62000 | 85000 | 0 | 4263009 | 0 | 4119445 | 1879026 | 506880 | 0 | 0 |  | 174852657 | 56687619 | 231540276 | 77421940 | 10968727 | 50092148 | 55641288 | 3843300 | 3835818 | 26644235 | 3078720 | 14100 | 0
Fuel Cost | 1245280 | 2379585.6 | 0 | 0 | 5560977.28 | 1637322.66 | 797390.72 | 5549285.9 | 4279150 | 10155848 | 0 | 6190381.92 | 83066211.2 | 10230873.6 | 10694947.2 | 6753975.67 | 1625473.2 | 0 | 0 | 3719462.4 | 9294000 | 8737074.72 | 15837139.2 | 8561636.72 | 9453657.6 | 6491620.2 | 5571104.16 | 8064885.6 | 6797375 | 7825010.16 | 366876 | 450000 | 0 | 0 | 0 | 8249838.96 | 0 | 0 | 0 | 0 | 0 | 3656367 | 0 | 61687339.35 | 0 | 47110597.17 | 0 | 10434081.6 | 7573894.8 | 7661353.35 | 11172454.8 | 14710195.2 | 4526726.4 | 373687.2 | 0 | 2455978.98 | 0 | 2178814.82 | 4980584 | 4775490 | 3028900 | 819468.84 | 2294976 | 582498 | 0 | 110400 | 855475.66 | 1520988 | 2576191.04 | 4504607.8 | 342563.76 | 177525 | 557249 | 353490 | 21058444.8 | 1082055 | 11823596.68 | 352709.28 | 0 | 1371760 | 1847040 | 1116288 | 1007100 | 2853438.12 | 0 | 1562940 | 1900320 | 1088208 | 0 | 0 | 1727782.83 | 5085686.4 | 4790592 | 355584 | 198487.68 | 14474016 | 46195757.52 | 0 | 4399428.55 | 29103360 | 1004245 | 0 |  | 55940507.7 | 5646355 | 5147015.04 | 9604310.4 | 14858332.8 | 59200128 | 0 | 6128161.2 | 6274972.8 | 4725570.56 | 7411140 | 3149850 | 590194.44 | 16140288 | 1439651.6 | 0 | 0 | 4932110.4 | 3096836.48 | 18061478.4 | 9350304 | 7953894.4 | 4978033.65 | 7180492.8 | 0 | 454872 | 196678.08 | 166117.594 | 0 | 0 | 14835138 | 1998260 | 2275450 | 0 | 0 | 0 | 60391063.7 | 0 | 8784230.4 | 0 | 0 |  | 605007121.3 | 340911437.444 | 945918558.744 | 54512793.334 | 55940507.7 | 37021737.67 | 447083511.74 | 14835138 | 0 | 315466425.5 | 21058444.8 | 0 | 0
Yesterday Day Peak | 65 | 120 | 0 | 0 | 365 | 89 | 30 | 345 | 261 | 0 | 0 | 400 | 200 | 90 | 65 | 55 | 139 | 0 | 0 | 0 | 89 | 84 | 32 | 74 | 82 | 21 | 34 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 25 | 0 | 84 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 60 | 0 | 50 | 0 | 15 | 68 | 92 | 26 | 16 | 2 | 120 | 0 | 100 | 372 | 300 | 170 | 8 | 100 | 20 | 0 | 5 | 51 | 85 | 0 | 30 | 19 | 11 | 33 | 20 | 126 | 47 | 32 | 20 | 0.8 | 58 | 74 | 47 | 50 | 163 | 0 | 57 | 86 | 46 | 0 | 0 | 44 | 10 | 280 | 22 | 11 | 0 | 273 | 0 | 0 | 180 | 0 | 150 |  | 462 | 0 | 294 | 78 | 66 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 50 | 35 | 0 | 16 | 0 | 18 | 9 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 165 | 0 | 178 | 95 | 0 | 0 | 0 |  | 9009.8 | DayPeak
Yesterday Evening Peak | 65 | 120 | 0 | 0 | 365 | 88 | 35 | 365 | 272 | 98 | 0 | 390 | 200 | 100 | 95 | 55 | 116 | 0 | 0 | 35 | 93 | 102 | 140 | 87 | 40 | 11 | 40 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 50 | 0 | 85 | 80 | 0 | 0 | 16 | 0 | 196 | 0 | 135 | 0 | 50 | 56 | 60 | 80 | 105 | 38 | 19 | 22 | 100 | 0 | 100 | 330 | 331 | 144 | 110 | 100 | 42 | 0 | 5 | 45 | 85 | 42 | 16 | 19 | 11 | 33 | 22 | 124 | 64 | 95 | 20 | 0 | 54 | 74 | 53 | 50 | 163 | 0 | 60 | 86 | 46 | 0 | 0 | 47 | 10 | 280 | 23 | 11 | 150 | 301 | 0 | 52 | 185 | 0 | 150 |  | 462 | 48 | 275 | 73 | 115 | 239 | 0 | 55 | 49 | 66 | 40 | 191 | 37 | 110 | 12 | 0 | 0 | 43 | 30 | 100 | 50 | 43 | 44 | 52 | 0 | 18 | 9 | 10 | 0 | 0 | 215 | 11 | 18 | 0 | 171 | 0 | 166 | 98 | 97 | 0 | 0 |  | 10791 | EvPeak
Forecast for Evening | 65 | 120 | 0 | 0 | 365 | 88 | 77 | 412 | 340 | 98 | 0 | 450 | 305 | 100 | 100 | 55 | 140 | 0 | 0 | 100 | 93 | 102 | 149 | 100 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 135 | 0 | 51 | 73 | 75 | 90 | 105 | 50 | 19 | 22 | 120 | 0 | 100 | 360 | 360 | 225 | 125 | 100 | 43 | 0 | 53 | 51 | 85 | 50 | 52 | 19 | 11 | 33 | 22 | 164 | 100 | 95 | 20 | 0 | 57 | 75 | 53 | 50 | 163 | 240 | 60 | 86 | 50 | 0 | 0 | 45 | 10 | 341 | 23 | 11 | 200 | 300 | 0 | 100 | 192 | 100 | 150 |  | 467 | 48 | 400 | 90 | 115 | 225 | 0 | 54 | 50 | 80 | 40 | 194 | 33 | 110 | 30 | 0 | 0 | 51 | 36 | 100 | 50 | 43 | 43 | 43 | 42 | 18 | 10 | 11 | 0 | 0 | 215 | 16 | 18 | 0 | 214 | 0 | 180 | 98 | 97
Forecast for Day | 65 | 120 | 0 | 0 | 300 | 88 | 40 | 350 | 320 | 50 | 0 | 450 | 305 | 100 | 100 | 55 | 100 | 0 | 0 | 100 | 93 | 102 | 149 | 100 | 88 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 225 | 0 | 100 | 0 | 51 | 73 | 75 | 90 | 105 | 50 | 19 | 10 | 120 | 0 | 100 | 360 | 360 | 200 | 125 | 100 | 43 | 0 | 53 | 51 | 85 | 0 | 52 | 19 | 11 | 33 | 21 | 105 | 100 | 95 | 20 | 2 | 57 | 75 | 53 | 50 | 163 | 240 | 60 | 86 | 50 | 0 | 0 | 45 | 10 | 341 | 23 | 11 | 0 | 200 | 0 | 50 | 150 | 0 | 150 |  | 467 | 0 | 400 | 51 | 115 | 225 | 0 | 0 | 36 | 70 | 40 | 194 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 43 | 43 | 0 | 18 | 10 | 11 | 0 | 0 | 150 |  | 18 | 0 | 214 | 0 | 180 | 98 | 97
Generation at 08:00(Today) | 65 | 120 | 0 | 0 | 300 | 87 | 35 | 345 | 321 | 0 | 0 | 400 | 200 | 10 | 15 | 15 | 70 | 0 | 0 | 0 | 7 | 7 | 16 | 10 | 32 | 0 | 12 | 18 | 18 | 36 | 19 | 25 | 22 | 33 | 17 | 0 | 0 | 85 | 80 | 0 | 0 | 8 | 0 | 198 | 0 | 50 | 0 | 32 | 16 | 0 | 68 | 53 | 25 | 19 | 11 | 100 | 0 | 100 | 295 | 276 | 191 | 73 | 100 | 42 | 0 | 5 | 51 | 85 | 0 | 8 | 19 | 11 | 33 | 15 | 100 | 71 | 8 | 20 | 0 | 58 | 74 | 50 | 50 | 100 | 102 | 60 | 86 | 47 | 0 | 0 | 45 | 10 | 310 | 23 | 11 | 0 | 127 | 0 | 0 | 130 | 0 | 150 | 0 | 467 | 0 | 320 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 192 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 42 | 8 | 0 | 18 | 9 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 131 | 96 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8007.3 | 8:00
| Highest Generation |  | 10791 | 21:00
| Day Peak Generation |  | 9009.8 | 12:00
| Evening Peak Generation |  | 10791 | 21:00
| HVDC Max Flow |  | 462 | 2:00
| HVDC EvPeak Flow |  | 462 | 21:00
| Load factor L.F |  | 89.4%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-07-09
Till now the maximum generation is : - |  |  | 11059 | 20:00 | Hrs on | 2018-07-07
The Summary of Yesterday's |  | 2018-07-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9009.8 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7794.4 | MW
Evening Peak Generation : |  | 10791 | MW Hour : | 21:00 | Available Max Generation : |  | 12540 | MW
E.P. Demand (at gen end) : |  | 10791 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10791 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1540 | MW
Total Gen. (MKWH) : |  | 231.5403 | System Load Factor : | 89.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -760 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-07-09
Actual : | 105.24 | Ft.(MSL) , | Rule curve : | 85.28 | Ft.( MSL )
Gas Consumed : | Total = | 963.78 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 91534531.004
|  | Coal : | 14835138 | Oil : | 762549937.24 | Total : | 868919606.244
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3925.9462 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1334.8795 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1195.9794 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1080.6582 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 976.5807 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 788.0657 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 440.8528 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 202.9111 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 607.7944 |  |  | 0 | 0%
Total | 0 |  | 10553.6679 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
3) Ghorasal Unit-4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Bibiyana 230 kV bus-2 and ICT-2 were shut down from 11:40 to 18:41 for bay extension by project division.
b) Hathazari S/S-Hathazari 132 kV Ckt was under shut down from 12:08 to 14:04 for check the breaker at S/S end.
c) Barisal 132/33 kV T1 & T2 transformers tripped at 16:10 from 33 kV side showing inst E/F & O/C due to 33 kV |  |  |  | About 90 MW Power interruption occurred under Barisal S/S
feeder fault and were switched on at 16:15. |  |  |  | area from 16:10 to 16:15.
d) Niamatpur 132/33 kV T1 transformer associated 33 kV bus were under shut down from 16:50 to 17:50 due to |  |  |  | About 12 MW Power interruption occurred under Niamatpur S/S
Tanor -1 33 kV R-phase feeder isolator red hot. |  |  |  | area from 16:50 to 17:50.
e) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 17:46 from both ends showing dist RST, auto reclose at Ashuganj
end and dist RST, Z1 & SOTF at Sirajganj end and was switched on at 18:28.
f) Ramganj 132/33 kV T1 transformer was under shut down from 20:05 to 20:24 due to 33 kV CT Y-phase red hot. |  |  |  | About 30 MW Power interruption occurred under Ramganj S/S
area from 20:05 to 20:24.
g) Bhulta-Haripur 132 kV Ckt was under shut down from 21:03 to 22:33 for CVT B-phase red hot at Bhulta end.
h) Bakulia-Sikalbaha 132 kV Ckt-1 was shut down at 06:06(09/07/2018) for C/M.
i) Bakulia 132/33 kV T1 transformer was shut down at 06:08(09/07/2018) for C/M.
j) Bashundhara 132/33 kV T3 transformer was under shut down from 05:17 to 06:00 (09/07/2018) for C/M.
k) Bibiyana-Shahjibazar 230 kV Ckt-1 & Bibiyana 230 kV bus-1 were under shut down from 22:12 to 00:14
(09/07/2018) for D/W.
l) After maintenance Bibiyana 230 kV diameter-5 was switched on at 01:34(09/07/2017).
m) Shahjibazar 330 MW GT-2 was synchronized at 02:17(09/07/2018).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-07-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 65 | 1448000
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2766960 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8689027
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 35 | 848288 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 88 | 2021386 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 9097190 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 98 | 1056800 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 272 | 7015000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 390 | 9239376 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1629120
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 200 | 5468480 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 95 | 1601040
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1105397
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 87 | 1344056 | Engine problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 489168
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 35 | 239040 | Low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 93 | 1487040 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 116 | 2500728 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 11 | 405980 | Low demand
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1325808
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 835248 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1131120
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 140 | 1637760
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1087580
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1248008
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 40 | 1578240 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1312980 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 771829
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 826800
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 872076
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 301 | 6363052
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 52 | 258031 | Low demand
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 58900
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 0 | 150 | 3697344
| Dhaka area Total |  |  |  | 5399 | 3772 | 81456852
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 386100 | Engine problem
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 38 | 692160 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 165 | 3835818 | # 5 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 196 | 4519219 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2150187
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 50 | 1187040
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 56 | 703240
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 60 | 787395
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1804920 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 439632
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 22 | 401280
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 105 | 2277120
| Chittagong area Total |  |  |  | 1561 | 942 | 19184111
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2698878 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | S/D due to gas shortage.
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2394302 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 144 | 4327000 | FGMO
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 8033200 | FGMO
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 331 | 6921000 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 42 | 869400
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 120000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 110 | 1187636 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 45 | 1043263 | Gas shortage
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1601040
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 42 | 237656
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2390600 | ST S/D
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 444888
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236700
** | Tripura |  | Imported power | 0 | 160 | 124 | 3078720
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 723700
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 16 | 607090 | Low demand
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 22 | 471320
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 150 | 835200 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1809 | 38221593
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 64 | 1442740 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 458064
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1286572
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14100
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 185 | 4070400
| Mymensingh Area Total |  |  |  | 522 | 364 | 7271876
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 1319000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 74 | 1776000
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3658254
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1162800
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1119000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 261168
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 60 | 1371000 | FGMO
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1776000
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 46 | 989280
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 0 | 0 | Under maint.
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 47 | 1857831
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 474112
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 280 | 7485300 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 5468480
| Sylhet Area Total |  |  |  | 1549 | 957 | 28718225
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 48 | 193700
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 462 | 10968727
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 73 | 1199040 | Engine problem
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 115 | 1792320
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 49 | 557280
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 239 | 3681600
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 66 | 401152
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 275 | 7682112 | Gas shortage
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 940500
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 55 | 383970
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 97 | 506880
| Khulna Area Total |  |  |  | 1769 | 1519 | 28307281
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2181120
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 12 | 42745 | Low demand
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 37 | 596156
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 191 | 4565000
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 98 | 1879026
| Barisal Area Total |  |  |  | 462 | 448 | 9264047
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 430752
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 30 | 288884
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 1080960
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 893696 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 467421
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 171 | 0 | FGMO
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 166 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 413520 | Engine problem
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 9 | 209232
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 10 | 219442
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 52 | 723840
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 2015790
| Rajshahi Area Total |  |  |  | 1123 | 736 | 6743537
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 215 | 3843300
120 | Rangpur GT |  | PDB | 1*20 | 20 | 11 | 62000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 85000
| Rangpur Area Total |  |  |  | 484 | 244 | 3990300
| Total |  |  |  | 15410 | 10791 | 223157822
| Eastern Grid Total |  |  |  | 11572 | 7844 | 174852657
| Western Grid Total |  |  |  | 3838 | 2947 | 48305165
| National Grid Total |  |  |  | 15410 | 10791 | 223157822
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-07-08 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7016 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3328 | MW
i) Dhaka area |  |  | 3825 | MW | i) Khulna area |  |  | 1336 | MW
ii) Chittagong area |  |  | 1032 | MW | ii) Rajshahi area |  |  | 1120 | MW
iii) Comilla area |  |  | 966 | MW | iii) Barisal area |  |  | 276 | MW
iv) Mymensingh area |  |  | 758 | MW | iv) Rangpur area |  |  | 596 | MW
v) Sylhet area |  |  | 435 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10344 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 138 | 1200 | Kishorganj | 85 | 1930 | Goalpara | 38 | 2100
Munsiganj | 110 | 2100 | Netrokona | 80 | 1930 | Central s/s | 72 | 2000
Sonargaon | 41 | 2100 | Jamalpur | 115 | 2200 | Noapara | 89 | 2100
Shyampur | 166 | 1000 | Sherpur | 84 | 2300 | Jessore | 144 | 1930
Bhulta | 180 | 1500 | Srimongal | 35 | 2100 | Jhenida | 98 | 2000
Madanganj | 58 | 900 | Shahjibazar | 101 | 2200 | Bottail | 126 | 2000
Shitalakhya | 109 | 1000 | Fenchuganj | 46 | 2000 | G.K Project | 53 | 2000
Rahim steel | 9 | 1400 | Kulawara | 39 | 2100 | Faridpur | 150 | 2100
Matuail | 96 | 1000 | Sylhet | 137 | 1930 | Madaripur | 140 | 2200
Ghorasal | 78 | 2100 | Chatak | 23 | 2100 | Gopalganj | 82 | 2100
Narsingdi | 116 | 100 | Sunamganj | 32 | 2100 | Bagerhat | 82 | 2100
Haripur (SBU) | 96 | 2200 | Biani Bazar | 39 | 2200 | Mongla | 38 | 1000
Ullon | 92 | 1500 | Comilla (S) | 152 | 1500 | Satkhira | 90 | 2200
Hasnabad | 202 | 2100 | Comilla(N) | 129 | 2000 | Gallamari | 44 | 1300
Magbazar | 135 | 1600 | Chandpur | 120 | 2100 | Magura | 52 | 193
Maniknagar | 98 | 1300 | Feni | 122 | 2200 | Chuadanga | 80 | 2200
Bangabhaban | 40 | 1200 | Chowmuhani | 176 | 2100 | Barisal | 120 | 2100
Narinda | 84 | 1200 | Ashuganj | 58 | 2200 | Patuakhali | 90 | 2100
Dhanmondi | 125 | 1200 | Daudkandi | 102 | 2100 | Bhandaria | 44 | 2100
Lalbag | 89 | 2100 | B.Baria | 131 | 2100 | Ishurdi | 55 | 2000
Madartek | 50 | 2000 | Ramganj | 33 | 2200 | Ruppur Paromanobik | 2 | 900
Mirpur | 107 | 1900 | Madunaghat | 52.5 | 1500 | Natore | 115 | 100
Kalyanpur | 120 | 1300 | Hathazari | 90 | 2100 | Bogra | 138 | 2000
Gulshan | 142 | 1500 | Khulshi | 162 | 1400 | Noagaon | 104 | 2000
Uttara | 96 | 1200 | Halishahar | 130 | 1500 | Rajshahi | 139 | 100
Kamrangirchar | 75 | 1900 | Baraulia | 161 | 300 | C.Nawabganj | 75 | 2000
Savar | 132 | 1400 | Sikalbaha | 36 | 1930 | Amnura | 44 | 1930
Bhasantec | 163 | 1300 | Dohazari | 30 | 2100 | Pabna | 111 | 2000
Agargaon | 49 | 1900 | Cox'sbazar | 82 | 100 | Shahjadpur | 88 | 2000
Satmosjid | 100 | 900 | Chandraghona | 32 | 1900 | Serajganj | 90 | 2000
Tongi | 138 | 1600 | Kaptai | 4 | 1930 | Niyamatpur | 50 | 2000
Kabirpur | 215 | 1200 | A. Khaer Stl. | 10 | 1700 | Joypurhat | 42 | 2000
Basundhara | 126 | 2000 | Bakulia | 106 | 1930 | Rangpur | 116 | 1930
Manikganj | 107 | 2000 | Julda | 17 | 200 | Lalmonirhat | 85 | 1930
Joydevpur | 238 | 1100 | TK chemical | 5.6 | 1200 | Saidpur | 97 | 1930
New Tongi | 109 | 2000 | Modern Steel | 11 | 400 | Purbasadipur | 91 | 100
Korda | 236 | 2100 | Shahmirpur | 28 | 100 | Thakurgaon | 65 | 1930
Dhamrai | 24 | 1930 | Abul Khair 230 | 109 | 500 | Palashbari | 96 | 100
Tangail | 171 | 2100 | BSRM | 111 | 1800 | Barapukuria | 44 | 100
Mymensing | 234 | 2100 | Khagrachhari | 17 | 2100 | Panchagar | 34 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-07-08
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 405 | 8:00 | 396 | 22:00 | Kaliakoir | 389 | 4:00 | 380 | 18:30
Bheramara | 227 | 4:00 | 220 | 9:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 228 | 15:00 | Tongi | 222 | 4:00 | 215 | 9:00
Ishurdi | 233 | 11:00 | 223 | 19:30 | Comilla (N) | 228 | 19:30 | 224 | 23:00
Ashuganj | 235 | 5:00 | 230 | 9:00 | Hathazari | 220 | 5:00 | 213 | 7:00
Serajganj | 225 | 18:30 | 215 | 19:30 | Megnaghat | 226 | 23:00 | 220 | 18:00
Baghabari | 223 | 11:00 | 215 | 20:00 | Fenchuganj | 237 | 13:00 | 229 | 19:00
Barapukuria | 230 | 6:00 | 219 | 21:00 | Siddhirganj | 224 | 4:00 | 218 | 9:00
Bogra | 218 | 18:30 | 201 | 19:30 | Maniknagar | 221 | 1:00 | 216 | 9:00
Khulna South | 242 | 18:30 | 230 | 1:00 | Old Airport | 223 | 4:00 | 216 | 9:00
Rampura | 221 | 3:00 | 216 | 10:00 | Barisal | 230 | 18:30 | 223 | 1:00
Haripur | 221 | 20:00 | 217 | 11:00 | AKSML | 218 | 6:00 | 210 | 1:00
Hasnabad | 223 | 2:00 | 217 | 10:00 | BSRM | 221 | 6:00 | 214 | 12:00
Aminbazar | 223 | 4:00 | 217 | 8:00 | Bibiyana | 234 | 6:00 | 227 | 19:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1930 | 129 | 900 | B.Baria | 137 | 1300 | 131 | 1800
Munsiganj | 136 | 2000 | 128 | 800 | Ramganj | 128 | 700 | 122 | 2400
Megnaghat | 135 | 1930 | 129 | 1000 | Madanhat | 132 | 1800 | 128 | 1700
Shyampur | 132 | 1900 | 124 | 900 | Hathazari | 130 | 800 | 126 | 1500
Bhulta | 126 | 600 | 121 | 900 | Khulshi | 127 | 500 | 120 | 1500
Madanganj | 137 | 1400 | 127 | 800 | Halishahar | 130 | 400 | 126 | 1500
Shitalakhya | 139 | 2000 | 128 | 1830 | Baraulia | 128 | 400 | 124 | 800
Rahim steal | 134 | 2000 | 130 | 800 | Sikalbaha | 130 | 600 | 120 | 1400
Matuail | 134 | 1930 | 128 | 1000 | Dohazari | 128 | 300 | 124 | 1400
Ghorasal | 136 | 2100 | 135 | 100 | Cox'sbazar | 125 | 1100 | 116 | 100
Narsinghdi | 130 | 1900 | 125 | 900 | Chandraghona | 131 | 700 | 128 | 1400
Haripur (SBU) | 134 | 300 | 130 | 1100 | Kaptai | 130 | 100 | 130 | 100
Ullon | 132 | 600 | 126 | 1200 | A. Khaer Stl. | 127 | 100 | 125 | 1400
Hasnabad | 134 | 500 | 130 | 1800 | Bakulia | 128 | 700 | 125 | 1400
Magbazar | 134 | 600 | 126 | 1200 | Julda | 130 | 700 | 126 | 1400
Maniknagar | 134 | 100 | 129 | 1200 | TK Chemical | 132 | 500 | 129 | 1500
Bangabhaban | 134 | 100 | 129 | 1200 | Modern Steel | 129 | 600 | 124 | 700
Narinda | 134 | 100 | 129 | 1200 | Shahmirpur | 130 | 600 | 126 | 1500
Dhanmondi | 134 | 100 | 129 | 1200 | Khagrachhari | 130 | 100 | 127 | 1500
Lalbag | 131 | 600 | 126 | 1200 | Goalpara | 137 | 1300 | 131 | 100
Madartek | 132 | 500 | 128 | 1200 | Central s/s | 137 | 1600 | 132 | 100
Mirpur | 134 | 400 | 128 | 1000 | Noapara | 135 | 1300 | 128 | 100
Kalyanpur | 135 | 200 | 130 | 800 | Jessore | 130 | 700 | 122 | 100
Gulshan | 133 | 500 | 126 | 1200 | Jhenida | 131 | 1600 | 118 | 2000
Uttara | 131 | 400 | 125 | 1200 | Bottail | 135 | 700 | 130 | 100
Kamrangirchar | 135 | 100 | 127 | 900 | G.K.Project | 142 | 1700 | 135 | 100
Savar | 133 | 400 | 127 | 900 | Faridpur | 135 | 1830 | 125 | 100
Bhasantec | 132 | 500 | 125 | 1200 | Madaripur | 135 | 1830 | 125 | 100
Agargaon | 132 | 400 | 127 | 1000 | Gopalganj | 138 | 1830 | 118 | 100
Satmosjid | 132 | 400 | 126 | 900 | Bagerhat | 136 | 1400 | 129 | 2100
Tongi | 138 | 200 | 126 | 1100 | Mongla | 132 | 1600 | 126 | 300
Kabirpur | 133 | 1300 | 128 | 2100 | Satkhira | 135 | 1400 | 128 | 2100
Basundhara | 129 | 100 | 124 | 900 | Gallamari | 137 | 1400 | 131 | 100
Manikganj | 138 | 1300 | 132 | 2100 | Magura | 130 | 1600 | 115 | 2000
Joydevpur | 141 | 1400 | 130 | 900 | Chuadanga | 126 | 1800 | 111 | 2000
New Tongi | 133 | 300 | 127 | 1500 | Barisal | 139 | 1100 | 135 | 1700
Kodda | 140 | 1800 | 130 | 700 | Patuakhali | 137 | 1600 | 130 | 100
Dhamrai | 136 | 600 | 129 | 2100 | Bhandaria | 136 | 1800 | 130 | 100
Tangail | 135 | 1100 | 125 | 2100 | Ishurdi | 141 | 1700 | 133 | 2000
Mymensing | 131 | 1300 | 121 | 2000 | Ruppur Paromanobik | 140 | 1200 | 133 | 1930
Kishorganj | 131 | 1100 | 122 | 100 | Natore | 140 | 1830 | 127 | 1930
Netrokona | 132 | 1300 | 120 | 100 | Bogra | 134 | 1830 | 117 | 1930
Jamalpur | 136 | 1700 | 124 | 600 | Noagaon | 118 | 700 | 108 | 2000
Sherpur | 136 | 1600 | 124 | 400 | Rajshahi | 137 | 1830 | 124 | 1930
Srimongal | 138 | 600 | 134 | 1800 | C.Nawabganj | 138 | 1830 | 123 | 1930
Shahjibazar | 138 | 1000 | 131 | 1900 | Amnura | 139 | 1600 | 128 | 1930
Fenchuganj | 135 | 400 | 131 | 1800 | Pabna | 135 | 1830 | 125 | 2000
Khulawara | 134 | 300 | 130 | 1830 | Shahjadpur | 140 | 1830 | 133 | 2000
Sylhet | 133 | 600 | 128 | 1800 | Serajganj | 131 | 1800 | 122 | 2000
Chatak | 132 | 500 | 126 | 1800 | Niyamatpur | 125 | 1830 | 102 | 2000
Sunamganj | 132 | 700 | 125 | 1900 | Joypurhat | 125 | 1830 | 105 | 2000
Biani Bazar | 133 | 700 | 126 | 1900 | Rangpur | 120 | 1800 | 102 | 1930
Comilla(s) | 129 | 1800 | 122 | 100 | Lalmonirhat | 115 | 1700 | 90 | 1930
Comilla(n) | 135 | 600 | 130 | 2300 | Saidpur | 119 | 1830 | 98 | 1930
Chandpur | 127 | 1500 | 121 | 2200 | Purbasadipur | 130 | 700 | 114 | 1930
Feni | 120 | 1700 | 115 | 2100 | Thakurgaon | 122 | 700 | 102 | 2000
Chowmuhani | 122 | 1100 | 115 | 100 | Palashbari | 123 | 1800 | 105 | 100
Ashuganj | 137 | 1400 | 133 | 100 | Barapukuria | 130 | 600 | 119 | 1930
Daudkandi | 137 | 1930 | 128 | 700 | Panchagar | 122 | 1900 | 96 | 1930
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-07-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 720 | 7712 | 2616 | 10328 |  |  |  | QF-LDC-12
0:30 | 710 | 7608.5 | 2606.5 | 10215 | Date: | 2018-07-08
1:00 | 700 | 7505 | 2597 | 10102
1:30 | 695 | 7388 | 2566.5 | 9954.5
2:00 | 690 | 7271 | 2536 | 9807
2:30 | 675 | 7216 | 2516.5 | 9732.5 | [5 empty] | Gen. at Eve. Peak | 10791 | 10791 MW (21:00 )
3:00 | 660 | 7161 | 2497 | 9658 | [6 empty] | 21:00
3:30 | 650 | 7103.5 | 2454 | 9557.5 | [5 empty] | Gen. at Day Peak | 9009.8 | 9009.8 MW (12:00 )
4:00 | 640 | 7046 | 2411 | 9457 | [6 empty] | 12:00
4:30 | 620 | 6901 | 2383.5 | 9284.5 | [5 empty] | Highest Generation | 10791
5:00 | 600 | 6756 | 2356 | 9112 | [6 empty] | 21:00
5:30 | 560 | 6531.5 | 2268.5 | 8800
6:00 | 520 | 6307 | 2181 | 8488
6:30 | 490 | 6136.5 | 2135.5 | 8272
7:00 | 460 | 5966 | 2090 | 8056
7:30 | 415 | 5970.15 | 2061.5 | 8031.65
8:00 | 370 | 5974.3 | 2033 | 8007.3
8:30 | 365 | 6225.8 | 2038 | 8263.8
9:00 | 360 | 6477.3 | 2043 | 8520.3
9:30 | 370 | 6560.75 | 2037.5 | 8598.25
10:00 | 380 | 6644.2 | 2032 | 8676.2
10:30 | 400 | 6735.1 | 2027.5 | 8762.6
11:00 | 420 | 6826 | 2023 | 8849
11:30 | 420 | 6859.4 | 2070 | 8929.4
12:00 | 420 | 6892.8 | 2117 | 9009.8
12:30 | 450 | 6976.25 | 2099.5 | 9075.75
13:00 | 480 | 7059.7 | 2082 | 9141.7
13:30 | 480 | 6950 | 2062 | 9012
14:00 | 480 | 6840.3 | 2042 | 8882.3
14:30 | 490 | 7085.05 | 2075 | 9160.05
15:00 | 500 | 7329.8 | 2108 | 9437.8
15:30 | 470 | 7272.8 | 2097.5 | 9370.3
16:00 | 440 | 7215.8 | 2087 | 9302.8
16:30 | 390 | 6964 | 2115 | 9079
17:00 | 340 | 6712.2 | 2143 | 8855.2
17:30 | 260 | 6437.15 | 2177.5 | 8614.65
18:00 | 180 | 6162.1 | 2212 | 8374.1
18:30 | 185 | 6515.55 | 2376 | 8891.55
19:00 | 190 | 6869 | 2540 | 9409
19:30 | 680 | 7797 | 2762 | 10559
20:00 | 760 | 7805 | 2818 | 10623 |  |  |  | Executive Engineer
20:30 | 700 | 7824.5 | 2882.5 | 10707 |  |  |  | Network Operation Division
21:00 | 640 | 7844 | 2947 | 10791
21:30 | 630 | 7842 | 2943.5 | 10785.5
22:00 | 620 | 7840 | 2940 | 10780 |  |  |  |  | Page 6 of 7
22:30 | 650 | 7844 | 2844 | 10688
23:00 | 680 | 7848 | 2748 | 10596
23:30 | 700 | 7780 | 2682 | 10462
24:00 | 720 | 7712 | 2616 | 10328
10791 MW (21:00 )
9009.8 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-07-08 |  | Energy | 231540276
[10 empty] | 2018-07-08 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3237 | 462 | 1935 | 2834 | 149 | 164 | 1413 | 0 | 134
0:30 | 3283.5 | 459 | 1988.5 | 2695 | 148.5 | 153.5 | 1354 | 0 | 133 | Date: | 2018-07-08
1:00 | 3330 | 456 | 2042 | 2556 | 148 | 143 | 1295 | 0 | 132
1:30 | 3320.5 | 459 | 2053.5 | 2469.5 | 149 | 143 | 1228 | 0 | 132 | [7 empty] | Total Energy | 231.5403 | Total Energy Gen 231.540 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 231.540 MKWHr
2:00 | 3311 | 462 | 2065 | 2383 | 150 | 143 | 1161 | 0 | 132 | [7 empty] | Energy not Served | 0
2:30 | 3309.5 | 462 | 2074 | 2302 | 151.5 | 153.5 | 1140 | 0 | 140 | [7 empty] | Energy Requirement | 231.5403
3:00 | 3308 | 462 | 2083 | 2221 | 153 | 164 | 1119 | 0 | 148
3:30 | 3310.5 | 462 | 2073 | 2163 | 149.5 | 164 | 1089.5 | 0 | 146 | [6 empty] | Shortage
4:00 | 3313 | 462 | 2063 | 2105 | 146 | 164 | 1060 | 0 | 144
4:30 | 3316 | 462 | 2038.5 | 2009 | 150 | 166 | 1003 | 0 | 140
5:00 | 3319 | 462 | 2014 | 1913 | 154 | 168 | 946 | 0 | 136
5:30 | 3288.5 | 462 | 1996.5 | 1695 | 152 | 168 | 909 | 0 | 129
6:00 | 3258 | 462 | 1979 | 1477 | 150 | 168 | 872 | 0 | 122
6:30 | 3212.5 | 462 | 1978 | 1345.5 | 151 | 168 | 838 | 0 | 117 |  |  |  |  | Coal
7:00 | 3167 | 462 | 1977 | 1214 | 152 | 168 | 804 | 0 | 112
7:30 | 3182 | 462 | 1950.5 | 1209 | 151 | 168 | 798 | 0 | 111 |  |  |  | Oil |  |  |  | ,
8:00 | 3197 | 462 | 1924 | 1204 | 150 | 168 | 792 | 0 | 110
8:30 | 3213 | 462 | 1918.5 | 1395 | 150 | 168 | 849 | 0 | 108
9:00 | 3229 | 462 | 1913 | 1586 | 150 | 168 | 906 | 0 | 106
9:30 | 3222 | 462 | 1891 | 1691 | 150 | 166 | 900.5 | 0 | 115
10:00 | 3215 | 462 | 1869 | 1796 | 150 | 164 | 895 | 0 | 124
10:30 | 3241 | 462 | 1825.5 | 1916 | 150 | 164 | 881 | 0 | 122
11:00 | 3267 | 462 | 1782 | 2036 | 150 | 164 | 867 | 0 | 120
11:30 | 3255 | 462 | 1789.5 | 2142.5 | 150 | 164 | 842.5 | 0 | 123
12:00 | 3243 | 462 | 1797 | 2249 | 150 | 164 | 818 | 0 | 126
12:30 | 3234.5 | 462 | 1787.5 | 2328.5 | 150 | 164.5 | 824 | 0 | 124
13:00 | 3226 | 462 | 1778 | 2408 | 150 | 165 | 830 | 0 | 122
13:30 | 3226 | 462 | 1778 | 2408 | 150 | 165 | 830 | 0 | 122
14:00 | 3226 | 462 | 1778 | 2408 | 150 | 165 | 830 | 0 | 122
14:30 | 3178 | 443 | 1743.5 | 2546.5 | 150 | 164.5 | 926 | 0 | 137
15:00 | 3130 | 424 | 1709 | 2685 | 150 | 164 | 1022 | 0 | 152
15:30 | 3117 | 424 | 1699.5 | 2653.5 | 150 | 159.5 | 1020.5 | 0 | 145
16:00 | 3104 | 424 | 1690 | 2622 | 150 | 155 | 1019 | 0 | 138
16:30 | 3057 | 424 | 1626.5 | 2528.5 | 150 | 155 | 1004.5 | 0 | 133
17:00 | 3010 | 424 | 1563 | 2435 | 150 | 155 | 990 | 0 | 128
17:30 | 3017.5 | 442.5 | 1456 | 2268.5 | 150 | 155 | 1005 | 0 | 120
18:00 | 3025 | 461 | 1349 | 2102 | 150 | 155 | 1020 | 0 | 112
18:30 | 3131.5 | 461.5 | 1411 | 2273.5 | 150 | 155 | 1205 | 0 | 104
19:00 | 3238 | 462 | 1473 | 2445 | 150 | 155 | 1390 | 0 | 96
19:30 | 3210 | 461 | 1842 | 3007 | 167 | 165 | 1597 | 0 | 110
20:00 | 3195 | 462 | 1900 | 3024 | 201 | 165 | 1568 | 0 | 108
20:30 | 3201 | 462 | 1924.5 | 3033.5 | 208 | 165 | 1597 | 0 | 116
21:00 | 3207 | 462 | 1949 | 3043 | 215 | 165 | 1626 | 0 | 124
21:30 | 3198.5 | 462 | 1953 | 3047 | 212.5 | 165 | 1618.5 | 0 | 129
22:00 | 3190 | 462 | 1957 | 3051 | 210 | 165 | 1611 | 0 | 134
22:30 | 3193 | 462 | 1948 | 3040 | 179.5 | 164.5 | 1569 | 0 | 132
23:00 | 3196 | 462 | 1939 | 3029 | 149 | 164 | 1527 | 0 | 130
23:30 | 3216.5 | 462 | 1937 | 2931.5 | 149 | 164 | 1470 | 0 | 132 | Max Temp. in Dhaka |  | 33° C
24:00 | 3237 | 462 | 1935 | 2834 | 149 | 164 | 1413 | 0 | 134
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 231.540 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 231.540 MKWHr
Note on W13: Author:

## Generation
2018-07-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 63 | 63 | 84 | 84 | 88 | 88 | 88 | 88 | 88 | 84 | 84 | 84 | 85 | 85 | 84 | 75 | 75 | 75 |  | 75 | 85 | 85 | 85 | 85 | 84 | 84 | 1928218
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1907600
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 386100
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 187 | 188 | 188 | 188 | 192 | 191 | 188 | 202 | 196 | 189 | 189 | 189 | 189 | 189 | 189 | 187 | 187 | 187 |  | 189 | 187 | 187 | 196 | 187 | 188 | 200 | 4519219
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 50 | 135 | 135 | 130 | 60 | 60 | 60 | 135 | 135 | 60 | 60 |  | 120 | 135 | 135 | 135 | 135 | 135 | 120 | 2150187
| Dohazari Peaking | 56 | 56 | 56 | 49 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 29 | 29 |  | 45 | 62 | 61 | 60 | 60 | 59 | 59 | 787395
12 | Hathazari peaking | 72 | 72 | 72 | 48 | 0 | [11 empty] | 33 | 56 |  | 61 | 85 | 56 | 56 | 56 | 48 | 48 | 703240
| Daudkandi bangla trak | [19 empty] | 95 | 200 | 200 | 150 | 150 | 150 | 50 | 835200
14 | Daudkandi Peaking 52MW | [19 empty] | 36 | 42 | 42 | 42 | 40 | 40 | 40 | 237656
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 120 | 115 | 110 | 110 | 71 | 71 | 70 | 70 | 70 | 84 | 128 | 139 | 141 | 70 | 70 | 70 | 70 | 128 |  | 140 | 140 | 138 | 116 | 115 | 115 | 110 | 2500728
18 | Summit Gazipur | 301 | 301 | 301 | 301 | 301 | 243 | 110 | 102 | 105 | 155 | 253 | 273 | 286 | 288 | 301 | 300 | 300 | 301 |  | 302 | 301 | 301 | 301 | 301 | 300 | 301 | 6363052
19 | Ashuganj 195MW Modular | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 73 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 50 | 89 | 125 | 110 | 72 | 72 | 81 | 1187636
20 | Ghorasal ST: Unit-1,2 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1448000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2766960
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 300 |  | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 8689027
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 2698878
29 | Ashuganj ST: Unit- 4
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2394302
32 | Ashuganj Engines TSK | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 20 | 20 | 20 | 40 | 39 | 39 | 39 | 36 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 869400
33 | Ashuganj CCPP 225 MW | 188 | 184 | 184 | 183 | 191 | 183 | 182 | 165 | 202 | 170 | 171 | 170 | 170 | 184 | 165 | 170 | 170 | 184 |  | 199 | 184 | 183 | 144 | 164 | 190 | 167 | 4327000
34 | Ashuganj CCPP(South) | 276 | 272 | 272 | 272 | 290 | 272 | 272 | 265 | 255 | 272 | 295 | 300 | 300 | 301 | 250 | 250 | 279 | 279 |  | 320 | 300 | 298 | 331 | 309 | 305 | 316 | 6921000
| Ashuganj CCPP(North) | 275 | 270 | 270 | 270 | 292 | 270 | 270 | 368 | 366 | 372 | 372 | 372 | 383 | 377 | 372 | 378 | 300 | 300 |  | 320 | 300 | 300 | 330 | 300 | 275 | 305 | 8033200
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2390600
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 412 | 413 | 414 | 421 | 420 | 415 | 350 | 345 | 390 | 355 | 345 | 345 | 345 | 344 | 375 | 345 | 345 | 340 |  | 350 | 345 | 350 | 365 | 405 | 405 | 405 | 9097190
40 | Meghnaghat CCPP 450MW | 440 | 450 | 450 | 450 | 450 | 410 | 410 | 410 | 420 | 420 | 420 | 400 | 400 | 360 | 390 | 390 | 390 | 390 |  | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 9239376
41 | Haripur Power CCPP 360MW | 334 | 342 | 352 | 352 | 352 | 352 | 352 | 331 | 306 | 296 | 265 | 261 | 251 | 252 | 252 | 252 | 252 | 251 |  | 272 | 271 | 272 | 272 | 273 | 272 | 273 | 7015000
42 | Mymensingh RPCL 210MW | 83 | 83 | 83 | 83 | 84 | 86 | 82 | 65 | 64 | 64 | 65 | 47 | 38 | 35 | 37 | 38 | 38 | 53 |  | 65 | 65 | 67 | 64 | 38 | 42 | 69 | 1442740
43 | Haripur NEPC 110MW | 105 | 25 | 0 | [9 empty] | 13 | 13 | 40 | 80 | 95 | 98 |  | 100 | 100 | 104 | 98 | 98 | 98 | 98 | 1056800
44 | Fenchugonj CCPP-1 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 50 | 56 | 52 | 54 |  | 54 | 54 | 54 | 54 | 56 | 60 | 60 | 1319000
45 | Fenchugonj CCPP-2 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 1776000
46 | Shajibazar 330 MW
47 | Shahjibazar GT: Unit- 8, 9 | 60 | 60 | 60 | 60 | 61 | 61 | 61 | 60 | 60 | 60 | 58 | 57 | 50 | 52 | 60 | 50 | 40 | 60 |  | 60 | 60 | 61 | 60 | 60 | 60 | 60 | 1371000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 50 | 50 | 58 | 50 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 40 | 10 |  | 10 | 86 | 86 | 86 | 86 | 86 | 86 | 1776000
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 46 | 20 | 20 | 44 | 44 | 46 | 10 |  | 10 | 45 | 46 | 46 | 46 | 47 | 47 | 989280
50 | Sylhet GT 150 MW
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 44 | 44 | 44 | 44 | 44 | 46 | 21 | 44 | 44 | 44 | 12 |  | 41 | 44 | 46 | 47 | 47 | 46 | 46 | 1857831
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5468480
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 261168
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 47 | 47 | 47 | 53 | 53 | 53 | 53 | 53 | 11 |  | 11 | 11 | 53 | 53 | 53 | 53 | 53 | 1162800
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 8 | 8 | 15 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 474112
57 | Summit Bibiana- 2 | 280 | 290 | 300 | 280 | 270 | 280 | 280 | 295 | 330 | 300 | 280 | 280 | 290 | 265 | 290 | 270 | 270 | 295 |  | 295 | 310 | 275 | 280 | 320 | 305 | 290 | 7485300
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 36 | 36 | 36 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 36 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 1248008
59 | Sikalbaha (Energis) | 50 | 50 | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1187040
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 17 | 16 | 17 | 17 | 17 | 17 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439632
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 489168
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 458064
63 | Tripura | 132 | 132 | 148 | 144 | 136 | 122 | 112 | 110 | 106 | 124 | 120 | 126 | 122 | 138 | 152 | 138 | 128 | 112 |  | 96 | 110 | 108 | 124 | 134 | 130 | 134 | 3078720
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 38 | 38 | 42 | 42 | 32 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 3 |  | 8 | 7 | 10 | 22 | 21 | 21 | 24 | 401280
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 444888
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236700
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 |  | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 723700
68 | Summit Comilla 25MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | 20 | 20 | 16 | 16 | 22 | 22 | 22 | 0 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 471320
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 31 | 32 | 712980
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 771829
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 826800
73 | Ghorashal (Regent) | 88 | 88 | 88 | 86 | 86 | 86 | 86 | 85 | 88 | 88 | 88 | 89 | 88 | 88 | 88 | 87 | 87 | 47 |  | 87 | 87 | 87 | 88 | 88 | 88 | 85 | 2021386
76 | Siddhirganj (Desh) | [19 empty] | 15 | 20 | 35 | 35 | 35 | 30 | 17 | 239040
77 | Siddhirganj (Dutch Bangla) | 93 | 93 | 50 | 50 | 7 | 7 | 7 | 7 | 7 | 30 | 80 | 89 | 91 | 93 | 85 | 90 | 50 | 7 |  | 7 | 10 | 50 | 93 | 93 | 93 | 93 | 1487040
78 | Gazipur (RPCL) | 50 | 25 | 25 | 25 | 8 | 8 | 8 | 8 | 10 | 25 | 25 | 25 | 44 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 872076
79 | Kodda 150MW | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 64 | 64 | 98 | 115 | 115 | 82 |  | 82 | 149 | 149 | 140 | 133 | 133 | 110 | 1637760
80 | Jamalpur 95MW | 95 | 95 | 48 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 32 | 64 | 64 | 90 | 95 | 95 | 24 |  | 24 | 95 | 95 | 95 | 95 | 95 | 95 | 1286572
81 | Lakdhanvi 52 MW | 25 | 25 | 25 | 25 | 0 |  |  |  | 0 | 10 | 24 | 30 | 34 | 34 | 34 | 43 | 52 | 52 |  | 52 | 52 | 52 | 16 | 16 | 16 | 16 | 607090
82 | Madanganj 102MW | 97 | 97 | 97 | 97 | 48 | 15 | 15 | 15 | 15 | 28 | 60 | 65 | 70 | 85 | 97 | 97 | 75 | 16 |  | 15 | 15 | 35 | 95 | 101 | 100 | 97 | 1601040
83 | Pagla (DPA ) | 10 | 0 | 0 | 0 | 0 | 0 |  |  | 10 | 21 | 21 | 21 | 21 | 21 | 51 | 51 | 51 | 51 |  | 51 | 51 | 11 | 11 | 11 | 10 | 11 | 405980
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 50 | 84 | 85 | 40 | 10 |  | 10 | 85 | 85 | 85 | 85 | 85 | 85 | 1601040
85 | Keraniganj (Powerpac) 100MW | 88 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 36 | 50 | 50 | 74 | 74 | 87 | 87 | 87 | 50 | 10 |  | 50 | 87 | 87 | 87 | 87 | 87 | 87 | 1344056
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 305 | 240 | 200 | 200 | 250 | 200 | 305 | 200 | 200 | 200 |  | 250 | 250 | 200 | 200 | 200 | 240 | 200 | 5468480
87 | Meghnaghat (IEL) | 100 | 100 | 92 | 56 | 28 | 7 | 7 | 7 | 7 | 40 | 88 | 90 | 90 | 90 | 90 | 90 | 50 | 30 |  | 30 | 100 | 79 | 100 | 100 | 100 | 100 | 1629120
88 | Ghorashal 78MW (MAX) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848288
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120000
91 | Juldah (Acorn) | 80 | 68 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 68 | 68 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1804920
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 47 |  | 16 | 50 | 49 | 50 | 50 | 50 | 50 | 1119000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 40 | 14 |  | 15 | 18 | 24 | 45 | 51 | 51 | 51 | 1043263
94 | Gagnagar (Orion) | 50 | 24 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 32 | 50 | 84 | 102 | 102 | 102 | 102 | 8 | 14 |  | 16 | 50 | 84 | 102 | 102 | 102 | 102 | 1325808
95 | Patenga 50MW | 26 | 26 | 26 | 26 | 24 | 21 | 22 | 22 | 22 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 |  | 25 | 31 | 30 | 38 | 45 | 45 | 51 | 692160
96 | Chittagong ECPV 108 MW | 99 | 99 | 99 | 94 | 92 | 92 | 92 | 90 | 90 | 92 | 92 | 92 | 92 | 93 | 94 | 94 | 95 | 92 |  | 97 | 105 | 105 | 105 | 105 | 105 | 105 | 2277120
97 | Katpotti 51 MW | 39 | 39 | 39 | 39 | 39 | 39 | 6 | 6 | 21 | 39 | 33 | 34 | 34 | 39 | 39 | 39 | 39 | 12 |  | 12 | 20 | 34 | 40 | 40 | 40 | 39 | 835248
98 | Bosila 108MW | 80 | 80 | 80 | 81 | 81 | 32 | 8 | 8 | 83 | 83 | 82 | 82 | 90 | 89 | 88 | 88 | 57 | 57 |  | 89 | 89 | 57 | 40 | 40 | 40 | 40 | 1578240
99 | Madanganj-55 MW | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 15 |  | 15 | 55 | 46 | 55 | 55 | 55 | 55 | 1105397
100 | Northern 55 MW | 55 | 55 | 55 | 55 | 55 | 18 | 18 | 18 | 18 | 32 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1087580
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 163 | 163 | 100 | 163 | 163 | 130 | 130 |  | 100 | 163 | 163 | 163 | 163 | 163 | 163 | 3658254
102 | Sarishabari (Solar) | [5 empty] | 0 | 0 | 0.3 | 0.3 | 1.2 | 1 | 0.8 | 0.7 | 2.3 | 1.8 | 0.8 | 0.2 | 0.1 |  | 0 | 0 | 0 |  |  |  |  | 14100
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 18 | 18 | 18 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 36 | 36 | 18 |  | 47 | 54 | 54 | 54 | 54 | 54 | 54 | 1131120
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [19 empty] | 33 | 50 | 52 | 52 | 52 | 51 | 51 | 258031
106 | United Mymensingh PPL | 165 | 175 | 180 | 180 | 187 | 150 | 100 | 100 | 186 | 185 | 166 | 180 | 172 | 174 | 174 | 170 | 170 | 180 |  | 175 | 180 | 185 | 185 | 185 | 185 | 185 | 4070400
112 | Aggreko Aurahati 100MW | [19 empty] | 7 | 50 | 51 | 0 | 0 |  |  | 58900
114 | Summit Gazipur-1 150MW | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3697344
115
116
117
118 | Eastern Zone Total | 7505 | 7271 | 7161 | 7046 | 6756 | 6307 | 5966 | 5974.3 | 6477.3 | 6644.2 | 6826 | 6892.8 | 7059.7 | 6840.3 | 7329.8 | 7215.8 | 6712.2 | 6162.1 | 0 | 6869 | 7797 | 7805 | 7844 | 7840 | 7848 | 7712 | 174852657
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 54 | 48 | 48 | 48 | 48 | 10 | 10 | 10 | 10 | 10 | 10 | 78 | 82 | 77 | 73 | 76 | 75 | 62 |  | 80 | 75 | 75 | 73 | 69 | 70 | 68 | 1199040
124 | Khulna (KPCL-2) | 83 | 97 | 97 | 97 | 81 | 16 | 16 | 16 | 16 | 50 | 66 | 66 | 66 | 66 | 66 | 76 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 64 | 64 | 1792320
125
126 | Khulna (Aggreko) 55MW | [19 empty] | 22 | 54 | 54 | 55 | 55 | 52 | 55 | 383970
127 | Faridpur Peaking | 42 | 42 | 42 | 42 | 42 | 42 | 18 | [10 empty] | 15 |  | 49 | 50 | 50 | 49 | 50 | 49 | 49 | 557280
128 | Khulna CCPP 225MW | 233 | 160 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 | 120 | 120 |  | 145 | 170 | 190 | 239 | 239 | 239 | 200 | 3681600
129
130
131
132
133
| Summit Barisal 110 MW | 96 | 96 | 96 | 96 | 96 | 96 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2181120
| Barisal GT: Unit-1, 2 | [19 empty] | 10 | 12 | 12 | 12 | 12 | 0 |  | 42745
136 | Bhola Aggreko 95MW | 96 | 95 | 95 | 96 | 96 | 95 | 95 | 96 | 94 | 94 | 94 | 95 | 96 | 96 | 12 | 12 | 12 | 12 |  | 54 | 75 | 75 | 98 | 98 | 96 | 98 | 1879026
137 | Bhola CCPP 194MW | 191 | 192 | 192 | 191 | 190 | 188 | 190 | 189 | 191 | 189 | 188 | 189 | 186 | 179 | 187 | 180 | 183 | 186 |  | 191 | 190 | 172 | 191 | 191 | 191 | 192 | 4565000
| Bhola (Venture) 33MW | 36 | 32 | 31 | 32 | 25 | 21 | 22 | 13 | 12 | 15 | 17 | 18 | 18 | 18 | 20 | 19 | 21 | 22 |  | 27 | 34 | 37 | 37 | 37 | 37 | 36 | 596156
140 | Bangla Trak Noapara | [19 empty] | 26 | 97 | 97 | 97 | 96 | 97 | 50 | 506880
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 40 | 40 | 40 | 40 | 40 | 33 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 940500
142 | Gopalganj Peaking | [13 empty] | 2 | 3 | 6 | 22 | 40 |  | 60 | 60 | 56 | 66 | 66 | 58 | 55 | 401152
143 | Bheramara GT-1,2,3 | [19 empty] | 32 | 49 | 48 | 48 | 48 | 32 | 0 | 193700
144
145 | Bheramara HVDC | 456 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 462 | 424 | 424 | 424 | 461 |  | 462 | 461 | 462 | 462 | 462 | 462 | 462 | 10968727
146 | Bheramara 360 MW | 385 | 383 | 383 | 383 | 380 | 375 | 368 | 345 | 329 | 320 | 310 | 294 | 280 | 250 | 275 | 275 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 7682112
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2
151 | Barapukuria Unit-3 | 148 | 150 | 153 | 146 | 154 | 150 | 152 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 167 | 201 | 215 | 210 | 149 | 149 | 3843300
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | 51 | 51 | 51 | 51 | 0 | [14 empty] | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 430752
Sirajgonj Unit-1 225MW (Gas)
157 | Sirajgonj Unit-1 225MW (Oil) | 162 | 167 | 168 | 167 | 174 | 175 | 168 | 164 | 181 | 171 | 158 | 165 | 160 | 161 | 181 | 162 | 163 | 162 |  | 167 | 176 | 168 | 171 | 179 | 167 | 158 | 4263009
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 162 | 159 | 167 | 165 | 173 | 163 | 170 | 166 | 184 | 174 | 164 | 178 | 163 | 162 | 181 | 162 | 161 | 159 |  | 164 | 172 | 165 | 166 | 165 | 136 | 131 | 4119445
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | 36 | 36 | 25 | 0 | [13 empty] | 10 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 288884
161 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 413520
162 | Bogra (EPL) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 209232
163 | Ullapara (Summit) | 10 | 10 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 219442
164 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 0 | 0 | 35 | 50 | 50 | 50 | 50 | 1080960
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 25 | 25 | 35 | 35 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 893696
166 | Katakhali Peaking | 44 | 44 | 44 | 44 | 44 | 0 | [13 empty] | 45 | 45 | 45 | 44 | 42 | 42 | 41 | 467421
167 | Santahar Peaking
168 | Rajlanka 52 MW | 52 | 52 | 52 | 0 |  |  | 8 | 8 | 8 | 8 | 8 | 16 | 25 | 25 | 43 | 43 | 43 | 43 |  | 51 | 52 | 52 | 52 | 52 | 51 | 51 | 723840
169 | Chapainawabganj-100 MW | 100 | 100 | 100 | 100 | 100 | 100 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 58 | 100 | 92 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 101 | 2015790
170
171
172 | Rangpur GT | [19 empty] | 15 | 12 | 13 | 11 | 10 | 12 | 12 | 62000
173 | Saidpur GT | [19 empty] | 0 | 18 | 18 | 18 | 16 | 16 | 16 | 85000
175
176
177
178 | Western Zone Total | 2597 | 2536 | 2497 | 2411 | 2356 | 2181 | 2090 | 2033 | 2043 | 2032 | 2023 | 2117 | 2082 | 2042 | 2108 | 2087 | 2143 | 2212 | 0 | 2540 | 2762 | 2818 | 2947 | 2940 | 2748 | 2616 | 56687619
178 | Total Generation | 10102 | 9807 | 9658 | 9457 | 9112 | 8488 | 8056 | 8007.3 | 8520.3 | 8676.2 | 8849 | 9009.8 | 9141.7 | 8882.3 | 9437.8 | 9302.8 | 8855.2 | 8374.1 | 0 | 9409 | 10559 | 10623 | 10791 | 10780 | 10596 | 10328 | 231540276
176
177