## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-03-01 |  | 2022-02-01 |  | 2021-03-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13662 | 2022-03-31 | 10737 | 2022-02-28 | 12790 | 24-03-2021 | 13792 | 2021-04-27
|  |  | 19:30 |  | 19:00 |  | 21:00 |  | 20:00
2 | Minimum Generation (MW) | 6823 | 2022-03-05 | 4663 | 2022-02-05 | 6990 | 04/03/21 | - | -
|  |  | 6:00 |  | 6:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13662 | 2022-03-31 | 10737 | 2022-02-28 | 12790 | 24-03-2021 | 13792 | 2021-04-27
|  |  | 19:30 |  | 19:00 |  | 21:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 12116 | 2022-03-27 | 9529 | 2022-02-28 | 11146 | 23-03-2021 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13662 | 2022-03-31 | 10737 | 2022-02-28 | 12790 | 24-03-2021 | 14097 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 19:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 12057.9032 |  | 9618.2857 |  | 11476.6774 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 10564 |  | 8531.3929 |  | 9678.4516 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 938 | 2022-03-29 | 746 | 2022-02-13 | 850 | 29/03/2021 | 956 | 27/3/2019
|  |  | 10:30 |  | 23:00 |  | 1:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 182 | 2022-03-23 | 136 | 2022-02-26 | 186 | 27/03/2021 | 194 | 12/06/19
|  |  | 18:30 |  | 18:30 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1551.2856 |  | 1150.9855 |  | 1525.7498 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 80.4189 |  | 63.5251 |  | 100.5824
22 | Net Generation of BPDB (MKWH) | 1470.8667 |  | 1087.4604 |  | 1425.1675
23 | Net Generation of IPP (MKWH) | 4916.0698 |  | 3220.9387 |  | 3900.6099
24 | Net Generation of REB (MKWH) | 144.2163 |  | 126.4229 |  | 123.4508
24 | Net Generation of Rental Power Plant (MKWH) | 498.1914 |  | 320.0645 |  | 358.3773
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7029.3442 |  | 4754.8865 |  | 5807.6055 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 3806.7453 |  | 2892.5467 |  | 3953.2485 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 475.2564 |  | 131.3412 |  | 286.3058 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 2203.7804 |  | 1350.3741 |  | 1161.4759 |  | 2203.78 | March-22
29 | Energy Generation by Hydro (MKWH) | 43.3314 |  | 33.9959 |  | 45.441 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 40.5844 |  | 33.0046 |  | 18.2866 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 540.0652 |  | 377.1491 |  | 443.4301 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 644.0891 |  | 529.8419 |  | 584.9063 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 84.4682 |  | 74.1352 |  | 68.2352 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13662 | 2022-03-31 | 19:30
Generation Period
| Dhaka | MW | 5024.63
| Chattogram | MW | 1283.3
| Cumilla | MW | 1200
| Mymensingh | MW | 1052
| Sylhet | MW | 443
a) | Total supply in East zone | MW | 9002.93
| Khulna | MW | 1579.8
| Barisal | MW | 372
| Rajshahi | MW | 1521
| Rangpur | MW | 764
b) | Total supply in West zone | MW | 4236.8
c) | Total supply in both zone ( a+b) | MW | 13239.73
Ref: | 27.21.0000.603.16.087.20.496 | Date: 18/04/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 900 | 2022-03-29 | 19:00
| b) Ishurdi end | MW | 340 | 2022-03-31 | 12:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 2470 | 2022-03-10 | 23:00
| b) Ishurdi end | MW | 194 | 2022-03-17 | 7:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.43
| b) Ishurdi end | MKWH | 75.3
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 280 | 2022-03-07 | 19:00
| b)Serajganj end | MW | 430 | 2022-03-31 | 12:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 390 | 2022-03-31 | 12:00
| b)Sirajganj end | MW | 290 | 2022-03-07 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 2.22 | 2022-03-05 | 12:00
| b)Sirajganj end | MKWH | 0.5 | 2022-03-15 | 12:00
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 22.308
| b)Sirajganj end | MKWH | 45.776
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 44.082
| b)Sirajganj end | MKWH | 22.822
30 | Transmission loss of EWI /NO-2 | % | 0.09
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Uttara | 132/33 kV transformer T-2 | 2022-03-04 05:03 | 2022-03-04 07:39 | 2:36 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Tongi(N) | 132 kV Bus coupler | 2022-03-05 09:28 | 2022-03-05 09:44 | 0:16 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-03-20 11:24 | 2022-03-20 12:23 | 0:59 | E/O | Due to cable burst | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformers T-1 ,& T2 | 2022-03-23 12:04 | 2022-03-23 12:40 | 0:36 | T | Due to bursting of CT | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-03-23 12:04 | 2022-03-23 12:59 | 0:55 | T |  | 227 | 208.0833 | Power interruption
Tongi | 132/33 kV transformer T-1 | 2022-03-23 14:02 | 2022-03-23 14:30 | 0:28 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformers T-1 | 2022-03-24 17:50 | 2022-03-24 18:11 | 0:21 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T-2 | 2022-03-24 17:50 | 2022-03-24 18:12 | 0:22 | T |  | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-02 | 2022-03-25 11:22 | 2022-03-25 11:22 | 0:00 |  | Due to sparking at 230 kV CB | 0 | 0 | No interruption
Kaliakoir | 400/230 kV transformers T-1 & T2 | 2022-03-27 07:47 | 2022-03-27 07:47 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-2 | 2022-03-29 07:10 | 2022-03-29 08:44 | 1:34 | T | Due to red-hot maint | 60 | 94 | Power interruption
|  |  | Total : | 8:07 |  | Unserved Energy: |  | 302.0833
Dhaka (South) Grid Circle :
Keraniganj | 132/33 kV transformer T-2 & 33 kV Bus-2 | 2022-03-02 09:07 | 2022-03-02 10:42 | 1:35 | T | Due to red-hot maint.of 33 kV Bus-2 | 20 | 31.6667 | Power interruption
Bhulta | 230 kV CB 155 | 2022-03-08 15:52 | 2022-03-08 16:51 | 0:59 | T | Due to supervision relay | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformers T-1 & T2 | 2022-03-10 05:35 | 2022-03-10 05:48 | 0:13 | T | Due to 33 kV feeder fault | 10 | 2.1667 | Power interruption
Ghorashal | 230 kV Bus | 2022-03-16 11:02 | 2022-03-16 16:30 | 0:13 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T02 | 2022-03-21 23:31 | 2022-03-22 01:33 | 5:28 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-03-22 01:37 | 2022-03-22 02:39 | 2:02 | T |  | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2022-03-22 07:01 | 2022-03-22 09:12 | 1:02 | T | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T02 | 2022-03-22 22:16 | 2022-03-22 00:26 | 2:11 | T | Due to red-hot maint | 0 | 0 | No interruption
Hasnabad | 33 kV Bus | 2022-03-24 06:06 | 2022-03-24 06:32 | 0:26 | T | Tripped showing master trip | 60 | 26 | Power interruption
Narsinghdi | 132/33 kV transformer T-1 | 2022-03-24 06:41 | 2022-03-24 06:49 | 0:08 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 | 2022-03-25 08:40 | 2022-03-25 09:04 | 0:24 | T | Due to 33 kV feeder fault | 10 | 4 | Power interruption
Narsinghdi | 132/33 kV transformer T-2 | 2022-03-28 10:01 | 2022-03-28 10:37 | 0:36 | T | Tripped showing bucholz relay | 42 | 25.2 | Power interruption
|  |  | Total : | 15:17 |  | Unserved Energy: |  | 89.0333
Chattogram Grid Circle :
T.K chemical | 132/33 kV transformer T1 | 2022-03-08 16:08 | 2022-03-08 18:04 | 1:56 | E/O | Due to Oil leakage maint. | 0 | 0 | No interruption
Halishahar | 132/33 kV transformers T-1 ,T 2& T3 | 2022-03-18 05:05 | 2022-03-18 05:57 | 0:52 | T | Tripped showing O/C & E/F relay | 60 | 52 | Power interruption
Madunaghat | 132/33 kV transformer T1 | 2022-03-23 11:07 | 2022-03-23 11:51 | 0:44 | T | Tripped showing E/F relay | 35 | 25.6667 | Power interruption
Halishahar | 132/33 kV transformers T1 & T3 | 2022-03-27 12:35 | 2022-03-27 12:53 | 0:18 | T | Due to 33 kV feeder fault | 75 | 22.5 | Power interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-03-28 18:35 | 2022-03-28 18:57 | 0:22 | T | Tripped showing O/C relay | 55 | 20.1667 | Power interruption
|  |  | Total : | 4:12 |  | Unserved Energy: |  | 120.3333
Cumilla Grid Circle :
Cumilla (N) | 132/33 kV transformers T3 | 2022-03-03 08:40 | 2022-03-03 12:24 | 3:44 | T | Due to elecrical fault | 50 | 186.6667 | Power interruption
| 132/33 kV transformers T4 | 2022-03-03 08:40 | 2022-03-03 09:17 | 0:37 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-03-05 06:30 | 2022-03-05 10:48 | 4:18 | T | Tripped showing protection relay | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T1 & T2 | 2022-03-18 08:43 | 2022-03-18 09:00 | 0:17 | T | Tripped showing O/C & E/F relay | 70 | 19.8333 | Power interruption
| 132/33 kV transformers T1 & T2 | 2022-03-22 17:35 | 2022-03-22 17:41 | 0:06 | T |  | 120 | 12 | Power interruption
Cumilla (N) | 132/33 kV transformers T3 | 2022-03-24 09:45 | 2022-03-24 09:54 | 0:09 | T | Tripped showing E/F relay | 162 | 24.3 | Power interruption
| 132/33 kV transformers T4 | 2022-03-24 09:45 | 2022-03-24 09:59 | 0:14 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T1 | 2022-03-26 09:23 | 2022-03-26 09:40 | 0:17 | T | Due to 33 kV feeder fault | 5 | 1.4167 | Power interruption
Chowmuhani | 132/33 kV transformer T2 | 2022-03-27 10:58 | 2022-03-27 12:24 | 1:26 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T2 | 2022-03-27 12:35 | 2022-03-27 13:23 | 0:48 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T2 | 2022-03-28 16:42 | 2022-03-28 16:56 | 0:14 | T | Tripped showing O/C relay | 30 | 7 | Power interruption
|  |  | Total : | 12:10 |  |  |  | 251.2167
Khulna Grid Circle :
Satkhira | 132/33 kV transformer T2 | 2022-03-02 19:10 | 2022-03-02 20:03 | 0:53 | T | Due to red-hot maint | 0 | 0 | No interruption
Madaripur | 132/33 kV transformers T1 & T2 | 2022-03-17 04:31 | 2022-03-17 05:17 | 0:46 | T | Due to 33 kV feeder fault | 50 | 38.3333 | Power interruption
Golapara | 132/33 kV transformer T6 | 2022-03-22 13:45 | 2022-03-22 13:45 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Narail | 132/33 kV transformers T1 | 2022-03-22 18:17 | 2022-03-22 22:35 | 4:18 | E/O | Due to bursting CT at 33 kV feeder
| 132/33 kV transformers T2 | 2022-03-22 18:17 | 2022-03-22 19:25 | 1:08 | E/O |  | 28 | 31.7333 | Power interruption 18:17 to 19:25
|  |  | Total : | 7:05 |  | Unserved Energy: |  | 70.0667
HVDC Grid Circle :
HVDC | HVDC 10CF15 400 kV filter | 2022-03-07 08:47 | 2022-03-07 08:47 | 0:00 | T | Due to bird fall down | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T02 | 2022-03-11 05:40 | 2022-03-11 10:16 | 4:36 | T | Due to winding temperature high | 0 | 0 | No interruption
Bottail | 132/33 kV transformerT2 | 2022-03-11 22:58 | 2022-03-12 03:54 | 4:56 | T | Tripped showing Diff. relay at 33 kV side | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T02 | 2022-03-12 01:57 | 2022-03-12 12:00 | 10:03 | T | Due to winding temperature high | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-03-15 04:22 | 2022-03-15 04:22 | 0:00 | T |  | 0 | 0 | No interruption
|  |  | Total : | 19:35 |  |  |  | 0
Bogura Grid Circle:
Bogura | 132/33 kV transformer T1 & 33 Bus | 2022-03-09 08:55 | 2022-03-09 10:33 | 1:38 | E/O | Due to red-hot maint | 35 | 57.1667 | Power interruption
Rangpur | 132/33 kV transformer T2 & 33 kV Bus | 2022-03-12 08:02 | 2022-03-12 09:08 | 1:06 | E/O | Due to red-hot maint | 45 | 49.5 | Power interruption
Bogura | 230/132 kV transformer T01 | 2022-03-15 02:45 | 2022-03-15 08:45 | 6:00 | T | Tripped showing lockout relay | 0 | 0 | No interruption
Amnura | 132/33 kV transformerT1 | 2022-03-16 11:58 | 2022-03-16 15:15 | 3:17 | E/O | Due to Oil leakage maint. | 0 | 0 | No interruption
Bogura (O) | 132/33 kV transformer T3 with 33 kV Bus | 2022-03-18 08:07 | 2022-03-18 08:56 | 0:49 | E/O | Due to red-hot maint | 26 | 21.2333 | Power interruption
Niyamatpur | 132/33 kV transformerT2 | 2022-03-20 20:04 | 2022-03-20 20:07 | 0:03 | E/O | Due to red-hot maint | 25 | 1.25 | Power interruption
Narail | 132/33 kV transformer T1 | 2022-03-24 06:47 | 2022-03-24 08:35 | 1:48 | E/O | Due to red-hot maint | 15 | 27 | Power interruption
Bogura (O) | 230/132 kV transformer T01 | 2022-03-27 23:27 | 2022-03-28 00:15 | 0:48 | T | Due to line overload | 0 | 0 | No interruption
Joldhaka | 132/33 kV transformerT2 | 2022-03-29 12:25 | 2022-03-29 13:30 | 1:05 | E/O | Due to red-hot maint at 33 kV Bus | 20 | 21.6667 | Power interruption
|  |  | Total : | 16:34 |  |  |  | 177.8167
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 83:00 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Tongi (N) 132 kV Ckt-1 | 2022-03-05 09:28 | 2022-03-05 18:24 | 8:56 | E/O | Due bursting of L/A | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-03-14 13:01 | 2022-03-14 13:08 | 9:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dhamrai | Dhamrai-kaliakoir 132 kV Ckt-1 | 2022-03-21 05:07 | 2022-03-21 08:27 | 3:20 | T | Tripped showing Dist. relay | 70 | 233.3333 | Power interruption
| Dhamrai-kaliakoir 132 kV Ckt-2 | 2022-03-21 05:07 | 2022-03-21 10:10 | 5:03 | T
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-03-26 02:54 | 2022-03-26 21:13 | 18:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 kV Ckt-1 | 2022-03-27 19:11 | 2022-03-27 19:35 | 0:24 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-1 | 2022-03-28 13:51 | 2022-03-28 13:57 | 0:06 | T | Tripped showing Dist. relay | 70 | 7 | Power interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2022-03-29 08:20 | 2022-03-29 10:46 | 0:06 | T | Due to red-hot maint | 20 | 2 | Power interruption
Tongi | Tongi-Kabirpur 132 kV Ckt-2 | 2022-03-29 16:20 | 2022-03-29 16:46 | 0:26 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-2 | 2022-03-30 05:58 | 2022-03-30 14:38 | 8:40 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
|  |  | Total : | 54:53 |  | Unserved Energy: |  | 242.3333
Dhaka (South) Grid Circle :
Sonargaon | Sonargaon-Sonargaon Orion P/S 132 kV Ckt-2 | 2022-03-01 09:40 | 2022-03-01 09:54 | 0:14 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption | 120.3333 | 251.2167
Ghorashal AIS | Ghorashal AIS-GIS 230 kV Ckt-2 | 2022-03-04 12:38 | 2022-03-04 15:48 | 3:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption | 14.7833
Hasnabad | 230 kV CB 155 | 2022-03-15 12:34 | 2022-03-15 13:07 | 0:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption | 135.1167
Sonargaon | Sonargaon-Haripur 132 kV Ckt | 2022-03-21 05:54 | 2022-03-21 06:10 | 0:16 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-03-24 04:40 | 2022-03-24 06:47 | 2:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV Ckt-2 | 2022-03-25 10:45 | 2022-03-25 11:05 | 0:20 | T | Tripped showing Auto reclose relay | 0 | 0 | No interruption
| Rampura-Bashundhara 132 kV Ckt-2 | 2022-03-25 10:47 | 2022-03-25 10:52 | 0:05 | T | Tripped showing Dist. relay | 100 | 8.3333 | Power interruption
| Rampura-Bashundhara 132 kV Ckt-1 | 2022-03-25 10:47 | 2022-03-25 13:01 | 2:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt-1 | 2022-03-27 06:31 | 2022-03-27 06:45 | 0:14 | T | Tripped showing Dist. relay | 65 | 15.1667 | Power interruption
Madanganj | Madanganj -Sitalakhya 132 kV Ckt | 2022-03-27 10:56 | 2022-03-27 14:36 | 0:14 | T | Due to red-hot maint | 0 | 0 | No interruption
Bhulta | Bhulta-Ghorashal 230 kV Ckt | 2022-03-27 14:37 | 2022-03-27 15:07 | 0:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV Ckt-2 | 2022-03-27 21:08 | 2022-03-27 23:59 | 2:51 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 & 2 | 2022-03-28 16:55 | 2022-03-28 17:03 | 0:08 | T | Tripped showing E/F. relay | 9 | 1.2 | Power interruption
Ghorashal | Ghorashal-Narsingdi 132 kV Ckt-2 | 2022-03-29 08:15 | 2022-03-29 08:46 | 0:31 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Kazla 132 kV Ckt-1 | 2022-03-29 20:02 | 2022-03-29 22:51 | 2:49 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-03-30 09:37 | 2022-03-30 10:21 | 0:44 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj (S) 230 kV Ckt-1 | 2022-03-31 05:52 | 2022-03-31 11:57 | 6:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 23:05 |  | Unserved Energy: |  | 24.7
Chattogram Grid Circle :
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2022-03-18 02:57 | 2022-03-18 03:37 | 0:40 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-1 | 2022-03-18 04:27 | 2022-03-18 06:28 | 2:01 | T | Tripped showing Dist.Z1 relay | 35 | 11.6667 | Power interruption 04:27 to 04:47
Juldah | Juldah-Sikalbaha(N) 132 kV Ckt | 2022-03-18 04:26 | 2022-03-18 05:07 | 0:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-03-22 06:19 |  |  | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Baraulia | Baroulia-KSRM 132 kV Ckt | 2022-03-22 13:09 | 2022-03-22 15:38 | 2:29 | T | Tripped showing O/C.& E/F relay | 0 | 0 | No interruption
| Baroulia-KSRM 132 kV Ckt | 2022-03-23 11:06 | 2022-03-23 11:23 | 0:17 | T | Tripped showing O/C. relay | 11 | 3.1167 | Power interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2022-03-26 10:56 | 2022-03-26 11:13 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Halishahar-Madunaghat 132 kV Ckt-1 | 2022-03-26 10:57 | 2022-03-26 11:09 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:37 |  | Unserved Energy: |  | 14.7833
Cumilla Grid Circle :
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-2 | 2022-03-02 09:15 | 2022-03-02 13:07 | 3:52 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur Desh 132 kV Ckt-1 | 2022-03-02 14:45 | 2022-03-02 16:08 | 1:23 | E/O | Due to gas filling | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-2 | 2022-03-04 12:24 | 2022-03-04 12:44 | 0:20 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-03-08 16:45 | 2022-03-08 16:59 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV Ckt-1 | 2022-03-17 05:24 | 2022-03-17 13:46 | 8:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2022-03-17 10:32 | 2022-03-17 17:50 | 7:18 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Ashuganj 230 kV Ckt-2 | 2022-03-21 07:13 | 2022-03-21 07:24 | 0:11 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-03-26 08:54 | 2022-03-26 09:25 | 0:31 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-2 | 2022-03-26 08:54 | 2022-03-26 09:26 | 0:32 | T |  | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-1 | 2022-03-26 16:08 | 2022-03-26 16:20 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-03-28 15:51 | 2022-03-28 16:22 | 0:31 | T | Tripped showing Dist. & O/C relay | 0 | 0 | No interruption
|  |  | Total : | 23:26 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2022-03-17 11:03 | 2022-03-17 13:31 | 2:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Orion P/S | Orion P/S-Bagerhat 132 kV Ckt | 2022-03-17 11:03 | 2022-03-17 11:22 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(new) | Gopalganj(new)-Gopalganj (Old) 132 kV Ckt-2 | 2022-03-18 09:42 | 2022-03-18 17:49 | 8:07 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2022-03-22 07:36 | 2022-03-22 09:24 | 1:48 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2022-03-25 15:49 | 2022-03-25 16:16 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 13:09 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Shahjadpur | Shahjadpur-Sirajagnj 132 kV Ckt | 2022-03-16 11:18 | 2022-03-16 11:39 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Shahjadpur-Sirajagnj 132 kV Ckt | 2022-03-17 09:46 | 2022-03-17 09:55 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Baghabari 132 kV Ckt | 2022-03-24 14:46 | 2022-03-24 15:20 | 0:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:04 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Sirajganj | Sirajganj-Baghabari 132 kV Ckt-1 | 2022-03-03 12:18 | 2022-03-03 13:10 | 0:52 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangur Confidence 132 kV Ckt-1 | 2022-03-10 10:40 | 2022-03-10 13:41 | 3:01 | E/O | Due to SF6 gas leakage | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV Ckt-2 | 2022-03-16 04:15 | 2022-03-16 14:52 | 10:37 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Saidpur | Saidpur-Rangpur 132 kV Ckt-1 & 2 | 2022-03-16 12:42 | 2022-03-16 13:31 | 0:49 | T | Tripped showing Dist. relay | 173 | 72.0833 | Power interruption 12:42 to 13:07
Barapukuria | Barapukuria-Rangpur 132 kV Ckt-1 & 2 | 2022-03-16 12:42 | 2022-03-16 13:07 | 0:25 | T
Rangpur Confi. | Rangpur Confi.-Rangpur S/S 132 kV CKt-1 & 2 | 2022-03-16 12:42 | 2022-03-16 13:43 | 1:01 | T | Tripped showing cloud operated | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-2 | 2022-03-19 09:16 | 2022-03-19 09:39 | 0:23 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Panchagarh 132 kV Ckt | 2022-03-29 06:10 | 2022-03-29 09:15 | 3:05 | E/O | Due to red-hot maint | 30 | 92.5 | Power interruption
|  |  | Total : | 20:13 |  | Unserved Energy: |  | 164.5833
Others :
Ullon | Ullon-Dhanmondi 132 kV Ckt-1 | 2022-03-03 17:15 | 2022-03-03 21:27 | 4:12 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 4:12 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 146:39 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: March 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Savar | 132/33 kV transformer T-3 | 2022-03-01 09:50 | 2022-03-01 14:30 | 4:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2022-03-02 09:10 | 2022-03-02 12:52 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-03 | 2022-03-02 09:26 | 2022-03-02 19:40 | 10:14 | S/O | Due to C/M work | 0 | 0
Mirpur | 132 kV main Bus | 2022-03-02 13:16 | 2022-03-02 20:37 | 7:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-A | 2022-03-03 10:04 | 2022-03-03 13:01 | 2:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-1 | 2022-03-03 09:48 | 2022-03-03 16:40 | 6:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Sholoshahar | 132/33 kV transformer T-1 |  | 2022-03-03 15:35 |  |  | new connection | 0 | 0 | No interruption
| 132/33 kV transformer T-2 |  | 2022-03-03 15:53 |  |  |  | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2022-03-05 11:30 | 2022-03-05 13:05 | 1:35 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-2 | 2022-03-05 11:54 | 2022-03-05 13:03 | 1:09 | S/O | Due to C/M work | 17 | 19.55 | Power interruption
Kallyanpur | 132/33 kV transformer T-2 | 2022-03-06 08:54 | 2022-03-06 08:54 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2022-03-06 08:58 | 2022-03-06 08:58 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-2 | 2022-03-06 09:42 | 2022-03-06 16:53 | 7:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | 230 kV CB 155 | 2022-03-06 09:47 | 2022-03-06 22:38 | 12:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-03 | 2022-03-07 14:46 | 2022-03-07 16:27 | 1:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Valuka | 132/33 kV transformer T-2 | 2022-03-08 07:25 | 2022-03-08 09:44 | 2:19 | S/O | Due to D/W work | 20 | 46.3333 | Power interruption
Savar | 33 kV Bus-B | 2022-03-08 08:45 | 2022-03-08 16:41 | 7:56 | S/O | Due to replacement work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T-4 | 2022-03-10 08:18 | 2022-03-10 10:29 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-2 | 2022-03-11 08:15 | 2022-03-11 13:13 | 4:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-4 | 2022-03-12 08:10 | 2022-03-12 12:52 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-1 | 2022-03-12 08:31 | 2022-03-12 11:04 | 2:33 | S/O | Due to C/M work | 44 | 112.2 | Power interruption
Tongi Milgate | 132/33 kV transformer GT-1 & GT-2 | 2022-03-13 12:02 | 2022-03-13 12:08 | 0:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformers T-3 & T4 & 33 kV Bus | 2022-03-14 08:21 | 2022-03-14 14:09 | 5:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2022-03-14 10:14 | 2022-03-14 11:10 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV transformer T-02 | 2022-03-15 07:16 | 2022-03-15 10:50 | 3:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2022-03-15 08:17 | 2022-03-15 16:54 | 8:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-01 | 2022-03-15 11:03 | 2022-03-15 13:45 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-02 | 2022-03-15 11:51 | 2022-03-15 12:50 | 0:59 | S/O | Due to C/M work | 40 | 39.3333 | Power interruption
Kishoreganj | 132/33 kV transformer T-2 | 2022-03-16 07:50 | 2022-03-16 09:20 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-03-16 08:35 | 2022-03-16 12:27 | 3:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 with 33 kv Bus | 2022-03-18 07:10 | 2022-03-18 09:55 | 2:45 | S/O | Due to installation.work | 28 | 77 | Power interruption
Satmosjid | 132/33 kV transformer T-2 | 2022-03-20 10:49 | 2022-03-20 12:24 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-03 | 2022-03-20 15:54 | 2022-03-20 17:50 | 1:56 | S/O | Due to C/M work | 25 | 48.3333 | Power interruption
Kishoreganj | 132/33 kV transformer T-1 | 2022-03-21 07:30 | 2022-03-21 07:42 | 0:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-03-21 12:28 | 2022-03-21 18:23 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-2 | 2022-03-22 06:40 | 2022-03-22 07:45 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-03-23 08:09 | 2022-03-23 10:00 | 1:51 | S/O | Due to C/M work | 30 | 55.5 | Power interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-03-28 08:14 | 2022-03-28 18:07 | 9:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 | 2022-03-28 08:09 | 2022-03-28 12:50 | 4:41 | S/O | Due to D/W work | 20 | 93.6667 | Power interruption
Mirpur | 132 kV main Bus | 2022-03-29 09:30 | 2022-03-29 09:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-A | 2022-03-29 08:06 | 2022-03-29 21:35 | 13:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 kV main Bus | 2022-03-29 09:30 | 2022-03-30 07:32 | 22:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV capacitor bank-2 | 2022-03-29 08:05 | 2022-03-29 08:05 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-2 with 33 kV Bus | 2022-03-31 06:15 | 2022-03-31 08:06 | 1:51 | S/O | Due to C/M work | 60 | 111 | Power interruption
Savar | 132/33 kV transformer T-3 | 2022-03-31 08:27 | 2022-03-31 11:44 | 3:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-3 | 2022-03-31 08:58 | 2022-03-31 14:20 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV transformer T-2 | 2022-03-31 11:53 | 2022-03-31 13:43 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 400/230 kV transformer T-02 |  | 2022-03-31 13:37 |  | S/O | After.maint work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2022-03-31 14:52 | 2022-03-31 18:55 | 4:03 | S/O | Due to C/M work | 60 | 243 | No interruption
|  |  | Total : | 194:43 |  | Unserved Energy: |  | 845.9167
Dhaka (South) Grid Circle :
Nawabganj | 132 kV bus coupler | 2022-03-02 09:46 | 2022-03-02 17:00 | 7:14 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformer T-2 | 2022-03-04 08:24 | 2022-03-04 08:24 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2022-03-05 09:20 | 2022-03-05 16:44 | 7:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-2 | 2022-03-05 09:39 | 2022-03-05 16:59 | 7:20 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230 kV bus-1 | 2022-03-06 08:55 | 2022-03-06 13:43 | 4:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-2 | 2022-03-06 09:29 | 2022-03-06 17:45 | 8:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | 230 kV future-1 bay | 2022-03-07 10:32 | 2022-03-07 12:55 | 2:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 230 kV future-4 bay | 2022-03-07 10:33 | 2022-03-07 12:48 | 2:15 | S/O | Due to A/M work | 0 | 0 | No interruption
Meghnaghat | 230 kV CB 805B | 2022-03-08 10:31 | 2022-03-08 12:09 | 1:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | 230 kV CB 805B | 2022-03-08 10:31 | 2022-03-08 17:02 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-1 | 2022-03-08 11:02 | 2022-03-08 12:06 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132 kV Bus | 2022-03-09 09:35 | 2022-03-09 14:25 | 4:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Moghbazar | 132/33 kV transformer T-3 | 2022-03-11 07:10 | 2022-03-11 07:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 | 2022-03-11 10:34 | 2022-03-11 12:15 | 1:41 | S/O | Due to C/M work | 20 | 33.6667 | Power interruption
Siddhirganj | 132 kV Bus-2 | 2022-03-12 09:50 | 2022-03-12 13:55 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T01 | 2022-03-14 10:43 | 2022-03-14 14:45 | 4:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T03 | 2022-03-14 15:10 | 2022-03-14 16:24 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-03-15 10:50 | 2022-03-15 11:55 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV transformer T02 | 2022-03-16 08:48 | 2022-03-16 16:40 | 7:52 | S/O | Due to A/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-2 | 2022-03-17 10:40 | 2022-03-17 13:25 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer T01 | 2022-03-19 07:20 | 2022-03-19 07:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-1 | 2022-03-21 06:50 | 2022-03-21 08:34 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-03-22 06:36 | 2022-03-22 08:22 | 1:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | 230 kV 953CB | 2022-03-22 10:16 | 2022-03-22 14:35 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalkhya | 132/33 kV transformer T-1 | 2022-03-22 13:04 | 2022-03-22 15:51 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T03 | 2022-03-23 07:19 | 2022-03-23 08:09 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 132 kV reserve Bus | 2022-03-23 09:02 | 2022-03-23 20:50 | 11:48 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-03-24 07:35 | 2022-03-24 07:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV transformer MTR-2 | 2022-03-24 08:43 | 2022-03-24 10:54 | 2:11 | S/O | Due to A/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-1 & T2 | 2022-03-24 10:00 | 2022-03-24 11:47 | 1:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | 132/33 kV transformer T-1 | 2022-03-25 06:55 | 2022-03-25 10:54 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 | 2022-03-27 10:46 | 2022-03-27 14:35 | 3:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T1 | 2022-03-29 09:16 | 2022-03-29 09:16 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 with 33 kv Bus | 2022-03-29 10:49 | 2022-03-29 11:06 | 0:17 | S/O | Due to maint. work | 15 | 4.25 | Power interruption
Munshiganj | 132/33 kV transformer T-2 | 2022-03-29 10:35 | 2022-03-29 15:12 | 4:37 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 116:21 |  | Unserved Energy: |  | 37.9167
Chattogram Grid Circle :
Hathazari | 230/132 kV transformer T02 | 2022-03-02 16:30 | 2022-03-02 16:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulshi | 132 kV Bus & 132/33 kV transformer T2 | 2022-03-04 06:44 | 2022-03-04 06:54 | 0:10 | S/O |  | 0 | 0 | No interruption
Chandraghona | 132/33 kV transformer T1 | 2022-03-10 10:04 | 2022-03-10 10:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T1 | 2022-03-11 21:40 | 2022-03-12 13:25 | 15:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| 33 kV Bus | 2022-03-12 07:15 | 2022-03-12 12:22 | 5:07 | S/O | Due to D/W work | 40 | 204.6667 | Power interruption
Halishahar | 132/33 kV transformer T3 | 2022-03-12 10:11 | 2022-03-12 16:12 | 6:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-03-12 17:04 | 2022-03-12 17:58 | 0:54 | S/O | Due to C/M work at 33 kV | 0 | 0 | No interruption
| 33 kV full Bus | 2022-03-12 15:00 | 2022-03-12 15:16 | 0:16 | S/O | Due to C/M work at 33 kV | 50 | 13.3333 | Power interruption
Baraulia | 132/33 kV transformer T2 | 2022-03-14 08:19 | 2022-03-14 14:42 | 6:23 | S/O | Due to C/M work | 10 | 63.8333 | Power interruption
Cox'sbazar | 132/33 kV transformer T2 | 2022-03-14 12:49 | 2022-03-14 13:14 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T3 | 2022-03-16 06:04 | 2022-03-16 08:55 | 2:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T1 | 2022-03-18 11:48 | 2022-03-18 12:35 | 0:47 | S/O | Due to C/M work | 5 | 3.9167 | Power interruption
Cox'sbazar | 132/33 kV transformer T3 | 2022-03-19 06:08 | 2022-03-19 09:52 | 3:44 | S/O | Due to A/M work | 40 | 149.3333 | Power interruption
Kulshi | 132/33 kV transformer T1 | 2022-03-19 08:21 | 2022-03-19 09:11 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-03-19 09:15 | 2022-03-19 09:42 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV bay |  | 2022-03-30 12:12 |  | S/O | After.maint work | 0 | 0 | No interruption
Halishahar | 132 kV bay |  | 2022-03-30 12:14 |  | S/O |  | 0 | 0 | No interruption
| 132 kV main bus | 2022-03-31 05:55 | 2022-03-31 08:09 | 2:14 | S/O | Due to C/M work | 55 | 122.8333 | Power interruption
|  |  | Total : | 45:54 |  | Unserved Energy : |  | 557.9167
Cumilla Grid Circle :
Fenchuganj | 230/132 kV transformer T-01 | 2022-03-01 09:08 | 2022-03-01 16:05 | 6:57 | S/O | Due to A/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-1 | 2022-03-02 08:01 | 2022-03-02 12:34 | 4:33 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-03-02 12:40 | 2022-03-02 15:08 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-03-02 15:41 | 2022-03-02 17:59 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-03-03 11:16 | 2022-03-03 12:10 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-03-03 12:14 | 2022-03-03 13:26 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132 kV Bus section -3 & 4 | 2022-03-04 07:58 | 2022-03-04 07:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-4 | 2022-03-04 07:47 | 2022-03-04 07:47 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T1 | 2022-03-04 12:00 | 2022-03-04 14:49 | 2:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132 kV Bus-3 & 4 | 2022-03-05 07:08 | 2022-03-05 16:51 | 9:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132 kV bus-2 |  | 2022-03-05 15:56 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 230 kV Bus-1 | 2022-03-06 10:01 | 2022-03-06 17:10 | 7:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T1 | 2022-03-06 15:15 | 2022-03-06 17:06 | 1:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T1 | 2022-03-08 09:06 | 2022-03-08 14:40 | 5:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-03-08 15:02 | 2022-03-08 18:58 | 3:56 | S/O | Due to tan delta test | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T2 | 2022-03-09 09:10 | 2022-03-09 16:00 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T3 | 2022-03-10 08:30 | 2022-03-10 13:10 | 4:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 | 2022-03-10 10:31 | 2022-03-10 13:47 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-03-10 13:18 | 2022-03-10 18:08 | 4:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T1 | 2022-03-14 07:15 | 2022-03-14 10:58 | 3:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T2 & 33 kV Bus | 2022-03-14 08:35 | 2022-03-14 11:58 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulaura | 132/33 kV transformer T2 | 2022-03-15 07:19 | 2022-03-15 10:58 | 3:39 | S/O | Due to C/M work | 5 | 18.25 | Power interruption
Fenchuganj | 132/33 kV transformer T2 |  | 2022-03-15 18:40 |  |  | After maint.work | 0 | 0 | No interruption
Chatak | 132/33 kV transformer T1 | 2022-03-16 06:16 | 2022-03-16 06:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-03-16 09:00 | 2022-03-16 09:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-03-24 07:14 | 2022-03-24 07:14 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-1 | 2022-03-24 12:54 | 2022-03-24 13:12 | 0:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-03-24 13:17 | 2022-03-24 13:30 | 0:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-03-24 13:34 | 2022-03-24 14:08 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-1 | 2022-03-25 08:04 | 2022-03-25 08:39 | 0:35 | S/O | Due to D/W work | 24 | 14 | Power interruption
| 132/33 kV transformer T-2 | 2022-03-25 08:57 | 2022-03-25 09:50 | 0:53 | S/O | Due to D/W work | 46 | 40.6333 | Power interruption
Sreemongal | 132/33 kV transformer T-1 | 2022-03-25 08:21 | 2022-03-25 10:03 | 1:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T4 with 33 kV Bus | 2022-03-29 11:11 | 2022-03-29 13:13 | 2:02 | S/O | Due to CT change | 20 | 40.6667 | Power interruption
Chowmuhani | 132/33 kV transformer T2 | 2022-03-31 08:45 | 2022-03-31 10:23 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2022-03-31 09:33 | 2022-03-31 11:06 | 1:33 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 89:13 |  | Unserved Energy : |  | 113.55
Khulna Grid Circle :
Madaripur | 132/33 kV transformer T3 |  | 2022-03-01 08:56 |  | S/O | After maint.work | 0 | 0 | No interruption
Payra | 132/33 kV transformers T3 & T4 | 2022-03-01 11:29 | 2022-03-01 15:50 | 4:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T-1 & 33 kV Bus-1 | 2022-03-03 08:25 | 2022-03-03 13:06 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna © | 132 kV Bus-1 | 2022-03-03 09:02 | 2022-03-03 16:42 | 7:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Mongla | 132 kV Bus | 2022-03-04 15:04 | 2022-03-04 16:47 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-2 with 33 kV Bus-2 | 2022-03-05 07:10 | 2022-03-05 11:02 | 3:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 with 33 kV Bus-2 | 2022-03-05 08:13 | 2022-03-05 15:08 | 6:55 | S/O | Due to C/M work | 3 | 20.75 | Power interruption
Faridpur | 132/33 kV transformer T-2 | 2022-03-06 10:04 | 2022-03-06 11:08 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-03-06 11:11 | 2022-03-06 11:33 | 0:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna © | 132/33 kV transformer T3 | 2022-03-07 07:07 | 2022-03-07 14:25 | 7:18 | S/O | Due to C/M work | 5 | 36.5 | Power interruption
Faridpur | 132/33 kV transformer T-1 & 33 kV Bus-1 & 2 | 2022-03-09 07:07 | 2022-03-09 10:27 | 3:20 | S/O | Due to C/M work | 40 | 133.3333 | Power interruption
Bhandaria | 132/33 kV transformer T-1 | 2022-03-10 11:20 | 2022-03-10 12:45 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-2 | 2022-03-10 08:42 | 2022-03-10 16:32 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-4 with 33 kV Bus | 2022-03-11 08:42 | 2022-03-11 11:12 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformers T-1 & T3 | 2022-03-12 08:18 | 2022-03-12 16:30 | 8:12 | S/O | Due to C/M work | 26 | 213.2 | Power interruption
Barisal(N) | 230/132 kV transformer T01 | 2022-03-12 09:41 | 2022-03-12 11:43 | 2:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T-1 | 2022-03-12 09:14 | 2022-03-12 14:26 | 5:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-2 | 2022-03-12 08:10 | 2022-03-12 10:03 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T-2 |  | 2022-03-13 14:11 |  |  | After maint.work | 0 | 0 | No interruption
Khulna © | 132/33 kV transformer T-2 | 2022-03-13 15:25 | 2022-03-13 16:42 | 1:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T-1 | 2022-03-16 08:41 | 2022-03-16 09:01 | 0:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-03-16 08:41 | 2022-03-16 08:41 |  |  |  | 0 | 0 | No interruption
Payra | 400/132 kV transformer T-02 |  | 2022-03-16 23:12 |  | S/O | After maint.work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-2 | 2022-03-18 07:10 | 2022-03-18 07:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 |  | 2022-03-20 16:45 |  | S/O | After maint.work | 0 | 0 | No interruption
Faridpur | 132 kV Bus-A | 2022-03-21 16:08 | 2022-03-21 16:56 | 0:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-3 with 132 kV Bus-A | 2022-03-22 09:34 | 2022-03-22 16:38 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal | 132 kV Bus-A | 2022-03-23 10:35 | 2022-03-23 11:20 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-2 | 2022-03-25 07:07 | 2022-03-25 07:07 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-03-25 09:29 | 2022-03-25 10:34 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-03-25 10:21 | 2022-03-25 11:33 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformers T-1 & T2 | 2022-03-29 07:03 | 2022-03-29 08:42 | 1:39 | S/O | Due to C/M work | 30 | 49.5 | Power interruption
Barisal(N) | 132/33 kV transformer T-5 | 2022-03-31 09:01 | 2022-03-31 16:06 | 7:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-3 | 2022-03-31 19:09 | 2022-03-31 20:56 | 1:47 | S/O | Due to C/M work | 52 | 92.7333 | No interruption
|  |  | Total : | 93:22 |  | Unserved Energy : |  | 546.0167
HVDC Grid Circle
Jashore | 132 kV Bus coupler |  | 2022-03-03 15:59 |  | S/O | After maint.work | 0 | 0 | No interruption
Jhenaidah(N) | 230 kV Bus-1 & 2 | 2022-03-04 07:42 |  |  | S/O | Due to protection test | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T1 | 2022-03-04 08:22 | 2022-03-04 16:35 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T1 | 2022-03-06 12:09 | 2022-03-06 18:09 | 6:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kustia | 132/33 kV transformer T1 | 2022-03-08 07:01 | 2022-03-08 08:27 | 1:26 | S/O | Due to D/W work | 8 | 11.4667 | Power interruption
Jhenaidah | 132/33 kV transformer T1 |  | 2022-03-13 14:12 |  | S/O | After maint.work | 0 | 0 | No interruption
Bheramara | 230/132 kV transformer T-02 | 2022-03-14 08:01 | 2022-03-14 15:57 | 7:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T2 | 2022-03-18 08:23 | 2022-03-18 08:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T2 | 2022-03-22 12:02 | 2022-03-22 13:13 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara GK | 132/33 kV transformer T1 | 2022-03-23 13:01 | 2022-03-23 14:46 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | 230 kV 20DF21 filter | 2022-03-27 10:41 | 2022-03-27 11:22 | 0:41 | S/O | Due to maint.work | 0 | 0 | No interruption
| 231 kV 20DF22 filter | 2022-03-27 11:29 | 2022-03-27 11:50 | 0:21 | S/O | Due to maint.work | 0 | 0 | No interruption
| 232 kV 20DF23 filter | 2022-03-27 12:05 | 2022-03-27 12:25 | 0:20 | S/O |  | 0 | 0 | No interruption
Ruppur | 132/11 kV transformer T1 | 2022-03-29 12:19 | 2022-03-29 13:17 | 0:58 | S/O | Due to maint.work by NESCO | 0 | 0 | No interruption
|  |  | Total : | 28:51 |  | Unserved Energy : |  | 11.4667
Bogura Grid Circle:
Sirajganj | 132/33 kV transformer T4 | 2022-03-01 09:00 | 2022-03-01 12:33 | 3:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T1 | 2022-03-01 12:45 | 2022-03-01 14:13 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV transformer T4 |  | 2022-03-03 16:40 |  |  | After maint.work | 0 | 0 | No interruption
Rajshahi(O) | 132 kV Bus | 2022-03-04 06:40 | 2022-03-04 11:46 | 5:06 | S/O | Due to C/M work | 60 | 306 | Power interruption
C.nawabganj | 132 kV Bus & 132/33 kV transformer T1 | 2022-03-04 06:44 | 2022-03-04 12:30 | 5:46 | S/O |  | 35 | 201.8333 | Power interruption
Natore | 132/33 kV transformers T1 & T2 | 2022-03-05 08:18 | 2022-03-05 09:44 | 1:26 | S/O | Due to D/W work | 61 | 87.4333 | Power interruption
Pabna | 132/33 kV transformer T1 | 2022-03-05 10:30 | 2022-03-05 12:25 | 1:55 | S/O | Due to 33 kV bay extension work | 4 | 7.6667 | Power interruption
Naogaon | 132/33 kV transformer T3 & 33 kV Bus | 2022-03-08 07:40 | 2022-03-08 09:10 | 1:30 | S/O | Due to D/W work | 40 | 60 | Power interruption
Rangpur | 132/33 kV transformers T1 & T2 with 33 kV Bus | 2022-03-11 07:18 | 2022-03-11 12:10 | 4:52 | S/O | Due to D/W work | 70 | 340.6667 | Power interruption
Bogura(O) | 132/33 kV transformer T1with 33 kv Bus-1 | 2022-03-11 07:35 | 2022-03-11 10:16 | 2:41 | S/O | Due to C/M work | 40 | 107.3333 | Power interruption
Rangpur | 132/33 kV transformer T1 with 33 kV Bus | 2022-03-12 09:15 | 2022-03-12 11:20 | 2:05 | S/O | Due to D/W work | 15 | 31.25 | Power interruption
Sherpur(Bogura) | 132/33 kV transformer T3 | 2022-03-14 08:55 | 2022-03-14 10:48 | 1:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformer T-01 | 2022-03-16 09:00 | 2022-03-16 11:40 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T3 & 33 kV Bus | 2022-03-19 07:46 | 2022-03-19 10:30 | 2:44 | S/O | Due to C/M work | 26 | 71.0667 | Power interruption
Mithapukur | 132/33 kV transformer T1 | 2022-03-23 15:38 | 2022-03-23 16:50 | 1:12 | S/O | Due to C/M work | 1111 | 1333.2 | Power interruption
Barapukuria | 132/33 kV transformer T3 | 2022-03-24 16:08 | 2022-03-24 17:34 | 1:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T4 | 2022-03-24 17:37 | 2022-03-24 18:21 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 & T2 & 33 kV Bus | 2022-03-25 11:05 | 2022-03-25 12:05 | 1:00 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 42:01 |  | Unserved Energy : |  | 2546.45
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 610:25 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: March2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-03-01 09:18 | 2022-03-01 15:06 | 5:48 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Agargaon 230 kV Ckt-1 | 2022-03-01 13:26 | 2022-03-01 16:23 | 2:57 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Agargaon 230 kV Ckt-1 | 2022-03-02 08:01 | 2022-03-02 13:45 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-1 | 2022-03-02 08:48 | 2022-03-02 20:38 | 11:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2022-03-03 09:55 | 2022-03-03 13:37 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 230 kV Ckt | 2022-03-05 10:00 | 2022-03-05 17:44 | 7:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV Ckt-1 | 2022-03-06 09:37 | 2022-03-06 19:42 | 10:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-03-06 11:37 | 2022-03-06 17:40 | 6:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2022-03-06 15:29 | 2022-03-06 18:40 | 3:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Uttara 3rd phase 132 kV Ckt | 2022-03-07 09:54 | 2022-03-07 17:08 | 7:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Tongi P/S 132 kV Ckt | 2022-03-07 11:23 | 2022-03-07 17:43 | 6:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-1 | 2022-03-07 14:21 | 2022-03-07 15:26 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV CKt-2 | 2022-03-07 15:27 | 2022-03-07 15:46 | 0:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2022-03-08 08:47 | 2022-03-08 17:08 | 8:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-03-08 09:14 | 2022-03-08 17:52 | 8:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-1 | 2022-03-08 09:48 | 2022-03-08 13:03 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Tongi P/S 132 kV Ckt | 2022-03-09 09:55 | 2022-03-09 17:04 | 7:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur S/S | Kabirpur S/S-Kodda P.P 132 kV Ckt-1 | 2022-03-09 12:43 | 2022-03-09 14:39 | 1:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 kV Ckt-2 | 2022-03-09 14:40 | 2022-03-09 15:02 | 0:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-03-10 09:36 | 2022-03-10 14:09 | 4:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Netrakona 132 kV Ckt-2 | 2022-03-11 12:35 | 2022-03-11 12:46 | 0:11 | S/O | due to fire broken out from gas pipe line | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-03-14 10:15 | 2022-03-14 11:11 | 0:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-03-15 07:18 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
2022-03-16 10:15
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-03-15 09:37 | 2022-03-15 15:17 | 5:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 |  | 2022-03-16 00:16 |  |  | After maint.work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-03-16 09:37 | 2022-03-16 15:17 | 5:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-03-16 11:56 | 2022-03-16 17:09 | 5:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-03-17 10:40 | 2022-03-17 17:55 | 7:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Tongi P/S 132 kV Ckt | 2022-03-18 10:10 | 2022-03-18 11:08 | 0:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghangaht 230 kV Ckt-1 | 2022-03-20 09:41 | 2022-03-20 16:37 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-03-21 08:40 | 2022-03-21 16:42 | 8:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghangaht 230 kV Ckt-1 | 2022-03-22 09:48 | 2022-03-22 16:11 | 6:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Meghangaht 230 kV Ckt-2 | 2022-03-24 09:38 | 2022-03-24 16:13 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| Aminbazar-Meghangaht 230 kV Ckt-1 | 2022-03-25 07:31 | 2022-03-25 07:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-03-25 08:23 | 2022-03-25 16:14 | 7:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV Ckt-1 | 2022-03-28 05:56 | 2022-03-28 09:27 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Uttara 132 kV Ckt | 2022-03-29 07:46 | 2022-03-29 07:46 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Aminbazar 230 kV Ckt-2 | 2022-03-30 06:21 | 2022-03-30 12:42 | 6:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 kV Ckt-1 | 2022-03-31 07:15 | 2022-03-31 10:46 | 3:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-2 | 2022-03-31 09:27 | 2022-03-31 12:54 | 3:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-03-31 10:48 | 2022-03-31 11:44 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV Ckt-1 | 2022-03-31 13:11 | 2022-03-31 17:28 | 4:17 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 189:59 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-2 | 2022-03-01 08:22 | 2022-03-01 08:22 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-2 | 2022-03-02 08:44 | 2022-03-02 18:10 | 9:26 | S/O | Due to A/M work | 0 | 0 | No interruption
Narsingdi | Narsingdi-B.Baria 132 kV Ckt-2 | 2022-03-05 08:32 | 2022-03-05 16:55 | 8:23 | S/O | Due to A/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj P/S 132 kV Ckt | 2022-03-05 09:06 | 2022-03-05 13:31 | 4:25 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Char-Sadipur 132 kV Ckt-1 | 2022-03-06 10:50 | 2022-03-06 14:57 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV Ckt | 2022-03-08 13:05 | 2022-03-08 18:08 | 5:03 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-APR 230 kV Ckt | 2022-03-09 09:26 | 2022-03-09 13:17 | 3:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal AIS | Ghorashal AIS-Ghorashal GIS 230 kV Ckt-2 | 2022-03-10 12:52 | 2022-03-10 14:14 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | Bhulta-Haripur 230 kV Ckt-2 | 2022-03-14 08:21 | 2022-03-14 16:22 | 8:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Postogula 132 kV Ckt-1 | 2022-03-14 10:46 | 2022-03-14 10:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Keraniganj 230 kV Ckt-2 | 2022-03-15 12:37 | 2022-03-15 13:07 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Keraniganj 230 kV Ckt-1 | 2022-03-15 12:16 | 2022-03-15 13:41 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hasnabad-Sitalakhya 132 kV Ckt | 2022-03-17 08:04 | 2022-03-17 10:25 | 2:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreenagar | Sreenagar -Keraniganj 132 kV Ckt-1 & 2 | 2022-03-18 06:05 | 2022-03-18 15:07 | 9:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV Ckt-1 |  | 2022-03-19 07:22 |  | S/O | Due to C/M work | 0 | 0 | No interruption
| Siddhirganj-Maniknagar 230 kV Ckt-1 |  | 2022-03-20 15:39 |  |  | After maint.work | 0 | 0 | No interruption
Haripur | Haripur-Fatullah 132 kV Ckt | 2022-03-21 07:16 | 2022-03-21 07:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Postogula 132 kV Ckt-2 | 2022-03-21 10:15 | 2022-03-21 12:53 | 2:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt | 2022-03-21 10:54 | 2022-03-21 16:13 | 5:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| Haripur-Haripur P/S 132 kV Ckt | 2022-03-22 07:30 | 2022-03-22 07:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 k Ckt-1 | 2022-03-23 09:03 | 2022-03-23 16:11 | 7:08 | S/O | Due to A/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Char-saidpur 132 kV Ckt |  | 2022-03-23 19:39 |  |  | After maint.work | 0 | 0 | No interruption
Ghorashal | Ghorashal -Bhulta 230 kV Ckt-2 | 2022-03-25 08:28 | 2022-03-25 18:01 | 9:33 | S/O | Due to wave trap removal | 0 | 0 | No interruption
Keraniganj | Keraniganj-Aminbazar 230 kV Ckt-1 | 2022-03-27 09:50 | 2022-03-27 22:30 | 12:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Fatullah 132 kV Ckt |  | 2022-03-28 13:57 |  |  | After maint.work | 0 | 0 | No interruption
| Haripur-Rahim steel 132 kV Ckt | 2022-03-28 08:48 | 2022-03-28 14:29 | 5:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-1 | 2022-03-28 10:07 | 2022-03-28 13:05 | 2:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Madanganj 132 kV Ckt | 2022-03-28 10:19 | 2022-03-28 10:19 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-1 |  | 2022-03-28 17:29 |  | S/O | After maint.work | 0 | 0 | No interruption
Ghorashal | Ghorashal -Ashuganj(S) 230 kV Ckt-1 |  | 2022-03-31 11:57 |  | S/O | After maint.work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV Ckt-1 | 2022-03-31 11:53 | 2022-03-31 16:59 | 5:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 | 2022-03-31 17:21 | 2022-03-31 19:57 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 111:35 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Shahmirpur | Shahmirpur-Sikalbaha 132 kV Ckt-1 | 2022-03-01 08:07 | 2022-03-01 13:03 | 4:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV Ckt-2 | 2022-03-02 09:08 | 2022-03-02 13:06 | 3:58 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV Ckt-2 | 2022-03-05 08:31 | 2022-03-05 16:08 | 7:37 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Hathazari P/P 132 kV Ckt | 2022-03-07 16:04 | 2022-03-07 18:00 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Feni 132 kV Ckt | 2022-03-08 06:16 | 2022-03-08 13:14 | 6:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Rampur 230 kV bay-1 | 2022-03-08 10:52 | 2022-03-08 11:40 | 0:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Rampur 230 kV bay-2 | 2022-03-08 11:42 | 2022-03-08 12:15 | 0:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Modern steel 132 kV Ckt | 2022-03-09 08:33 | 2022-03-09 14:02 | 5:29 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Bay-1 & 2 | 2022-03-10 06:40 | 2022-03-10 06:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV Ckt-2 | 2022-03-13 06:49 | 2022-03-13 17:55 | 11:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt -2 | 2022-03-14 07:29 | 2022-03-14 18:02 | 10:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-1 | 2022-03-14 09:20 | 2022-03-14 10:46 | 1:26 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madunaghat-Hathazari 132 kV Ckt-2 | 2022-03-14 11:07 | 2022-03-14 16:43 | 5:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt -2 | 2022-03-15 07:01 | 2022-03-15 16:56 | 9:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sholosahar 132 kV Ckt-1 | 2022-03-16 09:27 | 2022-03-16 13:29 | 4:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-03-16 07:12 | 2022-03-16 07:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV Ckt-1 | 2022-03-22 07:10 | 2022-03-22 07:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV Ckt-2 | 2022-03-23 09:27 | 2022-03-23 13:01 | 3:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt -2 | 2022-03-24 08:13 | 2022-03-24 12:44 | 4:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Khaghrachari | Khagrachari-Rangamati 132 kV Ckt-1 | 2022-03-24 10:22 | 2022-03-24 13:35 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Feni 132 kV Ckt-1 | 2022-03-29 07:04 | 2022-03-29 08:49 | 1:45 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baroierhat-PHP 132 kV Ckt | 2022-03-29 09:03 | 2022-03-29 10:10 | 1:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2022-03-30 05:58 | 2022-03-30 08:26 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-2 | 2022-03-31 08:26 | 2022-03-31 20:46 | 12:20 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 103:51 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
B.Baria | B.Baria-Narsingdi 132 kV Ckt-2 | 2022-03-01 08:32 | 2022-03-01 18:06 | 9:34 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV Ckt | 2022-03-03 06:48 | 2022-03-06 13:23 | 78:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sylhet-Chattak 132 kV Ckt-1 | 2022-03-03 07:08 | 2022-03-06 13:27 | 78:19 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Narsingdi 132 kV Ckt-2 | 2022-03-03 08:42 | 2022-03-03 17:58 | 9:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 |  | 2022-03-03 17:04 |  |  | new connection | 0 | 0 | No interruption
| Cumilla(N)-Cumilla(S) 132 kV Ckt-2 |  | 2022-03-03 17:15 |  |  |  | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-2 | 2022-03-04 07:29 | 2022-03-04 07:29 |  | S/O | Due to C/M work | 0 | 0 | No interruption
| Sylhet-Sylhet CCPP 132 kV Ckt | 2022-03-04 06:40 | 2022-03-04 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj P/S | Fenchuganj P/S-Chattak 132 kV Ckt | 2022-03-06 07:45 |  |  | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt-2 | 2022-03-06 08:29 | 2022-03-06 16:51 | 8:22 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV Ckt-2 | 2022-03-06 10:12 | 2022-03-06 14:57 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV Ckt |  | 2022-03-06 13:23 |  |  | After maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-03-06 15:01 | 2022-03-06 17:10 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Kulaura | Kulaura-Fenchuganj 132 kV Ckt-1 | 2022-03-06 18:32 | 2022-03-06 21:12 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt | 2022-03-07 09:58 | 2022-03-07 17:57 | 7:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 & 2 | 2022-03-07 09:18 | 2022-03-07 18:30 | 9:12 | S/O | Due to D/W work | 0 | 0 | No interruption
PHP | PHP-Feni 132 kV Ckt | 2022-03-08 06:16 | 2022-03-08 13:43 | 7:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV CKt-1 & 2 | 2022-03-08 06:20 | 2022-03-08 13:39 | 7:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Ashuganj 132 kV Ckt-3 | 2022-03-08 08:56 | 2022-03-08 17:27 | 8:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsarai EPZ | Mirsarai EPZ-BSRM 230 kV Ckt-2 | 2022-03-08 10:22 | 2022-03-08 14:37 | 4:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV CKt-2 | 2022-03-08 13:47 | 2022-03-08 17:33 | 3:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsarai EPZ | Mirsarai EPZ-BSRM 230 kV Ckt-2 | 2022-03-08 15:06 | 2022-03-08 16:54 | 1:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-03-09 09:28 | 2022-03-09 17:34 | 8:06 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-03-09 09:45 | 2022-03-09 15:48 | 6:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-Chauddagram 132 kV Ckt-1 | 2022-03-09 14:31 | 2022-03-09 17:30 | 2:59 | S/O | Due to D/W work | 0 | 0 | No interruption
| Feni-PHP 132 kV Ckt | 2022-03-10 07:02 | 2022-03-10 13:31 | 6:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV Ckt-2 | 2022-03-10 08:44 | 2022-03-10 08:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-03-10 10:01 | 2022-03-10 18:19 | 8:18 | S/O | Due to A/M work | 0 | 0 | No interruption
Lakdhanvi | Lakdhanvi-Chowddogram 132 kV Ckt | 2022-03-11 08:51 | 2022-03-11 08:51 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Lakdhanvi P.P 132 kV Ckt |  | 2022-03-12 18:33 |  | S/O | After maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-03-13 09:03 | 2022-03-13 16:51 | 7:48 | S/O | Due to SCADA work | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-03-14 09:06 | 2022-03-14 17:57 | 8:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt | 2022-03-15 09:49 | 2022-03-15 17:58 | 8:09 | S/O | Due to A/M work | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt | 2022-03-16 09:22 | 2022-03-16 17:27 | 8:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Chowddagram | Chowddagram-Feni 132 kV Ckt-2 | 2022-03-21 09:16 | 2022-03-21 18:07 | 8:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj P/S | Fenchuganj P/S-Sylhet 132 kV Ckt | 2022-03-30 06:40 | 2022-03-30 06:40 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj P/S 132 kV Ckt | 2022-03-31 07:14 | 2022-03-31 12:52 | 5:38 | S/O | Due to D/W work | 35 | 197.1667 | Power interruption
Ramganj | Ramganj-Chowmuhani 132 kV Ckt-1 | 2022-03-31 10:59 | 2022-03-31 15:54 | 4:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Surjamoninagar 132 kV Ckt-1 | 2022-03-31 11:28 | 2022-03-31 12:42 | 1:14 | S/O | Due to protection test | 0 | 0 | No interruption
| Cumilla(S)-Surjamoninagar 132 kV Ckt-2 | 2022-03-31 13:22 | 2022-03-31 13:53 | 0:31 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 329:54 |  | Unserved Energy: |  | 197.1667
Khulna Grid Circle :
Khulna (S) | Khulna (S)-Satkhira 132 kV Ckt-1 |  | 2022-03-03 09:43 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Faridpur 132 kV Ckt-1 & 2 | 2022-03-04 08:50 | 2022-03-04 18:05 | 9:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Madaripur | Madaripur-Gopalganj 132 kV Ckt-1 & 2 | 2022-03-04 08:50 | 2022-03-04 18:13 | 9:23 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV Ckt-2 | 2022-03-18 08:14 | 2022-03-18 12:08 | 3:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj (N) 132 kV Ckt-1 | 2022-03-23 09:07 | 2022-03-23 17:35 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
| Faridpur-Gopalganj (N) 132 kV Ckt-2 | 2022-03-23 09:21 | 2022-03-23 17:36 | 8:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Faridpur 132 kV Ckt-1 & 2 | 2022-03-24 06:29 | 2022-03-24 06:29 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulna (C) | Khulna ©-KPCL 132 kV CKT-2 | 2022-03-25 09:29 | 2022-03-25 15:01 | 5:32 | S/O | Due to PT test | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalganj 132 kV CKt-1 | 2022-03-28 10:47 | 2022-03-28 11:54 | 1:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Satkhira 132 kV Ckt-2 | 2022-03-29 08:30 | 2022-03-29 10:28 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj P.P | Gopalganj P.P-Payra 400 kV Ckt-1 | 2022-03-31 10:49 | 2022-03-31 18:00 | 7:11 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 55:03 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jashore | Jashore-Noapara 132 kV Ckt-1 | 2022-03-01 09:17 | 2022-03-01 11:40 | 2:23 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jashore-Noapara 132 kV Ckt-1 |  | 2022-03-01 12:25 |  |  | After maint.work | 0 | 0 | No interruption
Bheramara | Bheramara-G.K 132 kV Ckt-2 | 2022-03-07 10:18 | 2022-03-07 10:18 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV Ckt | 2022-03-09 08:32 | 2022-03-09 15:17 | 6:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Jhenaidah 230 kV Ckt-2 | 2022-03-09 08:23 | 2022-03-09 18:09 | 9:46 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC-Baharampur 400 kV Ckt-1 | 2022-03-09 11:04 | 2022-03-09 15:47 | 4:43 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC-Jhenaidah 230 kV Ckt-1 | 2022-03-10 10:05 | 2022-03-10 11:57 | 1:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah(N) | Jhenaidah(N)-Jessore 132 kV Ckt-1 | 2022-03-11 07:36 | 2022-03-11 15:03 | 7:27 | S/O | Due to DFDR work | 0 | 0 | No interruption
| Jhenaidah(N)-Jessore 132 kV Ckt-2 | 2022-03-12 08:29 | 2022-03-12 16:12 | 7:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | Jashore-Benapole 132 kV Ckt-1 | 2022-03-20 07:55 | 2022-03-20 16:08 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Benapole | Benapole-Jashore 132 kV Ckt-1 | 2022-03-22 08:23 | 2022-03-22 16:29 | 8:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah(N)132 kV Ckt-1 | 2022-03-22 09:43 | 2022-03-22 10:32 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Bottail 132 kV Ckt-1 | 2022-03-22 10:53 | 2022-03-22 11:42 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV Ckt | 2022-03-22 13:24 | 2022-03-22 13:58 | 0:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Benapole 132 kV Ckt-2 | 2022-03-23 07:54 | 2022-03-23 07:54 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-G.K 132 kV Ckt-2 | 2022-03-23 15:34 | 2022-03-23 21:18 | 5:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Sirajganj 230 kV Ckt-1 | 2022-03-25 09:29 | 2022-03-25 11:25 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-G.K 132 kV Ckt-2 | 2022-03-25 10:05 | 2022-03-25 12:32 | 2:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV Ckt-1 & 2 | 2022-03-27 08:27 | 2022-03-27 17:42 | 9:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 400 kV 10CF26 | 2022-03-28 08:56 | 2022-03-28 10:21 | 1:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV Ckt-1 | 2022-03-28 08:55 | 2022-03-28 14:06 | 5:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Benapole 132 kV Ckt-2 | 2022-03-30 07:58 | 2022-03-30 16:11 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 93:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-2 | 2022-03-01 08:13 | 2022-03-01 17:25 | 9:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | Natore-Ishurdi 132 kV Ckt-1 | 2022-03-03 13:23 | 2022-03-03 13:39 | 0:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV Ckt-2 | 2022-03-05 07:13 | 2022-03-05 19:17 | 12:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Bogura 230 kV Ckt-2 | 2022-03-15 09:29 | 2022-03-15 10:47 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barapukuria-Bogura 230 kV Ckt-2 | 2022-03-15 09:29 | 2022-03-15 10:47 | 1:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-angpur GT 132 kV Ckt | 2022-03-16 16:28 | 2022-03-16 16:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-2 | 2022-03-20 10:33 | 2022-03-20 15:57 | 5:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-1 | 2022-03-30 08:31 | 2022-03-30 16:22 | 7:51 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 37:23 |  | Unserved Energy: |  | 0
Others :
Ullon | Ullon-Dhanmondi 132 kV line-3 |  | 2022-03-03 16:17 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 921:06 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March 2022
| Area | Previous Month (February' 2022) |  |  |  | Current Month (March '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 7 | 1 | 135 | 143 | 19 | 2 | 89 | 110
2 | Dhaka (South) Grid Circle. | 15 | 4 | 95 | 114 | 28 | 1 | 68 | 97
3 | Chattogram Grid Circle. | 11 | 3 | 83 | 97 | 12 | 1 | 42 | 55
4 | Cumilla Grid Circle. | 17 | 4 | 110 | 131 | 19 | 3 | 73 | 95
5 | Khulna Grid Circle. | 10 | 6 | 52 | 68 | 7 | 3 | 45 | 55
6 | HVDC Grid Circle | 4 | 2 | 34 | 40 | 8 | - | 36 | 44
7 | Bogura Grid Circle. | 3 | 3 | 28 | 34 | 7 | 10 | 26 | 43
8 | Others |  | 1 | 5 | 6 |  | 1 | 1 | 2
9 | Total | 67 | 24 | 542 | 633 | 100 | 21 | 380 | 501
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March 2022 | [9 empty] | 555.*8
| Area | Previous Month (January' 2022) |  |  |  | Current Month (February '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total |  | 82.97
1 | Dhaka (North) Grid Circle. | 18.67 |  | 1174.2 | 1192.87 | 544.4133 |  | 845.92 | 1390.3333 |  | 1112.08 |  | 8.4
2 | Dhaka (South) Grid Circle. | 987.2 | 93 |  | 1080.2 | 113.7333 |  | 37.9167 | 151.65 |  | 1195.05 |  | 16.2
3 | Chattogram Grid Circle. | 157.75 | 40 | 418.92 | 616.67 | 135.1167 |  | 557.9167 | 693.0333 |  |  |  | 11.0833
4 | Cumilla Grid Circle. | 480.85 |  | 45.8 | 526.65 | 251.2167 |  | 310.7167 | 561.9333 |  |  |  | 22.9167
5 | Khulna Grid Circle. | 27.19 | 80.67 | 259.33 | 367.19 | 38.3333 | 31.73 | 546.02 | 616.0833 |  | 45.4333 |  | 58.6
6 | HVDC Grid Circle |  | 9.33 | 123.75 | 133.08 |  |  | 11.47 | 11.47 |  |  |  |  | 127.67 | 51.6
7 | Bogura Grid Circle. | 5.2 |  | 664.42 | 669.62 | 72.08 | 270.32 | 2205.7833 | 2548.1833 |  | 0 |  |  | 179.27
8 | Others |  |  |  | 0 |  |  |  | 0 |  | 16.5333 | 303.33
9 | Total | 1676.86 | 223 | 2686.42 | 4586.28 | 1154.8933 | 302.05 | 4515.7433 | 5972.6867 |  | 21 | 159.5
[11 empty] | 82.9667 | 462.83
[10 empty] | 38.93 |  | 88.25
[10 empty] | 20.27 |  | 2.93
[10 empty] | 59.2 |  | 91.18
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 2 | 10 | 12 |  | 2 | 10 | 1148
2 | Dhaka (South) | 5031.6 | 5 | 2 | 7 | 4 | 1 | 2 | 126.95
3 | Chattogram | 2042 | 3 | 6 | 9 | 3 | 2 | 4 | 678.25
4 | Khulna | 2434 | 2 | 6 | 8 | 1 | 1 | 6 | 616.09
5 | HVDC | 5954.3 | - | 1 | 1 | - | - | 1 | 11.47 |  |  | 58.03
6 | Bogura | 3145.6 | 6 | 9 | 16 | 1 | 1 | 13 | 2383.6 |  | 643.56
7 | Cumilla | 2981 | 6 | 4 | 10 | 5 | 3 | 2 | 364.7667 |  | 5329.1267
8 | Others | - | - | - | - | - | - | - | 0 |  | 5972.6867
| Total | 30390.1 | [6 empty] | 5329.1267
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.97%
4 | Khulna | 99.96%
5 | HVDC | 99.93% | [6 empty] | Executive Engineer
6 | Bogura | 99.9% | [6 empty] | Information Management Division
7 | Cumilla | 98.92% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March 2022 | [12 empty] | 2043.54
4646.17
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | - | 3 | 2 | - | 1 | 242.33
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 3 | - | 2 | 24.7
3 | Chattogram | 917 | - | 2 |  | 2 | 1 |  | 1 | 14.78
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 2 |  | 2 | - | 1 | 1 | 164.5833
7 | Cumilla | 1648.16 | - | 1 |  | 1 |  |  | 1 | 197.1667
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 643.56
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.92%
2 | Dhaka (South) | 99.91% | [9 empty] | 5317.6567
3 | Chattogram | 99.98% | [9 empty] | 643.56
4 | Khulna | 99.99% | [9 empty] | 5961.2167
5 | Bheramara (HVDC) | 99.99% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 99.86% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-03-01 | 10 | - | 5 | 05hr'20 min | 1 | 03hr'11 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kabirpur | 1 | 0:55 | 227 | 208.0833 | Due to tripping of 132/33 kV transformers T-1 ,T 2 & T3
Jamalpur | 1 | 1:34 | 60 | 94 | Due to red-hot maint 132/33 kV Transformer T2
Dhamrai | 1 | 3:20 | 70 | 233.3333 | Due to tripping of Dhamrai-kaliakoir 132 kV Ckt-1 & 2
Tongi | 1 | 0:06 | 70 | 7 | Due to tripping of Tongi-Bashundhara 132 kV Ckt-1
Kabirpur | 1 | 0:06 | 20 | 2 | Due to red-hot maint of Kabirpur-Manikganj 132 kV Ckt-1
Netrakona | 2 | 1:09 | 17 | 19.55 | Due to S/D of 132/33 kV transformer T-2
Valuka |  | 2:19 | 20 | 46.3333
Sherpur | 1 | 2:33 | 44 | 112.2 | Due to S/D of 132/33 kV transformer T-1
Joydevpur | 2 | 0:59 | 40 | 39.3333 | Due to S/D of 132/33 kV transformer T-2
Bhaluka |  | 2:45 | 28 | 77 | Due to S/D of 132/33 kV transformer T-1
Joydevpur | 1 | 1:56 | 25 | 48.3333 | Due to S/D of 132/33 kV transformer T-03
Bhaluka | 1 | 1:51 | 30 | 55.5 | Due to tripping of 132/33 kV transformer T-1
Netrakona | 1 | 4:41 | 20 | 93.6667 | Due to tripping of 132/33 kV transformer T-3
Mymensingh | 2 | 1:51 | 60 | 111 | Due to S/D of 132/33 kV transformer T-2
Kabirpur |  | 4:03 | 60 | 243
Keraniganj | 1 | 1:35 | 20 | 31.6667 | Due to red-hot maint 132/33 kV Transformer T2
Sreenagar | 1 | 0:13 | 10 | 2.1667 | Due to 33 kV feeder fault
Hasnabad | 1 | 0:26 | 60 | 26 | Due to tripping of 33 kV Bus
Sonargaon | 1 | 0:24 | 10 | 4 | Due to 33 kV feeder fault
Narsinghdi | 1 | 0:36 | 42 | 25.2 | Due to tripping of 132/33 kV transformer T-2
Rampura | 1 | 0:05 | 100 | 8.3333 | Due to tripping of Rampura-Bashundhara 132 kV Ckt-2
Haripur | 1 | 1:29 | 65 | 15.1667 | Due to tripping of Haripur-Bhulta 132 kV Ckt-1
Keraniganj | 1 | 0:08 | 9 | 1.2 | Due to tripping of Keraniganj-Sreenagar 132 kV Ckt-1 & 2
Sreenagar | 2 | 1:41 | 20 | 33.6667 | Due to tripping of 132/33 kV transformer T-1
|  | 0:17 | 15 | 4.25 | Due to S/D of 132/33 kV transformer T-1
Halishahar | 1 | 0:52 | 60 | 52 | Due to tripping of 132/33 kV transformers T-1 ,T 2 & T3
Madunaghat | 1 | 0:44 | 35 | 25.6667 | Due to tripping of 132/33 kV transformer T-1
Halishahar | 1 | 0:18 | 75 | 22.5 | Due to 33 kV feeder fault
Cox'sbazar | 1 | 0:22 | 55 | 20.1667 | Due to tripping of 132/33 kV transformer T-3
Khulshi | 1 | 2:01 | 35 | 11.6667 | Due to tripping of Khulshi-Halishahar 132 kV Ckt-1
Baraulia | 1 | 0:17 | 11 | 3.1167 | Due to tripping of Baroulia-KSRM 132 kV Ckt
Bakulia | 1 | 5:07 | 40 | 204.6667 | Due to S/D of 33 kV Bus
Halishahar | 1 | 0:16 | 50 | 13.3333 | Due to S/D of 33 kV full Bus
Baraulia | 1 | 6:23 | 10 | 63.8333 | Due to S/D of 132/33 kV transformer T-2
Halishahar |  | 0:47 | 5 | 3.9167 | Due to S/D of 132 kV Bus-2
Cox'sbazar | 1 | 3:44 | 40 | 149.3333 | Due to S/D of 132 kV Bus
Halishahar |  | 2:14 | 55 | 122.8333
Cumilla (N) |  | 3:44 | 50 | 186.6667 | Due to tripping of 132/33 kV transformer T-3
B.Baria |  | 0:17 | 70 | 19.8333 | Due to tripping of 132/33 kV transformers T-1 & T2
|  | 0:06 | 120 | 12
Cumilla (N) | 1 | 0:09 | 162 | 24.3 | Due to tripping of 132/33 kV transformer T-3
Chatak |  | 0:17 | 5 | 1.4167 | Due to 33 kV feeder fault
Cumilla (S) |  | 0:14 | 30 | 7 | Due to tripping of 132/33 kV transformer T-2
Kulaura |  | 3:39 | 5 | 18.25 | Due to S/D of 132/33 kV transformer T-2
Sylhet | 2 | 0:35 | 24 | 14 | Due to S/D of 132/33 kV transformer T-1
|  | 0:53 | 46 | 40.6333 | Due to S/D of 132/33 kV transformer T-2
Cumilla(N) | 1 | 2:02 | 20 | 40.6667 | Due to S/D of 132/33 kV transformer T-1
Sylhet | 1 | 5:38 | 35 | 197.1667 | Due to S/D of Sylhet-Fenchuganj P/S 132 kV Ckt
Madaripur | 1 | 0:46 | 50 | 38.3333 | Due to 33 kV feeder fault
Narail | 1 | 1:08 | 28 | 31.7333
Bhandaria | 1 | 6:55 | 3 | 20.75 | Due to S/D of 132/33 kV transformer T-2
Khulna © | 1 | 7:18 | 5 | 36.5 | Due to S/D of 132/33 kV transformer T-3
Madaripur | 1 | 8:12 | 26 | 213.2 | Due to S/D of 132/33 kV transformer T-4
Bagerhat | 1 | 1:39 | 30 | 49.5 | Due to S/D of 132/33 kV transformers T-1 & T2
| 1 | 1:47 | 52 | 92.7333 | Due to S/D of 132/33 kV transformer T-3
Faridpur |  | 3:20 | 40 | 133.3333 | Due to S/D of 132/33 kV transformer T-1
Kustia | 1 | 1:26 | 8 | 11.4667 | Due to S/D of 132/33 kV transformer T-1
Bogura | 1 | 1:38 | 35 | 57.1667 | Due to red-hot maint.of 132/ 33 kV Transformer T1
Rangpur | 1 | 1:06 | 45 | 49.5 | Due to red-hot maint.of 132/ 33 kV Transformer T2
Bogura (O) | 1 | 0:49 | 26 | 21.2333 | Due to red-hot maint.of 132/ 33 kV Transformer T3
Niyamatpur | 1 | 0:03 | 25 | 1.25 | Due to red-hot maint.of 132/ 33 kV Transformer T2
Narail | 1 | 1:48 | 15 | 27 | Due to red-hot maint.of 132/ 33 kV Transformer T1
Joldhaka | 1 | 1:05 | 20 | 21.6667 | Due to red-hot maint.of 132/ 33 kV Transformer T2
Saidpur | 1 | 0:49 | 173 | 72.0833 | Due to tripping of Saidpur-Rangpur 132 kV Ckt-1 & 2
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Thaurgaon | 1 | 3:05 | 30 | 92.5 | Due to red-hot maint.Thaurgaon-Panchagarh 132 kV Ckt
Rajshahi(O) | 1 | 5:06 | 60 | 306 | Due to S/D of 132 kV main Bus
C.nawabganj | 1 | 5:46 | 35 | 201.8333 | Due to S/D of 132/33 kV transformer T-1
Natore | 1 | 1:26 | 61 | 87.4333 | Due to S/D of 132/33 kV transformers T-1 & T2
Pabna | 1 | 1:55 | 4 | 7.6667 | Due to S/D of 132/33 kV transformer T-1
Naogaon | 1 | 1:30 | 40 | 60 | Due to S/D of 132/33 kV transformer T-3
Bogura(O) | 1 | 2:41 | 40 | 107.3333 | Due to S/D of 132/33 kV transformer T-1
Rangpur | 1 | 2:05 | 15 | 31.25
Bogura | 1 | 2:44 | 26 | 71.0667 | Due to S/D of 132/33 kV transformer T-3
Mithapukur | 1 | 1:12 | 1111 | 1333.2 | Due to S/D of 132/33 kV transformer T-1
| Total Unserved energy : |  |  | 5972.6833 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: March '2022
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Aftabnagar | 30 | 24 | 2022-03-01 | 13:00
2 | Agargaon | 90 | 28 | 2022-03-01 | 13:00
3 | Agrabad | 82 | 27 | 2022-03-01 | 18:30
4 | AKS | 15 | 26 | 2022-03-01 | 11:00
5 | AKSML | 179 | 25 | 2022-03-01 | 08:00
6 | Amnura | 72 | 27 | 2022-03-01 | 20:00
7 | Ashuganj | 43 | 30 | 2022-03-01 | 12:00
8 | Bagerhat | 107 | 30 | 2022-03-01 | 20:00
9 | Bakulia | 124 | 30 | 2022-03-01 | 19:00
10 | Banani | 61 | 27 | 2022-03-01 | 12:00
11 | Bangabhaban | 24 | 24 | 2022-03-01 | 11:00
12 | Barapukuria | 64 | 27 | 2022-03-01 | 21:00
13 | Sreenagar | 18 | 29 | 2022-03-01 | 23:00
14 | Char Saidpur | 0 | 0 | 2022-03-01 | 0:00
15 | Barishal | 66 | 30 | 2022-03-01 | 03:00
16 | Baroaulia | 79 | 29 | 2022-03-01 | 11:00
17 | Baroirhat | 56 | 26 | 2022-03-01 | 20:00
18 | Bashundhara | 175 | 24 | 2022-03-01 | 18:30
19 | BashundharaCement | 13 | 24 | 2022-03-01 | 01:00
20 | Motijheel | 61 | 27 | 2022-03-01 | 18:30
21 | Benapole | 68 | 27 | 2022-03-01 | 21:00
22 | Kazla | 124 | 28 | 2022-03-01 | 09:00
23 | Bhandaria | 54 | 30 | 2022-03-01 | 19:30
24 | Bhangura | 42 | 28 | 2022-03-01 | 19:00
25 | Bheramara(GK) | 62 | 31 | 2022-03-01 | 20:00
26 | Bhulta | 234 | 31 | 2022-03-01 | 23:00
27 | Bog-Sherpur | 66 | 27 | 2022-03-01 | 21:00
28 | Bogura | 184 | 27 | 2022-03-01 | 21:00
29 | Borhanuddin | 45 | 29 | 2022-03-01 | 21:00
30 | Keraniganj | 164 | 26 | 2022-03-01 | 20:00
31 | Banani | 164 | 30 | 2022-03-01 | 23:00
32 | Cantonment | 138 | 29 | 2022-03-01 | 15:00
33 | Chandpur | 78 | 30 | 2022-03-01 | 21:00
34 | Chandraghona | 32 | 24 | 2022-03-01 | 19:00
35 | Chapai | 82 | 31 | 2022-03-01 | 20:00
36 | Charsaidpur | 49 | 31 | 2022-03-01 | 19:30
37 | Chauddagram | 47 | 30 | 2022-03-01 | 22:00
38 | Chhatak | 27 | 27 | 2022-03-01 | 19:00
39 | Chowmuhani | 210 | 28 | 2022-03-01 | 19:30
40 | Chuadanga | 105 | 31 | 2022-03-01 | 21:00
41 | Coxsbazar | 121 | 26 | 2022-03-01 | 18:30
42 | Cumilla(N) | 163 | 26 | 2022-03-01 | 21:00
43 | Cumilla(S) | 180 | 29 | 2022-03-01 | 18:30
44 | Daudkandi | 142 | 31 | 2022-03-01 | 19:30
45 | Dhaka | 38 | 27 | 2022-03-01 | 13:00
46 | Dhamrai | 130 | 31 | 2022-03-01 | 19:00
47 | Dhanmondi | 210 | 28 | 2022-03-01 | 13:00
48 | Dohazari | 100 | 31 | 2022-03-01 | 20:00
49 | Dummy2 | 0 | #N/A | 2022-03-01 | #N/A
50 | Faridpur | 143 | 30 | 2022-03-01 | 21:00
51 | Fatullah | 73 | 31 | 2022-03-01 | 16:00
52 | Fenchuganj | 41 | 25 | 2022-03-01 | 18:30
53 | Feni | 127 | 27 | 2022-03-01 | 19:00
54 | Ghorashal | 81 | 31 | 2022-03-01 | 19:00
55 | Goalpara | 31 | 27 | 2022-03-01 | 13:00
54 | Hasnabad | 95 | 29 | 2022-03-01 | 18:30
56 | Hathazari | 101 | 30 | 2022-03-01 | 19:00
57 | Ishurdi | 73 | 31 | 2022-03-01 | 19:30
58 | Jaldhaka | 65 | 26 | 2022-03-01 | 19:00
59 | Jamalpur | 170 | 31 | 2022-03-01 | 19:30
60 | Jashore | 132 | 28 | 2022-03-01 | 19:00
61 | Jhenaidah | 124 | 28 | 2022-03-01 | 19:00
62 | Joydebpur | 229 | 30 | 2022-03-01 | 11:00
63 | Joypurhat | 68 | 25 | 2022-03-01 | 19:00
64 | Juldah | 31 | 30 | 2022-03-01 | 10:00
65 | Kabirpur | 288 | 28 | 2022-03-01 | 18:00
66 | Kachua | 66 | 29 | 2022-03-01 | 19:00
67 | Kallyanpur | 99 | 31 | 2022-03-01 | 19:30
68 | Kalurghat | 0 | #N/A | 2022-03-01 | #N/A
69 | Kamrangirchar | 75 | 28 | 2022-03-01 | 18:30
70 | Kaptai | 16 | 25 | 2022-03-01 | 16:00
71 | Kazla | 90 | 29 | 2022-03-01 | 18:30
72 | Keranigonj | 74 | 24 | 2022-03-01 | 13:00
73 | Khagrachori | 26 | 24 | 2022-03-01 | 19:00
74 | Khulna | 93 | 28 | 2022-03-01 | 19:00
75 | Khulshi | 183 | 28 | 2022-03-01 | 16:00
76 | Kishoreganj | 144 | 27 | 2022-03-01 | 19:00
77 | Kodda | 320 | 24 | 2022-03-01 | 16:00
78 | KSRM | 36 | 27 | 2022-03-01 | 18:00
79 | Kulaura | 40 | 27 | 2022-03-01 | 19:00
80 | Kurigram | 76 | 24 | 2022-03-01 | 18:30
81 | Kushtia | 138 | 30 | 2022-03-01 | 19:30
82 | Lalbag | 96 | 31 | 2022-03-01 | 13:00
83 | Lalmonirhat | 51 | 27 | 2022-03-01 | 19:00
84 | Madanganj | 179 | 25 | 2022-03-01 | 19:30
85 | Madaripur | 108 | 30 | 2022-03-01 | 22:00
86 | Madartek | 80 | 24 | 2022-03-01 | 00:00
87 | Madunaghat | 61 | 30 | 2022-03-01 | 18:30
88 | Magura | 62 | 29 | 2022-03-01 | 19:30
89 | Mahasthangarh | 80 | 30 | 2022-03-01 | 19:00
90 | Manikganj | 111 | 28 | 2022-03-01 | 13:00
91 | Maniknagar | 76 | 31 | 2022-03-01 | 13:00
92 | Matarbari | 128 | 31 | 2022-03-01 | 13:00
93 | Matuail | 64 | 24 | 2022-03-01 | 12:00
94 | Millgate | 168.9 | 22 | 2022-03-01 | 13:00
95 | Mirpur | 128 | 31 | 2022-03-01 | 19:00
96 | Mirsorai | 1 | 27 | 2022-03-01 | 19:00
97 | Agrabad | 42 | 24 | 2022-03-01 | 08:00
98 | 0 | 0 | 24 | 2022-03-01 | 00:00
99 | Mogbazar | 122 | 27 | 2022-03-01 | 12:00
100 | Mongla | 168.9 | 22 | 2022-03-01 | 14:00
101 | Motijheel | 31 | 29 | 2022-03-01 | 13:00
102 | Munshiganj | 102 | 26 | 2022-03-01 | 22:00
103 | Mymensingh | 248 | 27 | 2022-03-01 | 21:00
104 | Naogaon | 128 | 24 | 2022-03-01 | 20:00
105 | Narail | 55 | 28 | 2022-03-01 | 19:00
106 | Narinda | 74 | 31 | 2022-03-01 | 17:00
107 | Narshingdi | 181 | 26 | 2022-03-01 | 19:00
108 | Rajbari | 157 | 27 | 2022-03-01 | 20:00
109 | Nawabganj | 54.6 | 31 | 2022-03-01 | 22:00
110 | Netrakona | 133 | 24 | 2022-03-01 | 08:00
111 | New | 86 | 27 | 2022-03-01 | 12:00
112 | Niamatpur | 111 | 28 | 2022-03-01 | 22:00
113 | Noapara | 69 | 25 | 2022-03-01 | 19:00
114 | Pabna | 110 | 30 | 2022-03-01 | 19:30
115 | Palashbari | 132 | 25 | 2022-03-01 | 19:30
116 | Panchagarh | 61 | 29 | 2022-03-01 | 19:00
117 | Patuakhali | 117 | 28 | 2022-03-01 | 22:00
118 | PHP | 11 | 24 | 2022-03-01 | 20:00
119 | Purbachal | 19 | 31 | 2022-03-01 | 21:00
120 | Purbasadipur | 118 | 27 | 2022-03-01 | 19:00
121 | Rahim | 29 | 27 | 2022-03-01 | 16:00
122 | Rajbari | 68 | 30 | 2022-03-01 | 20:00
123 | Rajendrapur | 110 | 29 | 2022-03-01 | 19:00
124 | Rajshahi | 167 | 26 | 2022-03-01 | 22:00
125 | Rajshahi | 45 | 29 | 2022-03-01 | 22:00
126 | Ramganj | 92 | 28 | 2022-03-01 | 18:30
127 | Rampur | 16 | 29 | 2022-03-01 | 18:00
128 | Rangamati | 13 | 29 | 2022-03-01 | 19:00
129 | Rangpur | 151 | 28 | 2022-03-01 | 19:00
130 | Ruppur | 5 | 29 | 2022-03-01 | 10:00
131 | Saidpur | 113 | 28 | 2022-03-01 | 19:00
132 | Satkhira | 120 | 30 | 2022-03-01 | 21:00
133 | Satmasjid | 94 | 31 | 2022-03-01 | 18:30
134 | Savar | 191 | 27 | 2022-03-01 | 18:30
135 | Shahjadpur | 119 | 30 | 2022-03-01 | 19:00
136 | Shahjibazar | 113 | 24 | 2022-03-01 | 01:00
137 | Shahmirpur | 42 | 28 | 2022-03-01 | 19:30
138 | Shariatpur | 68 | 30 | 2022-03-01 | 20:00
139 | Sherpur | 150 | 26 | 2022-03-01 | 08:00
140 | Shikalbaha | 38 | 30 | 2022-03-01 | 12:00
141 | Shitalakhya | 128 | 31 | 2022-03-01 | 18:30
142 | Sholosohor | 0 | #N/A | 2022-03-01 | #N/A
143 | Shyampur | 200 | 24 | 2022-03-01 | 09:00
144 | Siddhirganj | 134 | 27 | 2022-03-01 | 15:00
145 | Sirajganj | 126 | 29 | 2022-03-01 | 20:00
146 | Sonargaon | 102 | 25 | 2022-03-01 | 00:00
147 | Sreemongol | 54 | 27 | 2022-03-01 | 19:30
148 | Srinagar | 43.93 | 31 | 2022-03-01 | 22:00
149 | SSM | 4 | 27 | 2022-03-01 | 18:00
150 | Sunamganj | 46 | 27 | 2022-03-01 | 20:00
151 | Sylhet | 142 | 24 | 2022-03-01 | 19:00
152 | Mitha Pukur | 246 | 26 | 2022-03-01 | 21:00
153 | Thakurgaon | 94 | 27 | 2022-03-01 | 19:00
154 | TK | 27.8 | 24 | 2022-03-01 | 22:00
155 | Tongi | 139 | 31 | 2022-03-01 | 15:00
156 | Ullon | 143 | 24 | 2022-03-01 | 18:00
157 | Uttara | 70 | 24 | 2022-03-01 | 18:30
158 | UttaraNew | 34 | 27 | 2022-03-01 | 12:00
159 | Zigatola | 42 | 24 | 2022-03-01 | 19:00

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March 2022
Area | MW | Date | Hour | Remarks
Dhaka | 5024.63 | 31.03.2022 | 19:30
Chattogram | 1439.5 | 30.03.2022 | 23:00
Khulna | 1209 | 31.03.2022 | 21:00
Rajshahi | 1097 | 26.03.2022 | 23:00
Cumilla | 496 | 23.03.2022 | 18:30
Mymensingh | 1658.8 | 30.03.2022 | 20:00
Sylhet | 384 | 29.03.2022 | 22:00
Barisal | 1529.6 | 27.03.2022 | 20:00
Rangpur | 915 | 27.03.2022 | 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Maximum & Minimum Voltages of Grid Sub-Stations. | [12 empty] | Reporting Month
Month: March '2022 | Month: March 2022
2022-03-01
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 416 | 4 | 2022-03-01 | 6:00 | 397 | 24 | 2022-03-01 | 17:00
2 | Bheramara | 400 | 404 | 5 | 2022-03-01 | 6:00 | 386 | 30 | 2022-03-01 | 16:00
3 | Ashuganj(N) | 400 | 490 | 28 | 2022-03-01 | 7:00 | 379 | 31 | 2022-03-01 | 15:00
4 | Payra | 400 | 423 | 30 | 2022-03-01 | 1:00 | 397 | 16 | 2022-03-01 | 1:00
5 | Kaliakoir | 400 | 406 | 10 | 2022-03-01 | 1:00 | 361 | 20 | 2022-03-01 | 16:00
6 | Bhulta | 400 | 421 | 13 | 2022-03-01 | 6:00 | 379 | 30 | 2022-03-01 | 12:00
7 | Gopalganj | 400 | 420 | 23 | 2022-03-01 | 15:00 | 388 | 24 | 2022-03-01 | 21:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2022-03-01 | 20:00 | 227 | 2 | 2022-03-01 | 10:00
2 | Ishurdi | 230 | 246 | 8 | 2022-03-01 | 3:00 | 224 | 28 | 2022-03-01 | 7:00
3 | Ashuganj | 230 | 252 | 8 | 2022-03-01 | 6:00 | 231 | 5 | 2022-03-01 | 11:00
4 | Serajganj | 230 | 242 | 8 | 2022-03-01 | 7:00 | 224 | 10 | 2022-03-01 | 7:00
5 | Baghabari | 230 | 241 | 7 | 2022-03-01 | 1:00 | 221 | 24 | 2022-03-01 | 10:00
6 | Barapukuria | 230 | 237 | 1 | 2022-03-01 | 22:00 | 216 | 27 | 2022-03-01 | 7:00
7 | Bogura | 230 | 238 | 2 | 2022-03-01 | 23:00 | 214 | 10 | 2022-03-01 | 7:00
8 | Rajshahi | 230 | 242 | 9 | 2022-03-01 | 20:00 | 212 | 27 | 2022-03-01 | 7:00
9 | Khulna South | 230 | 246 | 2 | 2022-03-01 | 3:00 | 221 | 8 | 2022-03-01 | 13:00
10 | Rampura | 230 | 238 | 8 | 2022-03-01 | 4:00 | 215 | 24 | 2022-03-01 | 12:00
11 | Haripur | 230 | 238 | 13 | 2022-03-01 | 3:00 | 215 | 22 | 2022-03-01 | 11:00
12 | Hasnabad | 230 | 237 | 9 | 2022-03-01 | 19:30 | 212 | 22 | 2022-03-01 | 11:00
13 | Shyampur | 230 | 239 | 8 | 2022-03-01 | 21:00 | 212 | 30 | 2022-03-01 | 13:00
14 | Aminbazar | 230 | 239 | 9 | 2022-03-01 | 1:00 | 210 | 24 | 2022-03-01 | 2:00
15 | Tongi | 230 | 239 | 5 | 2022-03-01 | 4:00 | 210 | 24 | 2022-03-01 | 15:00
16 | Comilla (N) | 230 | 241 | 8 | 2022-03-01 | 6:00 | 220 | 29 | 2022-03-01 | 18:30
17 | Hathazari | 230 | 244 | 11 | 2022-03-01 | 24:00 | 226 | 5 | 2022-03-01 | 11:00
18 | Megnaghat | 230 | 244 | 1 | 2022-03-01 | 22:00 | 220 | 22 | 2022-03-01 | 10:00
19 | Fenchuganj | 230 | 246 | 9 | 2022-03-01 | 21:00 | 230 | 23 | 2022-03-01 | 18:00
20 | Siddhirganj | 230 | 241 | 8 | 2022-03-01 | 6:00 | 213 | 1 | 2022-03-01 | 8:00 | [7 empty] | 7345
21 | Maniknagar | 230 | 240 | 8 | 2022-03-01 | 6:00 | 213 | 24 | 2022-03-01 | 15:00
22 | Old Airport | 230 | 239 | 8 | 2022-03-01 | 4:00 | 211 | 30 | 2022-03-01 | 13:00
23 | Barisal | 230 | 247 | 19 | 2022-03-01 | 2:00 | 230 | 29 | 2022-03-01 | 24:00
24 | Bhola 225 MW | 230 | 249 | 18 | 2022-03-01 | 8:00 | 236 | 17 | 2022-03-01 | 19:00
25 | AKSML | 230 | 245 | 12 | 2022-03-01 | 13:00 | 225 | 5 | 2022-03-01 | 11:00
26 | BSRM | 230 | 243 | 1 | 2022-03-01 | 22:00 | 225 | 24 | 2022-03-01 | 15:00
27 | Bibiyana | 230 | 247 | 2 | 2022-03-01 | 3:00 | 229 | 24 | 2022-03-01 | 17:00
28 | Bhulta | 230 | 241 | 8 | 2022-03-01 | 6:00 | 215 | 30 | 2022-03-01 | 12:00
29 | Ashuganj (S) | 230 | 327 | 4 | 2022-03-01 | 19:30 | 228 | 30 | 2022-03-01 | 13:00
30 | Kaliakoir | 230 | 237 | 10 | 2022-03-01 | 3:00 | 214 | 22 | 2022-03-01 | 10:00
31 | GPH | 230 | 244 | 1 | 2022-03-01 | 22:00 | 223 | 5 | 2022-03-01 | 11:00
132 kV Substation
1 | Aftabnagar | 132 | 140 | 25 | 2022-03-01 | 01:00 | 126 | 24 | 2022-03-01 | 12:00 | [5 empty] | 1 | Siddhirganj
2 | Agargaon | 132 | 140 | 27 | 2022-03-01 | 22:00 | 123 | 24 | 2022-03-01 | 15:00 | [5 empty] | 2 | Munsiganj
3 | Agrabad | 132 | 139 | 24 | 2022-03-01 | 07:00 | 123 | 26 | 2022-03-01 | 02:00 | [5 empty] | 3 | Sonargaon
4 | AKS | 132 | 139 | 24 | 2022-03-01 | 08:00 | 129 | 28 | 2022-03-01 | 15:00 | [5 empty] | 4 | Shyampur
5 | Aminbazar | 132 | 138 | 27 | 2022-03-01 | 21:00 | 125 | 31 | 2022-03-01 | 15:00 | [5 empty] | 5 | Bhulta
6 | Amnura | 132 | 135 | 29 | 2022-03-01 | 17:00 | 117 | 26 | 2022-03-01 | 12:00 | [5 empty] | 6 | Madanganj
7 | Ashuganj | 132 | 140 | 24 | 2022-03-01 | 08:00 | 133 | 24 | 2022-03-01 | 00:00 | [5 empty] | 7 | Shitalakhya
8 | Bagerhat | 132 | 136 | 24 | 2022-03-01 | 08:00 | 128 | 24 | 2022-03-01 | 19:30 | [5 empty] | 8 | Rahim Steal
9 | Bakulia | 132 | 139 | 24 | 2022-03-01 | 07:00 | 128 | 30 | 2022-03-01 | 13:00 | [5 empty] | 9 | Matuail
10 | Banani | 132 | 141 | 25 | 2022-03-01 | 02:00 | 127 | 27 | 2022-03-01 | 09:00 | [5 empty] | 10 | Ghorasal
11 | Bangabhaban | 132 | 162 | 29 | 2022-03-01 | 06:00 | 122 | 31 | 2022-03-01 | 18:30 | [5 empty] | 11 | Narsinghdi
12 | Barapukuria | 132 | 134 | 31 | 2022-03-01 | 16:00 | 122 | 27 | 2022-03-01 | 07:00 | [5 empty] | 12 | Haripur (SBU)
13 | Barguna | 132 | 138 | 24 | 2022-03-01 | 07:00 | 127 | 27 | 2022-03-01 | 01:00 | [5 empty] | 13 | Sreenagar
14 | Barishal | 132 | 0 | 0 | 2022-03-01 | 0 | 0 | 0 | 2022-03-01 | 0 | [5 empty] | 14 | Ullon
15 | Barishal | 132 | 143 | 24 | 2022-03-01 | 07:00 | 133 | 28 | 2022-03-01 | 19:00 | [5 empty] | 15 | Hasnabad
16 | Baroaulia | 132 | 140 | 24 | 2022-03-01 | 06:00 | 131 | 29 | 2022-03-01 | 12:00 | [5 empty] | 16 | Magbazar
17 | Baroirhat | 132 | 138 | 25 | 2022-03-01 | 06:00 | 129 | 27 | 2022-03-01 | 02:00 | [5 empty] | 17 | Maniknagar
18 | Bashundhara | 132 | 140 | 27 | 2022-03-01 | 21:00 | 122 | 24 | 2022-03-01 | 15:00
19 | BashundharaCement | 132 | 142 | 27 | 2022-03-01 | 21:00 | 125 | 24 | 2022-03-01 | 15:00 |  | 13 |  |  | Narinda
20 | Beanibazar | 132 | 138 | 25 | 2022-03-01 | 07:00 | 123 | 24 | 2022-03-01 | 00:00 |  | 14 |  |  | Dhanmondi
21 | Benapole | 132 | 138 | 25 | 2022-03-01 | 16:00 | 12 | 29 | 2022-03-01 | 12:00 |  | 15 |  |  | Lalbag
22 | Bhaluka | 132 | 129 | 29 | 2022-03-01 | 04:00 | 106 | 25 | 2022-03-01 | 21:00 |  | 16 |  |  | Madartek
23 | Bhandaria | 132 | 142 | 25 | 2022-03-01 | 09:00 | 127 | 31 | 2022-03-01 | 22:00 |  | 17 |  |  | Dhaka University
24 | Bhangura | 132 | 136 | 24 | 2022-03-01 | 01:00 | 129 | 28 | 2022-03-01 | 19:00 |  | 18 |  |  | Aftabnagar
25 | Bheramara | 132 | 137 | 24 | 2022-03-01 | 06:00 | 129 | 28 | 2022-03-01 | 07:00 |  | 19 |  |  | Fatullah
26 | Bheramara(GK) | 132 | 139 | 24 | 2022-03-01 | 06:00 | 130 | 28 | 2022-03-01 | 08:00 |  |  |  |  | Nawabganj
27 | Bhulta | 132 | 139 | 27 | 2022-03-01 | 22:00 | 121 | 24 | 2022-03-01 | 15:00 |  | 20 |  |  | Mirpur
28 | Bog-Sherpur | 132 | 135 | 24 | 2022-03-01 | 03:00 | 124 | 27 | 2022-03-01 | 07:00 |  | 21 |  |  | Kalyanpur
29 | Bogura | 132 | 136 | 24 | 2022-03-01 | 01:00 | 125 | 27 | 2022-03-01 | 07:00 |  | 22 |  |  | Gulshan
30 | Bogura | 132 | 136 | 24 | 2022-03-01 | 01:00 | 113 | 25 | 2022-03-01 | 05:00 |  | 23 |  |  | Uttara
31 | Brahmanbaria | 132 | 136 | 25 | 2022-03-01 | 08:00 | 13 | 31 | 2022-03-01 | 18:30 |  | 24 |  |  | Uttara(New)
32 | Cantonment | 132 | 139 | 27 | 2022-03-01 | 22:00 | 122 | 24 | 2022-03-01 | 15:00 |  | 25 |  |  | Kamrangirchar
33 | Chandpur | 132 | 141 | 24 | 2022-03-01 | 06:00 | 130 | 24 | 2022-03-01 | 13:00 |  | 26 |  |  | Savar
34 | Chandraghona | 132 | 141 | 24 | 2022-03-01 | 07:00 | 132 | 24 | 2022-03-01 | 18:30 |  | 27 |  |  | Bhasantec
35 | Chapai | 132 | 135 | 30 | 2022-03-01 | 18:00 | 119 | 27 | 2022-03-01 | 05:00 |  | 28 |  |  | Agargaon
36 | Charsaidpur | 132 | 142 | 29 | 2022-03-01 | 19:00 | 125 | 24 | 2022-03-01 | 15:00 |  | 29 |  |  | Satmosjid
37 | Chauddagram | 132 | 138 | 24 | 2022-03-01 | 06:00 | 129 | 27 | 2022-03-01 | 05:00 |  | 30 |  |  | Tongi
38 | Chhatak | 132 | 139 | 29 | 2022-03-01 | 03:00 | 122 | 24 | 2022-03-01 | 14:00 |  | 31 |  |  | Kabirpur
39 | Chowmuhani | 132 | 137 | 24 | 2022-03-01 | 06:00 | 125 | 31 | 2022-03-01 | 03:00 |  | 32 |  |  | Basundhara
40 | Chuadanga | 132 | 128 | 24 | 2022-03-01 | 09:00 | 112 | 27 | 2022-03-01 | 19:30 |  | 33 |  |  | Manikganj
41 | Coxsbazar | 132 | 127 | 24 | 2022-03-01 | 08:00 | 110 | 24 | 2022-03-01 | 18:30 |  | 34 |  |  | Joydevpur
42 | Cumilla(N) | 132 | 139 | 25 | 2022-03-01 | 08:00 | 130 | 24 | 2022-03-01 | 10:00 |  | 35 |  |  | New Tongi
43 | Cumilla(S) | 132 | 138 | 24 | 2022-03-01 | 07:00 | 118 | 31 | 2022-03-01 | 12:00 |  | 36 |  |  | Kodda
44 | Daudkandi | 132 | 138 | 28 | 2022-03-01 | 18:30 | 126 | 24 | 2022-03-01 | 23:00 |  | 37 |  |  | Dhamrai
45 | Dhaka | 132 | 140 | 25 | 2022-03-01 | 01:00 | 125 | 29 | 2022-03-01 | 10:00 |  | 38 |  |  | Rajendrapur
46 | Dhamrai | 132 | 142 | 27 | 2022-03-01 | 21:00 | 125 | 24 | 2022-03-01 | 15:00 |  | 39 |  |  | Valuka
47 | Dhanmondi | 132 | 139 | 25 | 2022-03-01 | 08:00 | 95 | 24 | 2022-03-01 | 06:00 |  | 40 |  |  | Tangail
48 | Dohazari | 132 | 134 | 24 | 2022-03-01 | 08:00 | 123 | 30 | 2022-03-01 | 13:00 |  | 41 |  |  | Mymensing
49 | Faridpur | 132 | 138 | 25 | 2022-03-01 | 18:00 | 13 | 27 | 2022-03-01 | 09:00 |  | 42 |  |  | Kishorganj
50 | Dummy2 | 132 | 0 | #N/A | 2022-03-01 | #N/A | 0 | #N/A | 2022-03-01 | #N/A |  | 43 |  |  | Netrokona
51 | Fatullah | 132 | 138 | 27 | 2022-03-01 | 22:00 | 125 | 24 | 2022-03-01 | 17:00 |  | 44 |  |  | Jamalpur
52 | Fenchuganj | 132 | 142 | 30 | 2022-03-01 | 09:00 | 130 | 24 | 2022-03-01 | 00:00 |  | 45 |  |  | Sherpur
53 | Feni | 132 | 140 | 24 | 2022-03-01 | 18:30 | 123 | 27 | 2022-03-01 | 03:00 |  | 46 |  |  | Srimongal
54 | Ghorashal | 132 | 140 | 25 | 2022-03-01 | 09:00 | 129 | 31 | 2022-03-01 | 14:00 |  | 47 |  |  | Shahjibazar
55 | Goalpara | 132 | 139 | 27 | 2022-03-01 | 18:00 | 132 | 27 | 2022-03-01 | 07:00 |  | 48 |  |  | Fenchuganj
56 | Gollamari | 132 | 138 | 24 | 2022-03-01 | 08:00 | 34 | 26 | 2022-03-01 | 08:00 |  | 49 |  |  | Khulawara
57 | Gopalganj | 132 | 141 | 24 | 2022-03-01 | 08:00 | 125 | 28 | 2022-03-01 | 19:30 |  | 50 |  |  | Sylhet
58 | Gopalganj_I | 132 | 145 | 24 | 2022-03-01 | 08:00 | 130 | 26 | 2022-03-01 | 23:00 |  | 51 |  |  | Chattak
59 | Gulshan | 132 | 139 | 25 | 2022-03-01 | 04:00 | 125 | 29 | 2022-03-01 | 10:00 |  | 52 |  |  | Sunamganj
60 | Halishahar | 132 | 139 | 24 | 2022-03-01 | 06:00 | 117 | 25 | 2022-03-01 | 06:00 |  | 53 |  |  | Biani Bazar
61 | Haripur | 132 | 142 | 27 | 2022-03-01 | 22:00 | 125 | 24 | 2022-03-01 | 17:00 |  | 54 |  |  | Comilla(South)
62 | HaripurSBU | 132 | 140 | 27 | 2022-03-01 | 22:00 | 126 | 24 | 2022-03-01 | 13:00 |  | ok |  |  | Comilla (North)
63 | Hasnabad | 132 | 140 | 27 | 2022-03-01 | 22:00 | 127 | 24 | 2022-03-01 | 15:00 |  | 56 |  |  | Chandpur
64 | Hathazari | 132 | 140 | 24 | 2022-03-01 | 03:00 | 132 | 25 | 2022-03-01 | 06:00 |  | 57 |  |  | Feni
65 | Ishurdi | 132 | 138 | 24 | 2022-03-01 | 06:00 | 130 | 28 | 2022-03-01 | 07:00 |  | 58 |  |  | Chowmuhani
66 | Jaldhaka | 132 | 132 | 31 | 2022-03-01 | 16:00 | 113 | 26 | 2022-03-01 | 07:00 |  | 59 |  |  | Ashuganj
67 | Jamalpur | 132 | 134 | 28 | 2022-03-01 | 11:00 | 115 | 31 | 2022-03-01 | 10:00 |  | 60 |  |  | Daudkandi
68 | Jashore | 132 | 137 | 24 | 2022-03-01 | 0.16667 | 131 | 29 | 2022-03-01 | 0.66667 |  | 61 |  |  | Brahminbaria
69 | Jhenaidah | 132 | 134 | 24 | 2022-03-01 | 05:00 | 123 | 29 | 2022-03-01 | 19:00 |  | 62 |  |  | Ramganj
70 | Jhenaidah | 132 | 134 | 24 | 2022-03-01 | 06:00 | 124 | 29 | 2022-03-01 | 19:00 |  | 63 |  |  | Chaddagram
71 | Joydebpur | 132 | 142 | 24 | 2022-03-01 | 05:00 | 132 | 24 | 2022-03-01 | 17:00 |  | 64 |  |  | PHP
72 | Joypurhat | 132 | 129 | 24 | 2022-03-01 | 01:00 | 111 | 26 | 2022-03-01 | 12:00
73 | Juldah | 132 | 141 | 24 | 2022-03-01 | 04:00 | 130 | 30 | 2022-03-01 | 12:00 |  | 65 |  |  | Kochua
74 | Kabirpur | 132 | 142 | 27 | 2022-03-01 | 21:00 | 122 | 28 | 2022-03-01 | 07:00 |  | 66 |  |  | Madanhat
75 | Kachua | 132 | 139 | 31 | 2022-03-01 | 11:00 | 128 | 31 | 2022-03-01 | 03:00 |  | 67 |  |  | Hathazari
76 | Kaliakoir | 132 | 141 | 26 | 2022-03-01 | 19:00 | 36 | 29 | 2022-03-01 | 18:30 |  | 68 |  |  | Khulshi
77 | Kallyanpur | 132 | 137 | 27 | 2022-03-01 | 22:00 | 124 | 30 | 2022-03-01 | 13:00 |  | 11 |  |  | Halishahar
78 | Kalurghat | 132 | 0 | #N/A | 2022-03-01 | #N/A | 0 | #N/A | 2022-03-01 | #N/A |  | 12 |  |  | Baraulia
79 | Kamrangirchar | 132 | 140 | 27 | 2022-03-01 | 22:00 | 127 | 30 | 2022-03-01 | 12:00 |  | 13
80 | Kaptai | 132 | 135 | 24 | 2022-03-01 | 00:00 | 131 | 29 | 2022-03-01 | 15:00
81 | Kazla | 132 | 135 | 28 | 2022-03-01 | 05:00 | 121 | 31 | 2022-03-01 | 19:00
82 | Keranigonj | 132 | 141 | 27 | 2022-03-01 | 22:00 | 127 | 30 | 2022-03-01 | 12:00
83 | Khagrachori | 132 | 138 | 24 | 2022-03-01 | 06:00 | 0.45 | 29 | 2022-03-01 | 00:00
84 | Khulna | 132 | 138 | 24 | 2022-03-01 | 06:00 | 131 | 27 | 2022-03-01 | 07:00
85 | Khulna(S) | 132 | 139 | 24 | 2022-03-01 | 06:00 | 131 | 27 | 2022-03-01 | 04:00
86 | Khulshi | 132 | 138 | 24 | 2022-03-01 | 07:00 | 129 | 28 | 2022-03-01 | 15:00
87 | Kishoreganj | 132 | 130 | 28 | 2022-03-01 | 11:00 | 118 | 24 | 2022-03-01 | 18:30
88 | Kodda | 132 | 143 | 24 | 2022-03-01 | 07:00 | 124 | 24 | 2022-03-01 | 12:00
89 | KSRM | 132 | 139 | 24 | 2022-03-01 | 06:00 | 132 | 24 | 2022-03-01 | 13:00
90 | Kulaura | 132 | 140 | 27 | 2022-03-01 | 07:00 | 129 | 24 | 2022-03-01 | 18:30
91 | Kurigram | 132 | 134 | 30 | 2022-03-01 | 15:00 | 110 | 26 | 2022-03-01 | 19:00
92 | Kushtia | 132 | 135 | 24 | 2022-03-01 | 06:00 | 127 | 27 | 2022-03-01 | 20:00
93 | Lalbag | 132 | 140 | 27 | 2022-03-01 | 22:00 | 127 | 24 | 2022-03-01 | 17:00
94 | Lalmonirhat | 132 | 130 | 29 | 2022-03-01 | 10:00 | 116 | 25 | 2022-03-01 | 07:00
95 | Madanganj | 132 | 142 | 27 | 2022-03-01 | 21:00 | 125 | 24 | 2022-03-01 | 15:00
96 | Madaripur | 132 | 145 | 24 | 2022-03-01 | 13:00 | 130 | 27 | 2022-03-01 | 00:00
97 | Madartek | 132 | 140 | 25 | 2022-03-01 | 02:00 | 125 | 29 | 2022-03-01 | 11:00
98 | Madunaghat | 132 | 140 | 24 | 2022-03-01 | 07:00 | 131 | 30 | 2022-03-01 | 11:00
99 | Magura | 132 | 135 | 24 | 2022-03-01 | 06:00 | 120 | 29 | 2022-03-01 | 19:30
100 | Mahasthangarh | 132 | 134 | 31 | 2022-03-01 | 16:00 | 122 | 27 | 2022-03-01 | 07:00
101 | Manikganj | 132 | 140 | 27 | 2022-03-01 | 21:00 | 120 | 24 | 2022-03-01 | 15:00
102 | Maniknagar | 132 | 137 | 27 | 2022-03-01 | 22:00 | 121 | 31 | 2022-03-01 | 18:00
103 | Matarbari | 132 | 137 | 29 | 2022-03-01 | 04:00 | 112 | 24 | 2022-03-01 | 18:30
104 | Matuail | 132 | 141.6 | 27 | 2022-03-01 | 22:00 | 124 | 24 | 2022-03-01 | 15:00
105 | Millgate | 132 | 141 | 27 | 2022-03-01 | 21:00 | 124 | 24 | 2022-03-01 | 15:00
106 | Mirpur | 132 | 137 | 27 | 2022-03-01 | 21:00 | 124 | 24 | 2022-03-01 | 13:00
107 | Mithapukur | 132 | 134 | 30 | 2022-03-01 | 15:00 | 18 | 26 | 2022-03-01 | 18:00
108 | Modern | 132 | 138 | 24 | 2022-03-01 | 06:00 | 130 | 30 | 2022-03-01 | 12:00
109 | Mogbazar | 132 | 140 | 24 | 2022-03-01 | 08:00 | 125 | 29 | 2022-03-01 | 12:00
110 | Mongla | 132 | 137 | 24 | 2022-03-01 | 08:00 | 127 | 31 | 2022-03-01 | 01:00
111 | Motijheel | 132 | 137 | 27 | 2022-03-01 | 22:00 | 122 | 31 | 2022-03-01 | 18:30
112 | Munshiganj | 132 | 143 | 27 | 2022-03-01 | 22:00 | 126 | 24 | 2022-03-01 | 15:00
113 | Mymensingh | 132 | 129 | 29 | 2022-03-01 | 06:00 | 113 | 24 | 2022-03-01 | 06:00
114 | Naogaon | 132 | 130 | 24 | 2022-03-01 | 01:00 | 1 | 26 | 2022-03-01 | 08:00
115 | Narail | 132 | 131 | 24 | 2022-03-01 | 06:00 | 119 | 28 | 2022-03-01 | 19:00
116 | Narinda | 132 | 0 | 24 | 2022-03-01 | 00:00 | 0 | 0 | 2022-03-01 | 00:00
117 | Narshingdi | 132 | 136 | 28 | 2022-03-01 | 16:00 | 117 | 24 | 2022-03-01 | 15:00
118 | Natore | 132 | 136 | 24 | 2022-03-01 | 18:00 | 126 | 27 | 2022-03-01 | 07:00
119 | Nawabganj | 132 | 140 | 27 | 2022-03-01 | 22:00 | 127 | 24 | 2022-03-01 | 10:00
120 | Netrakona | 132 | 127 | 30 | 2022-03-01 | 05:00 | 107 | 24 | 2022-03-01 | 06:00
121 | New | 132 | 140 | 27 | 2022-03-01 | 21:00 | 124 | 24 | 2022-03-01 | 15:00
122 | Niamatpur | 132 | 127 | 24 | 2022-03-01 | 03:00 | 106 | 26 | 2022-03-01 | 13:00
123 | Noapara | 132 | 137 | 24 | 2022-03-01 | 06:00 | 128 | 31 | 2022-03-01 | 01:00
124 | Pabna | 132 | 136 | 24 | 2022-03-01 | 06:00 | 128 | 26 | 2022-03-01 | 19:30
125 | Palashbari | 132 | 132 | 24 | 2022-03-01 | 01:00 | 116 | 27 | 2022-03-01 | 07:00
126 | Panchagarh | 132 | 137 | 31 | 2022-03-01 | 08:00 | 114 | 27 | 2022-03-01 | 07:00
127 | Patuakhali | 132 | 138 | 24 | 2022-03-01 | 07:00 | 128 | 26 | 2022-03-01 | 00:00
128 | PHP | 132 | 139 | 24 | 2022-03-01 | 07:00 | 128 | 27 | 2022-03-01 | 05:00
129 | Purbachal | 132 | 139 | 24 | 2022-03-01 | 05:00 | 125 | 31 | 2022-03-01 | 16:00
130 | Purbasadipur | 132 | 135 | 31 | 2022-03-01 | 13:00 | 114 | 26 | 2022-03-01 | 07:00
131 | Rahim | 132 | 142 | 27 | 2022-03-01 | 22:00 | 125 | 24 | 2022-03-01 | 16:00
132 | Rajbari | 132 | 138 | 28 | 2022-03-01 | 00:00 | 123 | 24 | 2022-03-01 | 12:00
133 | Rajendrapur | 132 | 137 | 25 | 2022-03-01 | 05:00 | 121 | 24 | 2022-03-01 | 13:00
134 | Rajshahi | 132 | 137 | 31 | 2022-03-01 | 18:00 | 123 | 26 | 2022-03-01 | 12:00
135 | Rajshahi | 132 | 138 | 30 | 2022-03-01 | 18:00 | 123 | 26 | 2022-03-01 | 12:00
136 | Ramganj | 132 | 139 | 24 | 2022-03-01 | 06:00 | 126 | 29 | 2022-03-01 | 05:00
137 | Rampur | 132 | 138 | 24 | 2022-03-01 | 08:00 | 130 | 30 | 2022-03-01 | 12:00
138 | Rampura | 132 | 140 | 25 | 2022-03-01 | 08:00 | 126 | 24 | 2022-03-01 | 12:00
139 | Rangamati | 132 | 140 | 24 | 2022-03-01 | 07:00 | 13 | 27 | 2022-03-01 | 19:30
140 | Rangpur | 132 | 133 | 30 | 2022-03-01 | 15:00 | 115 | 26 | 2022-03-01 | 19:00
141 | Ruppur | 132 | 137 | 24 | 2022-03-01 | 05:00 | 131 | 24 | 2022-03-01 | 20:00
142 | Saidpur | 132 | 133 | 29 | 2022-03-01 | 03:00 | 117 | 24 | 2022-03-01 | 07:00
143 | Satkhira | 132 | 138 | 30 | 2022-03-01 | 10:00 | 120 | 31 | 2022-03-01 | 00:00
144 | Satmasjid | 132 | 140 | 27 | 2022-03-01 | 22:00 | 123 | 24 | 2022-03-01 | 15:00
145 | Savar | 132 | 139 | 27 | 2022-03-01 | 21:00 | 123 | 29 | 2022-03-01 | 16:00
146 | Shahjadpur | 132 | 139 | 24 | 2022-03-01 | 01:00 | 131 | 26 | 2022-03-01 | 19:00
147 | Shahjibazar | 132 | 139 | 25 | 2022-03-01 | 08:00 | 130 | 24 | 2022-03-01 | 00:00
148 | Shahmirpur | 132 | 140 | 24 | 2022-03-01 | 06:00 | 130 | 30 | 2022-03-01 | 12:00
149 | Shariatpur | 132 | 143 | 24 | 2022-03-01 | 09:00 | 127 | 27 | 2022-03-01 | 22:00
150 | Sherpur | 132 | 133 | 28 | 2022-03-01 | 16:00 | 112 | 31 | 2022-03-01 | 13:00
151 | Shikalbaha | 132 | 141 | 24 | 2022-03-01 | 07:00 | 130 | 30 | 2022-03-01 | 12:00
152 | Shikalbaha | 132 | 139 | 24 | 2022-03-01 | 07:00 | 130 | 30 | 2022-03-01 | 13:00
153 | Shitalakhya | 132 | 142 | 27 | 2022-03-01 | 22:00 | 126.6 | 24 | 2022-03-01 | 15:00
154 | Sholosohor | 132 | 0 | #N/A | 2022-03-01 | #N/A | 0 | #N/A | 2022-03-01 | #N/A
155 | Shyampur | 132 | 137 | 28 | 2022-03-01 | 21:00 | 126 | 24 | 2022-03-01 | 09:00
156 | Shyampur | 132 | 137 | 27 | 2022-03-01 | 22:00 | 125 | 24 | 2022-03-01 | 17:00
157 | Siddhirganj | 132 | 159 | 31 | 2022-03-01 | 11:00 | 124 | 24 | 2022-03-01 | 15:00
158 | Sirajganj | 132 | 134 | 30 | 2022-03-01 | 18:30 | 124 | 27 | 2022-03-01 | 19:30
159 | Sonargaon | 132 | 141 | 27 | 2022-03-01 | 22:00 | 126 | 24 | 2022-03-01 | 10:00
160 | Sreemongol | 132 | 141 | 25 | 2022-03-01 | 08:00 | 132 | 24 | 2022-03-01 | 00:00
161 | Srinagar | 132 | 140 | 27 | 2022-03-01 | 22:00 | 122 | 30 | 2022-03-01 | 12:00
162 | SSM | 132 | 139 | 24 | 2022-03-01 | 06:00 | 130 | 27 | 2022-03-01 | 07:00
163 | Sunamganj | 132 | 136 | 25 | 2022-03-01 | 08:00 | 119 | 24 | 2022-03-01 | 01:00
164 | Sylhet | 132 | 137 | 27 | 2022-03-01 | 07:00 | 124 | 24 | 2022-03-01 | 18:30
165 | Tangail | 132 | 135 | 29 | 2022-03-01 | 02:00 | 120 | 31 | 2022-03-01 | 19:30
166 | Thakurgaon | 132 | 136 | 31 | 2022-03-01 | 08:00 | 111 | 27 | 2022-03-01 | 07:00
167 | TK | 132 | 140 | 24 | 2022-03-01 | 07:00 | 131 | 24 | 2022-03-01 | 18:30
168 | Tongi | 132 | 140 | 27 | 2022-03-01 | 22:00 | 35 | 31 | 2022-03-01 | 12:00
169 | Ullon | 132 | 139 | 24 | 2022-03-01 | 08:00 | 38 | 24 | 2022-03-01 | 06:00
170 | Uttara | 132 | 137 | 27 | 2022-03-01 | 22:00 | 122 | 24 | 2022-03-01 | 15:00
171 | UttaraNew | 132 | 137 | 30 | 2022-03-01 | 01:00 | 123 | 24 | 2022-03-01 | 15:00
172 | Zigatola | 132 | 141 | 27 | 2022-03-01 | 22:00 | 125 | 30 | 2022-03-01 | 13:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: March 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 50 | 140
Hasnabad | TR2 | 225 | 50 | 140 | 29.03.2022 | 10:00
| TR3 | 225 | 50 | 140
| TR1 | 225 | 190 | 550 | 22.03.2022 | 15:00
Tongi | TR2 | 225 | 190 | 550
| TR3 | 225 | 190 | 550
Haripur | TR1 | 225 | 115 | 330
| TR2 | 225 | 115 | 330 | 27.03.2022 | 9:00
| TR3 | 225 | 115 | 330
| TR1 | 225 | 196 | 560
Rampura | TR2 | 225 | 196 | 560 | 23.03.2022 | 15:00
| TR3 | 225 | 196 | 560
Keraniganj | ATR1 | 300 | 116 | 345
| ATR2 | 300 | 116 | 345 | 30.03.2022 | 17:00
| ATR3 | 300 | 116 | 345
| TR1 | 225 | 127 | 350
Aminbazar | TR2 | 225 | 127 | 350 | 31.03.2022 | 19:00
| TR3 | 225 | 133 | 367
Agargaon | TR1 | 300 | 158 | 442
| TR2 | 300 | 158 | 442 | 28.03.2022 | 13:00
Maniknagar | TR1 | 300 | 134 | 410 | 31.03.22 | 16:00
| TR2 | 300 | 134 | 410
Cumilla (N) | TR1 | 225 | 161 | 426 | 06.03.22 | 3:00
| TR2 | 225 | 160 | 427
Fenchuganj | AT2 | 300 | 283 | 742 | 31.03.22 | 19:30
| MT1 | 150 | 95 | 266
Hathazari | MT2 | 150 | 95 | 266 | 30.03.22 | 19:30
| MT3 | 150 | 95 | 266
| MT4 | 150 | 95 | 266
| TR1 | 225 | 89 | 232
Ishurdi | TR2 | 225 | 89 | 232 | 27.03.22 | 21:40
| TR3 | 225 | 89 | 232
Khulna(S) | TR1 | 225 | 73 | 186
| TR2 | 225 | 73 | 186 | 06/03/2022 | 19:00
| TR3 | 300 | 92 | 246
Bogura | TR1 | 225 | 127 | 367 | 24.03.22 | 19:30
| TR2 | 225 | 127 | 367
| TR3 | 225 | 172 | 478
Baghabari | TR1 | 300 | 165 | 460 | 270.03.22 | 22:00
| TR2 | 225 | 123 | 345
Rajshahi | ATR-01 | 300 | 130 | 390 | 27.03.2022 | 7:00
| ATR-02 | 300 | 130 | 390
Barapukuria | TR1 | 225 | 169 | 770 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 147 | 700 | 20.03.2022 | 19:00 | 132 kV current is being provided
| TR6 | 300 | 191 | 903
Bheramara | Transformer-1 | 225 | 66 | 192 | 23.03.2022 | 13:00
| Transformer-2 | 225 | 66 | 192
Shyampur | ATR-01 | 300 | 130 | 380 | 24.03.2022 | 9:00
| ATR-02 | 300 | 130 | 380
Kaliakoir | TR1 | 300 | 132 | 393 | 31.03.2022 | 19:00
Sikalbaha | ATR-1 | 300 | 181 | 496 | 20.03.2022 | 3:00
| ATR-2 | 300 | 181 | 496
Jhenaidah | T1(230/132 kV) | 300 | 144 | 406 | 30.03.2022 | 20:00
| T2(230/132 kV) | 300 | 144 | 406
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:March 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 215.3 | 337 | 24.03.2022 | 10:00
| TR2(400/230 kV) | 520 | 217.8 | 337
| TR1(400/132 kV) | 325 | 286.8 | 489 | 14.03.2022 | 19:30
| TR2(400/132 kV) | 325 | 286.7 | 491
Bibiyana | ICT1(400/230 kV) | 520 | 228 | 335 |  | 11:00
| ICT2(400/230kV) | 520 | 225 | 332 | 19.03.2022 | 15:00
Bhulta | ATR1(400/230 kV) | 520 | 228 | 410 | 30.03.2022 | 14:15
| ATR2(400/230kV) | 520 | 228 | 410
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 370 | 534 | 01.03.2022 | 8:41
Gopalganj | ATR1(400/138 kV) | 325 | 270 | 394 | 21.03.2022 | 19:30
| ATR2(400/138kV) | 325 | 270 | 394
Payra | GSUT1 | 270 | 207 | 922 | 23.03.2022 | 21:42
| GSUT2 | 270 | 207 | 913
| GSUT3 | 270 | 207 | 909
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:March 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-03-01 | 10490 | 10490 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-01 | 9499 | 9499 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-02 | 10667 | 10667 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-02 | 9491 | 9491 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-03 | 10844 | 10844 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-03 | 9486 | 9486 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-04 | 9443 | 9443 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-04 | 8104 | 8104 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-05 | 10895 | 10895 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-05 | 9171 | 9171 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-06 | 11024 | 11024 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-06 | 9857 | 9857 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-07 | 11424 | 11424 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-07 | 10123 | 10123 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-08 | 11802 | 11802 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-08 | 10327 | 10327 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-09 | 11895 | 11895 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-09 | 10381 | 10381 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-10 | 11722 | 11722 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-10 | 10466 | 10466 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-11 | 10372 | 10372 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-11 | 8958 | 8958 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-12 | 11669 | 11669 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-12 | 9715 | 9715 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-13 | 11621 | 11621 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-13 | 10708 | 10708 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-14 | 11899 | 11899 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-14 | 10873 | 10873 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-15 | 12170 | 12170 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-15 | 10955 | 10955 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-16 | 12631 | 12631 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-16 | 11132 | 11132 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-17 | 12597 | 12597 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-17 | 11164 | 11164 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-18 | 11521 | 11521 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-18 | 10217 | 10217 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-19 | 12075 | 12075 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-19 | 9622 | 9622 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-20 | 13038 | 13038 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-20 | 11430 | 11430 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-21 | 13024 | 13024 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-21 | 11435 | 11435 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-22 | 13096 | 13096 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-22 | 11773 | 11773 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-23 | 13412 | 13412 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-23 | 12003 | 12003 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-24 | 13284 | 13284 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-24 | 11630 | 11630 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-25 | 12418 | 12418 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-25 | 10407 | 10407 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-26 | 12593 | 12593 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-26 | 10189 | 10189 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-27 | 13108 | 13108 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-27 | 12116 | 12116 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-28 | 13347 | 13347 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-03-28 | 11642 | 11642 | - | - | - | - | - | - | - | - | - | - | - | -
2022-03-29 | 12769 | 12769 | - | - | [10 empty] | 2022-03-29 | 11507 | 11507
2022-03-30 | 13283 | 13283 | - | - | [10 empty] | 2022-03-30 | 11517 | 11517
2022-03-31 | 13662 | 13662 | [12 empty] | 2022-03-31 | 11586 | 11586
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13662 | 2022-03-31 | 19:30
2 | Maximum Day Peak Genaration | MW | 12116 | 2022-03-27 | 12:00
3 | Maximum Evening Peak Demand | MW | 13662 | 2022-03-31 | 12:00
4 | Minimum Generation | MW | 6823 | 2022-03-05 | 6:00
5 | Average of the daily evening peak Genaration | MW | 12057.9032
6 | Average of the daily day peak Genaration | MW | 10564
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 7753.8522
12 | Total Generation by BPDB | MkWh | 1551.2856 | % of total Gen. | 20.01%
13 | Total Generation by IPP | MkWh | 3023.4634 | '' | 38.99%
14 | A) Total Generation by Generation Companies | MkWh | 1892.6065 | '' | 24.41%
| B) Total Generation by REB | MkWh | 144.2163 | " | 1.86%
| C) Total Generation by RENTAL | MkWh | 498.1914 | " | 6.425%
| D) Total Imported from India (BIPTC) | MkWh | 559.5534 | " | 7.216%
| E) Total Imported from Tripura, India (A.C) | MkWh | 84.5357 | " | 1.09%
15 | Fuel wise Generation.
| A) Gas | MkWh | 3806.7453 | % of total Gen. | 49.09%
| B) Oil | MkWh | 2679.0368 | '' | 34.55%
| C) Hydro | MkWh | 43.3314 | '' | 0.5588%
| D) Solar | MkWh | 40.5844 | '' | 0.5234%
| E) Coal | MkWh | 540.0652 | '' | 6.965%
| F) BIPTC (Import from India) | MkWh | 559.5534 | '' | 7.216%
| G) A.C (Import from Tripura, India) | MkWh | 84.5357 | '' | 1.09%
16 | Maximun of the daily total Generation . | MkWh | 286.3817 | 2022-03-22
17 | Monthly Load factor | % | 84.4682
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 27966.2091
| A) Gas | M.Taka | 3890.8285
| B) Liquid fuel | M.Taka | 18445.564
| C) Coal | M.Taka | 2307.2617
| D) BIPTC (Import from India) | M.Taka | 2740.7956
| E) Tripura(Import from India) | M.Taka | 581.7592
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1179.8677 | 2022-03-15
| A) Gas | M.Taka | 150.1114 | 2022-03-20
| B) Liquid fuel | M.Taka | 943.5488 | 2022-03-15
| C) Coal | M.Taka | 106.42 | 2022-03-13
| D) BIPTC (Import from India) | M.Taka | 111.2801 | 2022-03-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.5665
| B) Excluding Hydro & Solar | Taka/kWhR | 5.6267
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.17 | 31/03/2022 | 06:00
b) | Actual | FT (MSL) | 85.08 | 31/03/2022 | 06:00
22 | Peak Genaration of March 2021 | MW | 12790 | 24-03-2021 | 21:00
23 | Peak Demand of March 2021 | MW | 12790 | 24-03-2021 | 21:00
24 | Maximum peak Generation recorded upto 31/03/2022 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 31/03/2022 | MW | 14097 | 27/04/21 | 12:00
26 | Maximum load shed recorded upto 31/03/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.