## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:April 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-04-01 |  | 2023-03-01 |  | 2022-04-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 15648 | 2023-04-19 | 12921 | 2023-03-13 | 14782 | 2022-04-16 | 15648 | 2023-04-19
|  |  | 21:00 |  | 19:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 5602 | 2023-04-01 | 6507 | 2023-03-20 | 4262 | 2022-04-20 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 15648 | 2023-04-19 | 12921 | 2023-03-13 | 14782 | 2022-04-16 | 15648 | 2023-04-19
|  |  | 21:00 |  | 19:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13415 | 2023-04-19 | 11515 | 2023-03-14 | 12895 | 2022-04-26 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 16221 | 2023-04-30 | 13046 | 2023-03-31 | 14782 | 2022-04-16 | 16096 | 2023-04-19
|  |  | 19:30 |  | 21:00 |  | 12:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 12833.0667 |  | 11615.6452 |  | 13536.3333
7 | Average Generation (MW) at Day Peak | 11504.2 |  | 10322.4194 |  | 11233.4
8 | Maximum Power Import from India, BIPTC (MW) | 936 | 2023-04-24 | 920 | 2023-03-02 | 935 | 2022-04-10 | 956 | 27/3/2019
|  |  | 11:30 |  | 23:00 |  | 21:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 165 | 2023-04-04 | 170 | 2023-03-13 | 172 | 2022-04-03 | 194 | 12/06/19
|  |  | 19:00 |  | 14:00 |  | 2:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1291 | 2023-04-16 | 236 | 2023-03-05 | 350 | 2022-04-07 | 4395 | 04/10/2022
|  |  | 21:00 |  | 19:00 |  | 22:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14599 | 2023-04-16 | 12052 | 2023-03-05 | 14008 | 2022-04-07 | 13200 | 04/10/2022
|  | - | 21:00 | - | 19:00 | - | 22:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-04-01 | 40 | 2023-03-03 | - | -
|  |  | 21:00 |  | 19:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 10593 | 2023-04-01 | 10693 | 2023-03-03 | - | -
|  |  | 21:00 |  | 19:00
14 | Maximum Load Shed (MW) at Day Peak | 1167 | 2023-04-15 | 356 | 2023-03-06 | - | -
|  |  | 21:00 |  | 12:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 12715 | 2023-04-15 | 10869 | 2023-03-06 | - | -
|  |  | 21:00 |  | 12:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-04-01 | 0 | 2023-03-08 | - | -
|  |  | 12:00 |  | 12:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 9272 | 2023-04-01 | 9421 | 2023-03-08 | - | -
|  |  | 12:00 |  | 12:00
18 | Nos. of Days Load Shed at Evening Peak | 21 |  | 18 |  | -
19 | Nos. of Days Load Shed at Day Peak | 15 |  | 12 |  | -
20 | Gross Generation of BPDB (MKWH) | 1652.1779 |  | 1561.2501 |  | 1929.4341 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 47.9101 |  | 46.9674 |  | 88.2498
22 | Net Generation of BPDB (MKWH) | 1604.2678 |  | 1514.2827 |  | 1841.1843
23 | Net Generation of IPP (MKWH) | 4861.0541 |  | 4695.4667 |  | 5255.3957
24 | Net Generation of REB (MKWH) | 114.4874 |  | 121.5861 |  | 131.5194
24 | Net Generation of Rental Power Plant (MKWH) | 397.804 |  | 299.4051 |  | 614.893
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6977.6134 |  | 6630.7407 |  | 7842.9924 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4284.183 |  | 4237.6738 |  | 4240.1479 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 117.8792 |  | 214.1302 |  | 633.9729 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1634.0628 |  | 1443.6516 |  | 2365.7466 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 9.4966 |  | 17.7881 |  | 45.2279 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 47.6176 |  | 146.7623 |  | 36.5217 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 932.2843 |  | 617.702 |  | 609.6252 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 678.729 |  | 535.4411 |  | 754.5062 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 74.4409 |  | 84.1419 |  | 87.447 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March-2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12921 | 2023-03-13 | 19:00
Generation Period
| Dhaka | MW | 5126.93
| Chattogram | MW | 1433.9
| Cumilla | MW | 1447
| Mymensingh | MW | 1081
| Sylhet | MW | 600
a) | Total supply in East zone | MW | 8126.25
| Khulna | MW | 1221
| Barisal | MW | 302.34
| Rajshahi | MW | 1076.6
| Rangpur | MW | 629
b) | Total supply in West zone | MW | 3228.94
c) | Total supply in both zone ( a+b) | MW | 11355.19
Ref: | 27.21.0000.603.16.087.20.666 | Date: 21/05/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 680 | 2023-04-23 | 20:00
| b) Ishurdi end | MW | 434 | 2023-04-01 | 4:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 940 | 2023-04-11 | 11:00
| b) Ishurdi end | MW | 320 | 2023-04-29 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 21.73
| b) Ishurdi end | MKWH | 68.15
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 360 | 2023-04-29 | 18:30
| b)Serajganj end | MW | 520 | 2023-04-01 | 23:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 490 | 2023-04-01 | 23:00
| b)Sirajganj end | MW | 340 | 2023-04-29 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 20.028
| b)Sirajganj end | MKWH | 113.25
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 112.07
| b)Sirajganj end | MKWH | 20.03
30 | Transmission loss of EWI /NO-2 | % | 0.886'%
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/3 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-04-07 05:17 | 2023-04-07 06:27 | 1:10 | T | Due to 33 kv Sk-vita-2 Feeder fault. | 35 | 40.8333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-04-16 03:07 | 2023-04-16 03:25 | 0:18 | T | 33Kv Nandina & Gopalpur feeder E/F ,O/C fault , then T-1 & T-2 LT side trip | 73 | 21.9 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-07 05:17 | 2023-04-07 06:27 | 1:10 | T | Due to 33 kv Sk-vita-2 Feeder fault. | 35 | 40.8333 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-16 03:07 | 2023-04-16 03:25 | 0:18 | T | 33Kv Nandina & Gopalpur feeder E/F ,O/C fault , then T-1 & T-2 LT side trip | 73 | 21.9 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-04-15 10:39 | 2023-04-15 11:16 | 0:37 | E/O | High temperature maintenance. | 40 | 24.6667 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-04-03 05:35 | 2023-04-03 07:49 | 2:14 | E/O | 33Kv Bus DS maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-04-03 05:35 | 2023-04-03 07:54 | 2:19 | E/O | Bus DS Maintenance | 15 | 34.75 | Power interruption
New Tongi 132/33kV Grid Sub-Station | Bus-1 | 2023-04-25 09:34 | 2023-04-25 13:18 | 3:44 | E/O | Reduce the excessive heat of TR-2 transformer LT side (R-phase) | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | T2(413T) HT | 2023-04-25 09:32 | 2023-04-25 13:16 | 3:44 | E/O | Reduce the excessive heat of TR-2 transformer LT side (R-phase) | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 HT | 2023-04-05 06:06 | 2023-04-05 11:09 | 5:03 | E/O | 33 KV Bus coupler Maintenance work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 LT | 2023-04-05 06:03 | 2023-04-05 11:10 | 5:07 | E/O | 33 KV Bus coupler Maintenance work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-04-15 07:46 | 2023-04-15 09:03 | 1:17 | E/O | 33 KV Bus coupler Maintenance work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-04-13 08:35 | 2023-04-13 12:58 | 4:23 | E/O | Hotspot maintenance | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-A | 2023-04-10 09:50 | 2023-04-10 11:24 | 1:34 | E/O | T-3(B) Removal works from system | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-04-05 09:27 | 2023-04-05 11:20 | 1:53 | E/O | Bay -03 bus to ds incoming red hot. | 13 | 24.4833 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-04-05 09:27 | 2023-04-05 11:20 | 1:53 | E/O | Line CT of 33kV Shakhipur feeder is redhot | 13 | 24.4833 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-04-18 07:32 | 2023-04-18 08:37 | 1:05 | E/O | Line CT of 33kV Shakhipur feeder is redhot | 6 | 6.5 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-04-01 19:29 | 2023-04-01 19:50 | 0:21 | E/O | Hotspot maintenance | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2023-04-01 19:29 | 2023-04-01 19:50 | 0:21 | E/O | Hotspot maintenance | 0 | 0 | No interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-04-08 23:43 | 2023-04-09 00:30 | 0:47 | E/O | Bay -03 bus to ds incoming red hot. | 46 | 36.0333 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2023-04-16 22:38 | 2023-04-16 23:53 | 1:15 | E/O | Line CT of 33kV Shakhipur feeder is redhot | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2023-04-16 22:37 | 2023-04-16 23:55 | 1:18 | E/O | Line CT of 33kV Shakhipur feeder is redhot | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 02 | 2023-04-16 11:18 | 2023-04-16 12:01 | 0:43 | E/O | Red Hot,Oile Level maintenance | 0 | 0 | No interruption
|  |  | Total : | 42:34 |  | Unserved Energy: |  | 276.3833
Dhaka (South) Grid Circle :
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2023-04-21 17:38 | 2023-04-21 23:38 | 6:00 | T | Stormy Rain | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) LT | 2023-04-21 17:38 | 2023-04-21 23:43 | 6:05 | T | Stormy Rain | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 HT | 2023-04-16 19:40 | 2023-04-16 19:50 | 0:10 | T | time delay over current with earth fault relay | 63 | 10.5 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 HT | 2023-04-19 13:33 | 2023-04-19 13:56 | 0:23 | T | 51HV Tripp. | 58 | 22.2333 | Power interruption
|  |  | Total : | 0:33 |  | Unserved Energy: |  | 32.7333
Chattogram Grid Circle :
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2023-04-13 22:03 | 2023-04-13 22:16 | 0:13 | T | Fault occured by 33 kv Rajastali feeder. Ins E/F. | 28 | 6.0667 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2023-04-13 22:22 | 2023-04-13 22:31 | 0:09 | T | Over Current | 89 | 13.35 | Power interruption
Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2023-04-20 21:25 | 2023-04-20 21:30 | 0:05 | T | Overcurrent | 90 | 7.5 | Power interruption
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 HT | 2023-04-01 07:20 | 2023-04-01 09:12 | 1:52 | T | Hathazari-shikolbaha ckt-2 trip. | 4 | 7.4667 | Power interruption
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 HT | 2023-04-15 16:42 | 2023-04-15 18:58 | 2:16 | T | Hathazari - Shikalbaha Ckt-2 Trip | 4 | 9.0667 | Power interruption
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 LT | 2023-04-01 07:20 | 2023-04-01 09:12 | 1:52 | T | Hathazari-shikolbaha ckt-2 trip. | 4 | 7.4667 | Power interruption
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 LT | 2023-04-15 16:42 | 2023-04-15 17:50 | 1:08 | T | Hathazari - Shikalbaha Ckt -2 trip | 4 | 4.5333 | Power interruption
Bakulia 132/33kV Grid Sub-Station | T-1 (402T) HT | 2023-04-06 19:10 | 2023-04-06 19:23 | 0:13 | E/O | Transformer tripped by O/C & E/F. | 10 | 2.1667 | Power interruption
Juldah 132/33kV Grid Sub-Station | 132/33 KV 406T T-1 HT | 2023-04-01 10:45 | 2023-04-01 11:43 | 0:58 | E/O | Red Hot Mantanance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-04 HT | 2023-04-01 11:40 | 2023-04-01 14:09 | 2:29 | E/O | Red hot maintenance | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-04 LT | 2023-04-01 11:40 | 2023-04-01 14:10 | 2:30 | E/O | Red hot maintenance | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 2023-04-01 14:17 | 2023-04-01 16:03 | 1:46 | E/O | Tr-02(416T) 33kv "R" phase bushing oil leakage | 15 | 26.5 | Power interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T LT | 2023-04-01 14:16 | 2023-04-01 16:06 | 1:50 | E/O | 33kv "R"phase bushing oil leakage | 15 | 27.5 | Power interruption
|  |  | Total : | 10:54 |  | Unserved Energy: |  | 111.6167
Cumilla Grid Circle :
Kachua 132/33kV Grid Sub-Station | TR-2 HT | 2023-04-23 22:17 | 2023-04-24 10:49 | 12:32 | T | pt fault | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | TR-2 LT | 2023-04-23 22:17 | 2023-04-24 10:51 | 12:34 | T | pt fault | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-04-02 20:22 | 2023-04-02 20:29 | 0:07 | T | Due to shaistaganj feeder fault. | 25 | 2.9167 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2023-04-21 07:14 | 2023-04-21 07:58 | 0:44 | T | o/c, E/F,87 signal , 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 65 | 47.6667 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T2 LT | 2023-04-21 07:14 | 2023-04-21 08:37 | 1:23 | T | 51n.50,87 signal. 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 25 | 34.5833 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 HT | 2023-04-21 07:14 | 2023-04-21 08:02 | 0:48 | T | genaral prip signa. 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 16 | 12.8 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-04-21 07:14 | 2023-04-21 08:02 | 0:48 | T | genaral trip. 33kv Barikandi feeder fault ( blue phase breaker pole brast) | 16 | 12.8 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 HT | 2023-04-18 12:00 | 2023-04-18 13:03 | 1:03 | E/O | 33 kv Bus-01 red hot | 20 | 21 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 LT | 2023-04-18 12:01 | 2023-04-18 13:03 | 1:02 | E/O | 33 kv Bus-01 Red Hot. | 20 | 20.6667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2023-04-15 22:59 | 2023-04-15 23:45 | 0:46 | E/O | Red hot remove. | 40 | 30.6667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-04-15 22:59 | 2023-04-15 23:45 | 0:46 | E/O | Red hot remove. | 40 | 30.6667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2023-04-20 05:58 | 2023-04-20 07:59 | 2:01 | E/O | Red hot Maintenance | 38 | 76.6333 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-04-20 05:57 | 2023-04-20 07:59 | 2:02 | E/O | 33Kv CT terminal R ph Red hot. | 38 | 77.2667 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 HT | 2023-04-06 19:12 | 2023-04-06 19:23 | 0:11 | E/O | load shift from India grid to BD grid | 24 | 4.4 | Power interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-3 LT | 2023-04-06 14:12 | 2023-04-06 19:23 | 5:11 | E/O | load shift from India grid to BD grid | 24 | 124.4 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2023-04-11 07:45 | 2023-04-11 09:08 | 1:23 | E/O | red hot & temperature raising point maintenance. | 20 | 27.6667 | Power interruption
Ramganj 132/33kV Grid Sub-Station | Transformer -02 LT | 2023-04-11 07:45 | 2023-04-11 09:08 | 1:23 | E/O | Temperature raising point & Red hot maintenance. | 20 | 27.6667 | Power interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T HT | 2023-04-15 11:21 | 2023-04-15 12:19 | 0:58 | E/O | Bus section -5 maintenance work by PDB division -1. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-04-15 06:28 | 2023-04-15 08:05 | 1:37 | E/O | 132 KV side ring bus R phase red hot maintenance | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-04-18 23:14 | 2023-04-18 23:56 | 0:42 | E/O | TR-04 33 kv side bus shutdown due to hobigonj old feeder redhot maintenance. | 45 | 31.5 | Power interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2023-04-16 23:45 | 2023-04-18 14:30 | 38:45 | E/O | Tr-3 33kV CT Redhot. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-04-16 23:42 | 2023-04-18 14:30 | 38:48 | E/O | Tr-3 33kV CT Redhot. | 0 | 0 | No interruption
|  |  | Total : | 125:34 |  |  |  | 583.3
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-04-11 14:10 | 2023-04-11 14:23 | 0:13 | T | Over current Earth fault for 33kv pirojpur WPDCL feeder. | 20 | 4.3333 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-04-12 10:10 | 2023-04-12 10:20 | 0:10 | T | Pirozput WZPDCl feeder fault. | 17 | 2.8333 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) HT | 2023-04-11 14:10 | 2023-04-11 14:23 | 0:13 | T | Over current Earth fault for 33kv pirojpur WPDCL feeder. | 20 | 4.3333 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) HT | 2023-04-12 10:10 | 2023-04-12 10:23 | 0:13 | T | Pirozpur WZPDCL feeder fault. | 17 | 3.6833 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-04-11 14:10 | 2023-04-11 14:24 | 0:14 | T | Over current Earth fault for 33kv pirojpur WPDCL feeder. | 20 | 4.6667 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-04-12 10:10 | 2023-04-12 10:24 | 0:14 | T | Pirozput WZPDCl feeder fault. | 17 | 3.9667 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-04-24 18:48 | 2023-04-24 19:51 | 1:03 | T | 33 kv BICL feeder fault | 6 | 6.3 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-04-24 18:48 | 2023-04-24 20:14 | 1:26 | T | 33 kv BICL feeder fault | 6 | 8.6 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2023-04-17 21:22 | 2023-04-17 21:39 | 0:17 | T | Over current | 155 | 43.9167 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2023-04-17 21:22 | 2023-04-17 21:39 | 0:17 | T | Definite over current | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-04-17 21:22 | 2023-04-17 22:12 | 0:50 | T | Due to over current | 65.5 | 54.5833 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2023-04-18 07:26 | 2023-04-18 12:51 | 5:25 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2023-04-21 08:02 | 2023-04-21 12:10 | 4:08 | E/O | Red hot maintenance of 33 kv side | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-04-21 08:01 | 2023-04-21 12:13 | 4:12 | E/O | Red hot maintenance of 33 side if T4 transformer. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-08 11:55 | 2023-04-08 12:25 | 0:30 | E/O | 33kv isolator maintenance of Jalokathi | 16 | 8 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-20 08:33 | 2023-04-20 11:12 | 2:39 | E/O | 33kv DS maintenance of jhalokathi PBS | 26 | 68.9 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-08 11:54 | 2023-04-08 12:28 | 0:34 | E/O | 33kv isolator maintenance of Jhalokathi feeder. | 16 | 9.0667 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-20 09:32 | 2023-04-20 11:13 | 1:41 | E/O | 33kv DS maintenance of Jhalokathi PBS | 26 | 43.7667 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 HT | 2023-04-23 14:17 | 2023-04-23 17:33 | 3:16 | E/O | 33 KV R & Y Phase CT Oil Leakage. | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-04-23 14:16 | 2023-04-23 17:35 | 3:19 | E/O | 33 KV R & Y Phase CT Oil Leakage. | 0 | 0 | No interruption
|  |  | Total : | 5:10 |  |  |  | 266.95
HVDC Grid Circle :
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-04-13 17:50 | 2023-04-13 18:26 | 0:36 | T | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 25 | 15 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-04-13 17:50 | 2023-04-13 18:26 | 0:36 | T | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 25 | 15 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | T | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 30 | 17 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | T | 132 KV PABNA CONNECTOR (R PHASE) FALL DOWN OVER BUS-1 | 30 | 17 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 HT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | T | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 42.5 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 LT | 2023-04-13 17:50 | 2023-04-13 18:24 | 0:34 | T | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 42.5 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2023-04-13 17:50 | 2023-04-14 04:35 | 10:45 | T | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 806.25 | Power interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 LT | 2023-04-13 17:50 | 2023-04-14 04:35 | 10:45 | T | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 75 | 806.25 | Power interruption
Ruppur 132/11kV Grid Sub-Station | AUX Tr-01 LT | 2023-04-13 17:48 | 2023-04-13 18:36 | 0:48 | T | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 0.1 | 0.08 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-04-24 15:10 | 2023-04-24 15:47 | 0:37 | T | 33 pbs feeder loop Y phase disconnect | 40 | 24.6667 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 LT | 2023-04-24 15:10 | 2023-04-24 15:47 | 0:37 | T | 33 kv pbs feeder Y phase Disconnect | 40 | 24.6667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 HT | 2023-04-19 12:35 | 2023-04-19 12:58 | 0:23 | T | Winding Temp high | 80 | 30.6667 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T-1 LT | 2023-04-19 12:35 | 2023-04-19 13:00 | 0:25 | T | Inter Trip From 132KV TR FDR | 80 | 33.3333 | Power interruption
Ruppur 132/11kV Grid Sub-Station | TR-01 LT | 2023-04-13 17:54 | 2023-04-13 18:40 | 0:46 | E/O | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 5 | 3.8333 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-04-12 19:56 | 2023-04-12 21:16 | 1:20 | E/O | 132 kV CT Red-Hot (Y-Phase) maintenance. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2023-04-05 10:59 | 2023-04-05 11:59 | 1:00 | E/O | Redhot Maintenance for R-phase LT Bosing side. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) HT | 2023-04-07 10:40 | 2023-04-07 12:35 | 1:55 | E/O | 132 kV Buss DS (421, Y-Phase) Red-hot Maintenance. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) LT | 2023-04-04 13:12 | 2023-04-04 14:35 | 1:23 | E/O | Red hot | 22 | 30.4333 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-3(425T) LT | 2023-04-06 22:27 | 2023-04-07 17:35 | 19:08 | E/O | Redhot | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2023-04-17 10:27 | 2023-04-17 11:59 | 1:32 | E/O | 33 kV T-4 Incoming DS (B-Phase) Red-hot Maintenance. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) LT | 2023-04-25 15:10 | 2023-04-25 16:32 | 1:22 | E/O | PBS outgoing Feeder Emergency Maintenance | 15 | 20.5 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 HT | 2023-04-07 07:15 | 2023-04-07 10:22 | 3:07 | E/O | red hot maintainence | 5 | 15.5833 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 HT | 2023-04-15 08:09 | 2023-04-15 10:18 | 2:09 | E/O | T1 transformer red hot maintainence | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-04-07 07:14 | 2023-04-07 10:23 | 3:09 | E/O | red hot maintainence | 5 | 15.75 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-04-15 08:08 | 2023-04-15 10:18 | 2:10 | E/O | T1 transformer red hot maintainence | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-2 HT | 2023-04-15 06:10 | 2023-04-15 07:50 | 1:40 | E/O | T2A 33 kv side Hot spot maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-2 LT | 2023-04-15 06:10 | 2023-04-15 07:51 | 1:41 | E/O | T2A 33 kv side Hot spot maintenance | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-04-13 10:59 | 2023-04-13 13:25 | 2:26 | E/O | 33kv T1A incommer B-Phase Rad hot Maintenance. | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-04-18 07:21 | 2023-04-18 09:02 | 1:41 | E/O | Red hot maintenance | 25 | 42.0833 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-04-13 10:58 | 2023-04-13 13:26 | 2:28 | E/O | 33kv T1A incommer B-Phase Rad hot Maintenance. | 25 | 61.6667 | Power interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-04-18 07:21 | 2023-04-18 09:02 | 1:41 | E/O | Red hot maintenance | 25 | 42.0833 | Power interruption
|  |  | Total : | 27:48 |  |  |  | 2106.8467
Bogura Grid Circle:
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-04-24 17:27 | 2023-04-24 17:43 | 0:16 | T | T1,132KV VCB trip due to PBS-1,33KV Raygonj feeder fault. | 3 | 0.8 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-04-24 17:27 | 2023-04-24 17:44 | 0:17 | T | T1,33KV VCB trip due to PBS-1,33KV Raygonj feeder fault. | 3 | 0.85 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-04-24 17:27 | 2023-04-24 17:42 | 0:15 | T | T2,33KV VCB trip due to PBS-1,33KV Raygonj feeder fault. | 3 | 0.75 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-04-17 20:44 | 2023-04-17 20:56 | 0:12 | T | trip | 67 | 13.4 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-01 04:42 | 2023-04-01 05:55 | 1:13 | T | Dabigonj-3, 33 KV feeder Fault for Bad Weather with Running and Tendering. | 18 | 21.9 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-13 13:37 | 2023-04-13 13:50 | 0:13 | T | under frequency | 26.5 | 5.7417 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-13 16:53 | 2023-04-13 16:58 | 0:05 | T | under frequency | 29 | 2.4167 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-01 04:42 | 2023-04-01 05:57 | 1:15 | T | Dabigonj-3, 33 KV feeder Fault for Bad Weather with Running and Tendering. | 18 | 22.5 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-13 13:37 | 2023-04-13 13:50 | 0:13 | T | under frequency | 26.5 | 5.7417 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-13 16:53 | 2023-04-13 16:58 | 0:05 | T | under frequency | 26.5 | 2.2083 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-04-12 15:27 | 2023-04-12 15:35 | 0:08 | E/O | For parallel operation T1 & T2 Xformar | 16 | 2.1333 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-04-20 09:41 | 2023-04-20 10:51 | 1:10 | E/O | High temperature @ T-3 132 KV CT Side (B-Phase) | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-04-20 09:41 | 2023-04-20 10:51 | 1:10 | E/O | High temperature @ T-3 132 KV CT Side (B-Phase) | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-04-20 09:29 | 2023-04-20 09:40 | 0:11 | E/O | T-3/T-4 Bus coupler because of T-3 Transformer S/D. | 20 | 3.6667 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-4 LT | 2023-04-20 09:29 | 2023-04-20 09:40 | 0:11 | E/O | T-3/T-4 Bus coupler close because of T-3 Transformer S/D. | 20 | 3.6667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-04-07 11:03 | 2023-04-07 12:05 | 1:02 | E/O | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-01 Transformer. The involved distribution entity(PBS 1&2) has been informed about this matter over the phone & they have no objection to power interruption. | 30 | 31 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-04-07 11:02 | 2023-04-07 12:04 | 1:02 | E/O | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-01 Transformer. | 30 | 31 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) HT | 2023-04-07 07:22 | 2023-04-07 08:56 | 1:34 | E/O | Red Hot has become visible/measured at different points of T-02 33kV BUS, CT, and DS at T-02 Transformer. | 20 | 31.3333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-04-07 07:21 | 2023-04-07 09:57 | 2:36 | E/O | Red Hot has become visible/measured at different points of T-02 33kV BUS, CT, and DS at T-02 Transformer. | 20 | 52 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-04-19 07:05 | 2023-04-19 07:30 | 0:25 | E/O | Red Hot has become visible/measured at 33kV T2+T3 connecting bus isolator. all operation has been conducted by the instruction of ALDC, Bogura with the permission of NLDC Dhaka. | 25 | 10.4167 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-01 14:26 | 2023-04-01 15:16 | 0:50 | E/O | Emergency Red Hot maintenance. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-01 15:45 | 2023-04-01 17:30 | 1:45 | E/O | Red Hot Bolt replace at CT P2 end. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-13 06:39 | 2023-04-13 08:28 | 1:49 | E/O | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-04 Transformer. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-04-13 06:38 | 2023-04-13 08:29 | 1:51 | E/O | Red Hot has become visible/measured at different points of 33kV BUS, CT, and DS at T-04 Transformer. | 20 | 37 | Power interruption
Naogaon 132/33kV Grid Sub-Station | T-1 HT | 2023-04-09 11:51 | 2023-04-10 00:38 | 12:47 | E/O | Emergency redhot maintenance. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-04-09 11:49 | 2023-04-10 00:41 | 12:52 | E/O | Emergency redhot maintenance. | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-04-05 01:50 | 2023-04-05 17:04 | 15:14 | E/O | Red hot and Flashing at 33kv BUS side of Tr-02. | 25 | 380.8333 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 417T LT | 2023-04-05 13:49 | 2023-04-05 17:04 | 3:15 | E/O | Red hot and Flashing at 33kv BUS side of Tr-02. | 25 | 81.25 | Power interruption
Niamatpur 132/33kV Grid Sub-Station | 417T LT | 2023-04-17 07:14 | 2023-04-17 16:52 | 9:38 | E/O | Transformer T-2 erection. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-04-24 23:44 | 2023-04-25 01:25 | 1:41 | E/O | T-3 33KV B phase TDS red hot maintenance . | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-04-24 22:55 | 2023-04-25 01:33 | 2:38 | E/O | T-3 33KV B phase TDS red hot maintenance . | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | T-01 (406T) HT | 2023-04-13 15:33 | 2023-04-13 17:33 | 2:00 | E/O | AUX-1Busing Y Phase Blast | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | T-01 (406T) LT | 2023-04-13 15:33 | 2023-04-13 17:50 | 2:17 | E/O | AUX-1Busing Y Phase Blast | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-04-12 14:14 | 2023-04-12 15:37 | 1:23 | E/O | Under frequency relay setting and testing of TR-2. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) HT | 2023-04-07 08:14 | 2023-04-07 09:36 | 1:22 | E/O | For 33 kv feeder red hot maintenance work | 13 | 17.7667 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-04-07 08:14 | 2023-04-07 09:36 | 1:22 | E/O | For 33 kv feeder red hot maintenance work. | 26 | 35.5333 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) HT | 2023-04-07 08:15 | 2023-04-07 09:34 | 1:19 | E/O | For 33 kv feeder red hot maintenance work | 13 | 17.1167 | Power interruption
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-04-07 08:15 | 2023-04-07 09:34 | 1:19 | E/O | For 33 kv feeder red hot maintenance work | 13 | 17.1167 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) HT | 2023-04-12 15:02 | 2023-04-12 16:38 | 1:36 | E/O | Due to clear of red hot at 33Kv busbar of NESCO, Saidpur | 28 | 44.8 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-04-12 15:01 | 2023-04-12 16:39 | 1:38 | E/O | NoneDue to clear of red hot at 33Kv busbar of NESCO, Saidpur | 28 | 45.7333 | Power interruption
|  |  | Total : | 92:09 |  |  |  | 918.675
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 309:52 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:April2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2023-04-01 14:07 | 2023-04-01 14:45 | 0:38 | T | None | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-2 | 2023-04-01 14:07 | 2023-04-01 14:47 | 0:40 | T | None | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Summit PS(Kodda) | 2023-04-01 14:07 | 2023-04-01 14:41 | 0:34 | T | None | 18 | 10.2 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kaliakoir Ckt | 2023-04-04 08:12 | 2023-04-04 08:32 | 0:20 | T | None | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-04-18 08:04 | 2023-04-18 08:22 | 0:18 | T | Amin Bazer 400KV X-former Comissioning Effect. | 67 | 20.1 | Power interruption
Sherpur 132/33kV Grid Sub-Station | UMPL-Sherpur Ckt-01 | 2023-04-22 09:10 | 2023-04-22 10:00 | 0:50 | T | N/A | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-04-08 13:59 | 2023-04-08 20:39 | 6:40 | T | fault at RPCL end | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-04-08 15:24 | 2023-04-08 16:09 | 0:45 | T | NLDC order | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-04-08 16:22 | 2023-04-08 16:39 | 0:17 | E/O | 132KV T4 R-phase LA Blast | 50 | 14.1667 | Power interruption
New Tongi 132/33kV Grid Sub-Station | New Tongi L-2 | 2023-04-25 09:33 | 2023-04-25 13:15 | 3:42 | E/O | Reduce the excessive heat of L-2 (Line BUS DS-201M ). | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-04-01 12:01 | 2023-04-01 12:35 | 0:34 | E/O | Shutdown taken by Kabirpur | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-04-12 13:22 | 2023-04-12 15:33 | 2:11 | E/O | Remove of red hot work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2023-04-18 06:32 | 2023-04-18 06:55 | 0:23 | E/O | Amin Bazer Ss 400/132 Kv X-former commissioning work. | 62 | 23.7667 | Power interruption
|  |  | Total : | 10:45 |  | Unserved Energy: |  | 68.2333
Dhaka (South) Grid Circle :
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-04-11 14:13 | 2023-04-11 14:27 | 0:14 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-04-15 06:09 | 2023-04-15 06:24 | 0:15 | T | None | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-04-21 17:34 | 2023-04-21 17:55 | 0:21 | T | Thunderstorm. | 50 | 17.5 | Power interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-1 | 2023-04-21 17:53 | 2023-04-21 22:19 | 4:26 | T | Heavy rain,storm | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-2 | 2023-04-21 17:53 | 2023-04-22 02:36 | 8:43 | T | Heavy rain,storm | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-04-21 17:40 | 2023-04-22 19:14 | 25:34 | T | Heavy rain,storm | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2023-04-21 17:33 | 2023-04-21 20:40 | 3:07 | T | Distance relay operated during heavy storm condition | 47 | 146.4833 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-04-21 17:45 | 2023-04-21 18:14 | 0:29 | T | Earth fault due to heavy storm | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-04-21 17:45 | 2023-04-21 18:49 | 1:04 | T | storm wearher | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Duadkandi 1 | 2023-04-03 08:35 | 2023-04-03 09:12 | 0:37 | T | Trip | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj Ckt-1 | 2023-04-21 17:53 | 2023-04-21 22:20 | 4:27 | T | Rainstorm | 88 | 391.6 | Power interruption
Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj- Ckt-2 | 2023-04-21 17:53 | 2023-04-22 02:34 | 8:41 | T | Heavy Rainstorm | 44 | 382.0667 | Power interruption
Bhulta 400/230kV Grid Sub-Station | Rampura-01 | 2023-04-02 18:26 | 2023-04-03 09:19 | 14:53 | T | Y-Phase trip, 67N trip, CR/DTT Received, General Trip | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | Haripur | 2023-04-10 13:13 | 2023-04-10 13:35 | 0:22 | T | Unknown | 94 | 34.4667 | Power interruption
Narshingdi 132/33kV Grid Sub-Station | Haripur | 2023-04-15 06:09 | 2023-04-15 06:25 | 0:16 | T | CB Not Trip but Voltage Zero. | 100 | 26.6667 | Power interruption
Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-04-01 15:27 | 2023-04-02 09:50 | 18:23 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Duadkandi 1 | 2023-04-05 10:58 | 2023-04-05 11:26 | 0:28 | E/O | Emergency maintenance work | 0 | 0 | No interruption
Hasnabad 132/33kV Grid Substation | Shitallakhya | 2023-04-22 00:40 | 2023-04-22 01:30 | 0:50 | E/O | Emergency maintenance work | 25 | 20.8333 | Power interruption
|  |  | Total : | 93:10 |  | Unserved Energy: |  | 1019.6167
Chattogram Grid Circle :
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2023-04-09 17:54 | 2023-04-09 18:10 | 0:16 | T | Transient fault | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Julda Ckt. line | 2023-04-15 02:31 | 2023-04-15 03:34 | 1:03 | T | O/C Fault at B phase | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-1 | 2023-04-15 16:42 | 2023-04-15 17:20 | 0:38 | T | DISTANCE Trip phase R&Y at Zone-2 | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-04-15 16:42 | 2023-04-15 17:20 | 0:38 | T | DISTANCE Trip phase R&Y at Zone-2 | 15 | 9.5 | Power interruption
KSRM 132/33kV Grid Sub-Station | Baraulia Feeder | 2023-04-15 16:42 | 2023-04-15 17:58 | 1:16 | T | under frequency, grid failure ! | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-2 | 2023-04-15 16:42 | 2023-04-15 22:08 | 5:26 | T | General trip[zone-02(9km),R,Y,B phase Fault] | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Hathazari-1 | 2023-04-15 16:42 | 2023-04-17 17:05 | 48:23 | T | General trip[R,Y,B phase fault,zcom/WET Trip] | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Modern Ckt | 2023-04-06 20:18 | 2023-04-07 00:43 | 4:25 | E/O | Red hot maintenance at Modern end. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2023-04-07 07:04 | 2023-04-07 09:47 | 2:43 | E/O | Red hot maintenance at Khulshi end. | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Khulshi-Ckt.-3 | 2023-04-07 07:20 | 2023-04-07 09:41 | 2:21 | E/O | Khulshi 132/33 kV grid s/s end red hot | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Shahmirpur 2 | 2023-04-15 03:13 | 2023-04-15 08:19 | 5:06 | E/O | Shahmirpur End Red Hot | 0 | 0 | No interruption
Modern Steel 132/11kV Grid Sub-Station | Modern Bakalia Ckt 2 | 2023-04-06 20:17 | 2023-04-07 00:45 | 4:28 | E/O | Red Hot is seen at the Cable clamp joint in the B phase of the 132kV Mod- Bak line at Modern Grid 132/11 kV Substation. | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | Hat-1 | 2023-04-19 07:10 | 2023-04-19 09:38 | 2:28 | E/O | Red Hot in Line Isolator | 40 | 98.6667 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | Kulshi | 2023-04-07 07:19 | 2023-04-07 09:25 | 2:06 | E/O | Working have to be done in Khulsi end | 40 | 84 | Power interruption
Baroaulia 132/33kV Grid Sub-Station | AKSPL | 2023-04-07 07:20 | 2023-04-07 09:58 | 2:38 | E/O | Working have to be done in Khulsi end | 20 | 52.6667 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2023-04-08 10:36 | 2023-04-08 12:47 | 2:11 | E/O | Bamboo trimming and removal from near to the line. | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Madunaghat GIS-01 | 2023-04-17 08:00 | 2023-04-17 17:05 | 9:05 | E/O | CT Change | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | Julda-2 | 2023-04-15 02:36 | 2023-04-15 08:17 | 5:41 | E/O | 213M/215G Line DS flashing at I clamp | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Interconnection-1 | 2023-04-17 16:01 | 2023-04-18 10:42 | 18:41 | E/O | Emergency maintenance at Shikalbaha 132 KV end. | 0 | 0 | No interruption
|  |  | Total : | 119:33 |  | Unserved Energy: |  | 244.8333
Cumilla Grid Circle :
Daudkandi 132/33kV Grid Sub-Station | Sonargaon-1 | 2023-04-21 17:48 | 2023-04-21 19:07 | 1:19 | T | Heavy Storm | 0 | 0 | No interruption
Bibiana 400/230kV Sub-Station | Bibiyana-III (Back feed) | 2023-04-02 14:25 | 2023-04-05 16:16 | 73:51 | T | Inter trip From power station | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-04-06 14:14 | 2023-04-06 14:29 | 0:15 | T | Earth Fault & overcurrent | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shajibazar-Sreemongal Ckt-02 | 2023-04-03 04:46 | 2023-04-03 04:57 | 0:11 | T | Stormy Wether | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | sreemangal-Shahjibazar circuit-2 | 2023-04-03 04:46 | 2023-04-03 04:57 | 0:11 | T | heavy raining and thunder. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-04-21 19:55 | 2023-04-21 19:59 | 0:04 | T | Thundering. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sunamganj 1 | 2023-04-03 10:05 | 2023-04-03 10:13 | 0:08 | T | None | 15 | 2 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-04-05 11:25 | 2023-04-05 11:30 | 0:05 | T | Due to bad weather | 0 | 0 | No interruption
Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-04-03 10:07 | 2023-04-03 10:16 | 0:09 | T | Unknown | 14 | 2.1 | Power interruption
Chauddagram 132/33kV Grid Sub-Station | Feni-1 | 2023-04-23 05:03 | 2023-04-23 08:40 | 3:37 | E/O | to reduced over load cumilla north 230/132 kv transformer by the command of XEN,(NOD),NLDC. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-2 | 2023-04-16 08:16 | 2023-04-16 14:47 | 6:31 | E/O | instruction by NLDC. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-04-22 02:28 | 2023-04-22 03:55 | 1:27 | E/O | For removing the torn OPGW cable from line. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-04-23 07:42 | 2023-04-23 22:39 | 14:57 | E/O | OPGW cable connection Works . | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-04-22 02:28 | 2023-04-22 03:55 | 1:27 | E/O | For removing the torn OPGW cable from line. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-04-23 07:42 | 2023-04-23 22:39 | 14:57 | E/O | OPGW cable connection Works | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-04-22 02:29 | 2023-04-22 03:48 | 1:19 | E/O | OPGW Fault restoration work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-04-23 07:46 | 2023-04-23 22:40 | 14:54 | E/O | OPGW restoration | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-04-22 02:29 | 2023-04-22 03:48 | 1:19 | E/O | OPGW Fault Restoration work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-04-23 07:47 | 2023-04-23 22:40 | 14:53 | E/O | OPGW Restoration | 0 | 0 | No interruption
|  |  |  | 76:13 |  | Unserved Energy: |  | 4.1
Page: 3/3 | [8 empty] | OF-LDC-24
Khulna Grid Circle :
Khulna (C) 132/33kV Grid Sub-Station | 132 kV Central- Noapara-2 | 2023-04-02 12:39 | 2023-04-02 13:16 | 0:37 | T | Not indentify | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | Jashore-1 | 2023-04-10 13:52 | 2023-04-10 15:22 | 1:30 | T | Distance Relay Fault | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 2 | 2023-04-02 12:39 | 2023-04-02 13:16 | 0:37 | T | Distance Relay Tripping | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-04-10 12:04 | 2023-04-10 12:48 | 0:44 | E/O | Hot spot maintenance | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-2 | 2023-04-10 11:22 | 2023-04-10 12:02 | 0:40 | E/O | Hot spot maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | Magura 1 | 2023-04-11 10:08 | 2023-04-11 16:45 | 6:37 | E/O | Hot spot maintenance | 0 | 0 | No interruption
|  |  |  | 2:44 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi 132/33kV Grid Sub-Station | 132 kV Pabna | 2023-04-13 17:50 | 2023-04-14 05:03 | 11:13 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 92 | 1031.9333 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Baghabari Line | 2023-04-13 17:50 | 2023-04-14 04:51 | 11:01 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 20 | 220.3333 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -1 | 2023-04-13 17:50 | 2023-04-14 04:45 | 10:55 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 65 | 709.5833 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -2 | 2023-04-13 17:51 | 2023-04-13 18:24 | 0:33 | T | 132 KV Pabna ckt conductor was break down (R phase) fall over BUS-1. | 65 | 35.75 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-1 | 2023-04-13 17:50 | 2023-04-13 18:33 | 0:43 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 1 | 0.71667 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kV Rupppur-2 | 2023-04-13 17:50 | 2023-04-14 04:53 | 11:03 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 1 | 11.05 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2023-04-13 17:50 | 2023-04-14 04:40 | 10:50 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 60 | 650 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2023-04-13 17:50 | 2023-04-14 04:40 | 10:50 | T | Pabna ckt conductor was break down (R phase) fall over BUS-1. | 60 | 650 | Power interruption
Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2023-04-24 19:12 | 2023-04-24 19:23 | 0:11 | T | C PHASE TO GROUND FAULT | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-1 | 2023-04-13 17:48 | 2023-04-13 18:35 | 0:47 | T | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 2.5 | 1.9583 | Power interruption
Ruppur 132/11kV Grid Sub-Station | 132kv Ishurdi Line-2 | 2023-04-13 17:48 | 2023-04-14 04:52 | 11:04 | T | 132kv Ruppur-ishwardi line-1&2 is dead for Ishwardi 132kv Busbar problem. | 2.5 | 27.6667 | Power interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-04-13 17:49 | 2023-04-14 04:48 | 10:59 | T | O/C | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2023-04-13 17:49 | 2023-04-14 04:48 | 10:59 | T | O/C | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | NOA-1(L3) | 2023-04-10 13:51 | 2023-04-10 15:20 | 1:29 | T | earth fault | 30 | 44.5 | Power interruption
Jashore 132/33kV Grid Sub-Station | NOA-2(L4) | 2023-04-10 13:51 | 2023-04-10 15:20 | 1:29 | T | overcurrent | 30 | 44.5 | Power interruption
BIPTC | Baharampur-4 | 2023-04-04 10:03 | 2023-04-04 20:03 | 10:00 | E/O | Shutdown is taken from Baharampur S/S end at 10:03 BST | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2023-04-05 10:04 | 2023-04-05 21:40 | 11:36 | E/O | Shutdown is taken from baharampur s/s end | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-04-16 08:16 | 2023-04-16 11:20 | 3:04 | E/O | Shahjadpur- Bhagabari 71 ckt 132 Kv ckt (Red hot) | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | Bhe-230 to Bhe-132 kV (GKP) Line Ckt-1 | 2023-04-19 10:18 | 2023-04-19 12:06 | 1:48 | E/O | Line Ckt-1 Line DS B phase redhot | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-04-13 20:07 | 2023-04-14 05:38 | 9:31 | E/O | Instruction of ALDC | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-04-19 19:28 | 2023-04-19 23:49 | 4:21 | E/O | Instruction of ALDC | 0 | 0 | No interruption
|  |  |  | 144:26 |  | Unserved Energy: |  | 3427.9917
Bogura Grid Circle:
Sirajgonj 230 kV Switching Station | Baghabari -02 | 2023-04-15 10:54 | 2023-04-15 16:48 | 5:54 | T | Trip | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-04-13 17:49 | 2023-04-14 04:40 | 10:51 | T | Ishurdi end fault | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-04-13 17:49 | 2023-04-14 04:40 | 10:51 | T | Ishurdi end trip. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Ishurdi-2 | 2023-04-24 19:12 | 2023-04-24 19:19 | 0:07 | T | Wather cluudy,thandaring. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-04-20 23:05 | 2023-04-21 04:58 | 5:53 | E/O | According to NLDC's instruction. | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-04-04 11:35 | 2023-04-04 12:23 | 0:48 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-04-04 12:29 | 2023-04-04 12:41 | 0:12 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-04-18 21:05 | 2023-04-19 07:38 | 10:33 | E/O | Due to emergency maint.work | 14 | 147.7 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | PS 230 KV Ckt1 | 2023-04-11 21:25 | 2023-04-12 16:34 | 19:09 | E/O | Sky wire red hot | 0 | 0 | No interruption
[6 empty] | Unserved Energy: |  | 147.7
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 446:51 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/14 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: April 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-04-16 08:38 | 2023-04-16 11:11 | 2:33 | S/O | Pbs works | 10 | 25.5 | Power interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-04-16 08:38 | 2023-04-16 11:11 | 2:33 | S/O | Pbs works | 10 | 25.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-04-08 08:30 | 2023-04-08 11:32 | 3:02 | S/O | PBS Bus Maintenance work. | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 HT | 2023-04-11 10:15 | 2023-04-11 11:44 | 1:29 | S/O | Relay Testing and df/dt setting implementation | 0 | 0 | No interruption
Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-04-11 11:47 | 2023-04-11 11:56 | 0:09 | S/O | Relay testing and df/dt setting implementation | 0 | 0 | No interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2023-04-25 09:35 | 2023-04-25 13:58 | 4:23 | S/O | Due to Test (Maintenance) Temperature Sensor. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-04-03 12:15 | 2023-04-03 16:26 | 4:11 | S/O | DS work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-04-04 06:00 | 2023-04-04 06:14 | 0:14 | S/O | DS work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) HT | 2023-04-09 06:17 | 2023-04-09 06:28 | 0:11 | S/O | Ds work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-04-03 12:15 | 2023-04-03 16:29 | 4:14 | S/O | DS work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-04-04 05:59 | 2023-04-04 06:15 | 0:16 | S/O | DS work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-1 (406T) LT | 2023-04-09 06:17 | 2023-04-09 06:29 | 0:12 | S/O | Ds work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-04-09 06:19 | 2023-04-09 14:38 | 8:19 | S/O | Ds work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) HT | 2023-04-13 06:22 | 2023-04-13 09:06 | 2:44 | S/O | None | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-04-09 06:18 | 2023-04-09 14:39 | 8:21 | S/O | Ds work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-2 (416T) LT | 2023-04-13 06:21 | 2023-04-13 09:07 | 2:46 | S/O | 33 kv T-02 BDS-1 Maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2023-04-04 06:00 | 2023-04-04 08:18 | 2:18 | S/O | DS work | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2023-04-04 05:59 | 2023-04-04 08:18 | 2:19 | S/O | DS work | 0 | 0 | No interruption
New Tongi 132/33kV Grid Sub-Station | T2(413T) LT | 2023-04-25 09:31 | 2023-04-25 13:17 | 3:46 | S/O | Project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-04-04 09:43 | 2023-04-04 10:42 | 0:59 | S/O | Project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-04-04 09:43 | 2023-04-04 10:43 | 1:00 | S/O | Project work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-04-04 10:45 | 2023-04-04 12:25 | 1:40 | S/O | Project Work | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-04-04 10:45 | 2023-04-04 12:25 | 1:40 | S/O | Maintenance work for rising temperature | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | 230 kV Bus-2 | 2023-04-04 08:12 | 2023-04-04 12:05 | 3:53 | S/O | Maintenance work for rising temperature | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 HT | 2023-04-17 06:10 | 2023-04-17 07:45 | 1:35 | S/O | CSD Test | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | T-03 LT | 2023-04-17 06:10 | 2023-04-17 07:45 | 1:35 | S/O | CSD test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-04-16 12:23 | 2023-04-16 13:33 | 1:10 | S/O | CSD Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-04-18 09:18 | 2023-04-18 13:43 | 4:25 | S/O | CSD Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230 kv Bus 01 | 2023-04-09 10:32 | 2023-04-09 16:32 | 6:00 | S/O | CT maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-06 09:54 | 2023-04-07 12:20 | 26:26 | S/O | Sf6 gas pressure checking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-12 11:04 | 2023-04-12 19:36 | 8:32 | S/O | Filling oil in conservator tank | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-15 14:04 | 2023-04-15 19:49 | 5:45 | S/O | Hotspot maintenance on 33kV POTHEAD by Desco | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-16 15:52 | 2023-04-16 17:47 | 1:55 | S/O | Hotspot maintenance on 33kV POTHEAD by Desco | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Bus-2 | 2023-04-17 14:52 | 2023-04-17 18:07 | 3:15 | S/O | TR-3 33 KV EPZ and Nayerhat feeder maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2023-04-05 11:28 | 2023-04-05 13:08 | 1:40 | S/O | TR-3 33 KV EPZ and Nayerhat feeder maintenance. | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2023-04-05 11:25 | 2023-04-05 12:48 | 1:23 | S/O | 33 KV Bus coupler Maintenance work | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-1 (132kV) HT | 2023-04-10 07:01 | 2023-04-10 10:01 | 3:00 | S/O | Maintenance work due to temperature increase of 33kv CB connector. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-2 (132kV) HT | 2023-04-18 15:15 | 2023-04-18 15:25 | 0:10 | S/O | Maintenance work due to temperature increase of 33kv CB connector. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2023-04-10 10:02 | 2023-04-10 11:14 | 1:12 | S/O | High Temperature Work | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-04-13 08:38 | 2023-04-13 12:55 | 4:17 | S/O | High Temperature work | 0 | 0 | No interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-04-11 09:06 | 2023-04-11 12:15 | 3:09 | S/O | Hotspot maintenance | 80 | 252 | Power interruption
Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2023-04-11 09:05 | 2023-04-11 12:16 | 3:11 | S/O | T-3(B) Removal works from system | 80 | 254.6667 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-04-18 07:32 | 2023-04-18 08:37 | 1:05 | S/O | Maintenance work due to temperature increase of 33kv CB connector. | 6 | 6.5 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 HT | 2023-04-16 09:49 | 2023-04-16 11:21 | 1:32 | S/O | High Temperature Work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-3 LT | 2023-04-16 09:49 | 2023-04-16 11:21 | 1:32 | S/O | High Temperature work | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) HT | 2023-04-08 08:22 | 2023-04-08 17:10 | 8:48 | S/O | T-3(B) Removal works from system | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Tr-3 (424T) LT | 2023-04-08 08:22 | 2023-04-08 17:20 | 8:58 | S/O | T-3(B) Removal works from system | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Transformer-3 (424T) HT | 2023-04-17 08:28 | 2023-04-17 09:47 | 1:19 | S/O | Maintanance Work. | 0 | 0 | No interruption
|  |  | Total : | 165:06 |  | Unserved Energy: |  | 564.1667
Dhaka (South) Grid Circle :
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 HT | 2023-04-06 09:28 | 2023-04-06 16:53 | 7:25 | S/O | Relay changing work. | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2023-04-22 15:02 | 2023-04-22 15:37 | 0:35 | S/O | Tr-02 (33kV) Incomer CT B-phase loop connection point oil leakage. | 30 | 17.5 | Power interruption
|  |  | Total : | 8:00 |  | Unserved Energy: |  | 17.5
Chattogram Grid Circle :
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) LT | 2023-04-04 13:05 | 2023-04-04 14:11 | 1:06 | S/O | Spare transformer T1 25/41 MVA Transfer. | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) HT | 2023-04-13 16:04 | 2023-04-13 17:01 | 0:57 | S/O | Maintainance | 0 | 0 | No interruption
Kalurghat 132/33kV Grid Sub-Station | TRFO-02(516T) HT | 2023-04-13 11:26 | 2023-04-13 16:04 | 4:38 | S/O | Maintainance | 0 | 0 | No interruption
|  |  | Total : | 6:41 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 HT | 2023-04-02 10:24 | 2023-04-02 11:53 | 1:29 | S/O | 33KV Balutopa Feeder BUS Isulator Problem. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-04-02 10:24 | 2023-04-02 11:53 | 1:29 | S/O | 33KV Balutopa Feeder BUS Isulator Problem. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-04-15 05:48 | 2023-04-15 11:20 | 5:32 | S/O | 33 kv Bus loop & 33 kv bus DS Y Phase (Capacitor Bank) Replacement work | 25 | 138.3333 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-04-20 06:32 | 2023-04-20 08:42 | 2:10 | S/O | 33kv bus s/down (T-1) for chow ckt-1 bus DS maintenance work. S/D taken BPDB. | 32 | 69.3333 | Power interruption
Kachua 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-08 10:31 | 2023-04-08 17:49 | 7:18 | S/O | Rectification of auxiliary TR-1 | 0 | 0 | No interruption
Kachua 132/33kV Grid Sub-Station | TR-1 LT | 2023-04-08 10:30 | 2023-04-08 17:50 | 7:20 | S/O | Rectification of auxiliary TR-1 | 0 | 0 | No interruption
Ramganj 132/33kV Grid Sub-Station | Transformer-01 LT | 2023-04-10 07:37 | 2023-04-10 08:58 | 1:21 | S/O | Red hot maintenance work. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-04-15 11:20 | 2023-04-15 12:19 | 0:59 | S/O | Bus section -5 maintenance work by PDB division -1. | 0 | 0 | No interruption
Brahmanbaria 132/33kV Grid Sub-Station | Aux. Tr-2 (PGCB) LT | 2023-04-15 11:20 | 2023-04-15 12:30 | 1:10 | S/O | Bus section -5 maintenance work by PDB division -1. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-04 11:44 | 2023-04-04 12:32 | 0:48 | S/O | Red hot maintenance of REB Feeder-2. | 0 | 0 | No interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-05 23:17 | 2023-04-06 00:34 | 1:17 | S/O | For red hot maintenance by REB. | 14 | 17.9667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-04-08 10:48 | 2023-04-08 13:00 | 2:12 | S/O | Red hot maintenance by REB 1& REB 2. | 12 | 26.4 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-04-05 23:17 | 2023-04-06 00:34 | 1:17 | S/O | For red hot maintenance by REB. | 14 | 17.9667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-04-08 10:48 | 2023-04-08 13:00 | 2:12 | S/O | Red hot maintenance by REB 1& REB 2. | 12 | 26.4 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-04-18 23:11 | 2023-04-18 23:59 | 0:48 | S/O | 33 kv Hobigonj old feeder redhot maintenance. | 45 | 36 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 HT | 2023-04-01 09:15 | 2023-04-01 10:54 | 1:39 | S/O | Jamuna feeder red hot maintenance. | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-06 LT | 2023-04-01 09:14 | 2023-04-01 10:55 | 1:41 | S/O | Jumuna feeder red hot maintenance. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 HT | 2023-04-06 10:59 | 2023-04-06 12:33 | 1:34 | S/O | None | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2023-04-06 10:58 | 2023-04-06 12:34 | 1:36 | S/O | None | 0 | 0 | Power interruption
|  |  | Total : | 43:52 |  | Unserved Energy: |  | 332.4
Khulna Grid Circle :
Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-04-17 08:15 | 2023-04-17 08:43 | 0:28 | S/O | Red-hot remove at 33kv Jhalokathi feeder. | 22 | 10.2667 | No interruption
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-04-17 07:15 | 2023-04-17 08:43 | 1:28 | S/O | Red-hot remove at 33kv Jhalokathi feeder. | 22 | 32.2667 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-04-12 09:22 | 2023-04-12 10:27 | 1:05 | S/O | Removal red hot of 33 kV side Y phase CT | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-04-18 05:38 | 2023-04-18 06:53 | 1:15 | S/O | Hot spot tightening work. | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-04-12 09:23 | 2023-04-12 10:28 | 1:05 | S/O | Removal red hot of 33 kV side Y phase CT | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-04-18 05:37 | 2023-04-18 06:54 | 1:17 | S/O | Hot spot tightening work. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 HT | 2023-04-18 07:26 | 2023-04-18 12:51 | 5:25 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-04-18 07:25 | 2023-04-18 12:53 | 5:28 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-15 07:26 | 2023-04-15 10:45 | 3:19 | S/O | Red Hot Maintenance at 33 kv Bus DS | 22 | 72.9667 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 HT | 2023-04-19 08:14 | 2023-04-19 12:35 | 4:21 | S/O | Red hot maintence | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-15 07:25 | 2023-04-15 10:48 | 3:23 | S/O | Red Hot Maintenance at 33 kv BUS DS | 22 | 74.4333 | Power interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-04-19 08:13 | 2023-04-19 12:37 | 4:24 | S/O | Red hot maintence | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2023-04-25 07:02 | 2023-04-25 08:21 | 1:19 | S/O | Transformer oil leakage | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T LT | 2023-04-25 07:01 | 2023-04-25 08:22 | 1:21 | S/O | Transformer oil leakage. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-04-05 08:07 | 2023-04-05 09:25 | 1:18 | S/O | SF6 Gas Leakage Maintenance. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-04-13 07:25 | 2023-04-13 11:21 | 3:56 | S/O | For Gas leakage of B phase | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-04-15 07:10 | 2023-04-15 12:16 | 5:06 | S/O | SF6 gas leakage maintenance | 0 | 0 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-04-05 08:06 | 2023-04-05 09:27 | 1:21 | S/O | SF6 Gas Leakage Maintenance. | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-04-13 07:25 | 2023-04-13 11:22 | 3:57 | S/O | For SF6 Gas leakage of B Phase | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-04-15 07:10 | 2023-04-15 12:17 | 5:07 | S/O | SF6 gas leakage maintenance | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) HT | 2023-04-11 10:08 | 2023-04-11 17:05 | 6:57 | S/O | New 132 KV bus connection with existing 132KV bus,and red hot maintenance work at 33KV incomer-01 TR-01 side DS. | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-04-11 10:10 | 2023-04-11 17:07 | 6:57 | S/O | New 132 KV Bus connection with Existing 132KV Bus and red hot maintenance work at 33 KV incomer -01, tr-01 side DS. | 0 | 0 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) HT | 2023-04-06 07:18 | 2023-04-06 09:01 | 1:43 | S/O | 33KV Bus Section -03 Shut Down. | 25 | 42.9167 | Power interruption
Bagerhat 132/33kV Grid Sub-Station | Transformer-3 ( 423 T) LT | 2023-04-06 07:17 | 2023-04-06 09:02 | 1:45 | S/O | 33KV Bus Section -03 Shut Down. | 25 | 43.75 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 HT | 2023-04-06 08:21 | 2023-04-12 22:33 | 158:12 | S/O | Project work | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-04-06 08:20 | 2023-04-12 22:34 | 158:14 | S/O | Project work | 0 | 0 | No interruption
|  |  | Total : | 390:11 |  | Unserved Energy : |  | 276.6
HVDC Grid Circle
BIPTC | 21T01 HT | 2023-04-15 05:20 | 2023-04-15 08:58 | 3:38 | S/O | Block-01 VCS Strainer cleaning with resin change | 0 | 0 | No interruption
BIPTC | 21T01 LT | 2023-04-15 05:20 | 2023-04-15 08:58 | 3:38 | S/O | Block-01 VCS Strainer cleaning with resin change . 511 mw power imported from India | 0 | 0 | No interruption
Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-04-19 09:33 | 2023-04-19 10:44 | 1:11 | S/O | for tighting work | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | TR-01 HT | 2023-04-04 13:23 | 2023-04-04 14:41 | 1:18 | S/O | 11kv annual maintenance | 0 | 0 | No interruption
Ruppur 132/11kV Grid Sub-Station | TR-02 HT | 2023-04-04 10:42 | 2023-04-04 13:09 | 2:27 | S/O | 11kv annual maintenance | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 HT | 2023-04-01 07:44 | 2023-04-03 12:30 | 52:46 | S/O | Aircell change | 0 | 0 | No interruption
Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2023-04-01 07:44 | 2023-04-03 12:30 | 52:46 | S/O | Aircell change | 0 | 0 | No interruption
|  |  | Total : | 507:55 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-04-01 09:28 | 2023-04-01 11:27 | 1:59 | S/O | Red hot | 20 | 39.6667 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-04-01 09:27 | 2023-04-01 11:29 | 2:02 | S/O | Red hot | 20 | 40.6667 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-04-01 09:30 | 2023-04-01 11:28 | 1:58 | S/O | Red hot | 20 | 39.3333 | Power interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-04-01 09:26 | 2023-04-01 11:30 | 2:04 | S/O | Red hot | 20 | 41.3333 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-04-17 08:45 | 2023-04-17 11:58 | 3:13 | S/O | T-2 blast wall work | 0 | 0 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-04-17 08:45 | 2023-04-17 11:58 | 3:13 | S/O | T-2 blast wall work | 0 | 0 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-04-15 06:28 | 2023-04-15 11:00 | 4:32 | S/O | CB & CT connector change & replacing copper flexible conductor. | 12 | 54.4 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-04-15 06:27 | 2023-04-15 11:01 | 4:34 | S/O | CB & CT connector change & replacing copper flexible conductor. | 12 | 54.8 | Power interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T HT | 2023-04-13 09:42 | 2023-04-13 11:37 | 1:55 | S/O | Red hat maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2023-04-13 09:42 | 2023-04-13 11:38 | 1:56 | S/O | Red hat maintenance | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T HT | 2023-04-13 12:08 | 2023-04-16 14:48 | 74:40 | S/O | oil sentrifuse | 0 | 0 | No interruption
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2023-04-13 12:07 | 2023-04-16 14:53 | 74:46 | S/O | oil centrifuge | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-04-07 07:40 | 2023-04-07 09:35 | 1:55 | S/O | 33KV BUS Corrective maintenance | 35 | 67.0833 | Power interruption
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) LT | 2023-04-07 07:40 | 2023-04-07 09:35 | 1:55 | S/O | 33KV BUS Corrective maintenance | 35 | 67.0833 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-04-18 09:17 | 2023-04-18 10:48 | 1:31 | S/O | 33kV CT High Junction Temperature | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-04-18 09:17 | 2023-04-18 10:49 | 1:32 | S/O | Same | 0 | 0 | No interruption
Niamatpur 132/33kV Grid Sub-Station | 417T HT | 2023-04-17 07:14 | 2023-04-17 16:28 | 9:14 | S/O | Transformer T-2 erection. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-04-12 09:44 | 2023-04-12 13:50 | 4:06 | S/O | Under Frequency Relay setting and testing of TR-1 | 0 | 0 | Power interruption
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-04-12 09:43 | 2023-04-12 14:06 | 4:23 | S/O | Under Frequency Relay setting and testing of TR-1 | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | 416T HT | 2023-04-12 14:15 | 2023-04-12 15:36 | 1:21 | S/O | Under frequency relay setting and testing of TR-2. | 0 | 0 | No interruption
|  |  | Total : | 202:49 |  | Unserved Energy : |  | 404.3667
Others :
No interruption
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1324:34 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/12 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: April2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-04-17 19:10 | 2023-04-17 21:05 | 1:55 | S/O | Temperature rise Bashundhara end(Red hot). | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Keranigonj-02 | 2023-04-01 10:20 | 2023-04-01 17:03 | 6:43 | S/O | Dead line cheking | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-1 | 2023-04-06 07:09 | 2023-04-06 08:54 | 1:45 | S/O | CSD Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-1 | 2023-04-16 09:56 | 2023-04-16 15:49 | 5:53 | S/O | 400/132 kV New ATR installation work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-04-04 10:12 | 2023-04-04 13:29 | 3:17 | S/O | CSD Commissioning | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-04-04 13:46 | 2023-04-04 17:19 | 3:33 | S/O | CSD Test | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-04-09 07:29 | 2023-04-09 12:31 | 5:02 | S/O | commissioning (CSD test) | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Lalbag Ckt-01 | 2023-04-11 07:53 | 2023-04-11 09:05 | 1:12 | S/O | Reduce high temperature at BkR down loop point. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2023-04-07 09:11 | 2023-04-07 16:05 | 6:54 | S/O | Dead line checking | 0 | 0 | No interruption
Kaliakoir 400/230/132kV Grid Sub-Station | Bibiyana 2 | 2023-04-04 09:35 | 2023-04-04 12:44 | 3:09 | S/O | By NLDC | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-04-08 12:11 | 2023-04-08 13:22 | 1:11 | S/O | Tree Trimining | 0 | 0 | No interruption
|  |  | Total : | 40:34 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-04-22 15:50 | 2023-04-22 18:48 | 2:58 | S/O | To remove long nylon net on top of tower no. 29 of Maniknagar Matuail Ckt. | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2023-04-01 15:42 | 2023-04-02 09:19 | 17:37 | S/O | OPG Cable joint and maintenance. | 0 | 0 | No interruption
Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-2 | 2023-04-09 06:15 | 2023-04-19 07:54 | 241:39 | S/O | Tower Erection | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2023-04-24 07:25 | 2023-04-24 20:03 | 12:38 | S/O | Due to replacemnet work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-01 | 2023-04-15 23:01 | 2023-04-16 22:58 | 23:57 | S/O | GULshan -01 C T & uper conducter replace | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Moghbazar-01 | 2023-04-05 05:34 | 2023-04-05 06:58 | 1:24 | S/O | Shutdown by NLDC | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-04-01 15:24 | 2023-04-02 09:22 | 17:58 | S/O | Work on other side by NLDC | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 1 | 2023-04-06 09:27 | 2023-04-06 16:53 | 7:26 | S/O | Relay Change | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Aminbazar-2 | 2023-04-01 10:13 | 2023-04-01 17:05 | 6:52 | S/O | Dead line checking at Aminbazar end. | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Fatullah-1(E06) | 2023-04-06 09:33 | 2023-04-06 12:05 | 2:32 | S/O | Due to Brid nesting | 0 | 0 | No interruption
Bhulta 400/230kV Grid Sub-Station | Rampura-02 | 2023-04-23 20:41 | 2023-04-24 20:02 | 23:21 | S/O | CT fault at Rampura 230/132 kV Grid Sub-station. | 0 | 0 | No interruption
|  |  | Total : | 358:22 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2023-04-07 07:19 | 2023-04-07 09:15 | 1:56 | S/O | development work | 0 | 0 | No interruption
AKS 132/33kV Grid Sub-Station | Khulshi | 2023-04-07 07:20 | 2023-04-07 09:54 | 2:34 | S/O | Shutdown for Khulshi Demand. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-04-08 10:35 | 2023-04-08 12:47 | 2:12 | S/O | Emergency work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-1 | 2023-04-12 11:10 | 2023-04-12 14:54 | 3:44 | S/O | Project work | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-1 | 2023-04-13 11:14 | 2023-04-13 14:54 | 3:40 | S/O | Work Done | 0 | 0 | No interruption
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-2 | 2023-04-13 14:56 | 2023-04-13 16:17 | 1:21 | S/O | Work Done | 0 | 0 | No interruption
|  |  | Total : | 15:27 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2023-04-11 15:39 | 2023-04-11 16:44 | 1:05 | S/O | SF6 gas filling | 71 | 76.9167 | Power interruption
Bibiana 400/230kV Sub-Station | Bibi-Kalia Ckt-II | 2023-04-04 09:39 | 2023-04-04 12:43 | 3:04 | S/O | Maintenance work | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-04-17 09:15 | 2023-04-17 16:51 | 7:36 | S/O | Sylhet ckt-1 CB replace work. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-04-18 08:23 | 2023-04-18 22:12 | 13:49 | S/O | Sylhet-chhatak Ckt-1 CB replace work. | 0 | 0 | No interruption
Chhatak 132/33kV Grid Sub-Station | Sylhet 01 | 2023-04-19 07:14 | 2023-04-19 11:05 | 3:51 | S/O | New Breaker Replacement | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-04-05 11:31 | 2023-04-05 11:40 | 0:09 | S/O | Maintenance | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-04-17 09:24 | 2023-04-17 16:51 | 7:27 | S/O | Due to CB Replace | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-04-18 08:28 | 2023-04-18 22:12 | 13:44 | S/O | work of chhatak end | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Chhatak Ckt-1 | 2023-04-19 07:17 | 2023-04-19 11:03 | 3:46 | S/O | Maintenance for Chhatak SS end. | 0 | 0 | No interruption
|  |  | Total : | 54:31 |  | Unserved Energy: |  | 76.9167
Khulna Grid Circle :
Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-2 | 2023-04-10 07:26 | 2023-04-10 09:27 | 2:01 | S/O | None | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-1 | 2023-04-06 07:15 | 2023-04-06 09:56 | 2:41 | S/O | Aminbazer work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 400kV Aminbazar Ckt-2 | 2023-04-09 07:36 | 2023-04-09 12:25 | 4:49 | S/O | Aminbazar 400kv ss side Project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Faridpur Ckt-2 | 2023-04-10 07:32 | 2023-04-10 09:27 | 1:55 | S/O | None | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2023-04-10 12:05 | 2023-04-10 12:48 | 0:43 | S/O | Ins by aldc | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2023-04-19 09:06 | 2023-04-19 12:59 | 3:53 | S/O | High Temperature Maintenance | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-02 | 2023-04-10 11:23 | 2023-04-10 12:03 | 0:40 | S/O | Instructions by Aldc | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-02 | 2023-04-19 09:12 | 2023-04-19 14:00 | 4:48 | S/O | High Temperature Maintenance | 0 | 0 | No interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2023-04-12 23:48 | 2023-04-13 01:22 | 1:34 | S/O | For temperature reduced | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-04-04 10:12 | 2023-04-04 12:28 | 2:16 | S/O | SCADA Operation work by BPDB,Khulna. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-04-04 13:25 | 2023-04-04 14:15 | 0:50 | S/O | SCADA work by BPDB,Khulna. | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | PDB 330MW CCPP | 2023-04-17 09:36 | 2023-04-17 12:16 | 2:40 | S/O | SCADA test by BPDB | 0 | 0 | No interruption
|  |  | Total : | 28:50 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC | Baharampur-3 | 2023-04-01 09:52 | 2023-04-01 21:17 | 11:25 | S/O | Due to maintenance work. | 0 | 0 | No interruption
BIPTC | Baharampur-3 | 2023-04-02 10:04 | 2023-04-02 21:02 | 10:58 | S/O | Due to maintenance work. | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2023-04-03 10:11 | 2023-04-03 20:02 | 9:51 | S/O | Due to maintenance work. | 0 | 0 | No interruption
BIPTC | Baharampur-4 | 2023-04-06 10:00 | 2023-04-06 20:01 | 10:01 | S/O | 400 kv Baharampur ckt-4 shutdown at baharampur end | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | Narail Ckt. - 1 | 2023-04-11 10:11 | 2023-04-11 16:58 | 6:47 | S/O | Work for Narail Sub-Station. | 0 | 0 | No interruption
|  |  | Total : | 49:02 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-1 | 2023-04-02 06:51 | 2023-04-02 17:23 | 10:32 | S/O | project work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Naogaon 132 KV Line-2 | 2023-04-01 06:46 | 2023-04-01 18:23 | 11:37 | S/O | Tower Height Extension. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-04-02 06:50 | 2023-04-02 17:24 | 10:34 | S/O | project work of Bogura s/s. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-04-03 06:39 | 2023-04-03 14:27 | 7:48 | S/O | S/D for Bogura side | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-04-04 07:25 | 2023-04-04 15:15 | 7:50 | S/O | bogura s/s reconducting work. | 0 | 0 | No interruption
Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-2 | 2023-04-01 06:46 | 2023-04-01 18:22 | 11:36 | S/O | Shutdown for Bogura side | 0 | 0 | No interruption
|  |  | Total : | 59:57 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 606:43 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April 2023
| Area | Previous Month (March' 2023) |  |  |  | Current Month (April '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 16 | 7 | 62 | 85 | 12 | 24 | 59 | 95
2 | Dhaka (South) Grid Circle. | 32 | 15 | 26 | 73 | 19 | 3 | 13 | 35
3 | Chattogram Grid Circle. | 14 | 4 | 37 | 55 | 14 | 18 | 9 | 41
4 | Cumilla Grid Circle. | 45 | 6 | 59 | 110 | 16 | 25 | 28 | 69
5 | Khulna Grid Circle. | 23 | 5 | 70 | 98 | 14 | 12 | 38 | 64
6 | HVDC Grid Circle | 21 | 1 | 8 | 30 | 28 | 24 | 12 | 64
7 | Bogura Grid Circle. | 20 |  | 36 | 56 | 14 | 35 | 26 | 75
8 | Others |  |  |  | 0 |  |  |  | 0
9 | Total | 171 | 38 | 298 | 507 | 117 | 141 | 185 | 443
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April2023
| Area | Previous Month (March' 2023) |  |  |  | Current Month (April '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 161.85 | 1882.33 | 402.67 | 2446.85 | 155.76 | 188.85 | 564.17 | 908.78
2 | Dhaka (South) Grid Circle. | 1156 | 121.4 | 122.83 | 1400.23 | 1031.51 | 20.83 | 17.5 | 1069.84
3 | Chattogram Grid Circle. | 64.48 | 466.5 | 175.67 | 706.65 | 67.12 | 289.33 | 0 | 356.45
4 | Cumilla Grid Circle. | 480 | 73.51 | 3111 | 3664.51 | 114.87 | 472.53 | 409.31 | 996.71
5 | Khulna Grid Circle. | 496.9 | 443.23 | 78.73 | 1018.86 | 137.216 | 129.73 | 276.6 | 543.546
6 | HVDC Grid Circle | 43.37 | 230 | 30 | 303.37 | 5302.9 | 231.93 | 0 | 5534.83
7 | Bogura Grid Circle. | 1227.38 | 676.8 | 208 | 2112.18 | 76.31 | 990.07 | 404.3667 | 1470.7467
8 | Others |  |  |  | 0 |  |  |  | 0
9 | Total | 3629.98 | 3893.77 | 4128.9 | 11652.65 | 6885.686 | 2323.27 | 1671.9467 | 10880.9027
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April2023
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 9 | 5 | 14 | 2 | 2 | 10 | 840.55
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 | 2 | 1 |  | 50.23
3 | Chattogram | 2042 | 10 | 0 | 10 | 4 |  | 6 | 111.6167
4 | Khulna | 2434 | 14 | 6 | 20 | 10 | 1 | 9 | 543.55
5 | HVDC | 5954.3 | 21 | 0 | 21 | 2 | 10 | 9 | 2106.8467
6 | Bogura | 3145.6 | 21 | 10 | 31 | 11 | 0 | 20 | 1323.042
7 | Cumilla | 2981 | 16 | 7 | 23 | 2 | 6 | 14 | 915.7
8 | Others | - | - | - |  | - | - | - | 0
| Total | 30390.1 | [6 empty] | 5891.5353
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.92%
4 | Khulna | 99.93%
5 | HVDC | 99.84% | [6 empty] | Executive Engineer
6 | Bogura | 99.89% | [6 empty] | Information Management Division
7 | Cumilla | 99.9% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April 2023
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | 3 | 7 | 3 | 1 | 0 | - | 68.23
2 | Dhaka (South) | 990.29 |  | 7 | 0 | 7 | 3 | 1 | 3 | - | 1019.62
3 | Chattogram | 917 | - | 4 | 0 | 4 | 0 | 1 | 2 | 3 | 244.83
4 | Khulna | 1238.4 | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | HVDC | 1325 | - | 12 | 0 | 12 | 0 | 3 | 9 | - | 3427.99
6 | Bogura | 1803.3 | - | 1 | 1 | 1 | 0 | 0 | 1 | - | 147.7
7 | Cumilla | 1648.16 | - | 2 | 1 | 3 | 1 | 1 | 1 | - | 81.02
8 | Others | - |  |  | - |  | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 4989.39
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.98%
4 | Khulna | 100%
5 | Bheramara (HVDC) | 99.8% | [7 empty] | Executive Engineer
6 | Bogura | 99.99% | [7 empty] | Information Management Division
7 | Cumilla | 99.99% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:April2023
Type of | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in | [5 empty] | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2023-04-01 | 10 | - | 6 | 07hr25 min | 2 | 01hr07 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/5 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:10 | 40.8333
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:18 | 21.9
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:10 | 40.8333
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:18 | 21.9
Joydebpur 132/33kV Grid Sub-Station | 1 | 0:37 | 24.6667
Kodda 132/33kV Grid Sub-Station | 1 | 2:14 | 0
Kodda 132/33kV Grid Sub-Station | 1 | 2:19 | 34.75
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:53 | 24.4833
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:53 | 24.4833
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:05 | 6.5
Sherpur 132/33kV Grid Sub-Station | 1 | 0:47 | 36.0333
Tongi 230/132/33kV Grid Sub-Station | 1 | 0:34 | 10.2
Mirpur 132/33kV Grid Sub-Station | 1 | 0:18 | 20.1
Tangail 132/33kV Grid Sub-Station | 1 | 0:17 | 14.1667
Mirpur 132/33kV Grid Sub-Station | 1 | 0:23 | 23.7667
Dhamrai 132/33kV Grid Sub-Station | 1 | 2:33 | 25.5
Dhamrai 132/33kV Grid Sub-Station | 1 | 2:33 | 25.5
Kabirpur 132/33kV Grid Sub-Station | 1 | 3:09 | 252
Kabirpur 132/33kV Grid Sub-Station | 1 | 3:11 | 254.6667
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:05 | 6.5
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:35 | 17.5
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:10 | 10.5
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:23 | 22.2333
Haripur 230/132kV Grid Sub-Station | 1 | 0:21 | 17.5
Siddhirganj 132/33kV Grid Sub-Station | 1 | 3:07 | 146.4833
Munshiganj 132/33kV Grid Sub-Station | 1 | 4:27 | 391.6
Munshiganj 132/33kV Grid Sub-Station | 1 | 8:41 | 382.0667
Narshingdi 132/33kV Grid Sub-Station | 1 | 14:53 | 34.4667
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:22 | 26.6667
Hasnabad 132/33kV Grid Substation | 1 | 0:50 | 20.8333
Chandraghona 132/33kV Grid Sub-Station | 1 | 0:13 | 6.0667
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:09 | 13.35
Page: 2/5 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:05 | 7.5
Madunaghat_I 400/230kV Grid Sub-Station | 1 | 1:52 | 7.4667
Madunaghat_I 400/230kV Grid Sub-Station | 1 | 2:16 | 9.0667
Madunaghat_I 400/230kV Grid Sub-Station | 1 | 1:52 | 7.4667
Madunaghat_I 400/230kV Grid Sub-Station | 1 | 1:08 | 4.5333
Bakulia 132/33kV Grid Sub-Station | 1 | 0:13 | 2.1667
Shahmirpur 132/33kV Grid Sub-Station | 1 | 1:46 | 26.5
Shahmirpur 132/33kV Grid Sub-Station | 1 | 1:50 | 27.5
Baroaulia 132/33kV Grid Sub-Station | 1 | 0:38 | 9.5
Baroaulia 132/33kV Grid Sub-Station | 1 | 2:28 | 98.6667
Baroaulia 132/33kV Grid Sub-Station | 1 | 2:06 | 84
Baroaulia 132/33kV Grid Sub-Station |  | 2:38 | 52.6667
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:07 | 2.9167
Sylhet 132/33kV Grid Sub-Station | 1 | 0:44 | 47.6667
Sylhet 132/33kV Grid Sub-Station | 1 | 1:23 | 34.5833
Sylhet 132/33kV Grid Sub-Station | 1 | 0:48 | 12.8
Sylhet 132/33kV Grid Sub-Station | 1 | 0:48 | 12.8
Chauddagram 132/33kV Grid Sub-Station | 1 | 1:03 | 21
Chauddagram 132/33kV Grid Sub-Station | 1 | 1:02 | 20.6667
Cumilla(N) 230/132/33kV Grid Sub-Station | 1 | 0:46 | 30.6667
Cumilla(N) 230/132/33kV Grid Sub-Station | 1 | 0:46 | 30.6667
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 2:01 | 76.6333
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 2:02 | 77.2667
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 0:11 | 4.4
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 5:11 | 124.4
Ramganj 132/33kV Grid Sub-Station | 1 | 1:23 | 27.6667
Ramganj 132/33kV Grid Sub-Station | 1 | 1:23 | 27.6667
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:42 | 31.5
Chhatak 132/33kV Grid Sub-Station | 1 | 0:08 | 2
Sunamganj 132/33kV Grid Sub-Station | 1 | 0:09 | 2.1
Feni 132/33kV Grid Sub-Station | 1 | 5:32 | 138.3333
Feni 132/33kV Grid Sub-Station | 1 | 2:10 | 69.3333
Page: 3/5 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
Kulaura 132/33kV Grid Sub-Station | 1 | 1:17 | 17.9667
Kulaura 132/33kV Grid Sub-Station | 1 | 2:12 | 26.4
Kulaura 132/33kV Grid Sub-Station | 1 | 1:17 | 17.9667
Kulaura 132/33kV Grid Sub-Station | 1 | 2:12 | 26.4
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:48 | 36
Chandpur 132/33kV Grid Sub-Station | 1 | 1:05 | 76.9167
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:13 | 4.3333
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:10 | 2.8333
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:13 | 4.3333
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:13 | 3.6833
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:14 | 4.6667
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:14 | 3.9667
Mongla 132/33kV Grid Sub-Station | 1 | 1:03 | 6.3
Mongla 132/33kV Grid Sub-Station | 1 | 1:26 | 8.6
Satkhira 132/33kV Grid Sub-Station | 1 | 0:17 | 43.9167
Satkhira 132/33kV Grid Sub-Station | 1 | 0:50 | 54.5833
Barishal 230/132kV Grid Sub-Station | 1 | 0:30 | 8
Barishal 132/33kV Grid Sub-Station | 1 | 2:39 | 68.9
Barishal 132/33kV Grid Sub-Station | 1 | 0:34 | 9.0667
Barishal 230/132kV Grid Sub-Station | 1 | 1:41 | 43.7667
Barishal 132/33kV Grid Sub-Station | 1 | 0:28 | 10.2667
Barishal 132/33kV Grid Sub-Station | 1 | 1:28 | 32.2667
Barishal 230/132kV Grid Sub-Station |  | 3:19 | 72.9667
Bagerhat 132/33kV Grid Sub-Station |  | 3:23 | 74.4333
Bagerhat 132/33kV Grid Sub-Station |  | 1:43 | 42.9167
Bagerhat 132/33kV Grid Sub-Station |  | 1:45 | 43.75
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:36 | 15
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:36 | 15
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:34 | 17
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:34 | 17
Ishurdi 230/132kV Grid Sub-Station | 1 | 0:34 | 42.5
Ishurdi 230/132kV Grid Sub-Station | 1 | 0:34 | 42.5
Page: 4/4 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
Ishurdi 230/132kV Grid Sub-Station | 1 | 10:45 | 806.25
Ishurdi 230/132kV Grid Sub-Station | 1 | 10:45 | 806.25
Ruppur 132/11kV Grid Sub-Station | 1 | 0:48 | 0.08
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:37 | 24.6667
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:37 | 24.6667
Kushtia 132/33kV Grid Sub-Station | 1 | 0:23 | 30.6667
Kushtia 132/33kV Grid Sub-Station | 1 | 0:25 | 33.3333
Ruppur 132/11kV Grid Sub-Station | 1 | 0:46 | 3.8333
Shahjadpur 132/33kV Grid Sub-Station | 1 | 1:23 | 30.4333
Shahjadpur 132/33kV Grid Sub-Station | 1 | 1:22 | 20.5
Jashore 132/33kV Grid Sub-Station | 1 | 3:07 | 15.5833
Jashore 132/33kV Grid Sub-Station | 1 | 3:09 | 15.75
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:41 | 42.0833
Jhenaidah 132/33kV Grid Sub-Station | 1 | 2:28 | 61.6667
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:41 | 42.0833
Ishurdi 132/33kV Grid Sub-Station | 1 | 11:13 | 1031.9333
Ishurdi 132/33kV Grid Sub-Station | 1 | 11:01 | 220.3333
Ishurdi 132/33kV Grid Sub-Station | 1 | 10:55 | 709.5833
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:33 | 35.75
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:43 | 0.71667
Ishurdi 132/33kV Grid Sub-Station | 1 | 11:03 | 11.05
Ishurdi 132/33kV Grid Sub-Station | 1 | 10:50 | 650
Ishurdi 132/33kV Grid Sub-Station | 1 | 10:50 | 650
Ruppur 132/11kV Grid Sub-Station | 1 | 0:47 | 1.9583
Ruppur 132/11kV Grid Sub-Station | 1 | 11:04 | 27.6667
Jashore 132/33kV Grid Sub-Station | 1 | 1:29 | 44.5
Jashore 132/33kV Grid Sub-Station | 1 | 1:29 | 44.5
Sirajganj 132/33kV Grid Sub-Station | 1 | 0:16 | 0.8
Sirajganj 132/33kV Grid Sub-Station | 1 | 0:17 | 0.85
Sirajganj 132/33kV Grid Sub-Station | 1 | 0:15 | 0.75
Naogaon 132/33kV Grid Sub-Station | 1 | 0:12 | 13.4
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:13 | 21.9
Jaldhaka 132/33kV Grid Sub-Station | 1 | 0:13 | 5.7417
Jaldhaka 132/33kV Grid Sub-Station | 1 | 0:05 | 2.4167
Page: 5/5 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:April2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:15 | 22.5
Jaldhaka 132/33kV Grid Sub-Station | 1 | 0:13 | 5.7417
Jaldhaka 132/33kV Grid Sub-Station | 1 | 0:05 | 2.2083
Bogura 132/33kV Grid Sub-Station | 1 | 0:08 | 2.1333
Bogura 132/33kV Grid Sub-Station | 1 | 0:11 | 3.6667
Bogura 132/33kV Grid Sub-Station | 1 | 0:11 | 3.6667
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:02 | 31
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:02 | 31
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:34 | 31.3333
Sirajganj 132/33kV Grid Sub-Station | 1 | 2:36 | 52
Sirajganj 132/33kV Grid Sub-Station | 1 | 0:25 | 10.4167
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:51 | 37
Niamatpur 132/33kV Grid Sub-Station | 1 | 15:14 | 380.8333
Niamatpur 132/33kV Grid Sub-Station | 1 | 3:15 | 81.25
Mithapukur 132/33kV Grid Sub-Station | 1 | 1:22 | 17.7667
Mithapukur 132/33kV Grid Sub-Station | 1 | 1:22 | 35.5333
Mithapukur 132/33kV Grid Sub-Station | 1 | 1:19 | 17.1167
Mithapukur 132/33kV Grid Sub-Station | 1 | 1:19 | 17.1167
Saidpur 132/33kV Grid Sub-Station | 1 | 1:36 | 44.8
Saidpur 132/33kV Grid Sub-Station | 1 | 1:38 | 45.7333
Sirajganj 132/33kV Grid Sub-Station | 1 | 10:33 | 147.7
Bog-Sherpur 132/33kV Grid Sub-Station | 1 | 1:59 | 39.6667
Bog-Sherpur 132/33kV Grid Sub-Station | 1 | 2:02 | 40.6667
Bog-Sherpur 132/33kV Grid Sub-Station | 1 | 1:58 | 39.3333
Bog-Sherpur 132/33kV Grid Sub-Station | 1 | 2:04 | 41.3333
Sirajganj 132/33kV Grid Sub-Station | 1 | 4:32 | 54.4
Sirajganj 132/33kV Grid Sub-Station | 1 | 4:34 | 54.8
Purbasadipur 132/33kV Grid Sub-Station | 1 | 1:55 | 67.0833
Purbasadipur 132/33kV Grid Sub-Station | 1 | 1:55 | 67.0833
Grand Total | 157 | 170:40 | 10880.93
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April 2023
Sl. No | Sub-station | Date and time | Load (MW)
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-04-16 10:00 | 66
2 | Agargaon 230/132kV Grid Sub-Station | 2023-04-16 13:00 | 105
3 | Banani 132/33kV Grid Sub-Station | 2023-04-17 12:00 | 89
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-04-16 10:00 | 30
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 202
6 | BashundharaCement 132/33kV Sub-Station | 2023-04-29 11:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2023-04-14 02:00 | 273
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-04-17 19:00 | 178
9 | Charsaidpur 132/33kV Sub-Station | 2023-04-17 23:00 | 50.5
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-04-10 13:00 | 46
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-04-16 20:00 | 130
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-04-17 13:00 | 181
13 | Fatullah 132/33kV Grid Sub-Station | 2023-04-15 15:00 | 70
14 | Ghorashal 132/33kV Sub-Station | 2023-04-17 19:00 | 81
15 | Gulshan 132/33kV Grid Sub-Station | 2023-04-17 13:00 | 156
16 | HaripurSBU 132/33kV Sub-Station | 2023-04-18 13:00 | 164
17 | Hasnabad 132/33kV Grid Substation | 2023-04-16 04:00 | 120
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-04-05 14:00 | 177
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-04-06 12:00 | 317
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-04-16 22:00 | 132
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-04-09 13:00 | 58
22 | Kazla 132/33kV Grid Sub-Station | 2023-04-13 12:00 | 102
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-04-05 15:00 | 82
24 | Kodda 132/33kV Grid Sub-Station | 2023-04-11 10:00 | 328
25 | Lalbag 132/33kV Grid Sub-Station | 2023-04-13 13:00 | 83
26 | Madanganj 132/33kV Grid Sub-Station | 2023-04-12 20:00 | 54
27 | Madartek 132/33kV Grid Sub-Station | 2023-04-16 22:00 | 107
28 | Manikganj 132/33kV Grid Sub-Station | 2023-04-18 20:00 | 135
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-04-18 15:00 | 108
30 | Matuail 132/33kV Grid Sub-Station | 2023-04-16 09:00 | 73
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-04-16 11:00 | 88
32 | Mirpur 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 172
33 | Mogbazar 132/33kV Grid Sub-Station | 2023-04-17 15:00 | 146
34 | Motijheel 132/33kV Grid Sub-Station | 2023-04-17 15:00 | 54
35 | Munshiganj 132/33kV Grid Sub-Station | 2023-04-18 | 121
36 | Narinda 132/33kV Grid Sub-Station | 2023-04-16 13:00 | 83
37 | Narshingdi 132/33kV Grid Sub-Station | 2023-04-19 20:00 | 200
38 | Nawabganj 132/33kV Grid Sub-Station | 2023-04-22 22:00 | 61.4
39 | New Tongi 132/33kV Grid Sub-Station | 2023-04-13 14:00 | 84
40 | Postogola 132/33kV Grid Sub-Station | 2023-04-17 | 49
41 | Purbachal 132/33kV Grid Sub-Station | 2023-04-17 23:00 | 24
42 | Rahim Steel 132/33kV Sub-Station | 2023-04-09 16:00 | 49
43 | Rajendrapur 132/33kV Grid Sub-Station | 2023-04-08 19:30 | 126
44 | Satmasjid 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 149
45 | Savar 132/33kV Grid Sub-Station | 2023-04-13 15:00 | 202
46 | Shitalakhya 132/33kV Grid Sub-Station | 2023-04-18 14:00 | 139
47 | Shyampur 132/33kV Grid Sub-Station | 2023-04-12 11:00 | 194
48 | Siddhirganj 132/33kV Grid Sub-Station | 2023-04-11 10:00 | 132
49 | Sonargaon 132/33kV Grid Sub-Station | 2023-04-16 19:30 | 105
50 | Sreepur 230/132/33kV Grid Sub-Station | 2023-04-15 23:00 | 91
51 | Srinagar 132/33kV Grid Sub-Station | 2023-04-18 21:00 | 54.8
52 | Tongi 230/132/33kV Grid Sub-Station | 2023-04-06 12:00 | 157
53 | Ullon 132/33kV Grid Sub-Station | 2023-04-15 | 59
54 | Uttara 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 111
55 | UttaraNew 132/33kV Grid Sub-Station | 2023-04-29 14:00 | 47
56 | Zigatola 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 100
57 | Agrabad 132/33kV Grid Sub-Station | 2023-04-15 20:00 | 98
58 | AKS 132/33kV Grid Sub-Station | 2023-04-02 14:00 | 16
59 | AKSML 230/33kV Grid Sub-Station | 2023-04-18 14:00 | 123
60 | Bakulia 132/33kV Grid Sub-Station | 2023-04-16 20:00 | 124
61 | Baroaulia 132/33kV Grid Sub-Station | 2023-04-12 | 72
Page: 2/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April 2023
Sl. No | Sub-station | Date and time | Load (MW)
62 | Baroirhat 132/33kV Grid Sub-Station | 2023-04-19 22:00 | 65
63 | BSRM 230/33kV Grid Sub-Station | 2023-04-08 20:00 | 114
64 | Chandraghona 132/33kV Grid Sub-Station | 2023-04-18 19:30 | 35
65 | Coxsbazar 132/33kV Grid Sub-Station | 2023-04-13 21:00 | 145
66 | Dohazari 132/33kV Grid Sub-Station | 2023-04-22 22:00 | 106
67 | GPH 230/33kV Grid Sub-Station | 2023-04-03 20:00 | 97
68 | Halishahar 132/33kV Grid Sub-Station | 2023-04-17 11:00 | 102
69 | Hathazari 230/132/33kV Grid Sub-Station | 2023-04-16 20:00 | 105
70 | Juldah 132/33kV Grid Sub-Station | 2023-04-10 12:00 | 34
71 | Kalurghat 132/33kV Grid Sub-Station | 2023-04-17 11:00 | 38
72 | Kaptai 132/33kV Sub-Station | 2023-04-16 18:30 | 5
73 | Khagrachori 132/33kV Grid Sub-Station | 2023-04-18 19:00 | 36
74 | Khulshi 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 197
75 | KSRM 132/33kV Grid Sub-Station | 2023-04-15 03:00 | 55.5
76 | Madunaghat 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 73
77 | Matarbari 132/33kV Sub-Station | 2023-04-16 07:00 | 98
78 | Mirsorai 230/33kV Grid Sub-Station | 2023-04-16 21:00 | 6.5
79 | Modern Steel 132/11kV Grid Sub-Station | 2023-04-01 | 0
80 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-04-12 19:30 | 41
81 | Rangamati 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 20
82 | Shahmirpur 132/33kV Grid Sub-Station | 2023-04-12 | 56
83 | Shikalbaha 132/33kV Sub-Station | 2023-04-18 20:00 | 38
84 | Sholosohor 132/33kV Grid Sub-Station | 2023-04-06 12:00 | 44
85 | SSM 132/33kV Grid Sub-Station | 2023-04-11 10:00 | 20
86 | TK chemical 132kV Grid Sub-Station | 2023-04-19 23:00 | 34
87 | Ashuganj 230/132/33kV Sub-Station | 2023-04-08 23:00 | 76
88 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-04-20 21:00 | 195
89 | Chandpur 132/33kV Grid Sub-Station | 2023-04-20 22:00 | 80
90 | Chauddagram 132/33kV Grid Sub-Station | 2023-04-17 20:00 | 75
91 | Chowmuhani 132/33kV Grid Sub-Station | 2023-04-18 22:00 | 252
92 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-04-13 23:00 | 208
93 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 201
94 | Daudkandi 132/33kV Grid Sub-Station | 2023-04-18 21:00 | 174
95 | Feni 132/33kV Grid Sub-Station | 2023-04-17 22:00 | 158
96 | Kachua 132/33kV Grid Sub-Station | 2023-04-18 19:30 | 97
97 | PHP 132/33kV Sub-Station | 2023-04-27 11:00 | 9
98 | Ramganj 132/33kV Grid Sub-Station | 2023-04-04 06:00 | 140
99 | Bhaluka 132/33kV Grid Sub-Station | 2023-04-15 19:30 | 184
100 | Jamalpur 132/33kV Grid Sub-Station | 2023-04-20 21:00 | 182
101 | Kishoreganj 132/33kV Grid Sub-Station | 2023-04-26 21:00 | 152
102 | Mymensingh 132/33kV Grid Sub-Station | 2023-04-13 21:00 | 270
103 | Netrakona 132/33kV Grid Sub-Station | 2023-04-26 20:00 | 146
104 | Sherpur 132/33kV Grid Sub-Station | 2023-04-20 22:00 | 174
105 | Tangail 132/33kV Grid Sub-Station | 2023-04-20 22:00 | 288
106 | Beanibazar 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 81
107 | Chhatak 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 37
108 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-04-17 04:00 | 51
109 | Kulaura 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 52
110 | Shahjibazar 132/33kV Grid Sub-Station | 2023-04-12 22:00 | 145
111 | Sreemongol 132/33kV Grid Sub-Station | 2023-04-19 22:00 | 74
112 | Sunamganj 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 62
113 | Sylhet 132/33kV Grid Sub-Station | 2023-04-19 20:00 | 163
114 | Bagerhat 132/33kV Grid Sub-Station | 2023-04-18 20:00 | 108
115 | Benapole 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 80
116 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-04-18 21:00 | 78
117 | Chuadanga 132/33kV Grid Sub-Station | 2023-04-14 21:00 | 120
118 | Faridpur 132/33kV Grid Sub-Station | 2023-04-17 20:00 | 180
119 | Goalpara 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 44
120 | Gollamari 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 61
121 | Gopalganj 132/33kV Grid Sub-Station | 2023-04-19 22:00 | 121.2
Page: 3/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April 2023
Sl. No | Sub-station | Date and time | Load (MW)
122 | Jashore 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 167
123 | Jhenaidah 132/33kV Grid Sub-Station | 2023-04-18 19:30 | 166
124 | Khulna (C) 132/33kV Grid Sub-Station | 2023-04-11 21:00 | 120
125 | Kushtia 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 156
126 | Madaripur 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 129
127 | Magura 132/33kV Grid Sub-Station | 2023-04-17 20:00 | 70
128 | Mongla 132/33kV Grid Sub-Station | 2023-04-18 04:00 | 36
129 | Narail 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 66
130 | Noapara 132/33kV Grid Sub-Station | 2023-04-11 19:30 | 54.5
131 | Rajbari 132/33kV Grid Sub-Station | 2023-04-18 21:00 | 86
132 | Satkhira 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 155
133 | Shariatpur 132/33kV Grid Sub-Station | 2023-04-17 22:00 | 94
134 | Barguna 132/33kV Grid Sub-Station | 2023-04-14 22:00 | 24
135 | Barishal 132/33kV Grid Sub-Station | 2023-04-18 19:00 | 134
136 | Barishal 230/132kV Grid Sub-Station | 2023-04-16 21:00 | 114
137 | Bhandaria 132/33kV Grid Sub-Station | 2023-04-16 21:00 | 60
138 | Borhanuddin 230/33kV Grid Sub-Station | 2023-04-10 21:00 | 72
139 | Patuakhali 132/33kV Grid Sub-Station | 2023-04-20 22:00 | 128
140 | Payra 400/132/33kV Grid Sub-Station | 2023-04-16 22:00 | 24.9
141 | Amnura 132/33kV Grid Sub-Station | 2023-04-21 04:00 | 100
142 | Bhangura 132/33kV Grid Sub-Station | 2023-04-20 22:00 | 56
143 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-04-11 03:00 | 80
144 | Bogura 132/33kV Grid Sub-Station | 2023-04-19 19:00 | 203
145 | Chapai 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 89
146 | Ishurdi 132/33kV Grid Sub-Station | 2023-04-18 21:00 | 86
147 | Joypurhat 132/33kV Grid Sub-Station | 2023-04-19 19:30 | 77
148 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 96
149 | Naogaon 132/33kV Grid Sub-Station | 2023-04-19 19:00 | 159
150 | Natore 132/33kV Grid Sub-Station | 2023-04-18 21:00 | 180
151 | Niamatpur 132/33kV Grid Sub-Station | 2023-04-07 22:00 | 116
152 | Pabna 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 138
153 | Rahanpur_I 400/132kV Grid Sub-Station | 2023-04-08 18:00 | 36
154 | Rajshahi 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 191
155 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-04-18 22:00 | 46
156 | Ruppur 132/11kV Grid Sub-Station | 2023-04-27 11:00 | 6.2
157 | Shahjadpur 132/33kV Grid Sub-Station | 2023-04-17 22:00 | 139
158 | Sirajganj 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 144
159 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-04-20 21:00 | 70
160 | Jaldhaka 132/33kV Grid Sub-Station | 2023-04-08 17:00 | 79
161 | Kurigram 132/33kV Grid Sub-Station | 2023-04-13 19:00 | 70
162 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-04-17 19:00 | 58
163 | Mithapukur 132/33kV Grid Sub-Station | 2023-04-13 19:00 | 71
164 | Palashbari 132/33kV Grid Sub-Station | 2023-04-17 21:00 | 146
165 | Panchagarh 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 59
166 | Purbasadipur 132/33kV Grid Sub-Station | 2023-04-20 21:00 | 135
167 | Rangpur 132/33kV Grid Sub-Station | 2023-04-14 18:30 | 155
168 | Saidpur 132/33kV Grid Sub-Station | 2023-04-11 16:00 | 117
169 | Thakurgaon 132/33kV Grid Sub-Station | 2023-04-19 21:00 | 114
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April 2023
Area | MW | Date | Hour | Remarks
Dhaka | 5390.63 | 2023-04-16 | 22:00
Chattogram | 1554 | 2023-04-16 | 22:00
Cumilla | 1550 | 2023-04-20 | 22:00
Mymensingh | 1175 | 2023-04-15 | 19:30
Sylhet | 611 | 2023-04-17 | 21:00
Khulna | 2018 | 2023-04-19 | 21:00
Barishal | 534.3 | 2023-04-16 | 21:00
Rajshahi | 1777.6 | 2023-04-18 | 21:00
Rangpur | 987 | 2023-04-19 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/4 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:April 2023
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 434 | 2023-04-27 18:00 | 375 | 2023-04-16 13:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 405 | 2023-04-23 19:00 | 365 | 2023-04-16 12:00
3 | Bibiana 400/230kV Sub-Station | 400 | 413 | 2023-04-27 17:00 | 393 | 2023-04-10 13:00
4 | BIPTC | 400 | 408 | 2023-04-01 05:00 | 386 | 2023-04-10 16:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 431 | 2023-04-27 18:00 | 375 | 2023-04-26 20:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 405 | 2023-04-23 19:00 | 373 | 2023-04-12 09:00
7 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 426 | 2023-04-16 19:30 | 371 | 2023-04-10 13:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 245 | 2023-04-27 18:00 | 215 | 2023-04-16 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 241 | 2023-04-01 19:00 | 204 | 2023-04-17 04:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 239 | 2023-04-01 06:00 | 221 | 2023-04-20 10:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 230 | 2023-04-01 06:00 | 200 | 2023-04-10 03:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 248 | 2023-04-27 19:00 | 208 | 2023-04-26 19:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 242 | 2023-04-27 18:00 | 221 | 2023-04-10 12:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 232 | 2023-04-01 06:00 | 210 | 2023-04-09 14:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 240 | 2023-04-15 15:00 | 215 | 2023-04-10 10:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-04-21 19:30 | 219 | 2023-04-10 14:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 247 | 2023-04-23 19:00 | 230 | 2023-04-14 10:00
11 | GPH 230/33kV Grid Sub-Station | 230 | 243 | 2023-04-16 18:00 | 214 | 2023-04-11 11:00
12 | Haripur 230/132kV Grid Sub-Station | 230 | 243 | 2023-04-27 18:00 | 218 | 2023-04-16 12:00
13 | Hasnabad 230/132kV Grid Sub-Station | 230 | 248 | 2023-04-27 18:00 | 219 | 2023-04-13 09:00
14 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-04-15 15:00 | 214 | 2023-04-11 11:00
15 | Ishurdi 230/132kV Grid Sub-Station | 230 | 244 | 2023-04-27 18:00 | 224 | 2023-04-10 12:00
16 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 243 | 2023-04-27 18:00 | 209 | 2023-04-21 22:00
17 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 245 | 2023-04-27 18:00 | 216 | 2023-04-16 11:00
18 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 247 | 2023-04-01 05:00 | 214 | 2023-04-26 20:00
19 | Maniknagar 230/132kV Grid Sub-Station | 230 | 243 | 2023-04-27 18:00 | 216 | 2023-04-11 11:00
20 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 250 | 2023-04-27 18:00 | 224 | 2023-04-17 16:00 |  | 7345
21 | Mirsorai 230/33kV Grid Sub-Station | 230 | 241 | 2023-04-16 16:00 | 213 | 2023-04-11 14:00
22 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 241 | 2023-04-30 19:00 | 218 | 2023-04-21 23:00
23 | Rampura 230/132kV Grid Sub-Station | 230 | 243 | 2023-04-27 18:00 | 217 | 2023-04-16 12:00
24 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 245 | 2023-04-16 19:30 | 215 | 2023-04-15 18:00
25 | Shyampur 230/132kV Grid Sub-Station | 230 | 245 | 2023-04-27 18:00 | 217 | 2023-04-16 12:00
26 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 243 | 2023-04-23 19:00 | 222 | 2023-04-10 12:00
27 | Sirajgonj 230 kV Switching Station | 230 | 246 | 2023-04-27 18:00 | 221 | 2023-04-09 12:00
28 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 243 | 2023-04-27 18:00 | 224 | 2023-04-11 17:00
29 | Tongi 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-04-23 08:00 | 213 | 2023-04-16 13:00
Page: 2/4 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:April 2023
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-23 19:00 | 123 | 2023-04-10 11:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-16 16:00 | 122 | 2023-04-11 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-16 19:00 | 123 | 2023-04-04 12:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-01 05:00 | 122 | 2023-04-22 23:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 147 | 2023-04-27 17:00 | 133 | 2023-04-05 12:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 146 | 2023-04-27 18:00 | 117 | 2023-04-26 20:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-16 19:00 | 121 | 2023-04-16 12:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-27 18:00 | 122 | 2023-04-10 11:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-27 18:00 | 122 | 2023-04-10 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 19:00 | 123 | 2023-04-08 21:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 19:30 | 121 | 2023-04-29 11:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-16 17:00 | 123 | 2023-04-10 14:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-04-27 18:30 | 117 | 2023-04-10 13:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-21 19:00 | 121 | 2023-04-10 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 143 | 2023-04-21 19:00 | 121 | 2023-04-02 22:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-23 11:00 | 121 | 2023-04-29 15:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-01 05:00 | 115 | 2023-04-10 14:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-29 20:00 | 113 | 2023-04-03 18:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-27 19:00 | 117 | 2023-04-21 19:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-01 06:00 | 125 | 2023-04-19 12:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-01 06:00 | 124 | 2023-04-13 18:30
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 138 | 2023-04-08 19:00 | 118 | 2023-04-19 16:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-01 05:00 | 120 | 2023-04-19 12:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 138 | 2023-04-01 05:00 | 122 | 2023-04-11 13:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-01 06:00 | 127 | 2023-04-05 14:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 144 | 2023-04-23 19:00 | 122 | 2023-04-10 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 19:30 | 114 | 2023-04-21 21:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-16 19:00 | 124 | 2023-04-10 10:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-24 18:00 | 125 | 2023-04-21 23:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 143 | 2023-04-21 18:00 | 127 | 2023-04-04 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 19:30 | 117 | 2023-04-10 14:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 20:00 | 122 | 2023-04-22 23:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 19:00 | 113 | 2023-04-22 23:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 17:00 | 113 | 2023-04-17 21:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 136 | 2023-04-15 18:00 | 113 | 2023-04-02 23:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-27 19:00 | 120 | 2023-04-10 14:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-21 19:00 | 124 | 2023-04-10 10:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-23 19:00 | 123 | 2023-04-10 13:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-23 19:00 | 120 | 2023-04-04 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 141.5 | 2023-04-21 18:00 | 125 | 2023-04-16 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-16 19:00 | 117 | 2023-04-19 04:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 18:00 | 122 | 2023-04-18 20:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 145 | 2023-04-21 18:30 | 127 | 2023-04-04 12:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 19:00 | 118 | 2023-04-10 14:00
45 | Ghorashal 132/33kV Sub-Station | 132 | 147 | 2023-04-23 11:00 | 127 | 2023-04-16 15:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-27 17:00 | 122 | 2023-04-26 20:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-27 18:00 | 121 | 2023-04-18 20:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-15 19:30 | 120 | 2023-04-26 20:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 18:00 | 122 | 2023-04-10 14:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-16 15:00 | 122 | 2023-04-15 18:30
51 | HaripurSBU 132/33kV Sub-Station | 132 | 144 | 2023-04-27 18:00 | 127 | 2023-04-16 12:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 142 | 2023-04-27 18:00 | 124 | 2023-04-09 12:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-01 06:00 | 128 | 2023-04-18 21:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 136 | 2023-04-01 05:00 | 113 | 2023-04-09 13:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-29 18:00 | 113 | 2023-04-09 09:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-27 17:00 | 117 | 2023-04-26 20:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 146 | 2023-04-06 04:00 | 123 | 2023-04-28 13:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-04-01 05:00 | 128 | 2023-04-03 15:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 134 | 2023-04-01 05:00 | 113 | 2023-04-09 09:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-15 16:00 | 121 | 2023-04-15 18:30
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-01 05:00 | 118 | 2023-04-10 12:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-27 19:00 | 117 | 2023-04-10 14:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-27 18:00 | 124 | 2023-04-04 12:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-08 16:00 | 124 | 2023-04-11 11:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-23 19:00 | 124 | 2023-04-17 16:00
66 | Kaptai 132/33kV Sub-Station | 132 | 140 | 2023-04-15 15:00 | 120 | 2023-04-24 14:00
Page: 3/4 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:April 2023
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
67 | Kazla 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-27 18:00 | 122 | 2023-04-10 12:00
68 | Khagrachori 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-16 18:00 | 122 | 2023-04-11 11:00 | Remarks
69 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 17:00 | 121 | 2023-04-26 20:00
70 | Khulshi 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-16 18:00 | 120 | 2023-04-11 14:00
71 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-01 06:00 | 115 | 2023-04-20 13:00
72 | Kodda 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-23 19:00 | 123 | 2023-04-29 11:00
73 | KSRM 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-15 13:00 | 123 | 2023-04-10 13:00
74 | Kulaura 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-23 11:00 | 126 | 2023-04-29 12:00
75 | Kurigram 132/33kV Grid Sub-Station | 132 | 135 | 2023-04-01 06:00 | 113 | 2023-04-09 19:30
76 | Kushtia 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-01 06:00 | 120 | 2023-04-21 20:00
77 | Lalbag 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-21 18:00 | 125 | 2023-04-02 12:00
78 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 136 | 2023-04-01 06:00 | 113 | 2023-04-09 19:00
79 | Madanganj 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-21 19:00 | 126 | 2023-04-17 16:00
80 | Madaripur 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-27 19:00 | 122 | 2023-04-26 20:00
81 | Madartek 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-23 19:00 | 123 | 2023-04-10 11:00
82 | Madunaghat 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-16 19:00 | 125 | 2023-04-01 23:00
83 | Magura 132/33kV Grid Sub-Station | 132 | 145 | 2023-04-27 17:00 | 121 | 2023-04-18 21:00
84 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-01 05:00 | 117 | 2023-04-19 13:00
85 | Manikganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-01 05:00 | 124 | 2023-04-19 14:00
86 | Maniknagar 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-27 18:00 | 123 | 2023-04-10 11:00
87 | Matarbari 132/33kV Sub-Station | 132 | 139 | 2023-04-16 19:30 | 113 | 2023-04-09 15:00
88 | Matuail 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-21 19:00 | 126 | 2023-04-01 10:00
89 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-22 07:00 | 118 | 2023-04-01 14:00
90 | Mirpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-27 18:00 | 121 | 2023-04-18 16:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-01 06:00 | 113 | 2023-04-11 13:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 140 | 2023-04-16 17:00 | 121 | 2023-04-16 12:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-27 18:00 | 124 | 2023-04-10 14:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-27 18:00 | 119 | 2023-04-26 20:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-21 18:00 | 122 | 2023-04-10 12:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 18:00 | 126 | 2023-04-17 16:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-29 19:30 | 113 | 2023-04-12 17:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 136 | 2023-04-30 22:00 | 113 | 2023-04-11 12:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-01 06:00 | 118 | 2023-04-17 21:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-21 18:30 | 118 | 2023-04-18 19:30
101 | Natore 132/33kV Grid Sub-Station | 132 | 138 | 2023-04-01 06:00 | 120 | 2023-04-13 19:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-08 18:30 | 124 | 2023-04-17 16:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-29 19:30 | 113 | 2023-04-04 22:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-22 08:00 | 124 | 2023-04-04 10:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-04-30 22:00 | 113 | 2023-04-04 12:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-27 17:00 | 121 | 2023-04-26 20:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-01 06:00 | 121 | 2023-04-13 19:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 137 | 2023-04-01 05:00 | 113 | 2023-04-10 07:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-27 01:00 | 113 | 2023-04-12 19:30
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 19:00 | 124 | 2023-04-01 21:00
111 | PHP 132/33kV Sub-Station | 132 | 139 | 2023-04-27 21:00 | 115 | 2023-04-10 12:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-27 18:00 | 125 | 2023-04-17 16:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-22 05:00 | 122 | 2023-04-10 11:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 135 | 2023-04-01 04:00 | 113 | 2023-04-09 16:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 144 | 2023-04-27 18:00 | 120 | 2023-04-02 10:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-27 18:00 | 122 | 2023-04-18 21:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-01 06:00 | 123 | 2023-04-29 12:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 138 | 2023-04-01 06:00 | 123 | 2023-04-21 23:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-27 19:00 | 113 | 2023-04-23 06:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-16 18:00 | 122 | 2023-04-11 11:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-04-01 06:00 | 114 | 2023-04-09 15:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 140 | 2023-04-01 05:00 | 128 | 2023-04-18 21:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-04-01 05:00 | 113 | 2023-04-09 16:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 145 | 2023-04-27 18:00 | 116 | 2023-04-26 20:00
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 144 | 2023-04-23 19:00 | 122 | 2023-04-16 12:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 18:00 | 120 | 2023-04-15 15:00
127 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-04-01 05:00 | 130 | 2023-04-12 10:00
128 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-20 23:00 | 130 | 2023-04-29 12:00
129 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-16 17:00 | 122 | 2023-04-11 14:00
130 | Shariatpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-27 18:00 | 122 | 2023-04-26 13:00
131 | Sherpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-29 18:00 | 113 | 2023-04-07 09:00
132 | Shikalbaha 132/33kV Sub-Station | 132 | 142 | 2023-04-16 17:00 | 120 | 2023-04-23 02:00
133 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-27 18:00 | 120 | 2023-04-12 16:00
134 | Sholosohor 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-15 15:00 | 119 | 2023-04-16 12:00
135 | Shyampur 132/33kV Grid Sub-Station | 132 | 145 | 2023-04-21 18:00 | 126 | 2023-04-04 12:00
136 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-04-21 18:00 | 127 | 2023-04-13 09:00
137 | Sirajganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-01 05:00 | 121 | 2023-04-19 12:00
Page: 4/4 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:April 2023
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
138 | Sonargaon 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-21 18:30 | 127 | 2023-04-01 10:00
139 | Sreemongol 132/33kV Grid Sub-Station | 132 | 138 | 2023-04-20 23:00 | 127 | 2023-04-29 12:00
140 | Srinagar 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-08 20:00 | 124 | 2023-04-17 16:00
141 | SSM 132/33kV Grid Sub-Station | 132 | 143 | 2023-04-16 19:00 | 127 | 2023-04-10 10:00
142 | Sunamganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-23 11:00 | 119 | 2023-04-22 22:00
143 | Sylhet 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-23 11:00 | 126 | 2023-04-27 13:00
144 | Tangail 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-29 19:30 | 119 | 2023-04-16 12:00
145 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-29 23:00 | 113 | 2023-04-09 12:00
146 | TK chemical 132kV Grid Sub-Station | 132 | 141 | 2023-04-16 17:00 | 124 | 2023-04-10 14:00
147 | Ullon 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-24 05:00 | 122 | 2023-04-10 14:00
148 | Uttara 132/33kV Grid Sub-Station | 132 | 140 | 2023-04-07 18:30 | 120 | 2023-04-18 16:00
149 | UttaraNew 132/33kV Grid Sub-Station | 132 | 141 | 2023-04-01 06:00 | 121 | 2023-04-18 15:00
150 | Zigatola 132/33kV Grid Sub-Station | 132 | 139 | 2023-04-23 18:30 | 124 | 2023-04-17 16:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [5 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:April 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 351 | 401.0449 | 2023-04-05 11:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 332 | 361.884 | 2023-04-05 13:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -258 | 294.9797 | 2023-04-04 12:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -258 | 294.9797 | 2023-04-04 12:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -228 | 231.8361 | 2023-04-29 19:30
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -226 | 229.6889 | 2023-04-29 19:30
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 200 | 207.9639 | 2023-04-05 09:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 234 | 243.6801 | 2023-04-24 15:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 4 | 92.0869 | 2023-04-15 15:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -505 | 510.249 | 2023-04-10 21:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -610 | 612.2981 | 2023-04-10 21:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -147 | 197.5677 | 2023-04-18 22:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 315 | 323.3481 | 2023-04-12 06:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 315 | 323.3481 | 2023-04-12 06:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -84 | 93.4719 | 2023-04-21 22:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -84 | 93.4719 | 2023-04-21 22:00
Rahanpur_I 400/132kV Grid Sub-Station | AT-1 -Gen | 400/132 | 230 | 242.8662 | 2023-04-21 22:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:April 2023
| transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 168 | 237.5879 | 2023-04-11 17:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 217 | 236.4847 | 2023-04-17 19:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 174 | 181.0414 | 2023-04-14
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 174 | 181.0414 | 2023-04-14
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 183 | 190.2446 | 2023-04-14
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 210 | 245.416 | 2023-04-20 22:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 157 | 183.5048 | 2023-04-20 22:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 197 | 206.228 | 2023-04-20 20:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 185 | 203.5927 | 2023-04-20 21:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 240 | 252.6678 | 2023-04-20 21:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 80 | 87.7268 | 2023-04-21 21:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 80 | 87.7268 | 2023-04-21 21:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -118 | 131.928 | 2023-04-20 20:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -118 | 131.928 | 2023-04-20 20:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 190 | 200.4894 | 2023-04-21
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 140 | 205.1828 | 2023-04-10 17:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 257 | 270.0704 | 2023-04-21
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 194 | 207.6343 | 2023-04-21 03:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 185 | 206.6132 | 2023-04-23 05:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 214 | 229.8956 | 2023-04-27 18:30
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 120 | 144.2221 | 2023-04-08 07:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 120 | 144.2221 | 2023-04-08 07:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 120 | 144.2221 | 2023-04-08 07:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 96 | 97.3242 | 2023-04-09 20:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 213 | 213.0845 | 2023-04-23 22:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 224 | 225.0778 | 2023-04-22 09:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 108 | 115.1694 | 2023-04-20 23:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 108 | 115.1694 | 2023-04-20 23:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 108 | 115.1694 | 2023-04-20 23:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 108 | 115.1694 | 2023-04-20 23:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 144 | 151.7893 | 2023-04-20 21:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 144 | 151.7893 | 2023-04-20 21:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 0 | 0 | 2023-04-01 11:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -249 | 265.8007 | 2023-04-10 14:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -189 | 267.9944 | 2023-04-14 23:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 155 | 164.8059 | 2023-04-18 17:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 84 | 86.5852 | 2023-04-25 01:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 155 | 164.8059 | 2023-04-18 17:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -143 | 144.8378 | 2023-04-09 20:00
Page: 2/2 | [5 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:April 2023
substation | transformer | voltage_level | mw | mva | date_time
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -143 | 144.8378 | 2023-04-09 20:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -185 | 187.9202 | 2023-04-06 21:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 182 | 197.2308 | 2023-04-17 14:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 182 | 197.2308 | 2023-04-17 14:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-01 (704T) | 230/132 | -116 | 116.2755 | 2023-04-08 21:00
Rajshahi 230/132/33kV Grid Sub-Station | ATR-02 (714T) | 230/132 | -116 | 116.2755 | 2023-04-08 21:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2023-04-01 12:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 0 | 0 | 2023-04-01 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 210 | 215.1953 | 2023-04-16 15:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 185 | 232.607 | 2023-04-06 14:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 210 | 215.1953 | 2023-04-16 15:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 214 | 244.3768 | 2023-04-30 22:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 214 | 244.3768 | 2023-04-30 22:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 37 | 150.6154 | 2023-04-23 01:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 117 | 125.3555 | 2023-04-02
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 247 | 247.8911 | 2023-04-25 19:30
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 259 | 259.5573 | 2023-04-24
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 132 | 186.6762 | 2023-04-11 18:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 179 | 179.4018 | 2023-04-13 05:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 192 | 271.529 | 2023-04-10 22:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 220 | 222.3151 | 2023-04-17 07:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 215 | 219.0639 | 2023-04-16 19:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:April-2023 | [6 empty] | (For Evening Peak) | [7 empty] | Month:April-2023 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-04-01 | 10593 | 10593 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-01 | 9272 | 9272 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-02 | 11412 | 11412 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-02 | 10102 | 10102 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-03 | 12363 | 12363 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-04-03 | 10525 | 10525 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-04 | 13362 | 13378 | 15 | 21:00 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | - | 2023-04-04 | 11485 | 11485 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-05 | 13253 | 13291 | 35 | 21:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | - | 2023-04-05 | 11833 | 11833 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-06 | 13265 | 13283 | 17 | 21:00 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | - | 2023-04-06 | 12314 | 12314 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-07 | 12813 | 12860 | 43 | 21:00 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | - | 2023-04-07 | 11282 | 11282 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-08 | 13871 | 13951 | 74 | 21:00 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 0 | 0 | - | 2023-04-08 | 11695 | 11924 | 27 | 12:00 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | -
2023-04-09 | 14176 | 14323 | 135 | 21:00 | 0 | 0 | 0 | 0 | 35 | 70 | 30 | 0 | 0 | - | 2023-04-09 | 12331 | 12369 | 35 | 12:00 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | -
2023-04-10 | 14380 | 14598 | 201 | 21:00 | 0 | 0 | 0 | 0 | 15 | 158 | 28 | 0 | 0 | - | 2023-04-10 | 12718 | 12868 | 138 | 12:00 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | -
2023-04-11 | 14800 | 14896 | 88 | 21:00 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | - | 2023-04-11 | 12948 | 13129 | 167 | 12:00 | 38 | 0 | 0 | 0 | 99 | 30 | 0 | 0 | 0 | -
2023-04-12 | 14932 | 15154 | 205 | 21:00 | 42 | 0 | 0 | 0 | 40 | 123 | 0 | 0 | 0 | - | 2023-04-12 | 13242 | 13421 | 165 | 12:00 | 33 | 0 | 0 | 0 | 10 | 90 | 0 | 0 | 32 | -
2023-04-13 | 15304 | 15636 | 306 | 21:00 | 0 | 0 | 0 | 35 | 50 | 206 | 15 | 0 | 0 | - | 2023-04-13 | 13188 | 13402 | 197 | 12:00 | 20 | 0 | 0 | 0 | 20 | 127 | 5 | 0 | 25 | -
2023-04-14 | 14830 | 15031 | 185 | 21:00 | 0 | 0 | 0 | 0 | 30 | 100 | 15 | 0 | 40 | - | 2023-04-14 | 12440 | 12582 | 131 | 12:00 | 18 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 3 | -
2023-04-15 | 13969 | 15000 | 950 | 21:00 | 60 | 80 | 170 | 120 | 120 | 195 | 80 | 35 | 90 | - | 2023-04-15 | 12715 | 13981 | 1167 | 12:00 | 313 | 217 | 0 | 188 | 202 | 155 | 16 | 0 | 76 | -
2023-04-16 | 14599 | 16000 | 1291 | 21:00 | 10 | 0 | 350 | 210 | 240 | 249 | 100 | 0 | 132 | - | 2023-04-16 | 13053 | 13981 | 1103 | 12:00 | 220 | 140 | 150 | 133 | 150 | 150 | 30 | 0 | 130 | -
2023-04-17 | 15604 | 16221 | 589 | 21:00 | 75 | 0 | 10 | 0 | 64 | 275 | 15 | 0 | 150 | - | 2023-04-17 | 13392 | 14550 | 1067 | 12:00 | 200 | 150 | 167 | 130 | 110 | 160 | 30 | 0 | 120 | -
2023-04-18 | 15626 | 16131 | 482 | 21:00 | 0 | 0 | 0 | 25 | 27 | 200 | 80 | 0 | 150 | - | 2023-04-18 | 13307 | 14400 | 1044 | 12:00 | 200 | 140 | 160 | 130 | 110 | 180 | 30 | 4 | 90 | -
2023-04-19 | 15648 | 16096 | 428 | 21:00 | 0 | 0 | 10 | 0 | 120 | 198 | 40 | 0 | 60 | - | 2023-04-19 | 13415 | 13800 | 368 | 12:00 | 0 | 0 | 0 | 0 | 0 | 261 | 107 | 0 | 0 | -
2023-04-20 | 14457 | 14558 | 96 | 21:00 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 25 | - | 2023-04-20 | 12898 | 13200 | 288 | 12:00 | 0 | 0 | 0 | 0 | 118 | 170 | 0 | 0 | 0 | -
2023-04-21 | 9781 | 9781 | 0 | 19:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-21 | 10948 | 11109 | 154 | 12:00 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | -
2023-04-22 | 11584 | 11606 | 21 | 21:00 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | - | 2023-04-22 | 9040 | 9040 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-23 | 9442 | 9442 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-23 | 8226 | 8226 | 0 | 9:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-24 | 10231 | 10231 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-24 | 9061 | 9061 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-25 | 11836 | 11857 | 20 | 21:00 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | - | 2023-04-25 | 9719 | 9719 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-26 | 12155 | 12155 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-26 | 10655 | 10655 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-27 | 7753 | 7753 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-04-27 | 11335 | 11335 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-28 | 12006 | 12100 | 90 | 21:00 | 0 | 0 | 0 | 0 | 25 | 65 | 0 | 0 | 0 | - | 2023-04-28 | 9539 | 9539 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-04-29 | 9235 | 9235 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-04-29 | 11099 | 11116 | 16 | 12:00 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0
2023-04-30 | 11712 | 11801 | 85 | 19:30 | 0 | 0 | 0 | 0 | 20 | 55 | 10 | 0 | 0 |  | 2023-04-30 | 11349 | 11349 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15456
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -
[15 empty] | -222 | 179 | 12
[15 empty] | -332 | 214 | 13
[15 empty] | -201 | 142 | 14
[15 empty] | -1031 | 1266 | 15
[15 empty] | -1401 | 928 | 16
[15 empty] | -617 | 1158 | 17
[15 empty] | -505 | 1093 | 18
[15 empty] | -448 | 385 | 19
[15 empty] | -101 | 302 | 20
[15 empty] | 0 | 161 | 21
[15 empty] | -22 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | -21 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | -94 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:November 2022 | Month:April 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 15648 | 2023-04-19 | 21:00
2 | Maximum Day Peak Genaration | MW | 13415 | 2023-04-19 | 12:00
3 | Maximum Evening Peak Demand | MW | 16221 | 2023-04-30 | 19:30
4 | Minimum Generation | MW | 5602 | 2023-04-01 | 6:00
5 | Average of the daily evening peak Genaration | MW | 12833.0667 | - | -
6 | Average of the daily day peak Genaration | MW | 11504.2 | - | -
7 | Maximum load shed | MW | 1291 | 2022-04-16 | 21:00
8 | Minimum load shed | MW | 0 | 2022-04-16 | 21:00
9 | Total nos. of load shed days | Day | 21 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 178.5333 | - | -
11 | Total Generation | MkWh | 7704.2524 | - | -
12 | Total Generation by BPDB | MkWh | 1652.1779 | % of total Gen. | 21.45%
13 | Total Generation by IPP | MkWh | 2357.3244 | '' | 30.6%
14 | A) Total Generation by Generation Companies | MkWh | 2503.7297 | '' | 32.5%
| B) Total Generation by REB | MkWh | 114.4874 | " | 1.486%
| C) Total Generation by RENTAL | MkWh | 397.804 | " | 5.163%
| D) Total Imported from India (BIPTC) | MkWh | 591.9469 | " | 7.683%
| E) Total Imported from Tripura, India (A.C) | MkWh | 86.7821 | " | 1.126%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4284.183 | % of total Gen. | 55.61%
| B) Oil | MkWh | 1751.942 | '' | 22.74%
| C) Hydro | MkWh | 9.4966 | '' | 0.1233%
| D) Solar | MkWh | 47.6176 | '' | 0.6181%
| E) Coal | MkWh | 932.2843 | '' | 12.1%
| F) BIPTC (Import from India) | MkWh | 591.9469 | '' | 7.683%
| G) A.C (Import from Tripura, India) | MkWh | 86.7821 | '' | 1.126%
16 | Maximun of the daily total Generation . | MkWh | 337.8275 | 2023-04-18
17 | Monthly Load factor | % | 74.4409 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 37382.2735 | - | -
| A) Gas | M.Taka | 4802.249 | - | -
| B) Liquid fuel | M.Taka | 22357.4123 | - | -
| C) Coal | M.Taka | 7010.9732 | - | -
| D) BIPTC (Import from India) | M.Taka | 2586.808 | - | -
| E) Tripura(Import from India) | M.Taka | 624.831 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1971.4583 | 2023-04-10
| A) Gas | M.Taka | 181.9622 | 2023-04-19
| B) Liquid fuel | M.Taka | 1490.9382 | 2023-04-10
| C) Coal | M.Taka | 323.8927 | 2023-04-13
| D) BIPTC (Import from India) | M.Taka | 95.7904 | 2023-04-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.7248
| B) Excluding Hydro & Solar | Taka/kWhR | 5.7662
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.34 | 30/04/2023 | 06:00
b) | Actual | FT (MSL) | 76.14 | 30/04/2023 | 06:00
22 | Peak Genaration of April 2022 | MW | 10389 | 2021-04-11 | 19:00
23 | Peak Demand of April 2022 | MW | 10389 | 2021-04-11 | 19:00
24 | Maximum peak Generation recorded upto 30/04/2023 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 30/04/2023 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 30/04/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | bar: FGMO Status 1 to FGMO Status 31
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | bar: FGMO Status 1; FGMO Status 16 to FGMO Status 31
8 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | bar: FGMO Status 1 to FGMO Status 18; FGMO Status 20 to FGMO Status 25; FGMO Status 29 to FGMO Status 31
9 | Ashuganj 225 MW CCPP | APSCL | 221 | bar: FGMO Status 1 to FGMO Status 11; FGMO Status 16 to FGMO Status 31
10 | Bheramara 410 MW CCPP | NWPGCL | 410
11 | Haripur 412 MW CCPP | EGCB | 412
12 | Fenchugonj CCPP Phase-1 | BPDB | 97
13 | Chandpur 150 MW CCPP | BPDB | 163
14 | Siddhirganj 2x120 MW GTPP | EGCB | 210
15 | Shikalbaha 225 MW CCPP | BPDB | 225
16 | Shikalbaha Peaking GT | BPDB | 150
17 | Shahjibazar 330 MW CCPP | BPDB | 330
18 | Ashuganj 450 MW CCPP(South) | APSCL | 360
19 | Fenchugonj CCPP Phase-2 | BPDB | 104
20 | Bhola 225 MW CCPP | BPDB | 194
21 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
22 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
23 | Siddhirganj 335 MW CCPP | EGCB | 335
24 | Bibiyana-III 400 MW CCPP | BPDB | 400 | bar: FGMO Status 1 to FGMO Status 31
25 | Sylhet 225 MW CCPP | BPDB | 231
26 | RPCL 210 MW CCPP | IPP | 210
27 | Khulna 225 MW CCPP | NWPGCL | 230
28 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
29 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
30 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
31 | Bibiyana South 400 MW CCPP | BPDB | 383
32 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
33 | Shajibazar 100 MW PP | BPDB | 100
34 | Payra 1320 MW Unit-1 | BCPCL | 622
35 | Kushiara 163 MW CCPP (KP) | IPP | 163
36 | Haripur 360MW CCPP(HPL) | IPP | 360
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
38 | Ashuganj 420 MW CCPP(East) | APSCL | 400 | bar: FGMO Status 1 to FGMO Status 11; FGMO Status 18 to FGMO Status 27
39 | Ashuganj 55 MW PP (Precision) | QRPP | 55 | bar: FGMO Status 19
due to gas shortage