## Daily Gen
Hourly Generation & Demand
Date: | 2017-04-05
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 6663 | 6663 | 0
2:00 | 6308 | 6308 | 0
3:00 | 6056 | 6056 | 0
4:00 | 5909 | 5909 | 0
5:00 | 5905 | 5905 | 0
6:00 | 5756 | 5756 | 0
7:00 | 6026 | 6026 | 0
8:00 | 6135 | 6135 | 0
9:00 | 6602 | 6602 | 0
10:00 | 6757 | 6757 | 0
11:00 | 6761 | 6761 | 0
12:00 | 6839 | 6839 | 0 | Day peak
13:00 | 6524 | 6524 | 0
14:00 | 6442 | 6442 | 0
15:00 | 6340 | 6340 | 0
16:00 | 5007 | 5007 | 0
17:00 | 5102 | 5102 | 0
18:00 | 5397 | 5397 | 0
18:30 | 0 | 0 | 0
19:00 | 6631 | 6631 | 0
19:30 | 6904 | 6904 | 0
20:00 | 6911 | 6911 | 0 | Evening peak
21:00 | 6779 | 6779 | 0
22:00 | 6580 | 6580 | 0
23:00 | 6384 | 6384 | 0
24:00 | 5913 | 5913 | 0

## forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [7 empty] | 2017-04-06 | Thursday
|  | Date (day): | 2017-04-06 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8397 | MW |  |  | (b) At Evening Peak Hour : |  | 9456 | MW
Sl. No. | Name of the Power Stations |  | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[8 empty] | On | 2017-04-05 | 2017-04-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Nos. of Unit X Capacity (MW) | MW | MW | MW | MW | MW | MW | MW | MW
1 | a) Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 40 | 40 | 40 | 40 |  | 45 | # 1 under maint.
| b) Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 180 | 100 | 0 | 0
| c) Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 110 | 190 | 190 | 190
| d) Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | 2016-01-10 |  | Long term maint.
| e) Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | #6(18/07/10)(18/07/10) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 91 | 74 | 96 | 100
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 43 | 44 | 45 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 50 | 60 | 70 | 70
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 76 | 82 | 85 | 85 |  | 26 | Engine problem
6 | Haripur GT: Unit-1, 2 |  | Gas | PDB | 2*32 | 64 | 40 | 40 | 40 | 40 | 40
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 390 | 340 | 250 | 300
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 13 | 13 | 110 | 110
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 269 | 336 | 321 | 300 | 24 |  | Gas shortage
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 380 | 400 | 450 | 70 |  | Gas shortage
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 40 | 7 | 90 | 100
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 0 | 0 | 305 | 305
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 81 | 75 | 80 | 100 |  |  | Low demand
14 | Madanganj-55 MW |  | HFO | IPP | 5*17.08+1*11.3 | 55 | 55 | 15 | 15 | 55 | 55
15 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 40 | 10 | 90 | 93 |  | 90 | Engine problem
16 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
17 | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
18 | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 85 | 100 | 210 |  | Gas shortage
19 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 30 | 100 | 100
20 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 96 | 92 | 100 | 100
| Siddhirganj CCPP-335 MW |  | Gas | EGCB |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 20 | 10 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 50 | 102 | 102 |  | 52 | Engine problem
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 6 | 40 | 43 |  | 45 | Engine problem
24 | Kodda Peaking |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 100 | 133 | 133
25 | Northern 55 MW |  | HFO | RPP |  | 55 | 55 | 56 | 18 | 55 | 55
26 | Southern Power |  | HFO | RPP | 3*19.3 | 55 | 55 | 55 | 17 | 55 | 55
27 | CLCPC Keranigonj 108 MW |  | HFO | IPP | 12*8.924 | 108 | 108 | 16 | 16 | 80 | 105
28 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 6*3.67+7*8.73 | 80 | 80 | 58 | 57 | 58 | 58 |  | 23 | Engine problem
29 | Summit Power, Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
30 | Summit Power, Rupganj |  | Gas | SIPP,REB | 4*8.74 | 33 | 33 | 16 | 30 | 33 | 33
31 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 26 | 0 | 43 | 43 |  | 52 | Engine problem
32 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
| Dhaka Area Total |  |  |  |  | 4854 | 4633 | 2509 | 2287 | 3256 | 3415 | 409 | 713
33 | a) Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| b) Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
34 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 18 | 26 | 25
35 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 46 | 40 | 42 | 50
36 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 109 | 95 | 128 | 128 |  | 100 | Unit-2 & 5 Under maint.
37 | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
| Sikalbaha 225 MW |  | Gas | PDB |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
38 | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 130 | 100 | 145 | 145
39 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 42 | 42 | 41 | 51 |  | 9 | Engine problem
40 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 60 | 0 | 60
41 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 48 | 102 | 16 | 102
42 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 50 | 100
43 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 |  | 22 | Transformer problem.
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 2 | 18 | 20 | 20
44 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 84 | 91 | 91 | 97 |  | 17 | Engine problem
| Chittagong area Total |  |  |  |  | 1416 | 1336 | 478 | 576 | 559 | 778 | 220 | 328
45 | a) Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 64 | 53 | 25 | 25 | 25 | 25 |  | 53 | #1 Under maint.
| b) Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 132 | 132 | 132 | 132
| c) Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 150 | 150
| d) Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
46 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 200 | 225 | 225
| Ashuganj CCPP(North) |  | Gas | APSCL |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
47 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 300 | 330 | 360
48 | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 29 | 32 | 29 | 32 |  | 13 | Engine problem
49 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 10 | 10 | 50 |  | Gas shortage
50 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 0 | 0 |  |  | Date expired
51 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 3 | 3 | 7 | 10 | 50 |  | Gas shortage
52 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.7+1*16 | 195 | 195 | 79 | 75 | 105 | 120 | 120 |  | Gas shortage
53 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 33 | 51 | 51 | 51
54 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 30 | 51 | 61 | 85
55 | Titas (Daudkandi) Peaking |  |  | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
56 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 86 | 88 | 85 | 78 |  | Gas shortage
57 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 16 | 0 | 19 | 19
58 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 0 | 11 | 11
** | Tripura |  |  | Imported Power |  | 100 | 100 | 76 | 56 | 77 | 100
59 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
60 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 0 | 0 | 42 | 43
61 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.6+2*6.9 | 25 | 25 | 18 | 0 | 22 | 22
| Comilla Area Total |  |  |  |  | 2140 | 2069 | 1372 | 1334 | 1552 | 1698 | 298 | 66
62 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 108 | 111 | 112 | 112 | 91 |  | Gas shortage
63 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
64 | Jamalpur IPP |  | HFO | IPP | 12*8.9 | 95 | 95 | 40 | 92 | 95 | 95
| Mymensingh Area Total |  |  |  |  | 327 | 319 | 168 | 225 | 229 | 229 | 91 | 0
65 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 60 | 60 | 60 | 60
66 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 60 | 73 | 73
67 | Shahjibazar 330 MW |  | Gas | PDB | 2*110 | 330 | 330 | 171 | 129 | 154 | 164 |  | 201 | GT-2 Under maint.
68 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 17 | 53 | 50 | 51
69 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 17 | 42 | 40 | 40
70 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 8 | 8
71 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 40 | 55 | 55
72 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 50 | 50 | 86
73 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Transformer problem
74 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 69 | 68 | 118 | 120 | 74
75 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18 | 20 |  | Gas shortage
76 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 22 | 48 | 45 | 45
77 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 23 | 24
78 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 341 | 240 | 341 | 341
79 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 0 | 10
| Sylhet Area Total |  |  |  |  | 1431 | 1396 | 857 | 824 | 1017 | 1095 | 94 | 201
80 | Bheramara GT: Unit- 1,2,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 0 | 0 | 30 |  | 30 | # 2 under maint.
81 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Long term maintenance
** | Bheramara Interconnector(HVDC ) |  |  | Imported Power |  | 500 | 500 | 492 | 492 | 499 | 499
82 | a) Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11
| b) Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
83 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 21 | 10 | 110 | 110
84 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 99 | 99 | 99
85 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 43
86 | Khulna CCPP |  | HSD | NWZPGCL | 1*158+1*72 | 230 | 230 | 130 | 120 | 140 | 230
87 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 29 | 0 | 75
| Bharamara 360 MW |  | Gas | NWZPGCL | 1*280+1*140 |  |  | 0 | 0 | 0 | 0 |  |  | On test
88 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
89 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 40 | 55
| Khulna Area Total |  |  |  |  | 1488 | 1419 | 717 | 833 | 928 | 1181 | 0 | 190
90 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 16 | 110 | 110
91 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
92 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 0 | 9 | 13 |  | 33 | Engine problem
93 | Bhola CCPP GT-1,2,ST |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 185 | 105 | 192 | 192
| Barisal Area Total |  |  |  |  | 377 | 367 | 263 | 121 | 311 | 345 | 0 | 33
94 | a) Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 |  |  | Gas shortage
| b) Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
95 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 40
96 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 50 | 0 | 50
97 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50
98 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 8 | 43 | 43 | 43
99 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 44
100 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 180 | 180 | 180 | 180 | 30 |  | Gas shortage
101 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36
102 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
103 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 7 | 7 | 7 |  | 3 | Engine problem
104 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
105 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 809 | 799 | 321 | 513 | 365 | 535 | 30 | 103
106 | a) Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 71 | 83 | 81 | 81
| b) Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 83 | 81 | 80 | 80
107 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 0 |  | 20 | Under maint.
108 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 19 | 19
109 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 0 | 0 | 0 | 0 | 0
| Rangpur Area Total |  |  |  |  | 337 | 240 | 154 | 198 | 180 | 180 | 0 | 20
| Total |  |  |  |  | 13179 | 12578 | 6839 | 6911 | 8397 | 9456 | 1142 | 1654
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6441.1881 | 6509 | 7908.5621 | 8905.9621
A. |  | 2017-04-05 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 6911 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 5007 | MW at | 16:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 6911 | MW
3 | Day peak Generation : |  |  | 6839 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 6509 | MW
4 | Evening peak Generation : |  |  | 6911 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 166.3623 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 115.9139 | MKWHr |  | By Oil: | 30.8227 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.8138 | MKWHr |  | By Hydro: | 2.5488 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 1142 | For Oil: | 0 | MW | Dhaka | 2626 | 2626 | 0
|  |  | For Water Shortage: |  |  | 100 | MW | Chittagong | 710 | 710 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 1654 | MW | Khulna | 832 | 832 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 875.86 | MMCFD |  |  | Rajshahi | 881 | 881 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 62903599.23 | ii) Oil : | Taka | 277718733.444 | Comilla | 267 | 267 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14843383.548 | Total | Taka | 355465716.222 | Mymensingh | 483 | 483 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 224 | 224 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -750 | MW at | 20:00 | hrs | Barisal | 22 | 22 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -500 | MW at | 10:00 | hrs | Rangpur | 464 | 464 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 25° C |  |  | Total | 6509 | 6509 | 0
B. |  | 2017-04-06 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 9456 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6700 | MW
4 | Reserve (Generation end) |  |  |  | 856 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 166.36 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 5169 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.9105 | MKWHr. | ii) During Peak demand: |  | 492 | MW at | 20:00 | hrs. | iii)Maximum: | 495 | 23:00
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.3526 | MKWHr.
*Cost for HVDC & Tripura energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.56 |  | (b) Today: | 86.38 |  | (c) Rule Curve: |  | 87
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2017-04-06
Till now the maximum generation is : - |  |  | 9036 MW | 21:00 | Hrs on | 2016-06-30
The Summary of Yesterday's |  | 2017-04-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6839 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 5169 | MW
Evening Peak Generation : |  | 6911 | MW Hour : | 19:00 | Max Generation : |  | 9456 | MW
E.P. Demand (at gen end) : |  | 6911 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 8600 | MW
Maximum Generation : |  | 6911 | MW Hour : | 20:00 | Reserve (Generation end) |  | 856 | MW
Total Gen. (MKWH) : |  | 166.3623 | System L/ Factor : | 100.3% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -500 | MW at | 10:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2017-04-06
Actual : | 86.38 | Ft.(MSL) , | Rule curve : | 87 | Ft.( MSL )
Gas Consumed : | Total | 875.86 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 62903599.23
|  | Coal : | 14843383.548 | Oil : | 277718733.444 | Total : | 355465716.222
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3232 |  |  | - | -
Chittagong Area | 0 | 0:00 | 904 |  |  | - | -
Khulna Area | 0 | 0:00 | 916 |  |  | - | -
Rajshahi Area | 0 | 0:00 | 884 |  |  | - | -
Comilla Area | 0 | 0:00 | 665 |  |  | - | -
Mymensingh Area | 0 | 0:00 | 505 |  |  | - | -
Sylhet Area | 0 | 0:00 | 324 |  |  | - | -
Barisal Area | 0 | 0:00 | 177 |  |  | - | -
Rangpur Area | 0 | 0:00 | 492 |  |  | - | -
Total | 0 |  | 8099 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010) |  | 10) Sikalbaha ST
| Nil |  |  | 2) Kaptai Unit-2 & 5 |  | 11) Siddhirgonj GT: Unit-1& 2
|  |  |  | 3) Ashuganj ST: Unit- 1 |  | 12) Siddhirgonj ST
|  |  |  | 4) Khulna ST 110 MW (04/11/2014) |  | 13) Tongi GT
|  |  |  | 5) Ghorasal Unit-1,5,6 |  | 14) Shahjibazar (Energyprima)
|  |  |  | 6) Baghabari 100 MW |  | 15) Ghorasal unit-3
14) Tongi GT
8) Chittagong Unit-1,2
9) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Comments on Power Interruption
a) Feni 132/33 kV T-2 transformer was under shut down from 09:11 to 12:05 due to Red hotat 33 kV CT R phase, B phase.
b) Ashugonj-Kishoregonj 132 Ckt-2 tripped at 12:23 from both end showing Dist. B,C from Ashugonj end and from Dist. B,C
from Kishoregonj and switched on at 12:26.
c) Hathazari-Kaptai 132 kV Ckt-1 was under shut down from 09:12 to 18:21.
d) Feni-Comilla(N) 132 kV line tripped at 12:26 from both end showing Dist. A,B,C,Z2 from Comilla(N) and Dist. A,Z1
from Feni and switched on at 11:11(06/04/2017).
e) Sylhet 132/33 kV T-2 transformer 33 kV bus was under shut down from 10:14 to 11:08 due to Red hot at 33 kV side.
f) Sylhet 132/33 kV T-1 transformer was under shut down from 11:22 to 13:53 due to Red hot at 33 kV Bus.
g) Kulaura 132/33 kV T-1 transformer was tripped at 13:26 showing O/C and switched on at 13:56.
h) Comilla(S)-S.M.Nagar both Ckt tripped at 12:25 showing C phase,Z1 at Comilla end and switched on at 13:02 and 13:38
respectively.
i) Comilla(N)-Feni 132 kV Ckt-1 tripped at 14:44 from Comilla end showing Dist. A,B phase,Z2,ARC and switched on at 14:53.
j) Ashugonj - B. Baria 132 kV Ckt-2 was tripped at 15:12 from both ends showing Dist. A,B phase at network end and
Dist. Z1,Z2 at B.Baria end and switched on at 15:43.
k) Feni-Hat hazari 132 kV Ckt-2 was tripped at 15:49 from Feni end showing Dist. A,Z1 and switched on at 16:15.
l) Ashugonj-Kishoregonj 132 kV Ckt-2 was tripped at 16:00 from both ends showing Dist. A at Ashugonj and Dist. B,C
at Kishoregonj end.
m) Baraulia 132/33 kV T-1 & T-2 transformers were tripped at 16:30 at 33 kV side only due to 33 kV Feeder fault and |  |  |  | About 48 MW power interruption occurred under Baraulia S/S area
switched on at 17:10. |  |  |  | from 16:30 to 17:10.
n) Bhola-Barisal 230 kV was tripped at 19:06 from both ends showing Dist at Bhola end and Dist. Z1,L3 trip and switched
on at 21:28.
o) Barisal-Bhandaria 132 kV Ckt tripped at 18:29 from both ends showing Dist. C from Barisal end and Dist. Z1 from
Bhandaria and tried to switched on at 20:30 and tripped again showing SOTF.
p) Hasnabad 33 kV bus was shut down at 21:45 to attend Red hot at 33 kV REB feeder.
q) Bhola 225 MW CCPP STG was shut down at 21:06 for maintenance.
r) EGCB 412 CCPP ST was shut down at 01:14 due to High positive ion in water.
s) Ghorasal P/S unit-3 tripped at 01:45 showing condenser vacumme pressure low.
t) Kodda PPP tripped at 23:20 showing fuel line problem and synchronized at 05:21(06/04/2017).
u) Ullon ring bus closed and Shiddhirgonj 132 kV Ckt-1&2 opened from ullon end at 06:05.
v) Cox'sbazar S/S 33 kV Bus is shut down at 06:14 (06/04/2017) for bus extension work and closed at 08:44. |  |  |  | About 50 MW power interruption occurred under Cox'sbazar S/S area
w) Ashugonj-Comila 230 kV Ckt-1 has been shut down at 07:09 due to Red hot at isolator at Ashugonj end. |  |  |  | from 06:14 (06/04/2017) to 08:44.
x) Bhola GT-1&2 have been shut down at 07:03 and 07:14 respectively.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Dispatch Circle |  | Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2017-04-05 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1a | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 0 | 861000 | Under maint.
40
1b | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 100 | 3632580 | Machine problem
1c | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 190 | 3119445 | 0
1d | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 0 | 0 | Under maint.
1e | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 |  | Long term maint.
2 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 74 | 1859370 | Low demand
3 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 44 | 1012600 | 0
4 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 60 | 1450400 | Low demand
5 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 82 | 17302227 | Engine problem
6 |  |  | 1*32 | PDB | 20 | 40 | 905900
| Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 0
|  |  | 1*32 | PDB | 0 | 0 |  | Under maint.
7 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 340 | 8805000 | Low demand
8 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 13 | 181500 | Low demand
9 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 336 | 7266000 | Frequency control
10 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 380 | 8806000 | Gas shortage
11 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 7 | 463680 | Low demand
12 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 305 | 0 | 0 | Reserve
13 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 75 | 1344768 | Low demand
14 | Madanganj-55 MW |  | 5*17.08+1*11.3 | IPP | 55 | 15 | 138434 | Low demand
15 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 10 | 441211 | Low demand
16 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 22 | 429300 | 0
17 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 0 | 0 | Machine problem
18 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 0 | 124000 | Gas shortage
19 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 100 | 30 | 119040 | Low demand
20 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 92 | 1334400 | Engine problem
| Siddhirganj CCPP-335 MW |  |  | EGCB |  | 0 | 0 | On test.
21 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 10 | 147750 | Low demand
22 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 50 | 905328 | Low demand
23 | Katpotti 52 MW |  |  | RPP | 51 | 6 | 103200 | Low demand
24 | Kodda Peaking |  | 9*17.06 | BPDB-RPCL | 149 | 100 | 1959840 | Low demand
25 | Northern 55 MW |  |  | RPP | 55 | 18 | 5324222 | Low demand
26 | Southern Power |  |  | RPP | 55 | 17 | 546670 | Low demand
27 | CLCPC Keranigonj 108 MW |  |  |  | 108 | 16 | 271680 | Low demand
28 | Summit Power,(Madhabdi+Ashulia) |  | 6*3.67+7*8.73 | SIPP, REB | 80 | 57 | 1248600 | Engine problem
29 | Summit Power, Maona |  | 4*8.73 | SIPP, REB | 33 | 33 | 700000 | 0
30 | Summit Power, Rupganj |  | 4*8.74 | SIPP, REB | 33 | 30 | 608900
31 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 0 | 499992 | Engine problem
32 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Under maintenance.
| Dhaka Area Total |  |  |  | 4633 | 2287 | 71913037
33 | a) Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 0 | 0 | Gas shortage
| b) Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint.
34 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 18 | 308160 | Low demand
35 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 40 | 815520 | Low demand
36 | Chittagong ECPV 108 MW |  |  | IPP | 108 | 91 | 1717440 | Engine problem
37 |  |  | 1*40 | PDB | 40 | 30 | 1648251
|  |  | 1*40 | PDB | 40 | 0 |  | Under maint.
| Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 35
|  |  | 1*50 | PDB | 50 | 30 | 900500
|  |  | 1*50 | PDB | 50 | 0 |  | Under maint.
38 | Shikalbaha ST |  | 1*60 | PDB | 40 | 0 | 0 | Gas shortage
| Shikalbaha 225 MW |  |  | PDB
39 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 100 | 2411468 | Frequency control
40 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 60 | 395355 | 0
41 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 102 | 1086579 | 0
42 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 10 | 140640 | Engine problem
43 | Shikalbaha (Energis) |  |  | RPP | 51 | 42 | 751680 | 0
44 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 0 | 0 | Transformer problem
* | Malancha, Ctg EPZ(United) |  |  |  |  | 18 | 376323
| Chittagong Area Total |  |  |  | 1336 | 576 | 10551916
45 | a) Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 53 | 0 | 593696 | #1 under maint.
|  |  | 1*64 | APSCL |  | 25 |  | 0
| b) Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 132 | 3163520 | 0
| c) Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 150 | 3572095 | 0
| d) Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 135 | 3235814
46 | Ashuganj CCPP 225 MW |  | 1*142+1*75 | APSCL | 221 | 200 | 7901880 | Frequency control
| Ashuganj CCPP(North) |  |  | APSCL |  | 0 | 0 | Under maint.
47 | Ashuganj CCPP(South) |  |  | APSCL | 360 | 300 | 4811200 | Frequency control
48 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 32 | 646056 | Engine problem
49 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 5 | 150720 | Gas shortage
50 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 0 | 0 | Date expired
51 | Ashuganj (United) |  | 14*4 | RPP | 53 | 3 | 72000 | Gas shortage
52 | Ashuganj Modular 200 MW |  | 20*9.7+1*16 | IPP | 195 | 75 | 1906909 | Gas shortage
53 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 51 | 843868
54 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 51 | 874520 | Gas shortage
55 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 0 | 0 | Reserve
56 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 86 | 2022260 | 0
57 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 0 | 221292
58 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 0 | 52740 | Low demand
** | Tripura |  |  |  | 100 | 56 | 1352640 | 0
59 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 33 | 652200 | 0
60 | Lakdanavi-52 MW |  |  | IPP | 52 | 0 | 0 | Reserve
61 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 0 | 371000 | feeder tripped
| Comilla Area Total |  |  |  | 2069 | 1334 | 32444410
62 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 111 | 2421000 | Gas shortage
63 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 22 | 486861 | 0
64 | Jamalpur RPP |  |  | IPP | 95 | 92 | 690376 | 0
| Mymensingh Area Total |  |  |  | 319 | 225 | 3598237
65 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 60 | 1315000 | 0
66 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 60 | 1441800 | 0
67 | Shahjibazar CCPP 330 MW |  | 2*110 | PDB | 330 | 129 | 2655570 | Under maint.
68 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 53 | 600000
69 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 42 | 521000 | 0
70 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 0 | 22800 | Engine problem
Engine problem
71 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 40 | 1082000 | Frequency control
72 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 50 | 816000 | Frequency control
73 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 0 | 0 | Under maint.
74 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 68 | 2212070 | Frequency control
75 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 0 | 0 | Engine problem
76 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 48 | 546240 | 0
77 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 24 | 524400 | 0
78 | Summit Bibiana-2 |  | 1*222+1*119 | IPP | 341 | 240 | 688620
79 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 10 | 119520 | 0
| Sylhet Area Total |  |  |  | 1396 | 824 | 12545020
|  |  | 1*20 | PDB | 16 | 0 | 170338
80 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 0
|  |  | 1*20 | PDB | 16 | 0 |  | Long term maint.
** | Bheramara Interconnector(HVDC) |  |  | Imported Power | 500 | 492 | 11910545 | 0
81 | a) Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint.
| b) Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
82 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 10 | 434400 | Low demand
83 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 99 | 1320000 | Engine problem
84 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 43 | 311040 | 0
85 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 230 | 120 | 3120960 | Low demand
86 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 29 | 0 | Low demand
87 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
| Bheramara 360 MW |  | 1*280+1*140 | NWZPGCL |  | 0 | 0 | On test
88 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 40 | 601500 | 0
89 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 0 | 0 | Reserve
| Khulna Area Total |  |  |  | 1419 | 833 | 17868783
90 | Summit Barisal 110MW |  | 7*17.076 | IPP | 110 | 16 | 1459200 | 0
91 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 0 | 0
|  |  | 1*20 | PDB | 14 | 0
92 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 0 | 240558 | Engine problem
93 | Bhola CCPP GT-1,2,ST |  | 2*63+1*68 | PDB | 194 | 105 | 3854297 | Low demand
| Barisal Area Total |  |  |  | 367 | 121 | 5554055
94 | a) Baghabari GT |  | 1*71 | PDB | 71 | 0 | 0 | Under maint.
| b) Baghabari GT |  | 1*100 | PDB | 100 | 0 | 0 | Under maint.
95 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 32 | 173672 | Low demand
96 | Bera Peaking |  | 9*8.29 | PDB | 71 | 50 | 136584 | 0
97 | Amnura |  | 7*7.79 | QRPP | 50 | 50 | 770160 | 0
98 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 43 | 313640 | 0
99 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 39 | 253928 | 0
100 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 180 | 4611545 | Gas shortage
101 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 36 | 217981 | 0
102 | Bogra (GBB) |  | 6*4 | RPP | 22 | 22 | 513200 | 0
103 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 10 | 7 | 173700 | 0
104 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 197334 | 0
105 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 43 | 628320 | 0
| Rajshahi Area Total |  |  |  | 799 | 513 | 7990064
106 | a) Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 83 | 1866764 | 0
| b) Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 81 | 1947055 | 0
107 | Rangpur GT |  | 1*20 | PDB | 20 | 16 | 36000 | 0
108 | Saidpur GT |  | 1*20 | PDB | 20 | 18 | 47000 | 0
109 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 0 | 0 | 0
| Rangpur Area Total |  |  |  | 240 | 198 | 3896819
| Total |  |  |  | 12578 | 6911 | 166362341
| Eastern Grid Total |  |  |  | 8488 | 5246 | 131052620
| Western Grid Total |  |  |  | 2600 | 1665 | 35309721
| National Grid Total |  |  |  | 11088 | 6911 | 166362341
*Data collected from respective power station over telephone.

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2017-04-05 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4310 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2199 | MW
i) Dhaka area |  |  | 2626 | MW | i) Khulna area |  |  | 832 | MW
ii) Chittagong area |  |  | 710 | MW | ii) Rajshahi area |  |  | 881 | MW
iii) Comilla area |  |  | 267 | MW | iii) Barisal area |  |  | 22 | MW
iv) Mymensingh area |  |  | 483 | MW | iv) Rangpur area |  |  | 464 | MW
v) Sylhet area |  |  | 224 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 6509 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1100 | Kishorganj | 53 | 2000 | Jessore | 128 | 1900
Munsiganj | 82 | 100 | Netrokona | 38 | 1900 | Jhenida | 72 | 2000
Megnaghat | 43 | 2100 | Jamalpur | 86 | 1930 | Bottail | 84 | 2000
Shyampur | 167 | 1200 | Sherpur | 48 | 1930 | G.K Project | 41 | 2000
Bhulta | 125 | 100 | Srimongal | 22 | 2100 | Faridpur | 100 | 100
Madanganj | 43 | 100 | Shahjibazar | 42 | 1930 | Madaripur | 88 | 100
Shitalakhya | 98 | 1000 | Fenchuganj | 14 | 1700 | Gopalganj | 42 | 100
Rahim steel | 7 | 900 | Khulawara | 20 | 2100 | Bagerhat | 52 | 2100
Matuail | 66 | 900 | Sylhet | 113 | 2100 | Mongla | 37 | 1000
Ghorasal | 69 | 100 | Chatak | 30 | 1900 | Satkhira | 71 | 1930
Narsingdi | 73 | 2100 | Comilla (S) | 66 | 1830 | Gallamari | 40 | 1200
Haripur (SBU) | 68 | 1930 | Comilla(N) | 51 | 1830 | Magura | 30 | 2100
Ullon | 66 | 1900 | Chandpur | 57 | 1100 | Chuadanga | 62 | 2000
Hasnabad | 135 | 1400 | Feni | 48 | 1400 | Barisal | 74 | 100
Magbazar | 114 | 1300 | Chowmuhani | 80 | 1200 | Patuakhali | 40 | 100
Maniknagar | 72 | 1400 | Ashuganj | 30 | 2000 | Bhandaria | 32 | 1830
Bangabhaban | 38 | 1000 | Daudkandi | 46 | 700 | Ishurdi | 35 | 1900
Narinda | 88 | 1300 | B.Baria | 63 | 2000 | Natore | 81 | 1900
Dhanmondi | 118 | 1200 | Madanhat | 51 | 1500 | Bogra | 185 | 2000
Lalbag | 91 | 1300 | Hathazari | 67 | 2100 | Noagaon | 86 | 1930
Madartek | 47 | 100 | Khulshi | 152 | 1300 | Rajshahi | 112 | 2200
Mirpur | 93 | 1400 | Halishahar | 103 | 1930 | C.Nawabganj | 60 | 2000
Kalyanpur | 99 | 1500 | Baraulia | 115 | 1300 | Amnura | 29 | 1900
Gulshan | 106 | 1200 | Sikalbaha | 18 | 1200 | Pabna | 77 | 1930
Uttara | 75 | 1200 | Dohazari | 38 | 1300 | Shahjadpur | 67 | 900
Kamrangirchar | 63 | 1200 | Cox'sbazar | 64 | 2000 | Serajganj | 70 | 900
Savar | 102 | 1000 | Chandraghona | 18 | 1400 | Niyamatpur | 66 | 1900
Bhasantec | 105 | 1200 | Kaptai | 4 | 2000 | Joypurhat | 30 | 1930
Agargaon | 39 | 1400 | A. Khaer Stl. | 10 | 1200 | Rangpur | 89 | 1930
Satmosjid | 70 | 1400 | Bakulia | 91 | 1500 | Lalmonirhat | 62 | 2100
Tongi | 109 | 1100 | Julda | 21 | 1300 | Saidpur | 83 | 1930
Kabirpur | 145 | 900 | TK chemical | 4 | 1200 | Purbasadipur | 66 | 2100
Basundhara | 97 | 1300 | Modern Steel | 16 | 1600 | Thakurgaon | 50 | 1900
Manikganj | 75 | 900 | Shahmirpur | 19 | 1700 | Palashbari | 65 | 1930
Joydevpur | 183 | 1300 | Abul Khair 230 | 190 | 1200 | Barapukuria | 33 | 2100
New Tongi | 103 | 1000 | BSRM | 70 | 1200 | Panchagar | 30 | 1930
Korda | 125 | 1200 | Goalpara | 20 | 1900
Tangail | 139 | 2100 | Central s/s | 75 | 1900
Mymensing | 137 | 2000 | Noapara | 72 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## L.curve
Date | 2017-04-05 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -680 | 5390 | 1736 | 7126 | -680 | 7126 | 0:00 | DAILY LOAD CURVE | 2017-04-05
0:30 | -650 | 5188 | 1706.5 | 6894.5 | -620 | 6894.5 | 1:00
1:00 | -620 | 4986 | 1677 | 6663 | -640 | 6663 | 2:00
1:30 | -630 | 4901.5 | 1584 | 6485.5 | -620 | 6485.5 | 3:00
2:00 | -640 | 4817 | 1491 | 6308 | -600 | 6308 | 4:00
2:30 | -630 | 4771 | 1411 | 6182 | -620 | 6182 | 5:00
3:00 | -620 | 4725 | 1331 | 6056 | -680 | 6056 | 6:00
3:30 | -610 | 4650.5 | 1332 | 5982.5 | -720 | 5982.5 | 7:00
4:00 | -600 | 4576 | 1333 | 5909 | -640 | 5909 | 8:00
4:30 | -610 | 4577 | 1330 | 5907 | -530 | 5907 | 9:00
5:00 | -620 | 4578 | 1327 | 5905 | -500 | 5905 | 10:00
5:30 | -650 | 4508.5 | 1322 | 5830.5 | -520 | 5830.5 | 11:00
6:00 | -680 | 4439 | 1317 | 5756 | -540 | 5756 | 12:00
6:30 | -700 | 4561 | 1330 | 5891 | -680 | 5891 | 13:00
7:00 | -720 | 4683 | 1343 | 6026 | -640 | 6026 | 14:00 |  |  |  | 6911 | 20:00
7:30 | -680 | 4710.5 | 1370 | 6080.5 | -640 | 6080.5 | 15:00 |  |  |  | 6839 | 12:00
8:00 | -640 | 4738 | 1397 | 6135 | -660 | 6135 | 16:00
8:30 | -585 | 4912 | 1456.5 | 6368.5 | -520 | 6368.5 | 17:00
9:00 | -530 | 5086 | 1516 | 6602 | -520 | 6602 | 18:00
9:30 | -515 | 5158.5 | 1521 | 6679.5 | -680 | 6679.5 | 18:30
10:00 | -500 | 5231 | 1526 | 6757 | -760 | 6757 | 19:00
10:30 | -510 | 5255 | 1504 | 6759 | -740 | 6759 | 19:30
11:00 | -520 | 5279 | 1482 | 6761 | -750 | 6761 | 20:00
11:30 | -530 | 5331.5 | 1468.5 | 6800 | -770 | 6800 | 21:00
12:00 | -540 | 5384 | 1455 | 6839 | -770 | 6839 | 22:00
12:30 | -610 | 5258 | 1423.5 | 6681.5 | -700 | 6681.5 | 23:00
13:00 | -680 | 5132 | 1392 | 6524 | -740 | 6524 | 24:00
13:30 | -660 | 5046.5 | 1380 | 6426.5 |  | 6426.5
14:00 | -640 | 4961 | 1368 | 6329 | 128.92 | 6329
14:30 | -640 | 4317.5 | 1373.5 | 5691 | 86.5 | 5691
15:00 | -640 | 3674 | 1379 | 5053 |  | 5053
15:30 | -650 | 3674 | 1356 | 5030 | 7867500 | 5030
16:00 | -660 | 3674 | 1333 | 5007 |  | 5007
16:30 | -590 | 3718 | 1336.5 | 5054.5 |  | 5054.5
17:00 | -520 | 3762 | 1340 | 5102 | 700 | 5102
17:30 | -520 | 3862.5 | 1387 | 5249.5 | 1800 | 5249.5
18:00 | -520 | 3963 | 1434 | 5397 | 100 | 5397
18:30 | -680 | 4500 | 1514 | 6014 | 1400 | 6014
19:00 | -760 | 5037 | 1594 | 6631 | 100 | 6631
19:30 | -740 | 5216 | 1688 | 6904 | 1800 | 6904
20:00 | -750 | 5246 | 1665 | 6911 | 1800 | 6911
20:30 | -760 | 5206 | 1639 | 6845 | 1800 | 6845
21:00 | -770 | 5166 | 1613 | 6779 | 2100 | 6779
21:30 | -770 | 5111.5 | 1568 | 6679.5 | 1900 | 6679.5
22:00 | -770 | 5057 | 1523 | 6580 | 1900 | 6580
22:30 | -735 | 5001.5 | 1480.5 | 6482 |  | 6482
23:00 | -700 | 4946 | 1438 | 6384 |  | 6384
23:30 | -720 | 4834.5 | 1314 | 6148.5 |  | 6148.5
24:00 | -740 | 4723 | 1190 | 5913 |  | 5913
*MAX.GEN.(E.P.) |  | 6911 |  | 20:00
*MAX.GEN.(D.P.) |  | 6839 |  | 12:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
6911 MW (20:00)
6839 MW (12:00)

## En.Curve
QF-LDC-12
Date | 2017-04-05 |  | Energy | 166362341 | 0
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | Tripura |  | DAILY ENERGY CURVE |  | 2017-04-05
0:00 | 999 | 492 | 3439 | 1166 | 165 | 118 | 200 | 0 | 90
0:30 | 979.5 | 492 | 3369 | 1067 | 165 | 119 | 179 | 0 | 87
1:00 | 960 | 492 | 3299 | 968 | 165 | 120 | 158 | 0 | 84
1:30 | 951.5 | 492.5 | 3300.5 | 842 | 165 | 120 | 99.5 | 0 | 83 | [5 empty] | 166.3623
2:00 | 943 | 493 | 3302 | 716 | 165 | 120 | 41 | 0 | 82 | [5 empty] | 0
2:30 | 1003.5 | 493.5 | 3306 | 558.5 | 165 | 111 | 28.5 | 0 | 81 | [5 empty] | 166.3623
3:00 | 1064 | 494 | 3310 | 401 | 165 | 102 | 16 | 0 | 80
3:30 | 1069 | 494 | 3291 | 345 | 166 | 102 | 16 | 0 | 74
4:00 | 1074 | 494 | 3272 | 289 | 167 | 102 | 16 | 0 | 68
4:30 | 1091 | 494 | 3260.5 | 286 | 166 | 102 | 16 | 0 | 69
5:00 | 1108 | 494 | 3249 | 283 | 165 | 102 | 16 | 0 | 70
5:30 | 1141 | 494 | 3143 | 283 | 163 | 103.5 | 16 | 0 | 68
6:00 | 1174 | 494 | 3037 | 283 | 161 | 105 | 16 | 0 | 66
6:30 | 1176 | 493 | 3098.5 | 337.5 | 163 | 115.5 | 16 | 0 | 63
7:00 | 1178 | 492 | 3160 | 392 | 165 | 126 | 16 | 0 | 60
7:30 | 1169.5 | 493 | 3169.5 | 457.5 | 162 | 109.5 | 16 | 0 | 61
8:00 | 1161 | 494 | 3179 | 523 | 159 | 93 | 16 | 0 | 62
8:30 | 1176 | 494 | 3209.5 | 691 | 159 | 97.5 | 33.5 | 0 | 62
9:00 | 1191 | 494 | 3240 | 859 | 159 | 102 | 51 | 0 | 62
9:30 | 1168.5 | 494 | 3255.5 | 968.5 | 160.5 | 106 | 49.5 | 0 | 67
10:00 | 1146 | 494 | 3271 | 1078 | 162 | 110 | 48 | 0 | 72
10:30 | 1166 | 493.5 | 3213.5 | 1126 | 158.5 | 109.5 | 48 | 0 | 73
11:00 | 1186 | 493 | 3156 | 1174 | 155 | 109 | 48 | 0 | 74
11:30 | 1194.5 | 492.5 | 3187.5 | 1174 | 154.5 | 109 | 48 | 0 | 74
12:00 | 1203 | 492 | 3219 | 1174 | 154 | 109 | 48 | 0 | 74
12:30 | 1184.5 | 492 | 3129.5 | 1149 | 156 | 110.5 | 48 | 0 | 75
13:00 | 1166 | 492 | 3040 | 1124 | 158 | 112 | 48 | 0 | 76
13:30 | 1136.5 | 491.5 | 3045 | 1103 | 159 | 112 | 40 | 0 | 77
14:00 | 1107 | 491 | 3050 | 1082 | 160 | 112 | 32 | 0 | 78
14:30 | 1080 | 491.5 | 3032 | 1072.5 | 159 | 103 | 40 | 0 | 77
15:00 | 1053 | 492 | 3014 | 1063 | 158 | 94 | 48 | 0 | 76
15:30 | 1014 | 492 | 2696.5 | 828 | 158 | 94 | 48 | 0 | 77
16:00 | 975 | 492 | 2379 | 593 | 158 | 94 | 48 | 0 | 78
16:30 | 972.5 | 491.5 | 2396.5 | 603.5 | 158.5 | 94 | 68 | 0 | 75
17:00 | 970 | 491 | 2414 | 614 | 159 | 94 | 88 | 0 | 72
17:30 | 964 | 491 | 2415 | 688 | 159.5 | 94 | 160 | 0 | 73 | Max Temp. in Dhaka |  | MMCFD
18:00 | 958 | 491 | 2416 | 762 | 160 | 94 | 232 | 0 | 74
18:30 | 1005 | 491.5 | 2716 | 937 | 161 | 94.5 | 298 | 0 | 92
19:00 | 1052 | 492 | 3016 | 1112 | 162 | 95 | 364 | 0 | 90
19:30 | 1081 | 491 | 3147 | 1189 | 158 | 95 | 409 | 0 | 92
20:00 | 1050 | 492 | 3232 | 1123 | 164 | 95 | 407 | 0 | 92
20:30 | 1070 | 492 | 3204 | 1090 | 163.5 | 95 | 373.5 | 0 | 92
21:00 | 1090 | 492 | 3176 | 1057 | 163 | 95 | 340 | 0 | 92
21:30 | 1066.5 | 491.5 | 3183 | 969 | 162 | 94.5 | 339.5 | 0 | 91
22:00 | 1043 | 491 | 3190 | 881 | 161 | 94 | 339 | 0 | 90
22:30 | 1035 | 493 | 3163.5 | 864 | 161.5 | 94 | 281.5 | 0 | 87
23:00 | 1027 | 495 | 3137 | 847 | 162 | 94 | 224 | 0 | 84
23:30 | 1043.5 | 495 | 3088.5 | 726 | 162.5 | 102.5 | 136.5 | 0 | 81
24:00 | 1060 | 495 | 3040 | 605 | 163 | 111 | 49 | 0 | 78
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Tripura

## volt
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2017-04-05
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 228 | 1:00 | 220 | 8:00 | Tongi | 215 | 17:00 | 205 | 11:00
Ishurdi | 233 | 18:00 | 220 | 7:00 | Comilla (N) | 229 | 17:00 | 215 | 0:00
Ashuganj | 234 | 18:00 | 230 | 7:00 | Hathazari | 225 | 22:00 | 204 | 12:00
Serajganj | 224 | 18:00 | 214 | 19:00 | Megnaghat | 221 | 16:00 | 214 | 13:00
Baghabari | 223 | 18:00 | 215 | 13:00 | Fenchuganj | 238 | 22:00 | 231 | 0:00
Barapukuria | 226 | 4:00 | 218 | 19:00 | Siddhirganj | 230 | 17:00 | 217 | 12:00
Bogra | 223 | 1:00 | 209 | 7:00 | Maniknagar | 230 | 18:30 | 215 | 12:00
Khulna South | 235 | 18:00 | 214 | 0:00 | Old Airport | 216 | 16:00 | 207 | 12:00
Rampura | 219 | 24:00 | 210 | 12:00 | Barisal | 239 | 22:00 | 227 | 13:00
Haripur | 216 | 16:00 | 210 | 9:00 | AKSML | 221 | 17:00 | 200 | 13:00
Hasnabad | 218 | 18:00 | 210 | 0:00 | BSRM | 225 | 22:00 | 204 | 12:00
Aminbazar | 217 | 16:00 | 208 | 7:00 | Bibiyana | 0 | 1:00 | 0 | 12:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 140 | 1700 | 130 | 900 | Madanhat | 137 | 1800 | 126 | 700
Munsiganj | 135 | 1700 | 128 | 800 | Hathazari | 135 | 1800 | 124 | 1200
Megnaghat | 132 | 1830 | 128 | 700 | Khulshi | 132 | 1800 | 120 | 1200
Shyampur | 132 | 1800 | 122 | 900 | Halishahar | 135 | 1800 | 121 | 1200
Bhulta | 125 | 1830 | 120 | 1000 | Baraulia | 132 | 1800 | 120 | 1200
Madanganj | 135 | 1600 | 128 | 800 | Sikalbaha | 134 | 1800 | 123 | 1200
Shitalakhya | 136 | 1600 | 127 | 900 | Dohazari | 135 | 2200 | 122 | 1200
Rahim steal | 134 | 1800 | 129 | 900 | Cox'sbazar | 132 | 2300 | 120 | 1200
Matuail | 134 | 1700 | 128 | 900 | Chandraghona | 135 | 1800 | 125 | 1200
Ghorasal | 136 | 1800 | 134 | 700 | Kaptai | 135 | 2200 | 125 | 800
Narsinghdi | 133 | 1700 | 127 | 1100 | A. Khaer Stl. | 131 | 1800 | 120 | 1200
Haripur (SBU) | 135 | 1700 | 129 | 1100 | Bakulia | 133 | 1800 | 121 | 1200
Ullon | 135 | 400 | 129 | 1200 | Julda | 133 | 2200 | 122 | 700
Hasnabad | 135 | 1700 | 128 | 1200 | TK Chemical | 136 | 2200 | 124 | 1200
Magbazar | 135 | 500 | 130 | 900 | Modern Steel | 133 | 2200 | 122 | 1200
Maniknagar | 134 | 2000 | 126 | 1200 | Shahmirpur | 132 | 2200 | 121 | 1200
Bangabhaban | 131 | 1800 | 126 | 1200 | Goalpara | 138 | 1800 | 128 | 400
Narinda | 135 | 1700 | 126 | 1000 | Central s/s | 139 | 1800 | 128 | 600
Dhanmondi | 134 | 2000 | 126 | 1200 | Noapara | 135 | 1000 | 124 | 700
Lalbag | 131 | 1800 | 123 | 1200 | Jessore | 130 | 1800 | 117 | 600
Madartek | 135 | 1700 | 132 | 1000 | Jhenida | 131 | 1800 | 115 | 500
Mirpur | 130 | 1600 | 123 | 1100 | Bottail | 135 | 300 | 123 | 1300
Kalyanpur | 133 | 1600 | 127 | 900 | G.K.Project | 135 | 1800 | 125 | 1300
Gulshan | 135 | 500 | 129 | 1000 | Faridpur | 135 | 1800 | 123 | 1300
Uttara | 132 | 1600 | 124 | 1100 | Madaripur | 135 | 1700 | 122 | 1300
Kamrangirchar | 135 | 1700 | 128 | 900 | Gopalganj | 142 | 1800 | 123 | 1300
Savar | 131 | 1600 | 124 | 1200 | Bagerhat | 136 | 2300 | 130 | 1300
Bhasantec | 132 | 1800 | 123 | 1200 | Mongla | 133 | 2300 | 125 | 600
Agargaon | 134 | 1600 | 125 | 1100 | Satkhira | 137 | 1800 | 125 | 400
Satmosjid | 132 | 1700 | 124 | 1200 | Gallamari | 138 | 1000 | 128 | 300
Tongi | 134 | 1500 | 126 | 1100 | Magura | 130 | 1800 | 110 | 300
Kabirpur | 136 | 1800 | 126 | 700 | Chuadanga | 125 | 1800 | 110 | 2000
Basundhara | 131 | 1800 | 125 | 1200 | Barisal | 135 | 300 | 127 | 1300
Manikganj | 138 | 1600 | 130 | 1100 | Patuakhali | 135 | 300 | 127 | 1300
Joydevpur | 135 | 600 | 129 | 1200 | Bhandaria | 135 | 1930 | 120 | 1300
New Tongi | 134 | 1700 | 127 | 900 | Ishurdi | 133 | 100 | 125 | 700
Kodda | 133 | 1500 | 130 | 1200 | Natore | 134 | 100 | 121 | 700
Tangail | 134 | 1500 | 125 | 900 | Bogra | 132 | 100 | 123 | 800
Mymensing | 136 | 1000 | 130 | 2000 | Noagaon | 130 | 100 | 119 | 800
Kishorganj | 137 | 1500 | 132 | 1830 | Rajshahi | 131 | 100 | 118 | 700
Netrokona | 140 | 1000 | 131 | 2000 | C.Nawabganj | 130 | 100 | 119 | 700
Jamalpur | 136 | 1100 | 128 | 2200 | Amnura | 135 | 1800 | 122 | 700
Sherpur | 137 | 1000 | 127 | 2200 | Pabna | 130 | 100 | 120 | 1300
Srimongal | 140 | 100 | 139 | 2100 | Shahjadpur | 137 | 1800 | 128 | 700
Shahjibazar | 139 | 100 | 136 | 2100 | Serajganj | 132 | 500 | 122 | 700
Fenchuganj | 137 | 1700 | 135 | 800 | Niyamatpur | 127 | 300 | 115 | 700
Khulawara | 137 | 1600 | 136 | 100 | Joypurhat | 130 | 100 | 118 | 700
Sylhet | 136 | 200 | 135 | 700 | Rangpur | 125 | 200 | 115 | 1900
Chatak | 137 | 200 | 135 | 800 | Lalmonirhat | 124 | 400 | 108 | 1900
Comilla(s) | 134 | 1400 | 129 | 1000 | Saidpur | 125 | 500 | 112 | 1900
Comilla(n) | 138 | 1700 | 132 | 1100 | Purbasadipur | 125 | 100 | 112 | 1900
Chandpur | 138 | 1900 | 130 | 1000 | Thakurgaon | 123 | 200 | 110 | 1830
Feni | 127 | 1700 | 120 | 1800 | Palashbari | 127 | 100 | 116 | 1900
Chowmuhani | 134 | 2100 | 125 | 1200 | Barapukuria | 126 | 400 | 118 | 1900
Ashuganj | 140 | 700 | 139 | 1200 | Panchagar | 121 | 300 | 100 | 1900
Daudkandi | 137 | 1700 | 130 | 800
B.Baria | 139 | 1000 | 136 | 700
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7