## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-11-13 | Monday
|  | Date (day): | 2023-11-13 |  | Monday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11599.6 | MW |  |  | (b) At Evening Peak Hour : |  | 13655 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-11-12 | 2023-11-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 76 | 70 | 75 | 33 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 335 | 340 | 340 | 72 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 155 | 147 | 150 | 160 | 200 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 225 | 225 | 225 | 225 | 225 |  | GT-1 under S/D due to Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 4 | 99 | 8 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 153 | 140 | 150 | 150 | 185 |  | GT-1 under S/D due to Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 35 | 65 | 65 | 65 |  | 37 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 28 | 29 | 30 | 45 | 30 |  | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 18 | 18 | 18 |  | 4 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 28 | 55 | 17 | 85 |  | 15 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 234 | 230 | 230 | 230 | 165 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 66 | 50 | 90 |  | 12 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 17 | 37 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 5 | 115 | 16 | 132 | 17 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 0 | 35 | 20 |  | Fuel shortage
| Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 31 | 31 | 31 |  | 49 | Engine problem
26 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
27 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
28 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 3 | 20 | 8 | 25 | 27 |  | Fuel shortage
29 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
30 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 35 | 50 | 80 | 130 | 170 |  | Fuel shortage
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
31 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 17 | 56 | 17 | 80 | 69 |  | Fuel shortage
32 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 17 | 70 | 30 | 105
33 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 50 | 71 | 17 | 71 | 33 |  | Fuel shortage
34 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 35 | 17 | 17 | 35 | 127 |  | Fuel shortage
35 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 35 | 0
36 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 35 | 20 |  | Fuel shortage
| Meghnaghat Unique power |  | Gas | IPP | 586 | 0 | 0 | 0 | 0 | 0 | 0
| Summit Meghanghat-2 589 MW(Gas) |  | Gas | IPP | 589 | 0 | 0 | 0 | 0 | 0 | 0
| Dhaka area Total |  |  |  |  | 5763 | 5422 | 1825 | 2273 | 1874 | 2567 | 1856 | 1075
37 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
38 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 4 | 8 | 8 | 17 | 8 |  | Fuel shortage
39 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
40 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 19 | 6 | 19 | 31 |  | Fuel shortage
41 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 121 | 121 | 121 | 121 |  | 109 | Engine problem
42 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 40 | 198 | 200 | 200 |  |  | Gas shortage
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
44 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 17 | 17 | 17 | 88 |  | Fuel shortage
45 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 8 | 16 | 8 | 16 | 82 |  | Fuel shortage
46 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
47 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
48 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
49 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 12 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 2 | 10 | 20
50 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
51 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
52 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 222 | 100 | 260 | 40 |  | Fuel shortage
53 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
54 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 17 | 17 | 17 | 93 |  | Fuel shortage
55 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 12 | 12 | 12 | 12 | 88 |  | Fuel shortage
56 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 17 | 17 | 99 |  | Fuel shortage
57 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 27 | 17 | 17 | 17
58 | SS Power I |  | Coal | SS Power | 1*612 | 612 | 612 | 310 | 309 | 300 | 310
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 4 | 10 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 344 | 336 | 350 | 350 |  |  | On test.
| Chattogram area Total |  |  |  |  | 3217 | 3157 | 1087 | 1368 | 1271 | 1456 | 1142 | 439
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
59 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 178 | 0 | 0 |  | 221 | Under maint.
60 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 45 | 25 | 280 | 310 | 50 |  | Gas shortage
61 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 280 | 280 | 280 | 80 |  | Gas shortage
62 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 270 | 330 | 300 | 330 | 70 |  | Gas shortage
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 25 | 30 | 15
| Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 0 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
64 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 30 | 30 | 165 |  | Gas shortae
65 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
66 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 5 | 115 | 12 | 120 |  | 30 | Engine problem
67 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 0
68 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
69 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 18 | 24 | 17 | 17 | 183 |  | Fuel shortage
70 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 17 | 15 | 17 |  | 5 | Engine problem
71 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 144 | 128 | 140
72 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
73 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 12 | 43 | 43 | 43 |  | 9 | Engine problem
74 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 12 | 12 | 12 | 12 |  | 13 | Engine problem
| Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
75 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 17 | 114 | 0 |  | Fuel shortage
76 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 57 | 28 | 58 | 55 |  | Fuel shortage
77 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 2 | 17 | 17 | 17 |  | 37 | Engine problem
78 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 18 | 93 | 34 | 95 | 20 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 2959 | 2896 | 1190 | 1463 | 1332 | 1708 | 638 | 478
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 62 | 73 | 70 | 80 | 122 |  | Gas shortage
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 18 | 18 |  | 4 | Contract Expired
| Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 0 | 95 | 0 | 0 | 0 | 0 | 0
81 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
82 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 65 | 95 | 84 | 100 | 100 |  | Fuel shortage
83 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 88 | 40 | 85 | 30 |  | Fuel shortage
84 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 38 | 0 | 50 | 0
85 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 222 | 262 | 269.6 | 289 | 122 | 4
86 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 41 | 42 | 43 |  | 27 | Machine problem.
87 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Engine problem
88 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 | 163 |  | Gas shortage
89 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
90 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 45 | 50
91 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 0 | 0 | 0 | 0
92 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 2 | 2 |  | 9 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 58 | 57 | 60 | 62
94 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 0 | 0 | 0 | 86 |  | Gas shortage
95 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 204 | 201 | 205 | 205 |  | 26 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 16 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
98 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 | 9 |  | Gas shortage
99 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 290 | 300 |  |  | FGMO
100 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 404 | 401 | 400 | 400 |  |  | FGMO
101 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
102 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 15 | 45 | 230 | 250 |  | 123 | ST under maint.
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1125 | 1110 | 1317 | 1355 | 258 | 705
103 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 919 | 918 | 919 | 801
104 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 2 | 16 | 0 | 16 | 99 |  | Fuel shortage
105 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 50
106 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
107 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 70 | 39 |  | Fuel shortage
108 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
109 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 | 40 |  | Fuel shortage
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
110 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 94 | 50 | 94 |  | 11 | Engine problem
111 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 15 | 15 | 32 | 73 |  | Fuel shortage
112 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 77 | 0 | 100 | 0
113 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 336 | 336 | 0 | 0 | 0 | 0
114 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 399 | 453 | 400 | 570 |  | 617
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3241 | 3237 | 1414 | 1496 | 1484 | 1633 | 907 | 628
115 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 16 | 110
116 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 17 | 24 | 21 | 25 |  | 15 | Engine problem
117 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 130 | 130 | 130 |  | 64 | ST under maint.
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 880 | 880 | 1244 | 1244
119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 38 | 150
121 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 140 | 200 | 140 | 200 | 107 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1387 | 1489 | 1809 | 2079 | 107 | 79
122 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
123 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 0 | 35 | 17 |  | Fuel shortage
124 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 20 |  | 51 | Engine problem
125 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 0 | 0 | 28 | 28
126 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 8 | 34 | 42 |  | 8 | Engine problem
127 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 40 |  | 10 | Engine problem
128 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
129 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Fuel shortage
130 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
131 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 414 | 350 | 414
132 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 24 | 38 | 12 |  | Fuel shortage
| Bogra 22 MW PP (GBB) |  | Gas | RPP | 0 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 64 | 40 | 85 |  | 19 | Engine problem
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 11 | 43 | 35 | 50 | 63 |  | Fuel shortage
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 20 | 55 | 35 | 55
139 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Imported power | 748*2 | 1496 | 1496 | 1119 | 1217 | 1200 | 1300
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1580 | 1858 | 1801 | 2170 | 1113 | 88
140 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
141 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 170 | 170 | 170 | 170 |  | 104 | Machine problem
142 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
143 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
144 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 101 | 34 | 113
145 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
146 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 90 | 70 | 115
147 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 34 | 0 | 30 | 0
148 | Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 200 | 200 | 167 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 1030 | 950 | 371 | 361 | 442 | 398 | 125 | 189
| Total |  |  |  |  | 25339 | 24599 | 10201 | 11680 | 11599.6 | 13655 | 6268 | 3685
A. |  | 2023-11-12 | (Yesterday) |  |  |  |  | Sunday
1 | Highest Generation : |  |  | 11680 | MW at | 18:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 18:00 | hrs.
2 | Minimum Generation : |  |  | 7754 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11680 | MW
3 | Day peak Generation : |  |  | 10201 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11185.39 | MW
4 | Evening peak Generation : |  |  | 11680 | MW at | 18:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 232.88 | MKWHr | By Solar | 2.5533 | MKWHr
| By Gas : | 107.6874 | MKWHr |  | By Oil: | 18.6822 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 75.8945 | MKWHr |  | By Hydro: | 2.9384 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.05712 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 6268 | MW | Dhaka | 4489.59 | 4489.59 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 3685 | MW | Chittagong | 1176.5 | 1176.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 9953 | MW | Khulna | 1222.2 | 1222.2 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 841.43 | MMCFD |  |  | Rajshahi | 998.6 | 998.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 110144700.404 | ii) Oil : | Taka | 238554575.84 | Comilla | 1017 | 1017 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 536374100.96 | Total | Taka | 885073377.204 | Mymensingh | 860 | 860 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 422 | 422 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 1050 | MW (W to E) at | 18:00 | hrs | Barisal | 305.5 | 305.5 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 710 | MW at | 21:00 | hrs | Rangpur | 694 | 694 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.6°C |  |  | Total | 11185.39 | 11185.39 |  | 0
B. |  | 2023-11-13 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 31.6°C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 13655 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 10300 | MW
4 | Reserve(Generation end) |  |  |  | 1655 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 239.2602 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7806 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2225 | MKWHr. | ii) HVDC Flow at Peak Time |  | 918 | MW at | 18:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8445 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 99.9 |  | (b) Today: | 99.66 |  | (c) Rule Curve: |  | 107.9
.

## YesterdayGen
2023-11-12 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | Meghnaghat Unique power | Summit Meghanghat-2 589 MW(Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 339 | 149 |  | 0 | 225 | 158 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 10 | 14 | 0 | 0 | 0 | 280 | 240 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 112 | 103 | 0 | 0 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 63 | 0 | 0 | 203 | 18 | 0 | 10 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 401 | 0 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 0 | 12 | 260 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 310 | 4 | 204 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 140 | 917 | 0 | 0 |  | 4972 | 3976 | 8948 | 3223 | 918 | 1607 | 0 | 109 | 2843 | 132 | 0 | 0 | 112 | 0 | 4 | 0 | 99.95
2:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 339 | 157 |  | 0 | 225 | 157 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 0 | 0 | 0 | 280 | 240 | 161 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 108 | 103 | 0 | 0 | 0 | 42 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 203 | 18 | 0 | 10 | 265 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 304 | 10 | 204 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 140 | 819 | 0 | 0 |  | 4802 | 3627 | 8429 | 3179 | 918 | 1593 | 0 | 0 | 2489 | 132 | 0 | 0 | 108 | 0 | 10 | 0 | 99.94
3:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 319 | 153 |  | 0 | 225 | 159 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 16 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 131 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 0 | 0 | 0 | 280 | 240 | 162 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 100 | 104 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 13 | 204 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 140 | 817 | 0 | 0 |  | 4615 | 3576 | 8191 | 3134 | 919 | 1410 | 0 | 0 | 2483 | 132 | 0 | 0 | 100 | 0 | 13 | 0 | 99.93
4:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 309 | 166 |  | 0 | 225 | 123 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 16 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 81 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31 | 0 | 0 | 0 | 280 | 240 | 140 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 96 | 104 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 8 | 203 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 354 | 0 | 140 | 810 | 0 | 0 |  | 4459 | 3380 | 7839 | 2950 | 919 | 1257 | 0 | 0 | 2477 | 132 | 0 | 0 | 96 | 0 | 8 | 0 | 99.92
5:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 309 | 179 |  | 0 | 180 | 112 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 81 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31 | 0 | 0 | 0 | 280 | 240 | 140 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 94 | 105 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 2 | 202 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 140 | 814 | 0 | 0 |  | 4374 | 3380 | 7754 | 2937 | 918 | 1234 | 0 | 0 | 2477 | 92 | 0 | 0 | 94 | 0 | 2 | 0 | 99.91
6:00 | 0 | 0 | 0 | 180 | 0 | 28 | 0 | 314 | 181 |  | 0 | 225 | 133 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31 | 0 | 0 | 0 | 35 | 355 | 180 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 96 | 105 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 300 | 1 | 202 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 140 | 817 | 0 | 0 |  | 4317 | 3551 | 7868 | 2778 | 919 | 1503 | 0 | 0 | 2479 | 92 | 0 | 0 | 96 | 0 | 1 | 0 | 99.9
7:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 351 | 151 |  | 0 | 225 | 155 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 27 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23 | 0 | 0 | 0 | 35 | 345 | 197 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 98 | 83 | 0 | 0 | 0 | 42 | 0 | 47 | 0 | 0 | 0 | 61 | 0 | 0 | 203 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 400 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 270 | 0 | 0 | 300 | 0 | 203 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 540 | 220 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 352 | 3 | 140 | 925 | 17 | 0 |  | 4539 | 3800 | 8339 | 2893 | 919 | 1602 | 0 | 27 | 2630 | 132 | 0 | 0 | 98 | 38 | 0 | 0 | 88.89
8:00 | 0 | 0 | 0 | 180 | 0 | 63 | 0 | 354 | 152 |  | 0 | 225 | 148 | 0 | 0 | 0 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 31 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 0 | 0 | 0 | 0 | 35 | 310 | 184 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 33 | 5 | 100 | 69 | 0 | 0 | 0 | 42 | 0 | 10 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 10 | 10 | 0 | 0 | 377 | 47 | 0 | 11 | 2 | 70 | 0 | 0 | 0 | 0 | 12 | 90 | 0 | 14 | 0 | 0 | 0 | 0 | 13 | 0 | 17 | 350 | 0 | 0 | 303 | 0 | 348 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 670 | 180 | 0 | 0 | 2 | 27 | 0 | 0 | 0 | 401 | 0 | 140 | 1010 | 68 | 0 |  | 4770 | 3945 | 8715 | 2803 | 919 | 1373 | 0 | 210 | 3042 | 132 | 0 | 0 | 100 | 136 | 0 | 0 | 88.88
9:00 | 0 | 0 | 0 | 180 | 0 | 69 | 0 | 346 | 154 |  | 0 | 225 | 142 | 0 | 0 | 0 | 230 | 0 | 0 | 5 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 92 | 40 | 0 | 0 | 0 | 32 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 15 | 305 | 201 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 102 | 69 | 0 | 0 | 0 | 42 | 0 | 42 | 0 | 0 | 0 | 62 | 0 | 0 | 206 | 17 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 15 | 15 | 12 | 0 | 0 | 402 | 47 | 17 | 17 | 3 | 82 | 0 | 9 | 0 | 0 | 12 | 40 | 8 | 32 | 10 | 9 | 0 | 0 | 22 | 5 | 0 | 270 | 0 | 0 | 303 | 0 | 342 | 0 | 0 |  | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 220 | 0 | 0 | 3 | 49 | 0 | 0 | 0 | 400 | 22 | 140 | 1011 | 118 | 0 |  | 4831 | 4251 | 9082 | 2751 | 920 | 1499 | 0 | 298 | 3116 | 132 | 0 | 0 | 102 | 264 | 0 | 0 | 99.87
10:00 | 0 | 0 | 0 | 180 | 0 | 67 | 0 | 339 | 157 |  | 0 | 225 | 144 | 0 | 17 | 0 | 231 | 0 | 0 | 9 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 25 | 25 | 0 | 0 | 46 | 75 | 0 | 0 | 0 | 42 | 0 | 0 | 0 |  | 2 | 0 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 15 | 270 | 180 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 16 | 10 | 33 | 12 | 116 | 65 | 0 | 0 | 2 | 43 | 0 | 42 | 0 | 0 | 0 | 61 | 0 | 0 | 207 | 17 | 0 | 9 | 275 | 16 | 5 | 0 | 10 | 0 | 0 | 24 | 0 | 17 | 18 | 12 | 0 | 0 | 401 | 47 | 17 | 17 | 4 | 88 | 0 | 17 | 0 | 0 | 12 | 15 | 17 | 42 | 25 | 17 | 0 | 0 | 27 | 18 | 0 | 270 | 0 | 0 | 303 | 0 | 344 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 750 | 220 | 0 | 0 | 4 | 65 | 0 | 0 | 0 | 400 | 30 | 140 | 1008 | 154 | 0 |  | 4884 | 4333 | 9217 | 2678 | 918 | 1498 | 0 | 425 | 3115 | 121 | 0 | 0 | 116 | 346 | 0 | 0 | 99.86
11:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 340 | 156 |  | 0 | 225 | 152 | 0 | 20 | 3 | 233 | 0 | 0 | 9 | 24 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 0 | 0 | 46 | 75 | 0 | 0 | 0 | 52 | 0 | 0 | 0 |  | 6 | 1 | 0 | 12 | 0 | 6 | 10 | 0 | 0 | 0 | 0 | 40 | 305 | 198 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 1 | 16 | 10 | 25 | 12 | 124 | 65 | 0 | 0 | 2 | 43 | 0 | 47 | 0 | 0 | 0 | 60 | 0 | 0 | 206 | 17 | 0 | 9 | 295 | 16 | 5 | 0 | 17 | 0 | 0 | 24 | 0 | 17 | 20 | 12 | 4 | 0 | 403 | 59 | 17 | 17 | 4 | 88 | 17 | 17 | 0 | 1 | 12 | 15 | 34 | 47 | 35 | 17 | 0 | 0 | 32 | 17 | 0 | 270 | 23 | 0 | 303 | 0 | 344 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 17 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 790 | 220 | 0 | 0 | 5 | 75 | 0 | 0 | 0 | 401 | 33 | 140 | 1004 | 173 | 0 |  | 5154 | 4462 | 9616 | 2768 | 919 | 1591 | 0 | 526 | 3152 | 121 | 0 | 24 | 124 | 391 | 0 | 0 | 99.85
12:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 340 | 155 |  | 0 | 225 | 153 | 4 | 35 | 15 | 234 | 0 | 0 | 28 | 58 | 5 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 3 | 0 | 46 | 75 | 0 | 0 | 4 | 40 | 0 | 0 | 0 |  | 6 | 8 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 45 | 340 | 204 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 12 | 16 | 10 | 33 | 12 | 128 | 62 | 0 | 0 | 2 | 40 | 0 | 47 | 0 | 0 | 0 | 58 | 0 | 0 | 204 | 16 | 0 | 10 | 310 | 16 | 5 | 0 | 35 | 0 | 0 | 65 | 0 | 17 | 19 | 12 | 18 | 5 | 404 | 49 | 17 | 17 | 4 | 88 | 17 | 17 | 17 | 9 | 12 | 15 | 50 | 38 | 35 | 17 | 0 | 2 | 32 | 18 | 0 | 270 | 27 | 0 | 310 | 0 | 344 | 0 | 0 |  | 919 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 11 | 0 | 0 | 0 | 0 | 20 | 880 | 220 | 0 | 0 | 5 | 77 | 0 | 0 | 0 | 399 | 34 | 140 | 1119 | 167 | 0 |  | 5449 | 4752 | 10201 | 2803 | 919 | 1672 | 0 | 778 | 3362 | 121 | 0 | 40 | 128 | 378 | 0 | 0 | 99.84
13:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 335 | 154 |  | 0 | 225 | 150 | 45 | 55 | 15 | 230 | 0 | 0 | 86 | 91 | 16 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 8 | 50 | 0 | 0 | 0 |  | 6 | 8 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 140 | 305 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 16 | 10 | 33 | 12 | 136 | 59 | 0 | 0 | 2 | 40 | 0 | 47 | 0 | 0 | 0 | 59 | 0 | 0 | 202 | 17 | 0 | 9 | 290 | 16 | 5 | 0 | 70 | 0 | 0 | 56 | 0 | 17 | 18 | 12 | 18 | 25 | 404 | 55 | 35 | 26 | 4 | 88 | 17 | 17 | 17 | 18 | 12 | 21 | 71 | 44 | 35 | 17 | 0 | 17 | 30 | 18 | 0 | 270 | 17 | 0 | 303 | 0 | 338 | 0 | 0 |  | 919 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 38 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 970 | 220 | 0 | 0 | 4 | 71 | 0 | 0 | 0 | 396 | 31 | 140 | 1150 | 167 | 0 |  | 5796 | 4842 | 10638 | 2811 | 919 | 1585 | 0 | 1187 | 3467 | 121 | 0 | 41 | 136 | 371 | 0 | 0 | 99.83
14:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 335 | 154 |  | 0 | 225 | 143 | 70 | 68 | 15 | 232 | 0 | 0 | 88 | 91 | 16 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 8 | 92 | 0 | 0 | 0 |  | 6 | 8 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 0 | 305 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 0 | 0 | 33 | 12 | 140 | 58 | 0 | 0 | 2 | 40 | 0 | 47 | 0 | 0 | 0 | 59 | 0 | 0 | 203 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 47 | 0 | 0 | 56 | 0 | 26 | 16 | 12 | 17 | 48 | 392 | 59 | 35 | 17 | 3 | 88 | 17 | 17 | 17 | 18 | 12 | 35 | 71 | 37 | 35 | 17 | 0 | 17 | 24 | 18 | 0 | 270 | 17 | 0 | 303 | 0 | 342 | 0 | 0 |  | 920 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 70 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 900 | 180 | 0 | 0 | 4 | 57 | 0 | 0 | 0 | 400 | 26 | 140 | 1120 | 135 | 0 |  | 5700 | 4638 | 10338 | 2691 | 920 | 1484 | 0 | 1262 | 3375 | 121 | 0 | 41 | 140 | 304 | 0 | 0 | 99.85
15:00 | 0 | 0 | 0 | 180 | 0 | 66 | 0 | 335 | 154 |  | 0 | 225 | 145 | 86 | 68 | 15 | 232 | 0 | 0 | 57 | 40 | 16 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 8 | 199 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 35 | 270 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 0 | 0 | 33 | 12 | 134 | 63 | 0 | 0 | 1 | 41 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 47 | 0 | 0 | 56 | 0 | 17 | 11 | 12 | 17 | 63 | 402 | 59 | 35 | 17 | 2 | 88 | 17 | 17 | 17 | 28 | 12 | 50 | 71 | 25 | 35 | 17 | 0 | 17 | 17 | 17 | 0 | 270 | 23 | 0 | 303 | 0 | 342 | 0 | 0 |  | 919 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 72 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 840 | 180 | 0 | 0 | 2 | 40 | 0 | 0 | 0 | 401 | 16 | 140 | 1120 | 93 | 0 |  | 5719 | 4457 | 10176 | 2810 | 919 | 1420 | 0 | 1194 | 3316 | 121 | 0 | 55 | 134 | 207 | 0 | 0 | 99.81
16:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 335 | 150 |  | 0 | 225 | 145 | 95 | 51 | 15 | 230 | 0 | 0 | 40 | 40 | 16 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 8 | 198 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 35 | 270 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 0 | 10 | 33 | 12 | 124 | 63 | 0 | 0 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 0 | 203 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 47 | 0 | 0 | 66 | 0 | 17 | 5 | 12 | 17 | 81 | 404 | 59 | 35 | 17 | 1 | 88 | 17 | 17 | 17 | 28 | 12 | 50 | 71 | 10 | 35 | 17 | 0 | 17 | 8 | 18 | 0 | 270 | 28 | 0 | 303 | 1 | 342 | 0 | 0 |  | 918 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 72 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 780 | 180 | 0 | 0 | 1 | 18 | 0 | 0 | 0 | 400 | 7 | 140 | 1123 | 39 | 0 |  | 5688 | 4312 | 10000 | 2818 | 918 | 1415 | 0 | 1196 | 3258 | 121 | 0 | 60 | 124 | 89 | 1 | 0 | 99.8
17:00 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 335 | 150 |  | 0 | 225 | 144 | 99 | 55 | 15 | 230 | 0 | 0 | 40 | 40 | 32 | 25 | 0 | 0 | 0 | 17 | 17 | 17 | 18 | 19 | 11 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 8 | 199 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 13 | 12 | 0 | 0 | 0 | 0 | 15 | 265 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 10 | 10 | 33 | 12 | 134 | 65 | 0 | 0 | 0 | 40 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 0 | 202 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 47 | 0 | 0 | 60 | 0 | 17 | 0 | 12 | 17 | 93 | 363 | 59 | 35 | 17 | 0 | 105 | 17 | 17 | 17 | 28 | 12 | 50 | 71 | 1 | 35 | 17 | 0 | 17 | 1 | 38 | 0 | 240 | 17 | 0 | 301 | 1 | 340 | 0 | 0 |  | 918 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 81 | 0 | 35 | 3 | 20 | 0 | 0 | 35 | 780 | 180 | 0 | 2 | 0 | 1 | 0 | 0 | 0 | 399 | 1 | 140 | 1121 | 3 | 0 |  | 5710 | 4310 | 10020 | 2726 | 918 | 1426 | 0 | 1338 | 3251 | 121 | 0 | 98 | 134 | 7 | 1 | 0 | 99.79
18:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 335 | 147 |  | 0 | 225 | 140 | 99 | 65 | 15 | 230 | 0 | 0 | 55 | 66 | 115 | 29 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 19 | 12 | 33 | 25 | 20 | 0 | 46 | 75 | 0 | 0 | 8 | 198 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 25 | 280 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 10 | 33 | 12 | 144 | 73 | 0 | 0 | 0 | 41 | 0 | 47 | 0 | 0 | 0 | 57 | 0 | 0 | 201 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 50 | 0 | 0 | 95 | 0 | 56 | 0 | 12 | 24 | 115 | 401 | 88 | 70 | 17 | 0 | 222 | 17 | 17 | 34 | 57 | 12 | 45 | 71 | 0 | 17 | 17 | 0 | 17 | 0 | 93 | 0 | 330 | 17 | 0 | 309 | 4 | 336 | 0 | 0 |  | 918 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 8 | 0 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 43 | 15 | 101 | 0 | 0 | 55 | 880 | 220 | 0 | 35 | 0 | 0 | 90 | 0 | 0 | 453 | 0 | 200 | 1217 | 0 | 0 |  | 6476 | 5204 | 11680 | 2944 | 918 | 1626 | 0 | 2108 | 3565 | 121 | 0 | 250 | 144 | 0 | 4 | 0 | 99.78
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 335 | 148 |  | 0 | 225 | 142 | 27 | 65 | 15 | 230 | 0 | 0 | 86 | 66 | 64 | 46 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 19 | 12 | 33 | 25 | 25 | 0 | 46 | 75 | 0 | 0 | 17 | 199 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 140 | 270 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 17 | 10 | 33 | 12 | 134 | 72 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 57 | 0 | 0 | 201 | 17 | 0 | 10 | 260 | 16 | 5 | 0 | 80 | 0 | 0 | 45 | 0 | 80 | 0 | 12 | 18 | 118 | 402 | 89 | 35 | 17 | 0 | 247 | 17 | 17 | 34 | 58 | 12 | 45 | 71 | 0 | 17 | 17 | 0 | 17 | 0 | 96 | 0 | 300 | 17 | 0 | 306 | 3 | 342 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 40 | 0 | 107 | 0 | 0 | 55 | 840 | 180 | 0 | 35 | 0 | 0 | 36 | 0 | 0 | 399 | 0 | 200 | 1218 | 0 | 0 |  | 6440 | 4756 | 11196 | 2957 | 919 | 1533 | 0 | 1924 | 3475 | 121 | 0 | 130 | 134 | 0 | 3 | 0 | 99.76
19:30 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 335 | 148 |  | 0 | 225 | 140 | 8 | 65 | 15 | 231 | 0 | 0 | 86 | 66 | 32 | 26 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 19 | 12 | 33 | 25 | 25 | 0 | 46 | 75 | 0 | 0 | 17 | 200 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 145 | 270 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 33 | 12 | 124 | 73 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 57 | 0 | 0 | 201 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 80 | 0 | 0 | 45 | 0 | 81 | 0 | 12 | 17 | 120 | 402 | 89 | 17 | 17 | 0 | 247 | 17 | 17 | 17 | 58 | 12 | 50 | 71 | 0 | 17 | 17 | 0 | 17 | 0 | 95 | 12 | 300 | 17 | 0 | 306 | 2 | 348 | 0 | 0 |  | 918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 50 | 0 | 70 | 0 | 0 | 55 | 820 | 180 | 0 | 35 | 0 | 0 | 35 | 0 | 0 | 400 | 0 | 200 | 1127 | 0 | 0 |  | 6362 | 4619 | 10981 | 2977 | 918 | 1543 | 0 | 1827 | 3371 | 121 | 0 | 98 | 124 | 0 | 2 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 335 | 143 |  | 0 | 225 | 147 | 9 | 65 | 15 | 230 | 0 | 0 | 78 | 66 | 32 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 19 | 12 | 33 | 25 | 25 | 0 | 46 | 75 | 0 | 0 | 17 | 199 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 160 | 270 | 172 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 33 | 12 | 124 | 73 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 60 | 0 | 0 | 201 | 18 | 0 | 10 | 260 | 16 | 5 | 0 | 45 | 0 | 0 | 45 | 0 | 80 | 0 | 12 | 17 | 120 | 402 | 89 | 17 | 17 | 0 | 232 | 17 | 17 | 0 | 58 | 12 | 50 | 71 | 0 | 17 | 17 | 0 | 17 | 0 | 95 | 14 | 300 | 17 | 0 | 306 | 3 | 346 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 50 | 0 | 37 | 0 | 0 | 55 | 800 | 180 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 405 | 0 | 200 | 1122 | 0 | 0 |  | 6271 | 4475 | 10746 | 2994 | 919 | 1535 | 0 | 1636 | 3349 | 121 | 0 | 65 | 124 | 0 | 3 | 0 | 99.76
21:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 334 | 146 |  | 0 | 225 | 147 | 8 | 65 | 15 | 231 | 0 | 0 | 32 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 18 | 19 | 12 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 17 | 198 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 19 | 12 | 3 | 0 | 0 | 0 | 320 | 270 | 172 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 10 | 25 | 12 | 124 | 83 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 60 | 0 | 0 | 201 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 45 | 0 | 0 | 18 | 0 | 81 | 0 | 12 | 17 | 120 | 402 | 89 | 17 | 17 | 0 | 124 | 17 | 17 | 0 | 58 | 12 | 50 | 71 | 0 | 17 | 17 | 0 | 0 | 0 | 77 | 49 | 300 | 17 | 0 | 306 | 1 | 348 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 820 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 200 | 1117 | 0 | 0 |  | 6140 | 4357 | 10497 | 3153 | 919 | 1560 | 0 | 1225 | 3361 | 121 | 0 | 33 | 124 | 0 | 1 | 0 | 99.76
22:00 | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 334 | 145 |  | 0 | 225 | 147 | 0 | 45 | 15 | 222 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 12 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 17 | 198 | 0 | 0 | 0 |  | 6 | 0 | 0 | 12 | 0 | 19 | 12 | 4 | 0 | 0 | 0 | 370 | 270 | 171 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 33 | 12 | 124 | 110 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 60 | 0 | 0 | 204 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 45 | 0 | 0 | 16 | 0 | 80 | 0 | 12 | 17 | 10 | 402 | 69 | 17 | 17 | 0 | 124 | 17 | 17 | 0 | 58 | 12 | 50 | 71 | 0 | 17 | 17 | 0 | 0 | 0 | 72 | 17 | 300 | 17 | 0 | 306 | 0 | 346 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 17 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 800 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 200 | 1062 | 0 | 0 |  | 5898 | 4282 | 10180 | 3214 | 919 | 1557 | 0 | 927 | 3285 | 121 | 0 | 33 | 124 | 0 | 0 | 0 | 99.74
23:00 | 0 | 0 | 0 | 180 | 0 | 73 | 0 | 335 | 156 |  | 0 | 225 | 153 | 0 | 32 | 0 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 12 | 33 | 25 | 0 | 0 | 46 | 75 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 19 | 12 | 9 | 0 | 0 | 0 | 355 | 270 | 164 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 16 | 15 | 11 | 33 | 12 | 126 | 110 | 0 | 0 | 0 | 42 | 0 | 47 | 0 | 0 | 0 | 40 | 0 | 0 | 204 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 12 | 17 | 10 | 377 | 16 | 0 | 17 | 0 | 124 | 17 | 17 | 0 | 58 | 12 | 90 | 71 | 0 | 0 | 17 | 0 | 0 | 0 | 55 | 0 | 300 | 17 | 0 | 306 | 3 | 350 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 740 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 401 | 0 | 200 | 1012 | 0 | 0 |  | 5624 | 4023 | 9647 | 3216 | 919 | 1485 | 0 | 581 | 3179 | 121 | 0 | 17 | 126 | 0 | 3 | 0 | 99.73
24:00 | 0 | 0 | 0 | 180 | 0 | 74 | 0 | 338 | 158 |  | 0 | 225 | 151 | 0 | 0 | 0 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 25 | 0 | 0 | 46 | 75 | 0 | 0 | 0 | 201 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 8 | 12 | 9 | 0 | 0 | 0 | 300 | 250 | 147 | 8 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 11 | 33 | 12 | 114 | 110 | 0 | 0 | 0 | 43 | 0 | 47 | 0 | 0 | 0 | 62 | 0 | 0 | 204 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17 | 0 | 365 | 0 | 0 | 17 | 0 | 106 | 17 | 17 | 0 | 34 | 12 | 98 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 18 | 0 | 260 | 17 | 0 | 305 | 8 | 350 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 0 | 166 | 975 | 0 | 0 |  | 5245 | 4052 | 9297 | 3108 | 919 | 1595 | 0 | 287 | 3128 | 121 | 0 | 17 | 114 | 0 | 8 | 0 | 99.72
KWH | 0 | 0 | 0 | 4378500 | 0 | 1485590 | 0 | 8153090 | 3760000 |  | 0 | 4495800 | 3477935 | 542400 | 631727 | 191611 | 5581475 | 0 | 0 | 566438 | 630288 | 318240 | 293768 | 0 | 0 | 0 | 129600 | 136205 | 140730 | 388260 | 456000 | 278640 | 720000 | 604500 | 143040 | 0 | 1534440 | 1404000 | 0 | 0 | 138344 | 2934036 | 0 | 0 | 0 |  | 81120 | 123984 | 0 | 188760 | 0 | 193920 | 269760 | 208320 | 0 | 0 | 0 | 3961500 | 6810000 | 4246000 | 16727 | 0 | 0 | 0 | 0 | 1075136 | 0 | 0 | 358906 | 314568 | 233280 | 772700 | 278630 | 2844480 | 1910400 | 0 | 0 | 11650 | 991000 | 0 | 944400 | 0 | 0 | 0 | 1259616 | 0 | 0 | 5107040 | 406000 | 0 | 240840 | 6874000 | 380160 | 120960 | 0 | 687491 | 0 | 0 | 765600 | 0 | 616896 | 133920 | 235200 | 258240 | 881527 | 9302000 | 997200 | 429120 | 337054 | 26160 | 1994727 | 269296 | 306945 | 160740 | 506520 | 236160 | 2346300 | 875520 | 302340 | 384480 | 301091 | 0 | 156960 | 208116 | 692160 | 138600 | 7045200 | 259273 | 0 | 7309090 | 57120 | 7367272 | 0 | 0 |  | 22222545 | 0 | 0 | 0 | 94080 | 0 | 0 | 0 | 0 | 0 | 0 | 2436000 | 471800 | 24864 | 0 | 0 | 0 | 0 | 0 | 109336 | 0 | 12780 | 0 | 16459 | 47524 | 0 | 0 | 236862 | 0 | 0 | 4134900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7776509 | 559200 | 0 | 566400 | 11952 | 273379 | 0 | 996 | 391008 | 19373500 | 4937891 | 0 | 96000 | 33600 | 491760 | 179328 | 0 | 0 | 9396364 | 211175 | 3806400 | 24506964 | 1133560 | 0 |  | 129326832 | 103553136 | 232879968 | 71922477 | 22222545 | 35764948 | 0 | 17823834 | 75894490 | 2938440 | 0 | 858357 | 2844480 | 2553277 | 57120 | 0
Fuel Cost | 0 | 0 | 0 | 6523965 | 0 | 1975834.7 | 0 | 8560744.5 | 4060800 |  | 0 | 4900422 | 3860507.85 | 6064032 | 8370382.75 | 2538845.75 | 6251252 | 0 | 0 | 8281323.56 | 8868152.16 | 5158670.4 | 2708540.96 | 0 | 0 | 0 | 1648512 | 1838767.5 | 1887189.3 | 291195 | 342000 | 0 | 0 | 0 | 2433110.4 | 0 | 414298.8 | 379080 | 0 | 0 | 2261924.4 | 3051397.44 | 0 | 0 | 0 |  | 1058616 | 2068053.12 | 0 | 2550147.6 | 0 | 2243654.4 | 342595.2 | 693705.6 | 0 | 0 | 0 | 4397265 | 7422900 | 4925360 | 21577.83 | 0 | 0 | 0 | 0 | 1795477.12 | 0 | 0 | 4827285.7 | 430958.16 | 174960 | 1352225 | 208972.5 | 20423366.4 | 2082336 | 0 | 0 | 185701 | 1357670 | 0 | 1643256 | 0 | 0 | 0 | 2443655.04 | 0 | 0 | 5158110.4 | 872900 | 0 | 476863.2 | 6874000 | 285120 | 91929.6 | 0 | 9384252.15 | 0 | 0 | 10320288 | 0 | 8544009.6 | 1565524.8 | 2427264 | 3527558.4 | 11697863.29 | 8557840 | 12125952 | 6205075.2 | 4263733.1 | 407049.6 | 23418094.98 | 2932633.44 | 3262825.35 | 2181241.8 | 6529042.8 | 2781964.8 | 2158596 | 11337984 | 4368813 | 4879051.2 | 3426415.58 | 0 | 2049897.6 | 2486986.2 | 10361635.2 | 1825362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 66667635 | 0 | 0 | 0 | 979372.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2728320 | 915292 | 271017.6 | 0 | 0 | 0 | 0 | 0 | 1710015.04 | 0 | 211636.8 | 0 | 224336.17 | 801729.88 | 0 | 0 | 179304.534 | 0 | 0 | 35063952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7698743.91 | 7515648 | 0 | 6700512 | 172706.4 | 3471913.3 | 0 | 11005.8 | 4746837.12 | 160800050 | 5036648.82 | 0 | 710400 | 380016 | 5768344.8 | 2749098.24 | 0 | 0 | 85412948.76 | 0 | 45562608 | 209534542.2 | 0 | 0 |  | 332106563.43 | 656024635.174 | 988131198.604 | 70191571.374 | 66667635 | 39953129.03 | 0 | 228816107.4 | 536374100.96 | 793378.8 | 0 | 9738468.44 | 20423366.4 | 15173441.2 | 0 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 340 | 155 |  | 0 | 225 | 153 | 4 | 35 | 15 | 234 | 0 | 0 | 28 | 58 | 5 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 11 | 33 | 25 | 3 | 0 | 46 | 75 | 0 | 0 | 4 | 40 | 0 | 0 | 0 |  | 6 | 8 | 0 | 12 | 0 | 6 | 12 | 0 | 0 | 0 | 0 | 45 | 340 | 204 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 12 | 16 | 10 | 33 | 12 | 128 | 62 | 0 | 0 | 2 | 40 | 0 | 47 | 0 | 0 | 0 | 58 | 0 | 0 | 204 | 16 | 0 | 10 | 310 | 16 | 5 | 0 | 35 | 0 | 0 | 65 | 0 | 17 | 19 | 12 | 18 | 5 | 404 | 49 | 17 | 17 | 4 | 88 | 17 | 17 | 17 | 9 | 12 | 15 | 50 | 38 | 35 | 17 | 0 | 2 | 32 | 18 | 0 | 270 | 27 | 0 | 310 | 0 | 344 | 0 | 0 |  | 919 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 17 | 0 | 11 | 0 | 0 | 0 | 0 | 20 | 880 | 220 | 0 | 0 | 5 | 77 | 0 | 0 | 0 | 399 | 34 | 140 | 1119 | 167 | 0 |  | 10201 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 76 | 0 | 335 | 147 |  | 0 | 225 | 140 | 99 | 65 | 15 | 230 | 0 | 0 | 55 | 66 | 115 | 29 | 0 | 0 | 0 | 35 | 35 | 35 | 18 | 19 | 12 | 33 | 25 | 20 | 0 | 46 | 75 | 0 | 0 | 8 | 198 | 0 | 0 | 0 | 0 | 6 | 16 | 0 | 12 | 0 | 19 | 12 | 2 | 0 | 0 | 0 | 25 | 280 | 178 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 10 | 33 | 12 | 144 | 73 | 0 | 0 | 0 | 41 | 0 | 47 | 0 | 0 | 0 | 57 | 0 | 0 | 201 | 17 | 0 | 10 | 270 | 16 | 5 | 0 | 50 | 0 | 0 | 95 | 0 | 56 | 0 | 12 | 24 | 115 | 401 | 88 | 70 | 17 | 0 | 222 | 17 | 17 | 34 | 57 | 12 | 45 | 71 | 0 | 17 | 17 | 0 | 17 | 0 | 93 | 0 | 330 | 17 | 0 | 309 | 4 | 336 | 0 | 0 |  | 918 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 8 | 0 | 8 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 43 | 15 | 101 | 0 | 0 | 55 | 880 | 220 | 0 | 35 | 0 | 0 | 90 | 0 | 0 | 453 | 0 | 200 | 1217 | 0 | 0 |  | 11680 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 340 | 160 |  | 0 | 225 | 150 | 100 | 65 | 15 | 230 | 0 | 0 | 85 | 90 | 132 | 45 | 0 | 0 | 0 | 17 | 35 | 35 | 18 | 19 | 12 | 33 | 25 | 25 | 0 | 46 | 75 | 0 | 0 | 17 | 200 | 0 | 0 | 0 |  | 6 | 16 | 0 | 12 | 0 | 19 | 12 | 20 | 0 | 0 | 0 | 310 | 280 | 0 | 30 | 0 | 30 | 0 | 0 | 51 | 0 | 0 | 43 | 17 | 11 | 33 | 12 | 140 | 80 | 0 | 18 | 0 | 43 | 0 | 50 | 0 | 0 | 0 | 62 | 0 | 0 | 205 | 17 | 0 | 10 | 300 | 16 | 2 | 0 | 130 | 0 | 0 | 100 | 0 | 80 | 0 | 12 | 17 | 120 | 400 | 85 | 105 | 17 | 0 | 260 | 17 | 17 | 114 | 58 | 12 | 250 | 71 | 0 | 35 | 17 | 0 | 17 | 0 | 95 | 35 | 330 | 17 | 0 | 310 | 10 | 350 | 0 | 0 |  | 801 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 50 | 70 | 0 | 130 | 25 | 110 | 0 | 0 | 0 | 35 | 20 | 85 | 28 | 42 | 40 | 52 | 38 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 414 | 94 | 0 | 50 | 32 | 113 | 0 | 0 | 55 | 1244 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 570 | 0 | 200 | 1300 | 0 | 0 |  | 8857 | 5363 | 14220 | 3856 | 902 | 2102 | 0 | 2991 | 3387 | 201 | 0 | 631 | 150 | 0 | 0 | 0 | 107.24
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 340 | 150 | 0 | 0 | 225 | 150 | 8 | 65 | 15 | 230 | 0 | 0 | 17 | 50 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 8 | 200 |  | 0 | 0 | 0 | 6 | 8 | 0 | 12 | 0 | 6 | 12 | 10 | 0 | 0 | 0 | 280 | 280 | 0 | 30 | 0 | 25 | 0 | 0 | 51 | 0 | 0 | 43 | 15 | 10 | 33 | 12 | 128 | 70 | 0 | 18 | 1.6 | 42 | 0 | 45 | 0 | 0 | 0 | 60 | 0 | 0 | 205 | 17 | 0 | 10 | 290 | 16 | 2 | 0 | 80 | 0 | 0 | 84 | 0 | 17 | 20 | 12 | 17 | 12 | 400 | 40 | 30 | 17 | 5 | 100 | 17 | 17 | 17 | 28 | 12 | 230 | 17 | 50 | 17 | 17 | 0 | 17 | 35 | 34 | 17 | 300 | 17 |  | 300 | 10 | 350 | 0 | 0 |  | 919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 28 | 34 | 30 | 8 | 24 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 50 | 0 | 35 | 15 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 38 | 6 | 100 | 70 | 0 |  | 400 | 30 | 140 | 1200 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 160 | 0 | 67 | 0 | 383 | 160 | 0 | 0 | 225 | 157 | 0 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 12 | 33 | 25 | 8 | 0 | 46 | 75 | 0 | 0 | 0 | 201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 0 | 0 | 0 | 310 | 275 | 0 | 30 | 0 | 27 | 0 | 0 | 51 | 0 | 0 | 0 | 15 | 11 | 33 | 12 | 106 | 70 | 0 | 0 | 1 | 43 | 0 | 44 | 0 | 0 | 0 | 62 | 0 | 0 | 203 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 10 | 0 | 17 | 0 | 401 | 57 | 17 | 0 | 2 | 0 | 0 | 15 | 0 | 0 | 12 | 230 | 0 | 22 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 280 | 0 | 0 | 306 | 0 | 354 | 0 | 0 | 0 | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 580 | 220 | 0 | 0 | 2 | 31 | 0 | 0 | 0 | 354 | 13 | 140 | 821 | 68 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
[22 empty] | 299565 | [26 empty] | 399366 | 399587 | [8 empty] | 299280 | [26 empty] | 299755 | [12 empty] | 299523 |  | 299563 |  | 399588 | 399244 | 299281 | 299229 | 299524 |  | 399747 |  |  |  |  | 399575 | 399337 | 399589 | 299230 | [7 empty] | 399245 |  | 299282 | 399274 |  | 399223 |  | 399630 | [12 empty] | 599468 | [32 empty] | 599787 |  | 499268 | 599634 | 43212 |  |  | 499270 | 599730 | [8 empty] | 599726 | [9 empty] | 292.3904
| Minimum Generation |  | 7754 | 5:00 | [202 empty] | 107687425
| Highest Generation |  | 11680 | 18:00 | [202 empty] | 107.6874 |  |  |  |  | 2.5533
| Day Peak Generation |  | 10201 | 12:00 | [202 empty] | 18682191
| Evening Peak Generation |  | 11680 | 18:00 | [202 empty] | 18.6822 |  |  | 35764948 |  | 2.9384
| HVDC Max Flow |  | 920 | 9:00 | [202 empty] | 22.2225 |  |  |  |  | 0.05712
| HVDC EvPeak Flow |  | 918 | 18:00 | [200 empty] | 232879968 |  | 2.8445 |  | 75.8945
| Load factor L.F |  | 83.08% | [166 empty] | 1275.5 | [36 empty] | 232.88

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-11-13
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-11-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10201 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7806
Evening Peak Generation : |  |  | 11680 | MW Hour : | 18:00 | Available Max Generation : |  | 13655
E.P. Demand (at gen end) : |  |  | 11680 | MW Hour : | 18:00 | Max Demand (Evening) : |  | 12000
Maximum Generation : |  |  | 11680 | MW Hour : | 18:00 | Reserve(Generation end) |  | 1655
Total Gen. (MKWH) : |  |  | 232.88 | System Load Factor : | 83.08% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 710 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-11-13
Actual : |  | 99.66 | Ft.(MSL) , | Rule curve : | 107.9 | Ft.( MSL )
Gas Consumed : |  | Total = | 841.43 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 110144700.404
: |  |  | Coal : | 536374100.96 | Oil : | 238554575.84 | Total : | 885073377.204
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4307.9931 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1182.1376 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1655.4666 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1438.4608 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1183.8221 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 880.2349 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 493.6451 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 411.1693 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 804.1802 |  |  | 0 | 0%
Total |  | 0 |  | 12357.1096 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:04 | 16:51 | Baroaulia 132/33kV S/S T2(415T) HT Scheduled S/D Due to Annual maintenance |  |  |  |  | 10.0MW load interruption.
08:04 | 16:51 | Baroaulia 132/33kV S/S T2(415T) HT Scheduled S/D Due to Annual maintenance
08:05 |  | Intraco Solar 30 MW Syncronized
08:05 | 13:16 | Halishahar 132/33kV S/S 423T(TR-3) HT Scheduled S/D Due to Due To 132/33 kV Tr-03
Transformer Annual Maintenance.
08:08 | 16:30 | Faridpur 132/33kV S/S Transformer-1 LT Scheduled S/D Due to Annual Maintenance
08:12 |  | Teknaf 20MW PP (Solartech) Shutdown
08:13 |  | Gazipur 100 MW PP Syncronized
08:16 |  | Anlima Energy Ltd. Syncronized
08:17 | 16:35 | Amnura 132/33kV S/S T-3 (426T) HT Scheduled S/D Due to Annual Maintenance
08:19 | 16:29 | Faridpur 132/33kV S/S Transformer-1 HT Scheduled S/D Due to Annual Maintenance
08:19 |  | Juldah 100 MW Unit-1 (Acorn) Syncronized
08:21 |  | Teknaf 20MW PP (Solartech) Syncronized
08:22 |  | Karnaphuli Power Ltd. Syncronized
08:24 | 16:47 | Rangpur-Saidpur 132kV Ckt-1 Scheduled S/D from Saidpur 132/33kV end Due to As the instructions
of ALDC, Bogura and QF-GMD-39 and from Rangpur 132/33kV end Due to Annual Maintenance Work
08:26 | 15:45 | Rajshahi 132/33kV S/S 132 kV RPP 50 Mw Scheduled S/D Due to Annual maintenance work.
08:27 |  | Siddhirganj 100 PP(Dutch Bangla) Syncronized
08:28 | 16:29 | Ishurdi-Pabna 132kV ckt Scheduled S/D from Ishurdi 132/33kV end Due to A/M and from Pabna 132/33kVend.
08:29 | 14:06 | Tangail 132/33kV S/S Tr-1 LT Scheduled S/D Due to Annual Maintenance
08:29 |  | Kanchan Purbachal Power Generation Ltd. Tripped
08:29 | 14:06 | Tangail 132/33kV S/S Tr-1 HT Scheduled S/D Due to Annual Maintenance
08:34 |  | Chandpur 115(Doreen) Syncronized
08:35 | 16:43 | Sirajganj 132/33kV S/S Sherpur-1 Scheduled S/D Due to Annual maintenance work
08:40 | 16:42 | Sherpur(Bogura)-Sirajgonj 132 kV Ckt-1 Scheduled S/D from Bog-Sherpur 132/33kV end Due to Annual maintenance
08:41 |  | Gagnagar 102 MW PP (Digital Power) Syncronized
08:42 | 16:36 | Sreemongol 132/33kV S/S 132/33kv T-1AB LT Scheduled S/D Due to Annual Maintenance.
08:42 | 16:35 | Sreemongol 132/33kV S/S 132/33kv T-1AB HT Scheduled S/D Due to Annual Maintenance.
08:44 |  | Meghnaghat 104 MW PP (OPCL) Syncronized
08:49 |  | Manikgonj 162MW PP(MPGL) Syncronized
08:52 | 16:55 | Ishwardi-Rooppur 132kV Ckt-1 Scheduled S/D from Ishurdi 132/33kV end Due to A/M and from
Ruppur 132/11kV end Due to Annual Maintenance
08:54 | 16:37 | Dohazari-Sikalbaha 132 kV Ckt-1 Scheduled S/D from Dohazari 132/33kV end Due to Annual
Maintenance Dead Line Checking
09:00 |  | Karnaphuli Hydro PP Unit 1,2,3 Control Room Syncronized with remarks:- unit-2
09:01 |  | Kodda 300 MW PP Unit-2 (Summit) Syncronized
09:02 |  | Madanganj 102 PP(Summit) Syncronized
09:03 |  | Tangail Palli Power Gen 22 MW Syncronized
09:06 |  | Sarishabari 3 MW Solar Plant Syncronized
09:11 |  | Rupsha 105 MW PP (Orion rupsha) Syncronized
09:12 |  | Karnaphuli Hydro PP Unit 4,5 Control Room Syncronized with remarks:- unit-5
09:17 | 15:52 | Sherpur 132/33kV S/S Bus A Scheduled S/D Due to Annual Maintenance.
09:17 | 16:28 | Beanibazar 132/33kV S/S 132 KV BUS-2 Scheduled S/D Due to Maintenance work
09:20 |  | Karnaphuli Hydro PP Unit 1,2,3 Control Room Shutdown with remarks:- unit-1
09:21 | 16:39 | Mymensingh-Netrokona 132kV Ckt-1 Scheduled S/D from Netrakona 132/33kV end Due to Annual
Maintenance and from Mymensingh 132/33kV end Due to Annual maintenance work
09:22 |  | Karnaphuli Hydro PP Unit 1,2,3 Control Room Syncronized with remarks:- unit-2
09:28 | 20:08 | Kallyanpur 132/33kV S/S GT-2 (132kV) HT Scheduled S/D Due to Annual Maintenance 33 kv Right Bus by DPDC.
09:36 | 16:50 | Joydebpur-Kodda B 132 kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to Annual Maintenance
09:36 | 16:45 | Mirpur-Uttara 3PH 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to Annual maintenance
09:49 | 11:49 | Kabirpur 132/33kV S/S XFR, T-3 HT Scheduled S/D Due to Tan Delta test work done by SPMD-1 of T-3
09:49 | 10:50 | Kabirpur 132/33kV S/S XFR, T-3 LT Scheduled S/D Due to Ten Delta testing work done by SPMD-1 of T-3 x-former
09:56 |  | Jodiac Power Syncronized
10:02 | 16:28 | BIPTC S/S 20DF42 Scheduled S/D Due to Annual Maintenance
10:14 | 16:30 | Madanganj-Shitalakhya 132kV ckt-1 Forced S/D from Shitalakhya 132/33kV end.
10:15 |  | Bagura 113 MW PP (Confidence)-2 Syncronized
10:16 | 16:32 | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Scheduled S/D Due to Annual Maintenance
10:22 |  | Mirsharai 150 MW Syncronized
10:24 |  | Chandpur 200MW (Desh energy) Syncronized
10:35 |  | Keraniganj 100 MW PP (Powerpac) Syncronized
10:39 | 12:41 | Kabirpur - Manikganj 132kV Ckt-1 Scheduled S/D from Kabirpur 132/33kV end Due to Relay test done by Spmd
10:44 |  | Chowmuhani 113 MW Syncronized
10:45 |  | Madanganj-55 MW PP(Summit) Syncronized
10:52 |  | Jangalia 52 MW PP (Lakdanavi) Syncronized
10:57 |  | Hathazari 100 MW peaking PP Syncronized
11:04 |  | Bashkhali 400kV bus was split.
11:20 |  | Ashuganj 150MW PP (Midland) Syncronized
11:22 | 17:53 | Rampal 400/230kV S/S Bus Reactor Scheduled S/D Due to Routine maintenances.
11:23 |  | Raozan 25 MW PP Syncronized
11:25 |  | Gazipur 52 MW PP Syncronized
11:26 |  | Meghnaghat 100 MW(IEL) Syncronized
11:33 |  | Feni Lanka Power Syncronized
11:42 |  | Confidence Power Bogura Unit-1 113 MW Syncronized
11:45 |  | Bhairob 54.5 MW Syncronized
11:52 |  | Kodda 150 MW PP B-R Syncronized
11:54 | 14:56 | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Kabirpur 132/33kV end Due to To relay test
work done by spmd 2
11:57 |  | Khulna 115 PP MW (KPCL-2) Syncronized
12:00 |  | Day peak generation: 10201 MW
12:03 |  | Ashuganj 450 MW CCPP(North) Syncronized with remarks:- ST
| 12:11 | Khulna(S) 230/132kV S/S TR-1 HT is restored.
| 12:12 | Khulna(S) 230/132kV S/S TR-1 LT is restored.
12:56 |  | Kabirpur 132/33kV S/S Aux. X-former-1 HT Scheduled S/D Due to Relay and tan delta test work done by spmd
12:57 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- ST
13:13 |  | Sikalbaha 225MW ST was sync.
13:22 |  | Ashugonj North 360MW GT was forced shutdown due to high vibration in generator bearing.
13:22 |  | Ashuganj 450 MW CCPP(North) Shutdown with remarks:- GT
13:35 |  | Feni 11 MW PP (Doreen) Shutdown
13:35 |  | Feni 22MW PP (Doreen) Tripped with remarks:- 33 kv failure.
13:56 | 15:24 | Kabirpur 132/33kV S/S XFR, T-I HT Scheduled S/D Due to Annual maintenance (Relay testing) |  |  |  |  | 70.0MW load interruption.
13:56 |  | Kabirpur 132/33kV S/S Aux. X-former-1 HT Scheduled S/D Due to Relay and tan delta test work done by spmd
| 13:58 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
14:01 |  | Ashuganj 450 MW CCPP(North) Syncronized with remarks:- GT
14:01 |  | Ashugonj North 360MW GT was synchronized.
14:40 | 15:02 | Benapole 132/33kV S/S Transformer-1(406T) LT Tripped showing ABB REF630 relays Due to Benapole |  |  |  |  | 38.0MW load interruption.
33 kv feeder fault
14:40 | 15:05 | Benapole 132/33kV S/S Transformer-2(416T) LT Tripped showing ABB REF630 relays Due to Benapole
33 KV feeder fault
15:15 |  | Shahjibazar 132/33kV S/S TR-06 LT Scheduled S/D Due to 33KV side B phase Incoming heat shrink burn.
Load flow by TR-04
15:15 |  | Shahjibazar 132/33kV S/S TR-06 HT Scheduled S/D Due to TR-06 33KV side B phase Incoming heat
shrink burn. Load flow by TR-04.
15:35 |  | Feni 11 MW PP (Doreen) Syncronized
| 15:54 | Gopalganj 400/132kV S/S ATR-03 HT is restored.
| 15:59 | Gopalganj 400/132kV S/S ATR-03 LT is restored.
| 16:07 | Jashore 132/33kV S/S JH-1(L2) is restored.
| 16:07 | Jhenaidah 230/132kV S/S Jhenaidah2-Jashore Ckt-1 is restored.
16:17 |  | Sympa Solar Power 8 MW Syncronized
16:21 |  | Manikganj 55 MW PP (Northern) Syncronized
16:33 |  | Nababganj 55 MW PP (Southern power ) Syncronized
16:39 |  | Kaptai 7 MW Solar PP Shutdown
16:40 |  | Feni 22MW PP (Doreen) Shutdown
16:42 |  | Feni 22MW PP (Doreen) Syncronized
16:44 |  | Kamalaghat 54 MW PP(Banco Energy) Syncronized
16:45 |  | Santahar 50 MW Peaking PP Syncronized
16:45 |  | Chapainawabganj 100 MW Peaking PP Syncronized
16:46 |  | Rangpur 113 MW PP (Confidence) Syncronized
16:50 |  | United Payra Power Ltd. Syncronized
16:56 |  | Madhumati 100 MW PP Syncronized
17:01 |  | Energypac Power Venture Thakurgaon Ltd. Syncronized
| 17:04 | Barishal 230/132kV S/S T-4 HT is restored.
| 17:05 | Amnura 132/33kV S/S T-3 (426T) LT is restored.
| 17:10 | Barishal 230/132kV S/S T-4 LT is restored.
17:10 |  | Sarishabari 3 MW Solar Plant Shutdown
17:11 |  | Teknaf 20MW PP (Solartech) Shutdown
17:16 |  | Sirajgonj 6.55 MW Solar Shutdown
17:17 |  | Teesta Solar Limited Shutdown
17:22 |  | Intraco Solar 30 MW Shutdown
17:22 |  | Spectra Solar Plant Ltd. Shutdown
17:23 |  | Mongla Orion 100 MW Solar PP Shutdown
17:29 |  | Sutiakhali 50 MW Solar PP Shutdown
17:30 |  | Sympa Solar Power 8 MW Shutdown
17:41 |  | Natore 52 MW PP (Rajlanka) Syncronized
17:43 |  | Katakhali 50 MW PP (Northern) Syncronized
18:00 |  | Evening Peak Generation :11680 MW
18:01 |  | Barisal 110 MW PP (Summit ) Syncronized
18:02 |  | Ashugonj North 360MW ST was synchronized.
18:09 |  | Madhumati 100 MW PP Shutdown
18:13 |  | Khulna 115 PP MW (KPCL-2) Shutdown
18:30 |  | Santahar 50 MW Peaking PP Shutdown with remarks:- due to zero demand
19:23 |  | Kanchan Purbachal Power Generation Ltd. Syncronized
19:31 |  | Katakhali 50 MW PP (Northern) Shutdown
19:37 |  | Barisal 110 MW PP (Summit ) Shutdown
19:38 |  | Feni Lanka Power Shutdown
19:41 |  | Natore 52 MW PP (Rajlanka) Shutdown
19:42 |  | Chapainawabganj 100 MW Peaking PP Shutdown
19:50 |  | United Payra Power Ltd. Shutdown
19:54 |  | Keraniganj 100 MW PP (Powerpac) Shutdown
20:05 | 20:38 | Jamalpur 132/33kV S/S T-3 HT Scheduled S/D Due to 33kv bus coupler D.S. red hot . |  |  |  |  | 12.0MW load interruption.
20:05 | 20:38 | Jamalpur 132/33kV S/S T-3 LT Scheduled S/D Due to 33kv bus coupler D.S. red hot .
| 20:08 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 HT is restored.
| 20:08 | Hasnabad 132/33kV S/S 132/33kV 414 T-2 LT is restored.
20:21 |  | Bhairob 54.5 MW Shutdown
20:26 |  | Energypac Power Venture Thakurgaon Ltd. Shutdown
20:47 |  | Hathazari 100 MW peaking PP Shutdown
20:48 |  | Confidence Power Bogura Unit-1 113 MW Shutdown
20:59 |  | Rangpur 113 MW PP (Confidence) Shutdown
21:13 |  | Manikganj 55 MW PP (Northern) Shutdown
21:24 |  | Siddhirganj 100 PP(Dutch Bangla) Shutdown
21:25 |  | Gagnagar 102 MW PP (Digital Power) Shutdown
21:30 |  | Meghnaghat 100 MW(IEL) Shutdown
21:36 |  | Narshingdi 22 MW PP (Doreen) Tripped
21:37 |  | Ashuganj 195 MW PP (APSCL-United) Syncronized
21:47 |  | Kamalaghat 54 MW PP(Banco Energy) Shutdown
22:01 |  | Nababganj 55 MW PP (Southern power ) Shutdown
22:19 |  | Bibiyana South 400 MW ST was sync.
22:19 |  | Bibiyana South 400 MW Syncronized with remarks:- st
22:35 |  | Narshingdi 22 MW PP (Doreen) Syncronized
22:39 |  | Gazipur 52 MW PP Shutdown
22:45 |  | Bagura 113 MW PP (Confidence)-2 Shutdown
22:45 |  | Mymensingh 200 MW PP (United) Shutdown
22:47 |  | Kanchan Purbachal Power Generation Ltd. Shutdown
22:47 |  | Kamalaghat 54 MW PP(Banco Energy) Shutdown
22:47 |  | Kodda 150 MW PP B-R Shutdown
22:51 |  | Tangail Palli Power Gen 22 MW Shutdown
22:54 |  | Kodda 300 MW PP Unit-2 (Summit) Shutdown
22:54 |  | Gazipur 100 MW PP Shutdown
22:55 |  | Raozan 25 MW PP Shutdown
22:56 |  | Manikgonj 162MW PP(MPGL) Shutdown
22:58 |  | Madanganj-55 MW PP(Summit) Shutdown
23:01 |  | Madanganj 102 PP(Summit) Shutdown
23:12 |  | Ashuganj 150MW PP (Midland) Shutdown with remarks:- manual update
23:17 |  | Jangalia 52 MW PP (Lakdanavi) Shutdown
23:26 |  | Rupsha 105 MW PP (Orion rupsha) Shutdown
23:28 |  | Kodda 149 MW PP Unit-1 (Summit) Shutdown
23:48 |  | Meghnaghat 104 MW PP (OPCL) Shutdown
23:51 |  | Jamalpur 115 MW PP (United) Shutdown
23:57 |  | Tangail 22 MW PP (Doreen) Shutdown
00:12 |  | Mirsharai 150 MW Shutdown
00:37 |  | Jodiac Power Shutdown
00:42 |  | Anwara 300 MW PP (United) Shutdown
00:48 |  | Juldah 100 MW PP Unit-3 (Acorn) Shutdown
00:49 |  | Juldah 100 MW Unit-1 (Acorn) Shutdown
00:54 |  | Chandpur 115(Doreen) Shutdown
00:58 |  | Chowmuhani 113 MW Shutdown
01:14 |  | Ashuganj 195 MW PP (APSCL-United) Shutdown
01:36 |  | Chandpur 200MW (Desh energy) Shutdown
01:36 |  | Sikalbaha 105 MW PP (Baraka Sikalbaha) Shutdown
01:36 |  | Ashuganj 51 MW PP (Midland) Shutdown
01:36 |  | Anlima Energy Ltd. Shutdown
01:40 |  | Patenga 50MW PP (Baraka) Shutdown
01:40 |  | Karnaphuli Power Ltd. Shutdown
01:48 |  | Juldah unit-2 (Acorn) Shutdown
03:28 |  | Narshingdi 22 MW PP (Doreen) Shutdown
03:40 |  | Fenchugonj 51 MW PP (Barakatullah) Shutdown
03:40 |  | Sylhet 10MW PP (Desh) Shutdown with remarks:- NLDC no demand.
03:40 |  | Feni 11 MW PP (Doreen) Shutdown
04:01 |  | Feni 22MW PP (Doreen) Planned Shutdown with remarks:- NLDC DEMAND ZERO
04:14 |  | Jangalia 33MW PP (Summit) Shutdown
05:00 |  | Minimum Generation: 7806 MW
05:53 |  | Kodda 150 MW PP B-R Syncronized
05:59 |  | BIPTC S/S 20DF21 Tripped showing 20DF21 Filter. relays.
06:00 |  | Teknaf 20MW PP (Solartech) Syncronized
06:02 |  | Kaptai 7 MW Solar PP Syncronized
06:04 |  | Sutiakhali 50 MW Solar PP Syncronized
06:10 |  | Ashuganj CCPP 225 MW Tripped with remarks:- GT
06:10 |  | Spectra Solar Plant Ltd. Syncronized
06:10 |  | Ashuganj 225MW tripped due to GT comp. serge protection trip |  |  |  |  | 130MW load interruption.
06:11 |  | Mongla Orion 100 MW Solar PP Syncronized
06:13 |  | Intraco Solar 30 MW Syncronized
06:15 |  | Sarishabari 3 MW Solar Plant Syncronized
06:15 |  | Sympa Solar Power 8 MW Syncronized
06:17 |  | Sirajgonj 6.55 MW Solar Syncronized
06:21 |  | Teesta Solar Limited Syncronized
06:22 |  | Jangalia 33MW PP (Summit) Syncronized
06:29 |  | Fenchugonj 51 MW PP (Barakatullah) Syncronized
06:33 |  | Sylhet 10MW PP (Desh) Syncronized with remarks:- NLDC demand.
06:34 |  | Ashuganj 51 MW PP (Midland) Syncronized
06:36 |  | Feni 22MW PP (Doreen) Syncronized
06:39 |  | Mymensingh 200 MW PP (United) Syncronized
06:43 |  | Jamalpur 115 MW PP (United) Syncronized
06:45 |  | Narshingdi 22 MW PP (Doreen) Syncronized
06:50 |  | Chandpur 200MW (Desh energy) Syncronized
06:51 |  | Juldah unit-2 (Acorn) Syncronized
06:58 |  | Joydebpur-Kodda B 132 kV Ckt-1 Scheduled S/D from Joydebpur 132/33kV end Due to OPGW Cable Change
06:58 |  | Joydebpur-Kodda B 132 kV Ckt-2 Scheduled S/D from Joydebpur 132/33kV end Due to OPGW Cable Change
07:01 |  | Gazipur 52 MW PP Syncronized
07:05 |  | Karnaphuli Power Ltd. Syncronized
07:05 |  | Feni 11 MW PP (Doreen) Syncronized
07:10 |  | Chowmuhani 132/33kV S/S TR1-415T HT Forced S/D Due to For Maintenance Works
07:22 |  | Ashuganj 50 MW PP Syncronized
07:25 |  | Gazipur 100 MW PP Syncronized
07:33 |  | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Scheduled S/D Due to Annual Maintenance
07:40 |  | Bhulta-Rampura 230 kV Ckt-4 Scheduled S/D from Rampura 230/132kV end Due to Annual Maintenance
07:41 |  | Ashuganj 195 MW PP (APSCL-United) Syncronized
07:45 |  | Natore 132/33kV S/S TR-3 (425 T) LT Scheduled S/D Due to Year maintenance
07:46 |  | Natore 132/33kV S/S TR-3 (425 T) HT Scheduled S/D Due to Yearly maintenance
07:54 |  | Aminbazar-Airport(Old) 230kV Ckt-2 Scheduled S/D from Aminbazar 400/230/132kV end Due to
Annual maintenance and from Agargaon 230/132kV end Due to Annual Maintenance

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-11-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 76 | 1485590 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 335 | 8153090 | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 147 | 3760000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 225 | 4495800 | GT-1 under S/D due to gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 99 | 542400 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 140 | 3477935 | GT-1 under S/D due to gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 65 | 631727 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 191611 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 29 | 293768 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 18 | 388260 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 55 | 566438 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 230 | 5581475 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 66 | 630288 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 129600 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 318240 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 136205 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 140730 | Fuel shortage
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 734640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 720000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 604500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 20 | 143040 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 50 | 687491 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 56 | 616896 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 70 | 429120 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 71 | 875520 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 384480 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 208116
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 138600 | Fuel shortage
| Meghnaghat Unique power |  | IPP | 586 | 0 | 0 | 0 | On test.
| Summit Meghanghat-2 589 MW(Gas) |  | IPP | 589 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5422 | 2273 | 40844060
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 8 | 138344 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 133920
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 193920 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 121 | 2938440 | Unit-2 under maint.
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 198 | 2934036
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 17 | 337054 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 16 | 123984 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 0 | 0 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 12 | 188760 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 12 | 235200 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 269760 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 208320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 222 | 1994727 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 269296 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 17 | 306945 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 12 | 236160 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 301091 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 17 | 259273 | Fuel shortage
| SS Power I |  | SS Power | 1*612 | 612 | 309 | 7309090 | Machine problem
| Cox's Bazar Wind |  | IPP | 66 | 0 | 4 | 57120 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 336 | 7367272 | On test.
| Chattogram area Total |  |  |  | 3157 | 1368 | 25828872
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 178 | 4246000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 25 | 3961500 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6810000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 330 | 7045200 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 0 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 0 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 16727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1075136
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 115 | 881527 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Under maint.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 24 | 258240 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 314568 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 233280
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 2844480
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 772700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 358906 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 278630 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 0 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 160740 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 506520 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 156960 | 33 kV feeder problem.
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 93 | 692160 | Fuel shortage
| Cumilla Area Total |  |  |  | 2896 | 1463 | 30613274
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 73 | 1910400 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Contract Expired
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 0 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11650
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 95 | 765600 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 88 | 997200 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 302340
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 81120 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 262 | 4068310
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 41 | 991000 | Under maint.
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 944400
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 0 | 0 | Gas shortage
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 120960 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 57 | 1259616
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 0 | Gas shortage
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 201 | 5107040
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 406000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 380160 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 6874000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 401 | 9302000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 240840
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 45 | 2346300 | ST U/M
| Sylhet Area Total |  |  |  | 2427 | 1110 | 27972316
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 918 | 22222545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 94080 | High voltage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 0 | 0 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 94 | 559200
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 15 | 11952 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 491760
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 336 | 0 | 0
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 453 | 9396364
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3237 | 1496 | 32775901
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 24864 | Low demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 24 | 471800 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 130 | 2436000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 880 | 19373500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4937891
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 96000 | High voltage
| Barisal 307 MW |  | IPP | 307*1 | 307 | 200 | 3806400 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1489 | 31146455
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 0 | 0 | Reserve
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 8 | 12780 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7776509
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 47524
135 | Bogra 22 MW PP (GBB) |  | RPP | 0 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236862
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 16459 | Low demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 64 | 109336 | Low demand
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 43 | 566400 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 391008 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33600
| Adani Power Jharkhanda Ltd |  | Imported power | 748*2 | 1496 | 1217 | 24506964
| Rajshahi Area Total |  |  |  | 3631 | 1858 | 33697442
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 170 | 4134900 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 101 | 273379 | Low demand
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 996
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 90 | 179328 | Low demand
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 211175
| Teesta Solar Limited |  | BPCL | 16*12.5 | 200 | 0 | 1133560
| Rangpur Area Total |  |  |  | 950 | 361 | 5933338
| Total |  |  |  | 24599 | 11680 | 232879968
| Eastern Grid Total |  |  |  | 14516 | 6476 | 129326832
| Western Grid Total |  |  |  | 10083 | 5204 | 103553136
| National Grid Total |  |  |  | 24599 | 11680 | 232879968
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-11-12
| (a) ENTIRE EASTERN GRID : |  | 7965.09 | MW | (b) ENTIRE WESTERN GRID : |  | 3220.3 | MW
| i) Dhaka area |  | 4489.59 | MW | i) Khulna area |  | 1222.2 | MW
| ii) Chittagong area |  | 1176.5 | MW | ii) Rajshahi area |  | 998.6 | MW
| iii) Comilla area |  | 1017 | MW | iii) Barisal area |  | 305.5 | MW
| iv) Mymensingh area |  | 860 | MW | iv) Rangpur area |  | 694 | MW
| v) Sylhet area |  | 422 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11185.39 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 22 | 18:30 | Kamrangirchar | 47.4 | 18:00 | Narinda | 62 | 13:00 | Sherpur | 108 | 18:00
2 | AKSML | 118 | 12:00 | Chowmuhani | 158 | 18:00 | Kaptai | N/A | N/A | Narshingdi | 145 | 22:00 | Shikalbaha | 26 | 12:00
3 | Aftabnagar | 30 | 13:00 | Chuadanga | 77 | 18:00 | Kazla | 78 | 00:00 | Natore | 97 | 18:00 | Shikalbaha-230 | N/A | N/A
4 | Agargaon | 79 | 13:00 | Coxsbazar | 110 | 18:00 | Keranigonj | 60 | 19:00 | Nawabganj | 29.4 | 21:00 | Shitalakhya | 94.2 | 18:00
5 | Agrabad | 80 | 14:00 | Cumilla(N) | 119 | 18:00 | Khagrachori | 24 | 18:00 | Netrakona | 90 | 19:00 | Sholosohor | 38 | 11:00
6 | Amnura | 35 | 18:00 | Cumilla(S) | 145 | 18:00 | Khulna | 70 | 18:00 | New | 45.6 | 11:00 | Shyampur | 152 | 09:00
7 | Ashuganj | 55 | 13:00 | Daudkandi | 118 | 19:00 | Khulshi | 173 | 13:00 | Niamatpur | 49 | 20:00 | Siddhirganj | 106 | 14:00
8 | BIPTC | N/A | N/A | Dhaka | 36 | 12:00 | Kishoreganj | 112 | 18:00 | Noapara | 36 | 18:00 | Sirajganj | 81 | 18:30
9 | BSRM | 136 | 03:00 | Dhamrai | 92 | 12:00 | Kodda | 262 | 15:00 | PHP | 3 | 11:00 | Sonargaon | 91 | 17:00
10 | Bagerhat | 67 | 18:00 | Dhanmondi | 111.7 | 13:00 | Kulaura | 32 | 18:00 | Pabna | 88 | 18:00 | Sreemongol | 49 | 18:00
11 | Bakulia | 84 | 18:00 | Dohazari | 66 | 18:30 | Kurigram | 51 | 18:00 | Palashbari | 80 | 18:00 | Sreepur | 58 | 15:00
12 | Banani | 28.4 | 14:00 | Faridpur | 108 | 18:30 | Kushtia | 106 | 18:00 | Panchagarh | 45 | 18:00 | Srinagar | 30.28 | 20:00
13 | Bangabhaban | 13 | 11:00 | Fatullah | 65 | 15:00 | Lalbag | 92 | 13:00 | Patuakhali | 72.5 | 21:00 | Sunamganj | 40 | 20:00
14 | Barapukuria | 47 | 18:00 | Fenchuganj | 27 | 17:00 | Lalmonirhat | 35 | 18:00 | Payra | 16 | 18:00 | Sylhet | 16 | 18:00
15 | Barguna | 14 | 21:00 | Feni | 89 | 18:00 | MI_Cement | 13.2 | 13:00 | Postogola | 51 | 13:00 | Sylhet-132 | 106 | 19:00
16 | Barishal | 82 | 13:00 | GPH | 93 | 06:00 | Madanganj | 32 | 00:00 | Purbachal | 18 | 19:00 | TK | 22 | 19:00
17 | Barishal-230 | 64 | 18:00 | Ghorashal | 53 | 21:00 | Madaripur | 66 | 19:30 | Purbasadipur | 91 | 18:00 | Tangail | 166 | 18:00
18 | Baroaulia | 57 | 01:00 | Goalpara | 32 | 18:00 | Madartek | 68.12 | 18:00 | Rahim | 48 | 13:00 | Thakurgaon | 71 | 18:00
19 | Baroirhat | 37 | 18:00 | Gollamari | 43 | 13:00 | Madunaghat | 31 | 18:30 | Rajbari | 48 | 18:00 | Tongi | 112 | 17:00
20 | Bashundhara | 131 | 18:00 | Gopalganj | 75.2 | 18:00 | Magura | 44 | 18:00 | Rajendrapur | 90 | 18:00 | Ullon | 34 | 18:00
21 | BashundharaCement | 6 | 07:00 | Gulshan | 98 | 13:00 | Mahasthangarh | 52 | 18:00 | Rajshahi | 104 | 18:00 | Uttara | 54 | 14:00
22 | Beanibazar | 44 | 18:00 | Halishahar | 92 | 18:00 | Manikganj | 93 | 18:00 | Rajshahi-230 | 23 | 13:00 | UttaraNew | 56 | 13:00
23 | Benapole | 44 | 18:00 | HaripurSBU | 159 | 12:00 | Maniknagar | 62 | 13:00 | Ramganj | 70 | 18:00 | Zigatola | 93 | 13:00
24 | Bhaluka | 131 | 18:30 | Hasnabad | 80 | 11:00 | Matarbari | 20 | 19:00 | Rampur | 25 | 19:00
25 | Bhandaria | 34 | 20:00 | Hathazari | 75 | 18:00 | Matuail | 68 | 11:00 | Rangamati | 16 | 18:00
26 | Bhangura | 22 | 18:00 | Ishurdi | 59 | 18:00 | Millgate | 92 | 15:00 | Rangpur | 102 | 18:00
27 | Bheramara(GK) | 43 | 18:00 | Jaldhaka | 57 | 18:00 | Mirpur | 118 | 14:00 | Ruppur | 5.4 | 16:00
28 | Bhulta | 217 | 00:00 | Jamalpur | 107 | 19:00 | Mirsorai | 4 | 09:00 | SSM | 15 | 01:00
29 | Bog-Sherpur | 48 | 18:00 | Jashore | 100 | 18:00 | Mirzapur | 0 | 00:00 | Saidpur | 83 | 18:00
30 | Bogura | 117 | 18:30 | Jhenaidah | 90 | 18:00 | Mithapukur | 32 | 18:00 | Satkhira | 85 | 18:00
31 | Borhanuddin | 32 | 19:00 | Joydebpur | 152 | 12:00 | Modern | 0 | 00:00 | Satmasjid | 82 | 18:00
32 | Brahmanbaria | 125 | 18:00 | Joypurhat | 37 | 18:00 | Mogbazar | 101.9 | 15:00 | Savar | 154 | 15:00
33 | Cantonment | 122 | 13:00 | Juldah | 19 | 12:00 | Mongla | 29 | 12:00 | SevenRings | 4.86 | 12:00
34 | Chandpur | 50 | 18:00 | KSRM | 39 | 08:00 | Motijheel | 35 | 13:00 | ShahCement | 34 | 17:00
35 | Chandraghona | 25 | 18:00 | Kabirpur | 241 | 18:00 | Munshiganj | 75 | 18:00 | Shahjadpur | 67 | 18:00
36 | Chapai | 48 | 13:00 | Kachua | 51 | 18:00 | Mymensingh | 159 | 18:00 | Shahjibazar | 93 | 18:00
37 | Charsaidpur | 26 | 14:00 | Kallyanpur | 69 | 21:00 | Naogaon | 85 | 18:00 | Shahmirpur | 43.5 | 17:00
38 | Chauddagram | 42 | 18:00 | Kalurghat | 36 | 15:00 | Narail | 40 | 18:00 | Shariatpur | 51 | 20:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-11-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 402 | 03:00 | 387 | 12:00 | Gopalganj | 411 | 04:00 | 396 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | 388 | 18:00 | 376 | 12:00
| Bhulta | 404 | 20:00 | 387 | 12:00 | Madunaghat_I | N/A | N/A | N/A | N/A
| Bibiana | 406 | 22:00 | 397 | 12:00 | Payra | 417 | 01:00 | 409 | 12:00
| BIPTC | 400 | 02:00 | 395 | 13:00 | Rahanpur | 413 | 03:00 | 401 | 12:00
| Bogura | N/A | N/A | N/A | N/A | Rampal | 413 | 05:00 | 401 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 04:00 | 226 | 12:00 | Hasnabad | 237 | 19:30 | 227 | 11:00
| AKSML | 230 | 20:00 | 216 | 12:00 | Hathazari | 230 | 19:00 | 218 | 12:00
| Aminbazar | 239 | 18:30 | 229 | 11:00 | Ishurdi | 236 | 03:00 | 222 | 11:00
| Ashuganj | 239 | 19:30 | 228 | 12:00 | Jhenaidah | 232 | 03:00 | 219 | 11:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 238 | 03:00 | 229 | 12:00
| Baghabari | 229 | 00:00 | 220 | 10:00 | Keranigonj | 237 | 05:00 | 226 | 12:00
| Barapukuria | 225 | 02:00 | 219 | 08:00 | Khulna(S) | 240 | 05:00 | 228 | 11:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | N/A | N/A | N/A | N/A
| Barishal | 240 | 04:00 | 234 | 12:00 | Maniknagar | 236 | 03:00 | 227 | 12:00
| Bheramara | 235 | 22:00 | 223 | 08:00 | Meghnaghat | 243 | 18:30 | 238 | 10:00
| Bhulta | 240 | 19:00 | 229 | 12:00 | Mirsorai | 228 | 20:00 | 219 | 12:00
| Bibiana | 234 | 19:00 | 226 | 12:00 | Rajshahi | 235 | 03:00 | 220 | 11:00
| BIPTC | 236 | 03:00 | 222 | 08:00 | Rampal | 239 | 05:00 | 229 | 12:00
| Bogura | 235 | 04:00 | 133 | 20:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 243 | 04:00 | 240 | 07:00 | Rampura | 237 | 20:00 | 228 | 12:00
| BSRM | 230 | 17:00 | 218 | 12:00 | Shikalbaha | 228 | 20:00 | 214 | 03:00
| Cumilla(N) | 236 | 19:00 | 224 | 12:00 | Shyampur | 236 | 04:00 | 227 | 12:00
| Fenchuganj | 233 | 00:00 | 229 | 12:00 | Siddhirganj | 239 | 05:00 | 232 | 10:00
| Ghorashal | 240 | 00:00 | 240 | 00:00 | Sirajgonj | 239 | 06:00 | 230 | 12:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 235 | 19:30 | 225 | 11:00
| GPH | 228 | 19:00 | 216 | 06:00 | Tongi | 236 | 19:30 | 222 | 12:00
| Haripur | 237 | 18:30 | 228 | 12:00
| 132 kV | KV |  | KV |  | Tongi
| Aftabnagar | 137 | 03:00 | 130 | 12:00 | Lalbag | 136 | 04:00 | 128 | 12:00
| Agargaon | 137 | 04:00 | 130 | 12:00 | Lalmonirhat | 134 | 19:00 | 126 | 11:00
| Agrabad | 133 | 19:00 | 124 | 12:00 | Madanganj | 136 | 18:30 | 129 | 11:00
| AKS | 132 | 19:00 | 124 | 12:00 | Madaripur | 132 | 19:00 | 119 | 13:00
| Aminbazar | 138 | 01:00 | 131 | 11:00 | Madartek | 137 | 05:00 | 129 | 12:00
| Amnura | 139 | 19:00 | 128 | 18:00 | Madunaghat | 134 | 18:30 | 126 | 12:00
| Ashuganj | 142 | 18:30 | 139 | 11:00 | Magura | 141 | 01:00 | 130 | 17:00
| Bagerhat | 134 | 16:00 | 124 | 12:00 | Mahasthangarh | 137 | 03:00 | 130 | 12:00
| Bakulia | 135 | 19:30 | 127 | 06:00 | Manikganj | 134 | 18:00 | 127 | 16:00
| Banani | 138 | 02:00 | 127 | 12:00 | Maniknagar | 138 | 03:00 | 132 | 12:00
| Bangabhaban | 139 | 04:00 | 131 | 12:00 | Matarbari | 132 | 22:00 | 118 | 12:00
| Barapukuria | 140 | 04:00 | 134 | 08:00 | Matuail | 135 | 20:00 | 129 | 11:00
| Barguna | 135 | 04:00 | 131 | 12:00 | Millgate | 138 | 02:00 | 126 | 12:00
| Barishal | 137 | 06:00 | 129 | 11:00 | Mirpur | 137 | 03:00 | 129 | 12:00
| Barishal-230 | 137 | 03:00 | 132 | 12:00 | Mirzapur | 135 | 18:30 | 129 | 12:00
| Baroaulia | 134 | 19:00 | 126 | 12:00 | Mithapukur | 137 | 19:00 | 113 | 23:00
| Baroirhat | 134 | 19:00 | 125 | 14:00 | MI_Cement | 137 | 19:00 | 129.6 | 11:00
| Bashundhara | 138 | 02:00 | 127 | 12:00 | Modern | 133 | 19:30 | 126 | 11:00
| BashundharaCement | 136 | 18:30 | 129 | 11:00 | Mogbazar | 137 | 05:00 | 131 | 12:00
| Beanibazar | 129 | 00:00 | 126 | 12:00 | Mongla | 133 | 15:00 | 123 | 12:00
| Benapole | 139 | 22:00 | 126 | 11:00 | Motijheel | 139 | 04:00 | 131 | 12:00
| Bhaluka | 134 | 03:00 | 127 | 12:00 | Munshiganj | 137 | 19:30 | 129 | 12:00
| Bhandaria | 134 | 05:00 | 126 | 11:00 | Mymensingh | 138 | 19:00 | 127 | 12:00
| Bhangura | 141 | 02:00 | 132 | 12:00 | Naogaon | 134 | 04:00 | 127 | 10:00
| Bheramara | 137 | 03:00 | 129 | 12:00 | Narail | 140 | 02:00 | 132 | 12:00
| Bheramara(GK) | 136 | 19:30 | 129 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bhulta | 127 | 19:30 | 119 | 12:00 | Narshingdi | 128 | 03:00 | 124 | 12:00
| Bog-Sherpur | 139 | 04:00 | 131 | 11:00 | Natore | 138 | 03:00 | 130 | 12:00
| Bogura | 138 | 06:00 | 132 | 10:00 | Nawabganj | 136 | 03:00 | 129 | 12:00
| Bogura-230 | 139 | 04:00 | 130 | 12:00 | Netrakona | 134 | 18:00 | 129 | 02:00
| Brahmanbaria | 128 | 05:00 | 124 | 11:00 | New | 138 | 03:00 | 127 | 12:00
| Cantonment | 137 | 03:00 | 130 | 12:00 | Niamatpur | 134 | 05:00 | 125 | 12:00
| Chandpur | 137 | 19:00 | 123 | 12:00 | Noapara | 136 | 02:00 | 127 | 10:00
| Chandraghona | 135 | 19:00 | 127 | 12:00 | Pabna | 139 | 03:00 | 126 | 12:00
| Chapai | 135 | 04:00 | 130 | 12:00 | Palashbari | 134 | 02:00 | 128 | 08:00
| Charsaidpur | 137 | 19:30 | 130 | 11:00 | Panchagarh | 133 | 18:00 | 120 | 12:00
| Chauddagram | 135 | 19:00 | 125 | 12:00 | Patuakhali | 134 | 04:00 | 132 | 00:00
| Chhatak | 129 | 00:00 | 127 | 12:00 | Payra | 136 | 03:00 | 133 | 11:00
| Chowmuhani | 132 | 22:00 | 121 | 12:00 | PHP | 134 | 19:00 | 124 | 12:00
| Chuadanga | 139 | 04:00 | 130 | 12:00 | Postogola | 138 | 19:00 | 131 | 12:00
| Coxsbazar | 125 | 19:30 | 116 | 12:00 | Purbachal | 138 | 01:00 | 126 | 12:00
| Cumilla(N) | 139 | 19:00 | 130 | 12:00 | Purbasadipur | 132 | 03:00 | 122 | 12:00
| Cumilla(S) | 138 | 19:00 | 126 | 15:00 | Rahanpur | 137 | 01:00 | 133 | 10:00
| Daudkandi | 130 | 16:00 | 123 | 00:00 | Rahim | 135 | 19:00 | 130 | 10:00
| Dhaka | 137 | 02:00 | 130 | 12:00 | Rajbari | 133 | 04:00 | 126 | 11:00
| Dhamrai | 136 | 03:00 | 129 | 12:00 | Rajendrapur | 135 | 18:30 | 126 | 12:00
| Dhanmondi | 135.7 | 20:00 | 129 | 12:00 | Rajshahi | 137 | 02:00 | 129 | 12:00
| Dohazari | 132 | 18:30 | 122 | 12:00 | Rajshahi-230 | 138 | 03:00 | 128 | 12:00
| Faridpur | 133 | 05:00 | 126 | 12:00 | Ramganj | 135 | 19:30 | 122 | 01:00
| Fatullah | 139 | 20:00 | 131 | 12:00 | Rampur | 133 | 19:00 | 126 | 12:00
| Fenchuganj | 132 | 00:00 | 130 | 12:00 | Rampura | 138 | 03:00 | 131 | 12:00
| Feni | 132 | 18:30 | 125 | 12:00 | Rangamati | 134 | 19:00 | 128 | 05:00
| Ghorashal | 141 | 08:00 | 136 | 12:00 | Rangpur | 134 | 18:00 | 127 | 13:00
| Goalpara | 135 | 16:00 | 127 | 12:00 | Ruppur | 139 | 01:00 | 133 | 08:00
| Gollamari | 134 | 17:00 | 127 | 12:00 | Saidpur | 135 | 06:00 | 125 | 12:00
| Gopalganj | 132 | 04:00 | 125 | 12:00 | Satkhira | 132 | 02:00 | 124 | 12:00
| Gopalganj-400 | 131 | 04:00 | 126 | 12:00 | Satmasjid | 136 | 03:00 | 129 | 12:00
| Gulshan | 138 | 05:00 | 131 | 12:00 | Savar | 136 | 04:00 | 128 | 12:00
| Halishahar | 134 | 19:30 | 126 | 12:00 | SevenRings | 143 | 19:30 | 135 | 12:00
| Haripur | 135 | 19:00 | 130 | 10:00 | ShahCement | 137 | 19:30 | 130 | 11:00
| HaripurSBU | 135 | 19:00 | 130 | 10:00 | Shahjadpur | 144 | 03:00 | 135 | 12:00
| Hasnabad | 138 | 19:30 | 133 | 09:00 | Shahjibazar | 128 | 06:00 | 124 | 15:00
| Hathazari | 136 | 19:00 | 128 | 12:00 | Shahmirpur | 134 | 19:00 | 128 | 05:00
| Ishurdi | 140 | 03:00 | 130 | 13:00 | Shariatpur | 132 | 04:00 | 126 | 12:00
| Jaldhaka | 134 | 06:00 | 125 | 12:00 | Sherpur | 137 | 18:00 | 122 | 23:00
| Jamalpur | 140 | 19:00 | 126 | 00:00 | Shikalbaha | 124 | 19:00 | 117 | 03:00
| Jashore | 138 | 22:00 | 127 | 08:00 | Shikalbaha-230 | 135 | 20:00 | 128 | 07:00
| Jhenaidah | 142 | 22:00 | 134 | 08:00 | Shitalakhya | 137 | 19:00 | 129.6 | 11:00
| Jhenaidah-230 | 142 | 03:00 | 134 | 11:00 | Sholosohor | 134 | 19:00 | 126 | 06:00
| Joydebpur | 141 | 20:00 | 131 | 11:00 | Shyampur | 138 | 19:00 | 131 | 12:00
| Joypurhat | 134 | 01:00 | 126 | 12:00 | Shyampur-230 | 138 | 19:00 | 131 | 11:00
| Juldah | 135 | 20:00 | 126 | 12:00 | Siddhirganj | 136 | 20:00 | 130 | 11:00
| Kabirpur | 136 | 19:00 | 124 | 12:00 | Sirajganj | 138 | 00:00 | 130 | 12:00
| Kachua | 137 | 19:00 | 125 | 11:00 | Sonargaon | 133 | 19:30 | 126 | 07:00
| Kaliakoir | 137 | 06:00 | 131 | 12:00 | Sreemongol | 128 | 02:00 | 126 | 00:00
| Kallyanpur | 138 | 01:00 | 131 | 11:00 | Sreepur | 136 | 05:00 | 129 | 12:00
| Kalurghat | 134 | 19:00 | 127 | 12:00 | Srinagar | 135 | 05:00 | 129 | 12:00
| Kamrangirchar | 136 | 03:00 | 129 | 12:00 | SSM | 137 | 19:00 | 131 | 13:00
| Kaptai | N/A | N/A | N/A | N/A | Sunamganj | 128 | 06:00 | 125 | 12:00
| Kazla | 138 | 03:00 | 132 | 12:00 | Sylhet | 130 | 01:00 | 128 | 11:00
| Keranigonj | 136 | 03:00 | 129 | 12:00 | Sylhet-132 | 130 | 01:00 | 129 | 00:00
| Khagrachori | 134 | 20:00 | 126 | 12:00 | Tangail | 134 | 18:00 | 128 | 23:00
| Khulna | 134 | 04:00 | 126 | 12:00 | Thakurgaon | 134 | 18:00 | 121 | 12:00
| Khulna(S) | 136 | 18:00 | 126 | 12:00 | TK | 134 | 18:00 | 129 | 06:00
| Khulshi | 133 | 19:30 | 125 | 06:00 | Tongi | 140 | 19:30 | 129 | 12:00
| Kishoreganj | 138 | 03:00 | 132 | 12:00 | Ullon | 136 | 19:30 | 129 | 12:00
| Kodda | 139 | 19:30 | 125 | 16:00 | Uttara | 138 | 03:00 | 130 | 12:00
| KSRM | 134 | 19:00 | 126 | 01:00 | UttaraNew | 138 | 03:00 | 125 | 12:00
| Kulaura | 132 | 07:00 | 129 | 12:00 | Zigatola | 136 | 04:00 | 129 | 12:00
| Kurigram | 133 | 04:00 | 126 | 08:00
| Kushtia | 138 | 22:00 | 130 | 12:00

## L-Curve
Date | 2023-11-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 858 | 5245 | 4052 | 9297 |  |  |  | QF-LDC-11
0:30 | 855 | 5108.5 | 4014 | 9122.5 | Date: | 2023-11-12
1:00 | 852 | 4972 | 3976 | 8948
1:30 | 831 | 4887 | 3801.5 | 8688.5
2:00 | 810 | 4802 | 3627 | 8429
2:30 | 805 | 4708.5 | 3601.5 | 8310 | [5 empty] | Gen. at Eve. Peak | 11680 | 11680 MW (18:00 )
3:00 | 800 | 4615 | 3576 | 8191 | [6 empty] | 18:00
3:30 | 790 | 4537 | 3478 | 8015 | [5 empty] | Gen. at Day Peak | 10201 | 10201 MW (12:00 )
4:00 | 780 | 4459 | 3380 | 7839 | [6 empty] | 12:00
4:30 | 790 | 4416.5 | 3380 | 7796.5 | [5 empty] | Highest Generation | 11680
5:00 | 800 | 4374 | 3380 | 7754 | [6 empty] | 18:00
5:30 | 800 | 4345.5 | 3465.5 | 7811
6:00 | 800 | 4317 | 3551 | 7868
6:30 | 850 | 4428 | 3675.5 | 8103.5
7:00 | 900 | 4539 | 3800 | 8339
7:30 | 900 | 4654.5 | 3872.5 | 8527
8:00 | 900 | 4770 | 3945 | 8715
8:30 | 1015 | 4800.5 | 4098 | 8898.5
9:00 | 1130 | 4831 | 4251 | 9082
9:30 | 1185 | 4857.5 | 4292 | 9149.5
10:00 | 1240 | 4884 | 4333 | 9217
10:30 | 1240 | 5019 | 4397.5 | 9416.5
11:00 | 1240 | 5154 | 4462 | 9616
11:30 | 1290 | 5301.5 | 4607 | 9908.5
12:00 | 1340 | 5449 | 4752 | 10201
12:30 | 1205 | 5622.5 | 4797 | 10419.5
13:00 | 1070 | 5796 | 4842 | 10638
13:30 | 1115 | 5748 | 4740 | 10488
14:00 | 1160 | 5700 | 4638 | 10338
14:30 | 1190 | 5709.5 | 4547.5 | 10257
15:00 | 1220 | 5719 | 4457 | 10176
15:30 | 1195 | 5703.5 | 4384.5 | 10088
16:00 | 1170 | 5688 | 4312 | 10000
16:30 | 1118 | 5699 | 4311 | 10010
17:00 | 1066 | 5710 | 4310 | 10020
17:30 | 1058 | 6093 | 4757 | 10850
18:00 | 1050 | 6476 | 5204 | 11680
18:30 | 1008 | 6458 | 4980 | 11438
19:00 | 966 | 6440 | 4756 | 11196
19:30 | 860 | 6362 | 4619 | 10981
20:00 | 740 | 6271 | 4475 | 10746 |  |  |  | Executive Engineer
20:30 | 725 | 6205.5 | 4416 | 10621.5 |  |  |  | Network Operation Division
21:00 | 710 | 6140 | 4357 | 10497
21:30 | 730 | 6019 | 4319.5 | 10338.5
22:00 | 750 | 5898 | 4282 | 10180 |  |  |  |  | Page 6 of 7
22:30 | 730 | 5761 | 4152.5 | 9913.5
23:00 | 710 | 5624 | 4023 | 9647
23:30 | 784 | 5434.5 | 4037.5 | 9472
24:00 | 858 | 5245 | 4052 | 9297
11680 MW (18:00 )
10201 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-11-12 |  | Energy |  | 232879968
QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 3108 | 919 | 1595 | 0 | 287 | 3128 | 121 | 0 | 17 | 114 | 0 | 8 | 0
0:30 | 3165.5 | 918.5 | 1601 | 0 | 198 | 2985.5 | 126.5 | 0 | 8.5 | 113 | 0 | 6 | 0 |  | Date: | 43780
1:00 | 3223 | 918 | 1607 | 0 | 109 | 2843 | 132 | 0 | 0 | 112 | 0 | 4 | 0
1:30 | 3201 | 918 | 1600 | 0 | 54.5 | 2666 | 132 | 0 | 0 | 110 | 0 | 7 | 0 | [8 empty] | Total Energy | 232.88 | 232.88 | Total Energy Gen 232.880 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.880 MKWHr
2:00 | 3179 | 918 | 1593 | 0 | 0 | 2489 | 132 | 0 | 0 | 108 | 0 | 10 | 0 | [8 empty] | Energy not Served | 0 | 0
2:30 | 3156.5 | 918.5 | 1501.5 | 0 | 0 | 2486 | 132 | 0 | 0 | 104 | 0 | 11.5 | 0 | [8 empty] | Energy Requirement | 232.88 | 232.88
3:00 | 3134 | 919 | 1410 | 0 | 0 | 2483 | 132 | 0 | 0 | 100 | 0 | 13 | 0
3:30 | 3042 | 919 | 1333.5 | 0 | 0 | 2480 | 132 | 0 | 0 | 98 | 0 | 10.5 | 0 | [7 empty] | Shortage
4:00 | 2950 | 919 | 1257 | 0 | 0 | 2477 | 132 | 0 | 0 | 96 | 0 | 8 | 0
4:30 | 2943.5 | 918.5 | 1245.5 | 0 | 0 | 2477 | 112 | 0 | 0 | 95 | 0 | 5 | 0
5:00 | 2937 | 918 | 1234 | 0 | 0 | 2477 | 92 | 0 | 0 | 94 | 0 | 2 | 0
5:30 | 2857.5 | 918.5 | 1368.5 | 0 | 0 | 2478 | 92 | 0 | 0 | 95 | 0 | 1.5 | 0
6:00 | 2778 | 919 | 1503 | 0 | 0 | 2479 | 92 | 0 | 0 | 96 | 0 | 1 | 0
6:30 | 2835.5 | 919 | 1552.5 | 0 | 13.5 | 2554.5 | 112 | 0 | 0 | 97 | 19 | 0.5 | 0 | [6 empty] | Coal
7:00 | 2893 | 919 | 1602 | 0 | 27 | 2630 | 132 | 0 | 0 | 98 | 38 | 0 | 0
7:30 | 2848 | 919 | 1487.5 | 0 | 118.5 | 2836 | 132 | 0 | 0 | 99 | 87 | 0 | 0 | [5 empty] | Oil
8:00 | 2803 | 919 | 1373 | 0 | 210 | 3042 | 132 | 0 | 0 | 100 | 136 | 0 | 0
8:30 | 2777 | 919.5 | 1436 | 0 | 254 | 3079 | 132 | 0 | 0 | 101 | 200 | 0 | 0
9:00 | 2751 | 920 | 1499 | 0 | 298 | 3116 | 132 | 0 | 0 | 102 | 264 | 0 | 0
9:30 | 2714.5 | 919 | 1498.5 | 0 | 361.5 | 3115.5 | 126.5 | 0 | 0 | 109 | 305 | 0 | 0
10:00 | 2678 | 918 | 1498 | 0 | 425 | 3115 | 121 | 0 | 0 | 116 | 346 | 0 | 0
10:30 | 2723 | 918.5 | 1544.5 | 0 | 475.5 | 3133.5 | 121 | 0 | 12 | 120 | 368.5 | 0 | 0
11:00 | 2768 | 919 | 1591 | 0 | 526 | 3152 | 121 | 0 | 24 | 124 | 391 | 0 | 0
11:30 | 2785.5 | 919 | 1631.5 | 0 | 652 | 3257 | 121 | 0 | 32 | 126 | 384.5 | 0 | 0
12:00 | 2803 | 919 | 1672 | 0 | 778 | 3362 | 121 | 0 | 40 | 128 | 378 | 0 | 0
12:30 | 2807 | 919 | 1628.5 | 0 | 982.5 | 3414.5 | 121 | 0 | 40.5 | 132 | 374.5 | 0 | 0
13:00 | 2811 | 919 | 1585 | 0 | 1187 | 3467 | 121 | 0 | 41 | 136 | 371 | 0 | 0
13:30 | 2811 | 919 | 1585 | 0 | 1187 | 3467 | 121 | 0 | 41 | 136 | 371 | 0 | 0
14:00 | 2811 | 919 | 1585 | 0 | 1187 | 3467 | 121 | 0 | 41 | 136 | 371 | 0 | 0
14:30 | 2810.5 | 919 | 1502.5 | 0 | 1190.5 | 3391.5 | 121 | 0 | 48 | 135 | 289 | 0 | 0
15:00 | 2810 | 919 | 1420 | 0 | 1194 | 3316 | 121 | 0 | 55 | 134 | 207 | 0 | 0
15:30 | 2814 | 918.5 | 1417.5 | 0 | 1195 | 3287 | 121 | 0 | 57.5 | 129 | 148 | 0.5 | 0
16:00 | 2818 | 918 | 1415 | 0 | 1196 | 3258 | 121 | 0 | 60 | 124 | 89 | 1 | 0
16:30 | 2772 | 918 | 1420.5 | 0 | 1267 | 3254.5 | 121 | 0 | 79 | 129 | 48 | 1 | 0
17:00 | 2726 | 918 | 1426 | 0 | 1338 | 3251 | 121 | 0 | 98 | 134 | 7 | 1 | 0
17:30 | 2835 | 918 | 1526 | 0 | 1723 | 3408 | 121 | 0 | 174 | 139 | 3.5 | 2.5 | 0
18:00 | 2944 | 918 | 1626 | 0 | 2108 | 3565 | 121 | 0 | 250 | 144 | 0 | 4 | 0
18:30 | 2950.5 | 918.5 | 1579.5 | 0 | 2016 | 3520 | 121 | 0 | 190 | 139 | 0 | 3.5 | 0
19:00 | 2957 | 919 | 1533 | 0 | 1924 | 3475 | 121 | 0 | 130 | 134 | 0 | 3 | 0
19:30 | 2977 | 918 | 1543 | 0 | 1827 | 3371 | 121 | 0 | 98 | 124 | 0 | 2 | 0
20:00 | 2994 | 919 | 1535 | 0 | 1636 | 3349 | 121 | 0 | 65 | 124 | 0 | 3 | 0
20:30 | 3073.5 | 919 | 1547.5 | 0 | 1430.5 | 3355 | 121 | 0 | 49 | 124 | 0 | 2 | 0
21:00 | 3153 | 919 | 1560 | 0 | 1225 | 3361 | 121 | 0 | 33 | 124 | 0 | 1 | 0
21:30 | 3183.5 | 919 | 1558.5 | 0 | 1076 | 3323 | 121 | 0 | 33 | 124 | 0 | 0.5 | 0
22:00 | 3214 | 919 | 1557 | 0 | 927 | 3285 | 121 | 0 | 33 | 124 | 0 | 0 | 0
22:30 | 3215 | 919 | 1521 | 0 | 754 | 3232 | 121 | 0 | 25 | 125 | 0 | 1.5 | 0
23:00 | 3216 | 919 | 1485 | 0 | 581 | 3179 | 121 | 0 | 17 | 126 | 0 | 3 | 0
23:30 | 3162 | 919 | 1540 | 0 | 434 | 3153.5 | 121 | 0 | 17 | 120 | 0 | 5.5 | 0 |  | Max Temp. in Dhaka |  | 31.6°C
24:00 | 3108 | 919 | 1595 | 0 | 287 | 3128 | 121 | 0 | 17 | 114 | 0 | 8 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 232.880 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 232.880 MKWHr
Note on W13: Author:

## Generation
g | 2023-11-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 1534440
2 | Karnaphuli Hydro PP Unit-4 & 5 | 40 | 40 | 40 | 40 | 0 |  | 40 | 40 | 40 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1404000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 138344
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 10 | 15 | 18 | 20 | 19 | 18 | 16 | 11 | 5 | 0 | [9 empty] | 133920
6 | Sikalbaha 225MW CCPP (Gas) | 131 | 131 | 131 | 81 | 81 | 38 | 27 | 31 | 32 | 42 | 52 | 40 | 50 | 92 | 199 | 198 | 199 | 198 |  | 199 | 200 | 199 | 198 | 198 | 201 | 201 | 2934036
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [25 empty] | 0 | 0
12 | Hathazari 100 MW peaking PP | [10 empty] | 1 | 8 | 8 | 8 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 |  |  |  |  | 123984
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 0 | [5 empty] | 11 | 17 | 17 | 17 | 17 | 26 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 337054
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 233 | 233 | 236 | 225 | 225 | 225 | 225 | 236 | 230 | 231 | 233 | 234 | 230 | 232 | 232 | 230 | 230 | 230 |  | 230 | 231 | 230 | 231 | 222 | 231 | 233 | 5581475
18 | Kodda 300 MW PP Unit-2 (Summit) | [9 empty] | 10 | 17 | 35 | 70 | 47 | 47 | 47 | 47 | 50 |  | 80 | 80 | 45 | 45 | 45 |  | 0 | 687491
19 | Ashuganj 195 MW PP (APSCL-United) | [23 empty] | 8 | 8 | 8 | 16727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 310 | 304 | 300 | 300 | 300 | 300 | 300 | 303 | 303 | 303 | 303 | 310 | 303 | 303 | 303 | 303 | 301 | 309 |  | 306 | 306 | 306 | 306 | 306 | 306 | 305 | 7309090
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP
33 | Ashuganj 225 MW CCPP | 161 | 161 | 162 | 140 | 140 | 180 | 197 | 184 | 201 | 180 | 198 | 204 | 178 | 178 | 178 | 178 | 178 | 178 |  | 171 | 171 | 172 | 172 | 171 | 164 | 147 | 4246000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 355 | 345 | 310 | 305 | 270 | 305 | 340 | 305 | 305 | 270 | 270 | 265 | 280 |  | 270 | 270 | 270 | 270 | 270 | 270 | 250 | 6810000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 35 | 35 | 35 | 15 | 15 | 40 | 45 | 140 |  | 35 | 35 | 15 | 25 |  | 140 | 145 | 160 | 320 | 370 | 355 | 300 | 3961500
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 270 | 350 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 240 | 330 |  | 300 | 300 | 300 | 300 | 300 | 300 | 260 | 7045200
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 339 | 319 | 309 | 309 | 314 | 351 | 354 | 346 | 339 | 340 | 340 | 335 | 335 | 335 | 335 | 335 | 335 |  | 335 | 335 | 335 | 334 | 334 | 335 | 338 | 8153090
Meghnaghat Unique power
Summit Meghanghat-2 589 MW(Gas)
40 | Meghnaghat 450 MW CCPP(MPL) | 225 | 225 | 225 | 225 | 180 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 4495800
41 | Haripur 360 MW CCPP(HPL) | 149 | 157 | 153 | 166 | 179 | 181 | 151 | 152 | 154 | 157 | 156 | 155 | 154 | 154 | 154 | 150 | 150 | 147 |  | 148 | 148 | 143 | 146 | 145 | 156 | 158 | 3760000
42 | RPCL 210MW CCPP | 103 | 103 | 104 | 104 | 105 | 105 | 83 | 69 | 69 | 65 | 65 | 62 | 59 | 58 | 63 | 63 | 65 | 73 |  | 72 | 73 | 73 | 83 | 110 | 110 | 110 | 1910400
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 14 | 32 | 42 | 47 | 38 | 44 | 37 | 25 | 10 | 1 | [9 empty] | 302340
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 40 | 40 | 40 | 41 | 40 | 40 | 41 |  | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 991000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 62 | 40 | 40 | 40 | 40 | 61 | 40 | 62 | 61 | 60 | 58 | 59 | 59 | 40 | 40 | 40 | 57 |  | 57 | 57 | 60 | 60 | 60 | 40 | 62 | 1259616
48 | Shahjibazar 86 MW PP (Shahjibazar)
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 206 | 207 | 206 | 204 | 202 | 203 | 203 | 203 | 202 | 201 |  | 201 | 201 | 201 | 201 | 204 | 204 | 204 | 5107040
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 406000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240840
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 120960
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 10 | 10 | 10 | 10 | 47 | 10 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 944400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 380160
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 265 | 270 | 270 | 290 | 300 | 300 | 275 | 280 | 275 | 295 | 310 | 290 | 285 | 275 | 270 | 275 | 270 |  | 260 | 270 | 260 | 280 | 270 | 280 | 290 | 6874000
| Bibiyana South 400 MW | 260 | 260 | 260 | 220 | 195 | 164 | 118 | 90 | 40 | 15 | 15 | 15 | 21 | 35 | 50 | 50 | 50 | 45 |  | 45 | 50 | 50 | 50 | 50 | 90 | 98 | 2346300
58 | Nababganj 55 MW PP (Southern power ) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 17 | 17 |  | 0 | 140730
59 | Tangail Palli Power Gen 22 MW | [9 empty] | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 |  | 0 | 81120
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 269760
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 |  | 15 | 18 | 388260
62 | Tangail 22 MW PP (Doreen)
63 | Impoprt (Tripura) | 112 | 108 | 100 | 96 | 94 | 96 | 98 | 100 | 102 | 116 | 124 | 128 | 136 | 140 | 134 | 124 | 134 | 144 |  | 134 | 124 | 124 | 124 | 124 | 126 | 114 | 2844480
64 | Malancha, Ctg. EPZ (United) | 14 | 14 | 20 | 31 | 31 | 31 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 2 | 2 | 2 | 3 | 4 | 9 | 9 | 208320
65 | Feni 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 10 | 17 |  | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 314568
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  |  | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 233280
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 772700
68 | Cumilla 25 MW PP (Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 5 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278630
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 278640
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 720000
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604500
73 | Ghorashal 108 MW PP (Regent) | 74 | 74 | 13 | 13 | 13 | 28 | 52 | 63 | 69 | 67 | 70 | 70 | 70 | 70 | 66 | 70 | 75 | 76 |  | 76 | 76 | 76 | 76 | 76 | 73 | 74 | 1485590
| Feni Lanka Power | [11 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 34 | 17 |  |  |  |  | 0 | 160740
| Chowmuhani 113 MW | [10 empty] | 1 | 9 | 18 | 18 | 28 | 28 | 28 | 57 |  | 58 | 58 | 58 | 58 | 58 | 58 | 34 | 506520
| Manikgonj 162MW PP(MPGL) | [8 empty] | 10 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 384480
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 5 | 9 | 9 | 28 | 86 | 88 | 57 | 40 | 40 | 55 |  | 86 | 86 | 78 | 32 |  |  | 0 | 566438
78 | Gazipur 52 MW PP | [11 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 20 |  | 25 | 25 | 25 | 8 | 8 |  | 0 | 143040
79 | Kodda 150 MW PP | [11 empty] | 5 | 16 | 16 | 16 | 16 | 32 | 115 |  | 64 | 32 | 32 | 16 | 16 |  | 0 | 318240
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [10 empty] | 1 | 12 | 43 | 43 | 43 | 43 | 43 | 43 |  | 16 | 16 | 16 | 16 | 16 | 16 |  | 358906
| Gazipur 100 MW PP | [8 empty] | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 70 |  | 35 | 17 | 17 | 17 | 17 |  | 0 | 429120
| Kaptai 7 MW Solar PP | [7 empty] | 2 | 3 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [10 empty] | 26160
| Jodiac Power | [9 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 269296
| Karnaphuli Power Ltd. | 17 | 0 | [6 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 306945
82 | Madanganj 102 PP(Summit) | [9 empty] | 17 | 20 | 35 | 55 | 68 | 68 | 51 | 55 | 65 |  | 65 | 65 | 65 | 65 | 45 | 32 | 0 | 631727
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 15 | 28 | 47 | 47 | 28 | 26 | 25 | 29 |  | 46 | 26 |  |  |  |  | 0 | 293768
86 | Meghnaghat CCPP ( Summit) | 158 | 157 | 159 | 123 | 112 | 133 | 155 | 148 | 142 | 144 | 152 | 153 | 150 | 143 | 145 | 145 | 144 | 140 |  | 142 | 140 | 147 | 147 | 147 | 153 | 151 | 3477935
87 | Meghnaghat 100 MW(IEL) | [11 empty] | 4 | 45 | 70 | 86 | 95 | 99 | 99 |  | 27 | 8 | 9 | 8 |  |  | 0 | 542400
| Meghnaghat 104 MW PP (OPCL) | [8 empty] | 8 | 17 | 34 | 50 | 71 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 0 | 875520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 12 | 0 | [6 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 188760
92 | Fenchuganj 44 MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 18 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1075136
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 8 | 24 | 24 | 58 | 91 | 91 | 40 | 40 | 40 | 66 |  | 66 | 66 | 66 | 16 |  |  | 0 | 630288
95 | Patenga 50MW PP (Baraka) | 6 | 0 | [5 empty] | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 13 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 8 | 193920
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 3 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 |  | 0 | 191611
100 | Manikganj 55 MW PP (Northern) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 35 |  |  | 0 | 136205
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 |  |  | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [9 empty] | 11650
103 | Kamalaghat 54 MW PP(Banco Energy) | [16 empty] | 17 | 35 |  | 35 | 35 | 35 | 17 |  |  | 0 | 129600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [6 empty] | 3 | 40 | 24 | 24 | 24 | 65 | 56 | 56 | 56 | 66 | 60 | 95 |  | 45 | 45 | 45 | 18 | 16 |  | 0 | 765600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 0 | 15 | 17 | 17 | 17 | 17 | 26 | 17 | 17 | 17 | 56 |  | 80 | 81 | 80 | 81 | 80 | 42 | 0 | 616896
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 0 | [5 empty] | 10 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 235200
116 | Chandpur 200 MW (Desh energy) | [10 empty] | 4 | 18 | 18 | 17 | 17 | 17 | 17 | 24 |  | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 258240
117 | Ashuganj 150 MW PP (Midland) | [11 empty] | 5 | 25 | 48 | 63 | 81 | 93 | 115 |  | 118 | 120 | 120 | 120 | 10 | 10 | 0 | 881527
118 | Bibiyana-III 400 MW CCPP | 401 | 358 | 359 | 358 | 360 | 360 | 400 | 377 | 402 | 401 | 403 | 404 | 404 | 392 | 402 | 404 | 363 | 401 |  | 402 | 402 | 402 | 402 | 402 | 377 | 365 | 9302000
| Jamalpur 115 MW PP (United) | [6 empty] | 24 | 47 | 47 | 47 | 59 | 49 | 55 | 59 | 59 | 59 | 59 | 88 |  | 89 | 89 | 89 | 89 | 69 | 16 | 0 | 997200
| Anwara 300 MW PP (United) | 16 | 0 | [5 empty] | 70 | 82 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 105 | 222 |  | 247 | 247 | 232 | 124 | 124 | 124 | 106 | 1994727
| Juldah unit-2 (Acorn) | 12 | 0 | [5 empty] | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 236160
| Anlima Energy Ltd. | 17 | 0 | [6 empty] | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 301091
| Bhairob 54.5 MW | [11 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  |  |  | 0 | 156960
| Spectra Solar Plant Ltd. | [6 empty] | 4 | 13 | 22 | 27 | 32 | 32 | 30 | 24 | 17 | 8 | 1 | [9 empty] | 208116
| Chandpur 115(Doreen) | [8 empty] | 5 | 18 | 17 | 18 | 18 | 18 | 17 | 18 | 38 | 93 |  | 96 | 95 | 95 | 77 | 72 | 55 | 18 | 692160
| Kanchan Purbachal Power Generation Ltd. | [7 empty] | 17 | [12 empty] | 12 | 14 | 49 | 17 |  | 0 | 138600
| Mirsharai 150 MW (Oil) | [10 empty] | 23 | 27 | 17 | 17 | 23 | 28 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 259273
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 4 | 10 | 13 | 8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 4 |  | 3 | 2 | 3 | 1 | 0 | 3 | 8 | 57120
| Matarbari 2*600 MW (CPGCL) | 204 | 204 | 204 | 203 | 202 | 202 | 203 | 348 | 342 | 344 | 344 | 344 | 338 | 342 | 342 | 342 | 340 | 336 |  | 342 | 348 | 346 | 348 | 346 | 350 | 350 | 7367272
120 | Eastern Zone Total | 4972 | 4802 | 4615 | 4459 | 4374 | 4317 | 4539 | 4770 | 4831 | 4884 | 5154 | 5449 | 5796 | 5700 | 5719 | 5688 | 5710 | 6476 |  | 6440 | 6362 | 6271 | 6140 | 5898 | 5624 | 5245 | 129326832
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [11 empty] | 2 | 16 | 16 | 16 | 16 | 16 | 16 | [7 empty] | 0 | 94080
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [9 empty] | 17 | 17 | 17 | 38 | 70 | 72 | 72 | 81 | 94 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 559200
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 8 | 27 | 49 | 65 | 75 | 77 | 71 | 57 | 40 | 18 | 1 | [9 empty] | 491760
131 | Rampal 1320 MW (BIFPCL) | 402 | 352 | 352 | 354 | 351 | 350 | 352 | 401 | 400 | 400 | 401 | 399 | 396 | 400 | 401 | 400 | 399 | 453 |  | 399 | 400 | 405 | 400 | 401 | 401 | 402 | 9396364
132 | United Payra Power Ltd. | [16 empty] | 2 | 35 |  | 35 | 35 |  |  |  |  | 0 | 96000
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 180 | 180 | 220 | 220 | 180 | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 180 | 180 | 220 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4937891
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 |  |  |  |  | 0 | 24864
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 200 |  | 200 | 200 | 200 | 200 | 200 | 200 | 166 | 3806400
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 130 | 130 | 80 | 80 | 80 | 130 | 80 | 122 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 92 | 130 |  | 72 | 80 | 80 | 78 | 78 | 80 | 80 | 2436000
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 20 | 19 | 19 | 17 | 18 | 17 | 15 | 16 | 16 | 17 | 19 | 19 | 17 | 17 | 19 | 24 |  | 22 | 24 | 24 | 25 | 24 | 23 | 22 | 471800
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [16 empty] | 3 | 15 | [7 empty] | 0 | 11952
146 | Bheramara HVDC | 918 | 918 | 919 | 919 | 918 | 919 | 919 | 919 | 920 | 918 | 919 | 919 | 919 | 920 | 919 | 918 | 918 | 918 |  | 919 | 918 | 919 | 919 | 919 | 919 | 919 | 22222545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 700 | 500 | 500 | 500 | 500 | 500 | 540 | 670 | 750 | 750 | 790 | 880 | 970 | 900 | 840 | 780 | 780 | 880 |  | 840 | 820 | 800 | 820 | 800 | 740 | 760 | 19373500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4134900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 4 | 4 | 2 | 1 | 0 | [9 empty] | 33600
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 350 | 350 | 300 | 200 | 200 | 330 | 350 | 250 | 300 | 300 | 350 | 414 | 350 | 300 | 250 | 250 | 250 | 414 |  | 370 | 370 | 370 | 370 | 370 | 270 | 370 | 7776509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 236862
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 8 | 8 |  |  |  |  | 0 | 12780
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [16 empty] | 15 | 38 | [8 empty] | 47524
169 | Natore 52 MW PP (Rajlanka) | [17 empty] | 8 |  | 8 | [5 empty] | 0 | 16459
170 | Chapainawabganj 100 MW Peaking PP | [16 empty] | 18 | 64 |  | 33 | 33 | [5 empty] | 109336
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [10 empty] | 8 | 11 | 35 | 35 | 35 | 35 | 35 | 43 |  | 40 | 50 | 50 | 50 | 50 |  | 0 | 566400
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 20 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 |  |  |  | 0 | 391008
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [16 empty] | 20 | 101 |  | 107 | 70 | 37 |  |  |  | 0 | 273379
177 | Sympa Solar Power 8MW | [6 empty] | 0 | [9 empty] | 0 | [9 empty] | 996
178 | Energypac Power Venture Thakurgaon Ltd. | [17 empty] | 90 |  | 36 | 35 | 35 |  |  |  | 0 | 179328
| Intraco Solar 30 MW | [6 empty] | 3 |  | 22 | 30 | 33 | 34 | 31 | 26 | 16 | 7 | 1 | [9 empty] | 211175
| Adani Power Jharkhanda Ltd | 917 | 819 | 817 | 810 | 814 | 817 | 925 | 1010 | 1011 | 1008 | 1004 | 1119 | 1150 | 1120 | 1120 | 1123 | 1121 | 1217 |  | 1218 | 1127 | 1122 | 1117 | 1062 | 1012 | 975 | 24506964
178 | Teesta Solar Limited | [6 empty] | 17 | 68 | 118 | 154 | 173 | 167 | 167 | 135 | 93 | 39 | 3 | [9 empty] | 1133560