## Daily Gen
Hourly Generation & Demand
Date: | 2016-05-03
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 5688 | 5688 | 0
2:00 | 5503 | 5503 | 0
3:00 | 5362 | 5362 | 0
4:00 | 5072 | 5072 | 0
5:00 | 5079 | 5079 | 0
6:00 | 4832 | 4832 | 0
7:00 | 5056 | 5056 | 0
8:00 | 5189 | 5189 | 0
9:00 | 5723 | 5723 | 0
10:00 | 6116 | 6116 | 0
11:00 | 6173 | 6173 | 0 | Day Peak
12:00 | 6131 | 6131 | 0
13:00 | 6113 | 6113 | 0
14:00 | 6367 | 6367 | 0
15:00 | 6561 | 6561 | 0
16:00 | 6587 | 6587 | 0
17:00 | 6577 | 6577 | 0
18:00 | 6657 | 6657 | 0
18:30 | 6952 | 6952 | 0
19:00 | 7146 | 7650 | 453.6
19:30 | 7256 | 7700 | 399.6
20:00 | 7342 | 7750 | 367.2
21:00 | 7400 | 7800 | 360 | Evening peak
22:00 | 7434 | 7700 | 239.4
23:00 | 7427 | 7650 | 200.7
24:00 | 7513 | 7513 | 0

## forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [7 empty] | 2016-05-04 | Wednesday
|  | Date (day): | 2016-05-04 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 7062 | MW |  |  | (b) At Evening Peak Hour : |  | 7946 | MW
Sl. No. | Name of the Power Stations |  | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[8 empty] | On | 2016-05-03 | 2016-05-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Nos. of Unit X Capacity (MW) | MW | MW | MW | MW | MW | MW | MW | MW
1a | Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 78 | 78 | 78 | 78
1b | Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
1c | Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | 2015-05-01
1d | Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110
1e | Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | (18/07/2010) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 100 | 101 | 100 | 100
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 43 | 46 | 45 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 65 | 65 | 71 | 72
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 100 | 96 | 96
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3*32 | 96 | 60 | 20 | 20 | 20 | 20 |  | 40 | #1,3 under maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 413 | 415 | 412 | 412
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 80 | 110 | 96 | 110
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 242 | 322 | 349 | 360 | 38 |  | Gas shortage.
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint. |  | 15/08/2016
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 91 | 99 | 100 | 100
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 142 | 144 | 305 | 305
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 81 | 95 | 100 | 100 |  | 5 | Engine problem
14 | Madanganj-55 MW |  | HFO | IPP | 5*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
15 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 81 | 85 | 85 | 85 |  | 15 | Transformer problem
16 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 18 | 21 | 0 | 22
17 | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 105 | 110 | 110 | 110 | 40 |  | Gas shortage.
18 | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 66 | 0 | 210 |  | Gas shortage.
19 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 96 | 98 | 30 | 94 | 98 | 98
20 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 73 | 88 | 92 | 92 |  | 12 | Engine problem
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 46 | 50 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 94 | 93 | 94 | 94 |  | 9 | Engine problem
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 12 | 43 | 43 |  | 39 | Engine problem
24 | Kodda Peaking |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 109 | 116 | 117 | 117 |  | 33 | Engine problem
| Southern Power |  | HFO | RPP |  |  |  | 0 | 0 | 0 | 0
| CLCPC Keranigonj 108 MW |  | HFO | RPP |  |  |  | 12 | 0 | 0 | 0
25 | Summit Power, Dhaka |  | Gas | SIPP,REB | 6*3.67+2*6.97+14*8.73 | 146 | 146 | 116 | 124 | 121 | 121 |  | 22 | Engine problem
26 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 34 | 43 | 43 | 43 |  | 9 | Engine problem
27 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas Shortage
| Dhaka Area Total |  |  |  |  | 4664 | 4433 | 2333 | 2596 | 2856 | 2838 | 393 | 1174
28a | Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
28b | Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 70 | 0 | 0 | 0 |  |  | Gas shortage
29 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 26 | 26 | 26 | 26
30 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 47 | 51 | 50 | 50
31 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 35 | 95 | 35 | 95 |  | 50 | # 5 Under maint.
32 | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under maint.
33 | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 0 | 45 | 145 | 145 | 80 |  | Gas Shortage
34 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 43 | 43 | 34 | 42 | 42 | 42
35 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 68 | 0 | 68
36 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 62 | 16 | 68
37 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 102 | 100 | 100
38 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 19 | 20 | 21 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 1 | 21 | 2 | 20
39 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 0 | 102 | 100 | 100
| Chittagong area Total |  |  |  |  | 1408 | 1328 | 328 | 634 | 537 | 736 | 300 | 50
40a | Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 128 | 97 | 44 | 0 | 0 | 0 |  | 97 | #1,2 Under maint.
40b | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 132 | 132 | 132 | 132
40c | Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 80 | 150
40d | Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
40e | Ashuganj : GT-2 |  | Gas | APSCL | 1*56 | 56 | 40 | 25 | 25 | 25 | 25 | 20 |  | Gas Shortage
41a | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | 2016-08-04
41b | Ashuganj CCPP 450 MW |  | Gas | APSCL |  |  |  | 30 | 0 | 0 | 0 |  |  | On test
42 | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 12 | 12 | 12 | 12 | 33 |  | Gas Shortage
43 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 57 | 57 | 57 | 57
44 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 98 | 99 | 98 | 98
45 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 53 | 53 | 53 | 53
46 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.7+1*16 | 195 | 195 | 165 | 193 | 177 | 185 | 2 |  | Gas Shortage
47 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 45 | 51
48 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 86 | 85 | 86 | 85
49 | Titas (Daudkandi) Peaking |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 49 | 0 | 50
50 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 20 | 90 | 89 | 120 | 73 |  | Gas Shortage
51 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 0 | 16 | 0 | 19
52 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 8 | 0 | 11
** | Tripura |  |  | Imported Power |  | 100 | 100 | 58 | 110 | 77 | 79
53 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 0 | 32 | 33 | 33
54 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 52 | 52 | 52 | 52
55 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.6+2*6.9 | 25 | 25 | 3 | 10 | 0 | 3
| Comilla Area Total |  |  |  |  | 1896 | 1789 | 1021 | 1209 | 1151 | 1350 | 128 | 314
56 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 125 | 155 | 156 | 160 | 47 |  | Gas shortage
57 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 14 | 14 | 14 |  | 8
| Mymensingh Area Total |  |  |  |  | 232 | 224 | 139 | 169 | 170 | 174 | 47 | 0
58 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 49 | 52 | 54 | 54
59 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 20 | 20 | 20
60 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 52 | 50 | 50
61 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 47 | 44 | 44
62 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
63 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 28 | 30 | 20 | 32 |  |  | # 9 under maint.
64 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
65 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 48 | 48 | 48
66 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 117 | 119 | 118 | 120 | 23 |  | Gas shortage
67 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 15 | 15 | 15 | 15 |  | 5 | Engine problem
68 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 42 | 47 | 45 | 45
69 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 24 | 16 | 24
70 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 347 | 350 | 341 | 341
71 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1101 | 1066 | 875 | 908 | 875 | 897 | 23 | 5
72 | Bheramara GT: Unit- 1,2,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 33 | 0 | 34
73 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | contract date experid 31/12/2013
** | Bheramara Interconnector(HVDC ) |  |  | Imported Power |  | 500 | 500 | 444 | 443 | 443 | 443
74a | Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11
74b | Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
75 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 99 | 105 | 93 | 110
76 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
77 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 40 | 40 | 41
78 | Khulna 150MW GT |  | HSD | NWZPGCL | 1*150 | 158 | 158 | 153 | 155 | 158 | 158
79 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 79 | 0 | 80
80 | Noapara (Quantam) |  | HFO | RPP | 5*9.9+6*9.5+2*9.2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | Long term maint.
81 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 40 | 40 | 40
82 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 30 | 45 | 55 | 55
| Khulna Area Total |  |  |  |  | 1517 | 1448 | 881 | 1055 | 944 | 1076 | 0 | 261
83 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 100 | 111 | 99 | 99
84 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 14 | 0 | 30
85 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 8 | 16 | 8 | 17 |  | 16 | Engine problem
86 | Bhola CCPP GT-1,2,ST |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 94 | 85 | 96 | 96 | 109 |  | Gas shortage
| Barisal Area Total |  |  |  |  | 377 | 367 | 202 | 226 | 203 | 242 | 0 | 16
87a | Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 60
87b | Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 101 | 104 | 100 | 100
88 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 32 | 0 | 32
89 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 50 | 0 | 57
90 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | Engine problem
91 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 8 | 43 | 8 | 43 |  | 7 | Engine problem
92 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 41
93 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under shut down |  | 31/05/2016
94 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 0 | 43
95 | Bogra (GBB) |  | Gas | RPP | 6*4 | 20 | 22 | 22 | 15 | 21 | 22
96 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 20 | 12 | 12 | 12 | 12 |  | 8 | Engine problem
97 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
98 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 44 | 43 | 43
| Rajshahi Area Total |  |  |  |  | 807 | 809 | 236 | 432 | 237 | 506 | 0 | 233
99a | Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 88 | 86 | 89 | 89
99b | Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 70 | 70 | 0 | 0 |  |  | 2016-03-05
100 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 18
101 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
102 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 40 | 0 | 0 | 0 | 20 |  | 40 | Engine problem
| Rangpur Area Total |  |  |  |  | 337 | 280 | 158 | 171 | 89 | 127 | 0 | 60
| Total |  |  |  |  | 12339 | 11744 | 6173 | 7400 | 7062 | 7946 | 891 | 2113
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 5690.8386 | 6822 | 6510.4005 | 7283
A. |  | 2016-05-03 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 7513 | MW at | 24:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 4832 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 7800 | MW
3 | Day peak Generation : |  |  | 6173 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 7182 | MW
4 | Evening peak Generation : |  |  | 7400 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 360 | MW
5 | Total Energy Generation : |  |  | 154.1801 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 92.8631 | MKWHr |  | By Oil: | 43.5787 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.9945 | MKWHr |  | By Hydro: | 1.468 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 891 | For Oil: | 0 | MW | Dhaka | 2820 | 2727 | 93 | (19:05-23:55)
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 890 | 844 | 46 | (19:05-23:55) |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 2113 | MW | Khulna | 870 | 818 | 52 | (19:05-23:55) |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 851.48 | MMCFD |  |  |  | Rajshahi | 742 | 694 | 48 | (19:05-23:55) |  | 19:00 |  | 453.6
8 | Fuel Cost : | i) Gas : | Taka | 56286516.977 | ii) Oil : | Taka | 444175185.306 | Comilla | 565 | 530 | 35 | (19:05-23:55) |  | 19:30 |  | 399.6
|  | iii) Coal : | Taka | 15546488.916 | Total | Taka | 516008191.199 | Mymensingh | 436 | 410 | 26 | (19:05-23:55) |  | 20:00 |  | 367.2
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 320 | 294 | 26 | (19:05-23:55) |  | 21:00 |  | 360
| ii) During Peak Demand : |  |  | -410 | MW at | 21:00 | hrs | Barisal | 154 | 145 | 9 | (19:05-23:55) |  | 22:00 |  | 239.4
| iii) Maximum : |  |  | -250 | MW at | 10:00 | hrs | Rangpur | 385 | 360 | 25 | (19:05-23:55) |  | 23:00 |  | 200.7
10 | Maximum Temperature in Dhaka was |  |  |  | 32.4° C |  |  | Total | 7182 | 6822 | 360
B. |  | 2016-05-04 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 7900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 7946 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 6400 | MW
4 | Reserve (Generation end) |  |  |  | 46 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 154.18 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 4700 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.7658 | MKWHr. | ii) During Peak demand: |  | 443 | MW at | 21:00 | hrs. | iii)Maximum: | 452 | 00:00 hrs
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.5101 | MKWHr.
*Cost for HVDC & Tripura energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.85 |  |  |  | (b) Today: | 73.03 | (c) Rule Curve: |  | 81.43
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2016-05-04
Till now the maximum generation is : - |  |  | 8348 MW | 21:00 | Hrs on | 2016-04-09
The Summary of Yesterday's |  | 2016-05-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6173 | MW Hour : | 11:00 | Min. Gen. at | 6:00 | 4700 | MW
Evening Peak Generation : |  | 7400 | MW Hour : | 21:00 | Max Generation : |  | 7946 | MW
E.P. Demand (at gen end) : |  | 7800 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 7900 | MW
Maximum Generation : |  | 7513 | MW Hour : | 24:00 | Reserve(Generation end) : |  | 46 | MW
Total Gen. (MKWH) : |  | 154.1801 | System L/ Factor : | 85.51% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -250 | MW at | 10:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2016-05-04
Actual : | 73.03 | Ft.(MSL) , | Rule curve : | 81.43 | Ft.( MSL )
Gas Consumed : | Total | 851.48 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : Gas : |  |  | 56286516.977
|  | Coal : | 15546488.916 | Oil : | 444175185.306 | Total : | 516008191.199
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 93 | (19:05-23:55) | 2909 |  |  | - | -
Chittagong Area | 46 | (19:05-23:55) | 814 |  |  | - | -
Khulna Area | 52 | (19:05-23:55) | 815 |  |  | - | -
Rajshahi Area | 48 | (19:05-23:55) | 791 |  |  | - | -
Comilla Area | 35 | (19:05-23:55) | 603 |  |  | - | -
Mymensingh Area | 26 | (19:05-23:55) | 459 |  |  | - | -
Sylhet Area | 26 | (19:05-23:55) | 287 |  |  | - | -
Barisal Area | 9 | (19:05-23:55) | 160 |  |  | - | -
Rangpur Area | 25 | (19:05-23:55) | 445 |  |  | - | -
Total | 360 | 0 | 7283 |  |  | 0 | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010) |  | 9) Sikalbaha 60MW (23/11/15)
| Nil |  |  | 2) Ashuganj ST: Unit-1(12/09/2015) |  | 10) Saidpur GT
|  |  |  | 3) Ashuganj CCPP 225 MW |  | 11) Bhola GT
|  |  |  | 4) Khulna ST 110 MW (04/11/2014) |  | 12) Chittagong ST: Unit-1,2
|  |  |  | 5) Ghorasal ST: Unit-4 (05/01/2015) |  | 13) Sirajganj-210 MW
|  |  |  | 6) Haripur GT- 1, 3 |  | 14) Kaptai Hydro: Unit-5,
|  |  |  | 7) Barapukuria ST unit:2 |  | 15) Ashuganj ST: Unit-2 (03/05/2016)
8) Meghan 450 MW(24/04/2016)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Comments on Power Interruption
a) Sikalbaha Peaking GT was shut down at 08:15 due to low gas pressure.
b) Hathazari-BSRM 230 kV Ckt tripped at 12:04 from both end showing E/F Y-phase at Hathazari end and
dist Z1 R-phase at BSRM end and was switched on at 12:31.
c) Hathazari-AKSM 230 kV Ckt tripped at 12:04 from AKSM end showing dist Z1 R-phase AR close,AR block
and was switched on at 12:34.
d) Hathazari-Feni 132 kV Ckt-1 tripped at 12:04 from Hathazari end showing inst' O/C at R-phase and was |  |  |  | About 740 MW power interruption occurred under Chittagong Zone
switched on at 12:19.At the same time following machines also tripped: |  |  |  | from 12:04 to 12:19.
Name of Plants | Load | Synchronized Time | Remarks
Chittagong ST: Unit-2 | 70 | - | About 304 MW genaration interruption occurred under Chittagong Zone.
Juldah (Acorn) | 80 | 12:36
Patenga 50MW | 47 | 12:39
Sikalbaha (Energis) | 42 | 12:52
Kaptai Hydro: Unit-1 | 34 | 12:32
Dohazari Peaking | 31 | 13:07
Total | 304
e) Hathazari-Feni 132 kV Ckt-2 tripped at 12:04 from both end showing dist ABC Z1 ,ARB at Feni end &
R-phase inst' O/C at Hathazari end and was switched on at 12:22.
f) Daudkandi-Comilla(N) 132 kV Ckt-1 was shut down from 13:46 to 15:15 for removing kite.
g) Chandpur 150 MW ST was synchronized at 14:14.
h) Mongla 132/33 kV T1 transformer was shut down from 18:46 to 19:05 for red hot maintenance.
i) After maintenance Ashuganj ST: Unit- 4 was synchronized at 22:29.
j) Barapukuria ST: Unit-2 was shut down at 23:45 due to super heater tube got burst.
k) Sreemongal-Shahjibazar 132 kV Ckt-2 tripped at 03:57 (04/05/2016) from both ends showing dist A-phase
at Sreemongal end & dist relay at Shahjibazar end and was switched on at 04:16.
l) Feni 132/33 kV T1 transformer tripped at 06:20 (04/05/2016) operating Buchholz relay.
m) Meghnaghat CCPP(Summit) GT-1 was synchronized at 07:38(04/05/2016).
n) Bheramara 132 kV B-bus was shut down at 07:20 (04/05/2016) for project work.
Sub Divisional Engineer |  |  | Executive Engineer | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division | Load Dispatch Circle |  |  | Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2016-05-03 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1a | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 38 | 1772000
40
1b | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 0 | 0 | under maint
1c | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 0 | 0 | Under maint
1d | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 110 | 2362500
1e | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 |  | Long term maint.
2 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 101 | 2389670
3 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 46 | 1068380
4 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 65 | 1537500 | Engine problem
5 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 100 | 2303136
6 |  |  | 1*32 | PDB | 20 | 20 | 485000
| Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 0 |  | Under maintenance
|  |  | 1*32 | PDB | 20 | 0 |  | Under maint.
7 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 415 | 10507600
8 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 110 | 1366100
9 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 322 | 6718000 | Gas shortage
10 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 0 | 0 | Under maint.
11 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 99 | 1555200
12 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 305 | 144 | 2833000 | Machine problem
13 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 95 | 1704984 | Engine problem
14 | Madanganj-55 MW |  | 5*17.08+1*11.3 | IPP | 55 | 55 | 1142400
15 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 85 | 1367229 | Transformer problem
16 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 21 | 400464
17 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 110 | 2583000 | Gas Shortage
18 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 0 | 0 | Gas Shortage
19 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 98 | 94 | 1152000
20 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 88 | 1423500 | Engine problem
21 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 50 | 676660
22 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 93 | 2034864 | Engine problem
23 | Katpotti 52 MW |  |  | RPP | 51 | 12 | 131040 | Engine problem
24 | Kodda Peaking |  | 9*17.06 | BPDB-RPCL | 149 | 116 | 1909920 | Engine problem
| Southern Power |  |  | RPP |  | 0 | 0 | on test
| CLCPC Keranigonj 108 MW |  |  |  |  | 0 | 0 | on test
25 | Summit Power,Dhaka |  | 6*3.67+2*6.97+14*8.73 | SIPP, REB | 146 | 124 | 9750120 | Engine problem
26 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 43 | 1001556 | Engine problem
27 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Gas Shortage
| Dhaka Area Total |  |  |  | 4433 | 2596 | 60175823
28a | Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 0 | 0 | Gas shortage
28b | Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 0 | 1100000 | Gas shortage
29 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 26 | 405000
30 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 51 | 994560
31 | Chittagong ECPV 108 MW |  |  | IPP | 108 | 102 | 1597440
32 |  |  | 1*40 | PDB | 40 | 40 | 1205765
|  |  | 1*40 | PDB | 40 | 24
| Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 0
|  |  | 1*50 | PDB | 50 | 31 | 262200
|  |  | 1*50 | PDB | 50 | 0 |  | Under maint.
33 | Shikalbaha ST |  | 1*60 | PDB | 40 | 0 | 0 | Gas Shortage
34 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 45 | 885313 | Gas shortage
35 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 68 | 352050 | Low demand
36 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 62 | 772711 | Low demand
37 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 102 | 1651920
38 | Shikalbaha (Energis) |  |  | RPP | 43 | 42 | 592800
39 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 20 | 460128 | Engine problem
* | Malancha, Ctg EPZ(United) |  |  |  |  | 21 | 288960 | Engine problem
| Chittagong Area Total |  |  |  | 1328 | 634 | 10568847
40a | Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 97 | 0 | 641447 | Under maint.
|  |  | 1*64 | APSCL |  | 0 |  | Under maint.
40b | Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 132 | 3104204
40c | Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 0 | 59370 | Under maint.
40d | Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 135 | 3235814
40e | Ashuganj : GT-2 |  | 1*56 | APSCL | 40 | 25 | 0 | Gas Shortage
41a | Ashuganj CCPP 225 MW |  | 1*142+1*75 | APSCL | 217 | 0 | 1229120 | Under maint.
41b | Ashuganj CCPP 450 MW |  |  | APSCL | 0 | 0 | 626403 | On test
42 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 12 | 287704 | Gas Shortage
43 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 57 | 1332480
44 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 99 | 2307700
45 | Ashuganj (United) |  | 14*4 | RPP | 53 | 53 | 1249000
46 | Ashuganj Modular 200 MW |  | 20*9.7+1*16 | IPP | 195 | 193 | 4215297
47 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 51 | 1178984
48 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 85 | 1977000
49 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 49 | 251272
50 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 90 | 0 | Gas Shortage
51 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 16 | 184320 | Engine problem
52 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 8 | 82260 | Engine problem
** | Tripura |  |  |  | 100 | 110 | 1510080
53 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 32 | 536000
54 | Lakdamavi-52 MW |  |  | IPP | 52 | 52 | 838637
55 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 10 | 136580 | Engine problem
| Comilla Area Total |  |  |  | 1789 | 1209 | 24983672
56 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 155 | 3022000 | Gas shortage
57 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 14 | 302076
| Mymensingh Area Total |  |  |  | 224 | 169 | 3324076
58 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 52 | 1118000
59 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 20 | 192000
60 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 52 | 1181400
61 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 47 | 1092000
62 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 8 | 190512 | Engine problem
63 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 30 | 934000 | # 9 under maint.
64 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 86 | 2004480
65 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 48 | 1076400
66 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 119 | 2398290 | Gas shortage
67 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 15 | 365000
68 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 47 | 1053060
69 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 24 | 439296
70 | Summit Bibiana-2 |  | 1*222+1*119 | IPP | 341 | 350 | 7765100
71 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 10 | 238140
| Sylhet Area Total |  |  |  | 1066 | 908 | 20047678
|  |  | 1*20 | PDB | 16 | 16 | 480000
72 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 0
|  |  | 1*20 | PDB | 16 | 17
73 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
** | Bheramara Interconnector(HVDC) |  |  | Imported Power | 500 | 443 | 10765818
74a | Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint
74b | Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
75 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 105 | 1732800
76 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 115 | 2301120
77 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 40 | 335520
78 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 158 | 155 | 2613120
79 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 79 | 261200 | Engine problem
80 | Noapara (Quantam) |  | 9.9*5+9.5*6+9.2*2 | RPP | 101 | 0 | 0 | All Engine problem, Long term maint
81 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 40 | 805875
82 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 45 | 539980 | Low demand
| Khulna Area Total |  |  |  | 1448 | 1055 | 19835433
83 | Summit Barisal 110MW |  | 7*17.076 | IPP | 110 | 111 | 2319360
84 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 14 | 175440
|  |  | 1*20 | PDB | 14 | 0
85 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 16 | 204415 | Engine problem
86 | Bhola CCPP GT-1,2,ST |  | 2*63+1*68 | PDB | 194 | 85 | 2214974 | Gas shortage
| Barisal Area Total |  |  |  | 367 | 226 | 4914189
87a | Baghabari GT |  | 1*71 | PDB | 71 | 0 | 0 | Under maint.
87b | Baghabari GT |  | 1*100 | PDB | 100 | 104 | 2269000
88 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 32 | 151640
89 | Bera Peaking |  | 9*8.29 | PDB | 71 | 50 | 363029
90 | Amnura |  | 7*7.79 | QRPP | 50 | 42 | 724880 | Engine problem
91 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 43 | 335397 | Engine problem
92 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 37 | 399189
93 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 0 | 0 | Under maint.
94 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 42 | 261683
95 | Bogra (GBB) |  | 6*4 | RPP | 22 | 15 | 463930
96 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 20 | 12 | 276480 | Engine problem
97 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 240210
98 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 44 | 731520
| Rajshahi Area Total |  |  |  | 809 | 432 | 6216958
99a | Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 86 | 2087564
99b | Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 70 | 1906909
100 | Rangpur GT |  | 1*20 | PDB | 20 | 15 | 119000
101 | Saidpur GT |  | 1*20 | PDB | 20 | 0 | 0 | Under maint.
102 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 40 | 0 | 0 | Engine problem
| Rangpur Area Total |  |  |  | 280 | 171 | 4113473
| Total |  |  |  | 11744 | 7400 | 154180149
| Eastern Grid Total |  |  |  | 8488 | 5516 | 119100096
| Western Grid Total |  |  |  | 2600 | 1884 | 35080053
| National Grid Total |  |  |  | 11088 | 7400 | 154180149
*Data collected from respective power station over telephone.

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2016-05-03 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 4938 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2151 | MW
i) Dhaka area |  |  | 2727 | MW | i) Khulna area |  |  | 870 | MW
ii) Chittagong area |  |  | 890 | MW | ii) Rajshahi area |  |  | 742 | MW
iii) Comilla area |  |  | 565 | MW | iii) Barisal area |  |  | 154 | MW
iv) Mymensingh area |  |  | 436 | MW | iv) Rangpur area |  |  | 385 | MW
v) Sylhet area |  |  | 320 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 7089 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 104 | 1500 | Kishorganj | 42 | 2000 | Noapara | 54 | 2000
Munsiganj | 92 | 1900 | Netrokona | 46 | 2200 | Jessore | 116 | 2300
Megnaghat | 44 | 1200 | Jamalpur | 67 | 1300 | Jhenida | 66 | 2300
Shyampur | 130 | 2400 | Sherpur | 38 | 100 | Bottail | 72 | 2300
Bhulta | 116 | 2200 | Srimongal | 28 | 1930 | G.K Project | 32 | 100
Madanganj | 30 | 2400 | Shahjibazar | 56 | 2100 | Faridpur | 104 | 2200
Shitalakhya | 95 | 1830 | Fenchuganj | 30 | 1900 | Madaripur | 73 | 2200
Rahim steel | 6 | 1800 | Khulawara | 20 | 1930 | Gopalganj | 45 | 2000
Matuail | 61 | 1000 | Sylhet | 123 | 1930 | Bagerhat | 60 | 2100
Ghorasal | 87 | 2000 | Chatak | 41 | 1930 | Mongla | 29 | 100
Narsingdi | 63 | 1900 | Comilla (S) | 114 | 2300 | Satkhira | 62 | 2300
Haripur (SBU) | 60 | 1100 | Comilla(N) | 53 | 2200 | Gallamari | 41 | 1500
Ullon | 82 | 1900 | Chandpur | 58 | 2300 | Magura | 29 | 2200
Hasnabad | 126 | 1900 | Feni | 76 | 2100 | Chuadanga | 45 | 2300
Magbazar | 112 | 1200 | Chowmuhani | 126 | 1930 | Barisal | 92 | 2300
Maniknagar | 60 | 1800 | Ashuganj | 58 | 2300 | Patuakhali | 36 | 2300
Bangabhaban | 34 | 1300 | Daudkandi | 52 | 2400 | Bhandaria | 32 | 2200
Narinda | 74 | 1800 | B.Baria | 72 | 2400 | Ishurdi | 35 | 2100
Dhanmondi | 116 | 1100 | Madanhat | 48 | 2100 | Natore | 66 | 2100
Lalbag | 64 | 1830 | Hathazari | 88 | 2100 | Bogra | 158 | 100
Madartek | 32 | 2000 | Khulshi | 166 | 1930 | Noagaon | 80 | 1900
Mirpur | 82 | 1930 | Halishahar | 124 | 1200 | Rajshahi | 102 | 2000
Kalyanpur | 102 | 2000 | Baraulia | 126 | 2400 | C.Nawabganj | 45 | 2000
Gulshan | 116 | 1500 | Sikalbaha | 34 | 2300 | Amnura | 16 | 100
Uttara | 81 | 1900 | Dohazari | 66 | 2100 | Pabna | 63 | 2000
Kamrangirchar | 88 | 1900 | Cox'sbazar | 51 | 2300 | Shahjadpur | 58 | 1400
Savar | 87 | 1800 | Chandraghona | 25 | 2000 | Serajganj | 54 | 1800
Bhasantec | 83 | 1900 | Kaptai | 4 | 1900 | Niyamatpur | 36 | 1930
Agargaon | 32 | 1600 | A. Khaer Stl. | 11 | 700 | Joypurhat | 31 | 1300
Satmosjid | 40 | 1830 | Bakulia | 102 | 1900 | Rangpur | 76 | 2000
Tongi | 91 | 1900 | Julda | 17 | 1900 | Lalmonirhat | 49 | 2100
Kabirpur | 184 | 1830 | TK chemical | 1 | 100 | Saidpur | 67 | 1300
Basundhara | 118 | 1900 | Modern Steel | 16 | 900 | Purbasadipur | 65 | 1200
Manikganj | 68 | 1830 | Shahmirpur | 24 | 2400 | Thakurgaon | 46 | 700
Joydevpur | 217 | 1800 | Abul Khair 230 | 191 | 900 | Palashbari | 62 | 1800
New Tongi | 109 | 1200 | BSRM | 61 | 300 | Barapukuria | 30 | 100
Tangail | 99 | 2200 | Goalpara | 33 | 1930 | Panchagar | 24 | 1830
Mymensing | 140 | 2100 | Central s/s | 72 | 2200
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## L.curve
Date | 2016-05-03 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -510 | 4711 | 1479 | 6190 | -510 | 6190 | 0:00 | DAILY LOAD CURVE | 2016-05-03
0:30 | -580 | 4578 | 1361 | 5939 | -650 | 5939 | 1:00
1:00 | -650 | 4445 | 1243 | 5688 | -660 | 5688 | 2:00
1:30 | -655 | 4386.5 | 1209 | 5595.5 | -660 | 5595.5 | 3:00
2:00 | -660 | 4328 | 1175 | 5503 | -660 | 5503 | 4:00
2:30 | -660 | 4273 | 1159.5 | 5432.5 | -640 | 5432.5 | 5:00
3:00 | -660 | 4218 | 1144 | 5362 | -520 | 5362 | 6:00
3:30 | -660 | 4126 | 1091 | 5217 | -530 | 5217 | 7:00
4:00 | -660 | 4034 | 1038 | 5072 | -370 | 5072 | 8:00
4:30 | -650 | 4028.5 | 1047 | 5075.5 | -270 | 5075.5 | 9:00
5:00 | -640 | 4023 | 1056 | 5079 | -250 | 5079 | 10:00
5:30 | -580 | 3889 | 1066.5 | 4955.5 | -320 | 4955.5 | 11:00
6:00 | -520 | 3755 | 1077 | 4832 | -340 | 4832 | 12:00
6:30 | -525 | 3861.5 | 1082.5 | 4944 | -440 | 4944 | 13:00
7:00 | -530 | 3968 | 1088 | 5056 | -430 | 5056 | 14:00 |  |  |  | 7513 | 24:00
7:30 | -450 | 3998 | 1124.5 | 5122.5 | -340 | 5122.5 | 15:00 |  |  |  | 6173 | 11:00
8:00 | -370 | 4028 | 1161 | 5189 | -300 | 5189 | 16:00
8:30 | -320 | 4218 | 1238 | 5456 | -310 | 5456 | 17:00
9:00 | -270 | 4408 | 1315 | 5723 | -310 | 5723 | 18:00
9:30 | -260 | 4546 | 1373.5 | 5919.5 | -250 | 5919.5 | 18:30
10:00 | -250 | 4684 | 1432 | 6116 | -300 | 6116 | 19:00
10:30 | -285 | 4690 | 1454.5 | 6144.5 | -310 | 6144.5 | 19:30
11:00 | -320 | 4696 | 1477 | 6173 | -380 | 6173 | 20:00
11:30 | -330 | 4661 | 1491 | 6152 | -410 | 6152 | 21:00
12:00 | -340 | 4626 | 1505 | 6131 | -500 | 6131 | 22:00
12:30 | -390 | 4643 | 1479 | 6122 | -550 | 6122 | 23:00
13:00 | -440 | 4660 | 1453 | 6113 | -580 | 6113 | 24:00
13:30 | -435 | 4842.5 | 1454.5 | 6297 |  | 6297
14:00 | -430 | 5025 | 1456 | 6481 | 128.92 | 6481
14:30 | -385 | 5033.5 | 1496 | 6529.5 | 86.5 | 6529.5
15:00 | -340 | 5042 | 1536 | 6578 |  | 6578
15:30 | -320 | 5042 | 1540.5 | 6582.5 | 7867500 | 6582.5
16:00 | -300 | 5042 | 1545 | 6587 |  | 6587
16:30 | -305 | 5019 | 1563 | 6582 |  | 6582
17:00 | -310 | 4996 | 1581 | 6577 | 700 | 6577
17:30 | -310 | 4992 | 1625 | 6617 | 1800 | 6617
18:00 | -310 | 4988 | 1669 | 6657 | 100 | 6657
18:30 | -250 | 5186 | 1766 | 6952 | 1400 | 6952
19:00 | -300 | 5308 | 1838 | 7146 | 100 | 7650
19:30 | -310 | 5351 | 1905 | 7256 | 1800 | 7700
20:00 | -380 | 5423 | 1919 | 7342 | 1800 | 7750
20:30 | -395 | 5469.5 | 1901.5 | 7371 | 1800 | 7775
21:00 | -410 | 5516 | 1884 | 7400 | 2100 | 7800
21:30 | -455 | 5567 | 1850 | 7417 | 1900 | 7750
22:00 | -500 | 5618 | 1816 | 7434 | 1900 | 7700
22:30 | -525 | 5622.5 | 1808 | 7430.5 |  | 7675
23:00 | -550 | 5627 | 1800 | 7427 |  | 7650
23:30 | -565 | 5683.5 | 1786.5 | 7470 |  | 7581.5
24:00 | -580 | 5740 | 1773 | 7513 |  | 7513
*MAX.GEN.(E.P.) |  | 7513 |  | 24:00
*MAX.GEN.(D.P.) |  | 6173 |  | 11:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
7400 MW (21:00)
6173 MW (11:00)

## En.Curve
QF-LDC-12
Date | 2016-05-03 |  | Energy | 154180149 | 2245000
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | Tripura |  | DAILY ENERGY CURVE |  | 2016-05-03
0:00 | 886 | 452 | 2944 | 1236 | 171 | 38 | 152 | 0 | 90
0:30 | 862.5 | 448 | 2933 | 1076.5 | 171.5 | 38 | 106.5 | 0 | 87
1:00 | 839 | 444 | 2922 | 917 | 172 | 38 | 61 | 0 | 84
1:30 | 836 | 444 | 2926 | 825 | 172 | 38 | 52.5 | 0 | 83 | [5 empty] | 154.1801
2:00 | 833 | 444 | 2930 | 733 | 172 | 38 | 44 | 0 | 82 | [5 empty] | 1.6022
2:30 | 820 | 444 | 2951.5 | 660 | 172.5 | 39 | 34 | 0 | 81 | [5 empty] | 155.7824
3:00 | 807 | 444 | 2973 | 587 | 173 | 40 | 24 | 0 | 80
3:30 | 819.5 | 444 | 2914 | 496 | 172 | 40 | 20 | 0 | 74
4:00 | 832 | 444 | 2855 | 405 | 171 | 40 | 16 | 0 | 68
4:30 | 843 | 444 | 2841.5 | 414 | 170 | 40 | 16 | 0 | 69
5:00 | 854 | 444 | 2828 | 423 | 169 | 40 | 16 | 0 | 70
5:30 | 849 | 444 | 2701 | 428 | 171.5 | 40.5 | 16 | 0 | 68
6:00 | 844 | 444 | 2574 | 433 | 174 | 41 | 16 | 0 | 66
6:30 | 791.5 | 444 | 2663 | 520.5 | 173 | 35.5 | 16 | 0 | 63
7:00 | 739 | 444 | 2752 | 608 | 172 | 30 | 16 | 0 | 60
7:30 | 724.5 | 444 | 2685 | 741.5 | 172.5 | 30 | 16 | 0 | 61
8:00 | 710 | 444 | 2618 | 875 | 173 | 30 | 16 | 0 | 62
8:30 | 724.5 | 443.5 | 2717.5 | 1022.5 | 171.5 | 30 | 16 | 0 | 62
9:00 | 739 | 443 | 2817 | 1170 | 170 | 30 | 16 | 0 | 62
9:30 | 728.5 | 443.5 | 2838.5 | 1371.5 | 164 | 30 | 16 | 0 | 67
10:00 | 718 | 444 | 2860 | 1573 | 158 | 30 | 16 | 0 | 72
10:30 | 729.5 | 444 | 2840 | 1629 | 158 | 32.5 | 16 | 0 | 73
11:00 | 741 | 444 | 2820 | 1685 | 158 | 35 | 16 | 0 | 74
11:30 | 718.5 | 444 | 2811.5 | 1673 | 162.5 | 34.5 | 39 | 0 | 74
12:00 | 696 | 444 | 2803 | 1661 | 167 | 34 | 62 | 0 | 74
12:30 | 687 | 443.5 | 2796.5 | 1623 | 170 | 48.5 | 49 | 0 | 75
13:00 | 678 | 443 | 2790 | 1585 | 173 | 63 | 36 | 0 | 76
13:30 | 652.5 | 443.5 | 2831 | 1698.5 | 173 | 49 | 59 | 0 | 77
14:00 | 627 | 444 | 2872 | 1812 | 173 | 35 | 82 | 0 | 78
14:30 | 682 | 443.5 | 2852.5 | 1844.5 | 172 | 50 | 100 | 0 | 77
15:00 | 737 | 443 | 2833 | 1877 | 171 | 65 | 118 | 0 | 76
15:30 | 727 | 443 | 2861.5 | 1895 | 169 | 65 | 123.5 | 0 | 77
16:00 | 717 | 443 | 2890 | 1913 | 167 | 65 | 129 | 0 | 78 | Max Temp. in Dhaka |  | 32.4° C
16:30 | 715.5 | 443.5 | 2894.5 | 1872.5 | 169.5 | 47.5 | 165 | 0 | 75
17:00 | 714 | 444 | 2899 | 1832 | 172 | 30 | 201 | 0 | 72
17:30 | 704.5 | 444 | 2916.5 | 1844 | 172.5 | 30 | 239.5 | 0 | 73
18:00 | 695 | 444 | 2934 | 1856 | 173 | 30 | 278 | 0 | 74
18:30 | 745 | 444 | 2970 | 1970 | 171 | 68 | 319 | 0 | 92
19:00 | 769 | 444 | 3001 | 1968 | 174 | 95 | 445 | 504 | 90
19:30 | 786 | 443 | 3005 | 1982 | 173 | 95 | 520 | 444 | 92
20:00 | 793 | 444 | 3025 | 2021 | 174 | 95 | 529 | 408 | 92
20:30 | 817 | 443.5 | 3037 | 2034.5 | 165 | 95 | 525 | 404 | 92
21:00 | 841 | 443 | 3049 | 2048 | 156 | 95 | 521 | 400 | 92
21:30 | 868 | 443.5 | 3061 | 2023.5 | 155 | 94.5 | 520.5 | 333 | 91
22:00 | 895 | 444 | 3073 | 1999 | 154 | 94 | 520 | 266 | 90
22:30 | 889.5 | 443.5 | 3084 | 1994.5 | 154.5 | 93 | 512 | 244.5 | 87
23:00 | 884 | 443 | 3095 | 1990 | 155 | 92 | 504 | 223 | 84
23:30 | 905 | 443 | 3132.5 | 2016 | 120.5 | 90.5 | 501 | 111.5 | 81
24:00 | 926 | 443 | 3170 | 2042 | 86 | 89 | 498 | 0 | 78
|  | 1490 |  |  |  |  | 2380 | 3338
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Tripura

## volt
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2016-05-03
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 220 | 1:00 | 220 | 1:00 | Tongi | 216 | 7:00 | 204 | 10:00
Ishurdi | 233 | 5:00 | 226 | 8:00 | Comilla (N) | 226 | 7:00 | 218 | 18:30
Ashuganj | 235 | 3:00 | 229 | 10:00 | Hathazari | 219 | 1:00 | 202 | 17:00
Serajganj | 223 | 16:00 | 219 | 1:00 | Megnaghat | 219 | 5:00 | 209 | 10:00
Baghabari | 222 | 12:00 | 217 | 1:00 | Fenchuganj | 236 | 7:00 | 226 | 19:00
Barapukuria | 225 | 2:00 | 221 | 13:00 | Siddhirganj | 230 | 5:00 | 219 | 10:00
Bogra | 223 | 16:00 | 215 | 24:00 | Maniknagar | 229 | 5:00 | 217 | 10:00
Khulna South | 238 | 19:00 | 229 | 22:00 | Old Airport | 216 | 7:00 | 199 | 18:30
Rampura | 216 | 4:00 | 208 | 11:00 | Barisal | 242 | 18:00 | 228 | 15:00
Haripur | 214 | 3:00 | 210 | 1:00 | AKSML | 220 | 24:00 | 200 | 15:00
Hasnabad | 216 | 7:00 | 205 | 18:30 | BSRM | 220 | 1:00 | 206 | 15:00
Aminbazar | 214 | 4:00 | 203 | 18:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 500 | 131 | 900 | Madanhat | 134 | 1900 | 125 | 1700
Munsiganj | 135 | 1300 | 132 | 900 | Hathazari | 132 | 100 | 124 | 1200
Megnaghat | 135 | 2000 | 130 | 700 | Khulshi | 135 | 100 | 126 | 1600
Shyampur | 133 | 400 | 125 | 1000 | Halishahar | 130 | 100 | 122 | 1100
Bhulta | 126 | 400 | 121 | 1100 | Baraulia | 130 | 100 | 120 | 1830
Madanganj | 136 | 2100 | 130 | 800 | Sikalbaha | 131 | 1900 | 123 | 1300
Shitalakhya | 138 | 700 | 126 | 1830 | Dohazari | 132 | 1900 | 123 | 1600
Rahim steal | 135 | 2200 | 130 | 1000 | Cox'sbazar | 131 | 1600 | 120 | 1700
Matuail | 135 | 2300 | 130 | 900 | Chandraghona | 131 | 1900 | 123 | 1200
Ghorasal | 138 | 700 | 134 | 100 | Kaptai | 131 | 1830 | 125 | 1100
Narsinghdi | 134 | 2100 | 128 | 1000 | A. Khaer Stl. | 129 | 100 | 123 | 900
Haripur (SBU) | 136 | 2300 | 131 | 900 | Bakulia | 130 | 1900 | 120 | 1500
Ullon | 134 | 400 | 130 | 1500 | Julda | 130 | 100 | 120 | 1600
Hasnabad | 132 | 700 | 124 | 1000 | TK Chemical | 133 | 100 | 122 | 1600
Magbazar | 128 | 400 | 120 | 1200 | Modern Steel | 130 | 100 | 119 | 1500
Maniknagar | 133 | 300 | 128 | 1000 | Shahmirpur | 131 | 1900 | 121 | 1400
Bangabhaban | 133 | 300 | 128 | 1000 | Goalpara | 139 | 1900 | 134 | 300
Narinda | 133 | 300 | 128 | 1000 | Central s/s | 139 | 1200 | 134 | 400
Dhanmondi | 134 | 400 | 130 | 1200 | Noapara | 135 | 700 | 129 | 1700
Lalbag | 126 | 300 | 118 | 1000 | Jessore | 130 | 700 | 120 | 1700
Madartek | 127 | 1000 | 120 | 1830 | Jhenida | 131 | 900 | 116 | 2300
Mirpur | 127 | 300 | 120 | 1830 | Bottail | 134 | 1830 | 129 | 2200
Kalyanpur | 131 | 700 | 126 | 1800 | G.K.Project | 136 | 600 | 131 | 1000
Gulshan | 127 | 700 | 119 | 1830 | Faridpur | 134 | 1900 | 126 | 1500
Uttara | 127 | 700 | 119 | 1830 | Madaripur | 136 | 1930 | 125 | 1500
Kamrangirchar | 124 | 100 | 120 | 1800 | Gopalganj | 141 | 1830 | 131 | 1000
Savar | 130 | 700 | 123 | 1830 | Bagerhat | 139 | 1900 | 132 | 700
Bhasantec | 128 | 700 | 123 | 1500 | Mongla | 135 | 600 | 130 | 2300
Agargaon | 129 | 700 | 124 | 1830 | Satkhira | 136 | 1200 | 129 | 2300
Satmosjid | 128 | 700 | 123 | 1830 | Gallamari | 138 | 1900 | 134 | 400
Tongi | 137 | 800 | 129 | 1800 | Magura | 132 | 700 | 116 | 1700
Kabirpur | 135 | 1300 | 126 | 1830 | Chuadanga | 130 | 600 | 123 | 1000
Basundhara | 130 | 700 | 120 | 1800 | Barisal | 139 | 1900 | 130 | 1500
Manikganj | 136 | 400 | 126 | 1830 | Patuakhali | 139 | 1930 | 126 | 1500
Joydevpur | 135 | 2300 | 128 | 1830 | Bhandaria | 138 | 1900 | 130 | 1500
New Tongi | 136 | 500 | 126 | 1800 | Ishurdi | 135 | 500 | 131 | 800
Tangail | 131 | 400 | 120 | 1000 | Natore | 134 | 1600 | 130 | 100
Mymensing | 128 | 600 | 119 | 2100 | Bogra | 132 | 1600 | 128 | 800
Kishorganj | 130 | 600 | 125 | 1700 | Noagaon | 130 | 1900 | 125 | 100
Netrokona | 129 | 600 | 120 | 1600 | Rajshahi | 134 | 1500 | 128 | 100
Jamalpur | 121 | 500 | 114 | 1700 | C.Nawabganj | 134 | 1830 | 125 | 1000
Sherpur | 120 | 500 | 113 | 1600 | Amnura | 137 | 1900 | 130 | 100
Srimongal | 140 | 100 | 136 | 2100 | Pabna | 130 | 500 | 125 | 1000
Shahjibazar | 141 | 700 | 136 | 2100 | Shahjadpur | 136 | 1600 | 133 | 1300
Fenchuganj | 140 | 500 | 137 | 1400 | Serajganj | 131 | 1700 | 127 | 1000
Khulawara | 139 | 100 | 137 | 1400 | Niyamatpur | 128 | 1600 | 122 | 1300
Sylhet | 137 | 300 | 135 | 1600 | Joypurhat | 130 | 500 | 123 | 100
Chatak | 138 | 500 | 134 | 1930 | Rangpur | 126 | 1600 | 120 | 1000
Comilla(s) | 134 | 700 | 128 | 2000 | Lalmonirhat | 122 | 500 | 116 | 1000
Comilla(n) | 135 | 1000 | 131 | 900 | Saidpur | 125 | 600 | 116 | 1300
Chandpur | 138 | 700 | 131 | 900 | Purbasadipur | 127 | 1600 | 120 | 1000
Feni | 125 | 700 | 117 | 1830 | Thakurgaon | 123 | 1600 | 111 | 1100
Chowmuhani | 130 | 700 | 122 | 1930 | Palashbari | 127 | 500 | 123 | 1300
Ashuganj | 139 | 600 | 135 | 1930 | Barapukuria | 125 | 200 | 121 | 1300
Daudkandi | 135 | 2100 | 131 | 900 | Panchagar | 119 | 600 | 108 | 1300
B.Baria | 141 | 800 | 134 | 1800
| Sub Assistant Engineer |  |  |  |  | Sub Divisional Engineer
| Network Operation Division |  |  |  |  | Network Operation Division
Page 7 of 7