## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-07-02 | Sunday
|  | Date (day): | 2023-07-02 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12548.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14653 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-01 | 2023-07-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 180 | 120 | 120 | 60 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180 |  | 190 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 6 | 6 | 6 | 6 | 102 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 397 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 327 | 343 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 35 | 9 | 9 | 9 | 91 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 305 | 313 | 310 | 310 |  |  | FGMO
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 17 | 34 | 100 | 2 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 20 | 0 | 0 | 0 | 0
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 14 | 15 |  | 7 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 158 | 200 | 150 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 8 | 40 | 60 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 45 | 100 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 8 | 8 | 42 | 60 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 17 | 54 |  |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 64 | 149 |  |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 30 | 34 | 45 | 45 |  | 35 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 15 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 19 | 19 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 0 | 0 | 8 | 50 |  |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 0 | 17 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 0 | 17 | 17 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 51 | 70 | 72 | 32 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 6 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 6 | 17 | 35 | 20 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5867 | 2374 | 2401 | 3489 | 4159 | 638 | 992
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 108 | 108 | 110 | 110 | 70 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 18 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 46 | 6 | 50
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 65 | 35 | 60 | 195 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 149 | 149 | 150 | 150 |  | 75 | ST under maint.
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 34 | 17 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 40 | 63 | 32 | 70 | 28 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 50 | 50 | 50 | 52 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 46 | 69 | 46 | 69 | 31 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 50 | 100 | 100 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 13 | 13 | 13 | 13 | 9 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 26 | 34 | 25 | 35
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 296 | 88 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 17 | 34 | 17 | 34 | 76 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 90 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 51 | 34 | 51 | 65 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 54 | 18 | 163 | 163 |  |  | On test.
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 18 | 10
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 779 | 1262 | 1054 | 1458 | 725 | 405
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 193 | 200 | 200 |  |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 320 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Under maint
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 322 | 329 | 340 | 340 | 60 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 47 | 46 | 46
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 185 | 190 | 190
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 18 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 70 | 150 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 44 | 47 | 30 | 45
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 63 | 104 | 50 | 100 | 100 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 146 | 146 | 161
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 24 | 33 | 32 | 32
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43 | 9 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 12 | 12 | 12 |  | 13 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 52 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 28 | 58 | 9 | 55 | 58
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 17 | 54 | 18 | 54
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1293 | 1765 | 1709 | 1933 | 227 | 581
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 106 | 205 | 200 | 200
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 19 | 20 | 20
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 8 | 32 | 68 | 85 | 115 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 85 | 24 | 85 | 30 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 19 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 178 | 341 | 375.6 | 402 | 0 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 0 | 0 | 0 |  | 163 | ST under maint.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 44 | 50 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 25 | 49 | 50 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 60 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 60 | 85 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 | 231 |  | Gas line maint.
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 17 | 17
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 24 | 15 | 24 |  |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 315 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 0 | 0 | 0 | 250 |  | 400 | Under maint.
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 100 | 128 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 757 | 817 | 1072 | 1331 | 231 | 1080
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 908 | 934 | 934
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 0 | 49 | 49 | 97 |  | 18 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 28 |  | 26 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 200 | 200 |  | 30 | Engine problem
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 36 | 78 |  | 31 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 410 | 350 | 380 | 30
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 40 | 16 | 24 | 16 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 0 | 54 | 54 | 51 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 105 | 15 | 50 | 55 |  | Fuel shortage
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 17 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  | 617 | Under maint
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 2905 | 2901 | 1316 | 1512 | 1774 | 1845 | 168 | 722
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 16 | 48 | 62 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 18 | 29 | 25 | 38
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 270 | 360 | 360 | 360 | 884 |  | Unit-1 under S/D
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 178 | 140 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 150 | 160 | 150 | 150 | 157 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 681 | 824 | 853 | 1031 | 1103 | 129
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 65 | 70 | 70
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 30 | 30 |  | 22 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 30 | 35 |  | 36 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 28 | 0 | 0 | 0 | 0 | 28 |  | Fuel shortage
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 30 |  | 20 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 214 | 180 | 200 | 10 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 166 | 220 | 180 | 200 | 20 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 376 | 422 | 414 | 414
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 0 | 40 | 80 |  | 24 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 200
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 74 | 70 | 113 | 0
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113 | 0
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*1 | 748 | 748 | 459 | 557 | 550 | 550
| Rajshahi Area Total |  |  |  |  | 2927 | 2905 | 1061 | 1708 | 1726 | 2086 | 472 | 120
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 180 | 180 | 180 | 180
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 0 | 106 | 113 | 113
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 0 | 115 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 14 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 64 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 262 | 401 | 496 | 408 | 125 | 85
| Total |  |  |  |  | 24143 | 23370 | 8701 | 11031 | 12548.6 | 14653 | 3689 | 4114
A. |  | 2023-07-01 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 11198 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8071 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11031 | MW
3 | Day peak Generation : |  |  | 8701 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10529.67 | MW
4 | Evening peak Generation : |  |  | 11031 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 235.5631 | MKWHr | By Solar | 1.3064 | MKWHr
| By Gas : | 136.6751 | MKWHr |  | By Oil: | 26.1354 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 45.8076 | MKWHr |  | By Hydro: | 0.91614 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3689 | MW | Dhaka | 2614.57 | 2614.57 |  | 0 |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 4114 | MW | Chittagong | 1219.5 | 1219.5 |  | 0 |  | 19:00 |  | 0
|  |  | Total = |  |  | 7803 | MW | Khulna | 1496 | 1496 |  | 0 |  | 19:30 |  | 0
7 | Total Gas Supplied : |  |  | 1107.47 | MMCFD |  |  | Rajshahi | 1224.6 | 1224.6 |  | 0 |  | 20:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 155249945.246 | ii) Oil : | Taka | 331132100.31 | Comilla | 1234 | 1234 |  | 0 |  | 21:00 |  | 0
|  | iii) Coal : | Taka | 92196818 | Total | Taka | 578578863.556 | Mymensingh | 929 | 929 |  | 0 |  | 22:00 |  | 0
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 467 | 467 |  | 0 |  | 23:00 |  | 0
| ii) During Peak Demand : |  |  | 740 | MW (E to W) at | 21:00 | hrs | Barisal | 473 | 473 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 580 | MW at | 13:00 | hrs | Rangpur | 872 | 872 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 31.8° C |  |  | Total | 10529.67 | 10529.67 |  | 0
B. |  | 2023-07-02 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 31.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14653 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
4 | Reserve(Generation end) |  |  |  | 2853 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 248.2269 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8750 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.7484 | MKWHr. | ii) HVDC Flow at Peak Time |  | 908 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9741 | MKWHr. | iii) Maximum HVDC Flow : |  | 909 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.22 |  | (b) Today: | 73.21 |  | (c) Rule Curve: |  | 84.61
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-07-01 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 180 | 100 | 0 | 6 | 0 | 357 | 282 |  | 0 | 450 | 251 | 9 | 0 | 0 | 270 | 0 | 206 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 85 | 35 | 0 | 104 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 33 | 46 | 0 | 50 | 13 | 36 | 0 | 0 | 0 | 280 | 240 | 187 | 8 | 0 | 25 | 0 | 0 | 43 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 130 | 71 | 0 | 21 | 0 | 43 | 30 | 47 | 48 | 112 | 0 | 62 | 86 | 0 | 203 | 18 | 0 | 10 | 80 | 24 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 26 | 0 | 88 | 51 | 43 | 0 | 19 | 0 | 17 | 0 | 88 | 17 | 17 | 109 | 31 | 50 | 0 | 49 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 253 | 0 |  | 905 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 346 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 360 | 224 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 561 | 0 | 0 |  | 5848 | 3696 | 9544 | 3885 | 905 | 2056 | 0 | 956 | 1514 | 35 | 0 | 63 | 130 | 0 | 0 | 0 | 73.22
2:00 | 0 | 0 | 120 | 100 | 0 | 6 | 0 | 356 | 282 |  | 0 | 380 | 277 | 0 | 0 | 0 | 270 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 85 | 35 | 0 | 106 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 33 | 46 | 0 | 50 | 13 | 36 | 0 | 0 | 0 | 280 | 240 | 185 | 8 | 0 | 10 | 0 | 0 | 43 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 126 | 71 | 0 | 20 | 0 | 43 | 30 | 47 | 49 | 112 | 0 | 40 | 40 | 0 | 203 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 0 | 0 | 0 | 66 | 0 | 17 | 0 | 88 | 51 | 0 | 0 | 19 | 0 | 17 | 0 | 88 | 17 | 17 | 106 | 28 | 50 | 15 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 295 | 0 |  | 905 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 162 | 0 | 346 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 250 | 227 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 140 | 565 | 0 | 0 |  | 5564 | 3564 | 9128 | 3668 | 905 | 2059 | 0 | 842 | 1430 | 35 | 0 | 63 | 126 | 0 | 0 | 0 | 73.22
3:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 356 | 282 |  | 0 | 330 | 295 | 0 | 0 | 0 | 270 | 0 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 85 | 35 | 0 | 108 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 33 | 46 | 0 | 50 | 13 | 36 | 0 | 0 | 0 | 280 | 240 | 182 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 126 | 71 | 0 | 20 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 40 | 40 | 0 | 203 | 0 | 0 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 88 | 51 | 0 | 0 | 19 | 0 | 17 | 0 | 83 | 17 | 17 | 106 | 29 | 50 | 28 | 17 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 296 | 0 |  | 905 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 303 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 250 | 225 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 140 | 566 | 0 | 0 |  | 5494 | 3431 | 8925 | 3599 | 905 | 2011 | 0 | 754 | 1432 | 35 | 0 | 63 | 126 | 0 | 0 | 0 | 73.22
4:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 356 | 282 |  | 0 | 330 | 301 | 0 | 0 | 0 | 270 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 15 | 19 | 0 | 85 | 35 | 0 | 108 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 33 | 46 | 0 | 20 | 13 | 42 | 0 | 0 | 0 | 285 | 240 | 191 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 126 | 70 | 0 | 20 | 0 | 43 | 30 | 47 | 49 | 80 | 0 | 40 | 10 | 0 | 205 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 88 | 51 | 0 | 0 | 19 | 0 | 17 | 0 | 88 | 17 | 17 | 70 | 29 | 50 | 38 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 295 | 0 |  | 905 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 308 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 250 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 416 | 0 | 0 |  | 5424 | 3251 | 8675 | 3616 | 905 | 2008 | 0 | 641 | 1281 | 35 | 0 | 63 | 126 | 0 | 0 | 0 | 73.22
5:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 357 | 281 |  | 0 | 330 | 268 | 0 | 0 | 0 | 270 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 15 | 19 | 0 | 85 | 35 | 0 | 108 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 0 | 33 | 46 | 0 | 6 | 13 | 42 | 0 | 0 | 0 | 280 | 240 | 184 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 122 | 70 | 0 | 20 | 0 | 43 | 30 | 47 | 48 | 80 | 0 | 40 | 10 | 0 | 204 | 0 | 0 | 0 | 265 | 0 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 88 | 51 | 0 | 0 | 47 | 0 | 17 | 0 | 88 | 17 | 17 | 70 | 29 | 50 | 50 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 294 | 0 |  | 906 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 179 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 308 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 250 | 226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 417 | 0 | 0 |  | 5361 | 3252 | 8613 | 3610 | 906 | 1954 | 0 | 643 | 1280 | 35 | 0 | 63 | 122 | 0 | 0 | 0 | 73.22
6:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 314 | 282 |  | 0 | 300 | 290 | 0 | 0 | 0 | 240 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 15 | 19 | 0 | 0 | 35 | 0 | 106 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 46 | 0 | 0 | 13 | 42 | 0 | 0 | 0 | 280 | 240 | 183 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 116 | 104 | 0 | 20 | 0 | 43 | 30 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 204 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 50 | 51 | 0 | 0 | 67 | 0 | 17 | 0 | 88 | 17 | 17 | 70 | 21 | 50 | 50 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 18 | 0 | 230 | 0 | 0 | 297 | 0 |  | 905 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 179 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 227 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 140 | 418 | 2 | 0 |  | 5083 | 3173 | 8256 | 3439 | 905 | 1888 | 0 | 554 | 1284 | 35 | 0 | 30 | 116 | 5 | 0 | 0 | 73.22
7:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 307 | 282 |  | 0 | 300 | 288 | 0 | 0 | 0 | 240 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 5 | 15 | 19 | 0 | 0 | 35 | 0 | 102 | 0 | 0 | 151 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 13 | 42 | 0 | 0 | 0 | 280 | 240 | 183 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 110 | 104 | 0 | 20 | 0 | 43 | 30 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 203 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 51 | 0 | 0 | 45 | 0 | 17 | 1 | 87 | 17 | 17 | 70 | 9 | 50 | 50 | 14 | 3 | 0 | 17 | 0 | 17 | 6 | 18 | 0 | 230 | 0 | 0 | 294 | 0 |  | 906 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 179 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 227 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 140 | 418 | 10 | 0 |  | 5024 | 3154 | 8178 | 3427 | 906 | 1844 | 0 | 499 | 1281 | 35 | 0 | 30 | 110 | 46 | 0 | 0 | 0
8:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 307 | 282 |  | 0 | 300 | 298 | 0 | 0 | 0 | 240 | 0 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 0 | 35 | 0 | 110 | 0 | 0 | 149 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 13 | 42 | 0 | 0 | 0 | 290 | 240 | 192 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 30 | 0 | 20 | 10 | 32 | 20 | 108 | 103 | 0 | 20 | 0 | 43 | 30 | 11 | 10 | 80 | 0 | 40 | 10 | 0 | 84 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 10 | 25 | 51 | 0 | 0 | 24 | 0 | 17 | 1 | 88 | 17 | 17 | 70 | 9 | 12 | 50 | 17 | 7 | 0 | 17 | 0 | 17 | 2 | 18 | 0 | 230 | 0 | 0 | 291 | 0 |  | 900 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 225 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 2 | 140 | 416 | 60 | 0 |  | 4903 | 3168 | 8071 | 3333 | 900 | 1841 | 0 | 419 | 1277 | 35 | 0 | 30 | 108 | 128 | 0 | 0 | 0
9:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 307 | 282 |  | 0 | 300 | 273 | 0 | 0 | 0 | 240 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 0 | 35 | 0 | 112 | 0 | 0 | 149 | 0 | 0 | 0 |  | 0 | 0 | 0 | 12 | 0 | 0 | 13 | 42 | 0 | 0 | 0 | 280 | 240 | 183 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 28 | 0 | 20 | 10 | 25 | 20 | 116 | 104 | 0 | 12 | 0 | 43 | 30 | 11 | 10 | 112 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 0 | 285 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 15 | 25 | 51 | 0 | 0 | 24 | 0 | 17 | 4 | 88 | 17 | 17 | 70 | 9 | 12 | 50 | 32 | 7 | 0 | 17 | 0 | 17 | 7 | 18 | 0 | 230 | 0 | 0 | 351 | 0 |  | 901 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 226 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 6 | 140 | 416 | 18 | 0 |  | 4942 | 3144 | 8086 | 3241 | 901 | 1910 | 0 | 434 | 1337 | 35 | 0 | 28 | 116 | 84 | 0 | 0 | 0
10:00 | 0 | 0 | 120 | 110 | 0 | 6 | 0 | 363 | 327 |  | 0 | 300 | 291 | 6 | 0 | 0 | 240 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 8 | 19 | 0 | 0 | 35 | 0 | 110 | 0 | 2 | 145 | 0 | 0 | 0 |  | 0 | 0 | 0 | 46 | 0 | 0 | 13 | 35 | 0 | 0 | 0 | 280 | 240 | 183 | 8 | 0 | 10 | 0 | 0 | 10 | 0 | 28 | 0 | 20 | 10 | 24 | 20 | 116 | 104 | 0 | 20 | 0 | 43 | 30 | 11 | 10 | 112 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 15 | 50 | 51 | 0 | 0 | 24 | 0 | 17 | 5 | 88 | 17 | 17 | 70 | 9 | 50 | 50 | 36 | 12 | 0 | 20 | 0 | 17 | 6 | 18 | 0 | 260 | 0 | 0 | 0 | 0 |  | 902 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 326 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 250 | 184 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 5 | 140 | 415 | 22 | 0 |  | 4874 | 3145 | 8019 | 3356 | 902 | 1957 | 0 | 546 | 984 | 35 | 0 | 28 | 116 | 95 | 0 | 0 | 0
11:00 | 0 | 0 | 120 | 170 | 0 | 6 | 0 | 399 | 327 |  | 0 | 330 | 297 | 24 | 0 | 0 | 270 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 5 | 19 | 0 | 0 | 35 | 0 | 110 | 0 | 8 | 147 | 0 | 0 | 0 |  | 0 | 4 | 0 | 46 | 0 | 6 | 13 | 26 | 0 | 0 | 0 | 290 | 0 | 199 | 26 | 0 | 10 | 0 | 0 | 10 | 0 | 36 | 0 | 20 | 10 | 24 | 15 | 120 | 104 | 0 | 20 | 1 | 43 | 30 | 11 | 10 | 112 | 0 | 60 | 40 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 50 | 51 | 0 | 0 | 24 | 0 | 17 | 3 | 88 | 17 | 17 | 70 | 9 | 45 | 0 | 52 | 32 | 0 | 34 | 0 | 17 | 12 | 18 | 0 | 401 | 36 | 0 | 0 | 0 |  | 903 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 250 | 178 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 6 | 140 | 416 | 27 | 0 |  | 5067 | 3113 | 8180 | 3240 | 903 | 2017 | 0 | 601 | 986 | 35 | 0 | 76 | 120 | 202 | 0 | 0 | 0
12:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 400 | 327 |  | 0 | 420 | 305 | 35 | 0 | 0 | 300 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 0 | 35 | 0 | 108 | 0 | 8 | 149 | 0 | 0 | 0 |  | 0 | 40 | 0 | 46 | 0 | 6 | 13 | 26 | 0 | 0 | 0 | 280 | 0 | 184 | 102 | 0 | 10 | 0 | 0 | 18 | 0 | 44 | 0 | 20 | 10 | 24 | 15 | 122 | 106 | 0 | 20 | 1 | 43 | 30 | 25 | 25 | 112 | 0 | 61 | 60 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 50 | 63 | 0 | 0 | 24 | 0 | 17 | 3 | 88 | 17 | 17 | 17 | 28 | 50 | 100 | 53 | 19 | 0 | 34 | 0 | 17 | 6 | 17 | 0 | 322 | 54 | 0 | 0 | 0 |  | 904 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 270 | 178 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 14 | 150 | 459 | 64 | 0 |  | 5381 | 3320 | 8701 | 3414 | 904 | 2288 | 0 | 595 | 1059 | 35 | 0 | 138 | 122 | 146 | 0 | 0 | 0
13:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 381 | 327 |  | 0 | 420 | 306 | 43 | 0 | 0 | 300 | 0 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 15 | 19 | 0 | 0 | 35 | 0 | 110 | 0 | 8 | 146 | 0 | 0 | 0 |  | 0 | 55 | 2 | 58 | 0 | 6 | 13 | 26 | 0 | 0 | 0 | 300 | 0 | 196 | 175 | 0 | 10 | 0 | 0 | 30 | 0 | 44 | 0 | 20 | 10 | 24 | 20 | 128 | 134 | 0 | 22 | 1 | 43 | 30 | 25 | 25 | 80 | 0 | 61 | 60 | 0 | 0 | 0 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 50 | 68 | 0 | 0 | 24 | 0 | 17 | 4 | 88 | 17 | 17 | 17 | 29 | 50 | 120 | 53 | 41 | 0 | 34 | 0 | 17 | 0 | 18 | 0 | 337 | 54 | 0 | 177 | 0 |  | 904 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 270 | 179 | 0 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 13 | 150 | 457 | 65 | 0 |  | 5720 | 3306 | 9026 | 3453 | 904 | 2337 | 0 | 622 | 1234 | 35 | 0 | 155 | 128 | 158 | 0 | 0 | 0
14:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 342 | 328 |  | 0 | 420 | 274 | 42 | 0 | 0 | 300 | 0 | 121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 15 | 19 | 0 | 0 | 35 | 0 | 110 | 0 | 8 | 149 | 0 | 0 | 0 |  | 0 | 55 | 33 | 58 | 0 | 6 | 13 | 26 | 0 | 0 | 0 | 280 | 0 | 184 | 185 | 0 | 25 | 0 | 0 | 30 | 0 | 43 | 0 | 20 | 10 | 24 | 20 | 132 | 155 | 0 | 22 | 0 | 43 | 30 | 25 | 25 | 80 | 0 | 61 | 60 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 50 | 68 | 0 | 0 | 24 | 0 | 17 | 3 | 88 | 17 | 17 | 17 | 29 | 50 | 124 | 53 | 30 | 0 | 34 | 0 | 17 | 1 | 18 | 0 | 323 | 54 | 0 | 266 | 0 |  | 905 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 378 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 250 | 178 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 11 | 150 | 459 | 68 | 0 |  | 5753 | 3291 | 9044 | 3401 | 905 | 2335 | 0 | 621 | 1305 | 35 | 0 | 185 | 132 | 125 | 0 | 0 | 0
15:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 341 | 326 |  | 0 | 400 | 287 | 42 | 0 | 0 | 260 | 0 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 7 | 0 | 0 | 35 | 0 | 108 | 0 | 8 | 148 | 0 | 0 | 0 |  | 0 | 54 | 32 | 58 | 0 | 6 | 13 | 26 | 0 | 0 | 0 | 280 | 0 | 184 | 185 | 0 | 25 | 0 | 0 | 5 | 0 | 43 | 0 | 20 | 10 | 24 | 20 | 134 | 154 | 0 | 22 | 1 | 43 | 30 | 25 | 25 | 0 | 0 | 61 | 60 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 7 | 50 | 68 | 0 | 0 | 24 | 0 | 17 | 2 | 87 | 17 | 17 | 17 | 36 | 50 | 0 | 54 | 10 | 0 | 34 | 0 | 17 | 0 | 25 | 0 | 320 | 54 | 0 | 272 | 0 |  | 905 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 181 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 15 | 150 | 460 | 28 | 0 |  | 5401 | 3246 | 8647 | 3162 | 905 | 2192 | 0 | 643 | 1312 | 35 | 0 | 183 | 134 | 81 | 0 | 0 | 73.22
16:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 343 | 287 |  | 0 | 350 | 271 | 42 | 0 | 0 | 260 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 15 | 0 | 0 | 0 | 35 | 0 | 107 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 53 | 32 | 58 | 0 | 6 | 13 | 19 | 0 | 0 | 0 | 280 | 0 | 184 | 185 | 0 | 25 | 0 | 0 | 5 | 0 | 43 | 1 | 20 | 10 | 24 | 7 | 126 | 158 | 0 | 0 | 0 | 43 | 30 | 11 | 10 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 260 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 5 | 50 | 68 | 0 | 0 | 8 | 0 | 17 | 1 | 88 | 17 | 17 | 17 | 36 | 50 | 0 | 53 | 5 | 0 | 34 | 0 | 17 | 0 | 53 | 0 | 292 | 36 | 0 | 250 | 0 |  | 906 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 181 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 11 | 150 | 460 | 25 | 0 |  | 5064 | 3077 | 8141 | 3016 | 906 | 1885 | 0 | 648 | 1290 | 35 | 0 | 164 | 126 | 71 | 0 | 0 | 73.22
17:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 345 | 287 |  | 0 | 320 | 312 | 18 | 0 | 0 | 240 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 15 | 7 | 0 | 0 | 35 | 0 | 105 | 0 | 8 | 146 | 0 | 0 | 0 |  | 0 | 48 | 36 | 58 | 0 | 6 | 13 | 19 | 0 | 0 | 0 | 325 | 0 | 209 | 120 | 0 | 25 | 0 | 0 | 5 | 0 | 41 | 8 | 20 | 10 | 0 | 0 | 80 | 155 | 0 | 0 | 0 | 43 | 30 | 11 | 10 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 275 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 4 | 60 | 69 | 0 | 0 | 8 | 0 | 17 | 1 | 88 | 17 | 24 | 17 | 38 | 50 | 0 | 43 | 0 | 0 | 34 | 0 | 17 | 0 | 56 | 0 | 333 | 36 | 0 | 0 | 0 |  | 906 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 250 | 181 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 12 | 150 | 450 | 30 | 0 |  | 4813 | 3141 | 7954 | 3168 | 906 | 1867 | 0 | 644 | 1030 | 35 | 0 | 161 | 80 | 63 | 0 | 0 | 73.22
18:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 380 | 337 |  | 0 | 370 | 289 | 13 | 0 | 0 | 44 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 16 | 0 | 15 | 19 | 0 | 0 | 35 | 0 | 109 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 10 | 13 | 23 | 0 | 0 | 0 | 280 | 0 | 175 | 120 | 0 | 45 | 0 | 0 | 5 | 0 | 41 | 8 | 20 | 10 | 32 | 0 | 112 | 206 | 0 | 0 | 0 | 43 | 30 | 11 | 10 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 1 | 50 | 78 | 5 | 0 | 11 | 0 | 34 | 0 | 120 | 17 | 34 | 52 | 38 | 50 | 0 | 17 | 0 | 0 | 36 | 0 | 17 | 0 | 56 | 4 | 292 | 36 | 0 | 0 | 0 |  | 906 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 13 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 336 | 0 | 0 | 0 | 0 | 25 | 0 | 1 | 0 | 250 | 181 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 2 | 150 | 561 | 18 | 0 |  | 4967 | 3330 | 8297 | 3096 | 906 | 2011 | 0 | 777 | 1141 | 35 | 0 | 190 | 112 | 29 | 0 | 0 | 73.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 360 | 333 |  | 0 | 380 | 313 | 17 | 5 | 0 | 45 | 0 | 103 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 10 | 0 | 20 | 6 | 15 | 19 | 0 | 0 | 35 | 30 | 109 | 0 | 23 | 147 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 24 | 0 | 0 | 0 | 345 | 0 | 203 | 130 | 0 | 47 | 0 | 0 | 28 | 0 | 43 | 29 | 20 | 10 | 32 | 12 | 136 | 204 | 0 | 0 | 0 | 43 | 30 | 29 | 33 | 0 | 0 | 60 | 85 | 0 | 0 | 0 | 0 | 0 | 265 | 0 | 11 | 0 | 10 | 0 | 0 | 32 | 0 | 10 | 0 | 100 | 104 | 25 | 0 | 58 | 12 | 34 | 0 | 170 | 17 | 34 | 52 | 56 | 90 | 15 | 32 | 0 | 17 | 51 | 0 | 17 | 0 | 53 | 12 | 350 | 36 | 0 | 0 | 0 |  | 906 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 23 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 138 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 313 | 0 | 0 | 24 | 35 | 45 | 0 | 0 | 35 | 250 | 184 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 150 | 558 | 0 | 0 |  | 5756 | 3552 | 9308 | 3289 | 906 | 2146 | 0 | 1408 | 1138 | 65 | 0 | 220 | 136 | 0 | 0 | 0 | 73.22
19:30 | 0 | 0 | 150 | 180 | 0 | 6 | 0 | 396 | 354 |  | 0 | 420 | 302 | 17 | 17 | 0 | 45 | 0 | 201 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 20 | 6 | 15 | 19 | 0 | 0 | 35 | 30 | 109 | 0 | 25 | 149 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 24 | 0 | 0 | 0 | 310 | 0 | 188 | 130 | 0 | 47 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 10 | 32 | 12 | 138 | 202 | 0 | 19 | 0 | 43 | 30 | 47 | 42 | 0 | 0 | 60 | 85 | 0 | 0 | 18 | 0 | 0 | 310 | 0 | 11 | 0 | 40 | 0 | 0 | 32 | 0 | 17 | 0 | 100 | 104 | 70 | 0 | 85 | 17 | 34 | 0 | 280 | 17 | 34 | 52 | 56 | 90 | 45 | 53 | 0 | 17 | 51 | 0 | 17 | 0 | 54 | 17 | 322 | 36 | 0 | 0 | 0 |  | 908 | 0 | 405 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 24 | 65 | 28 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 422 | 0 | 0 | 45 | 67 | 70 | 0 | 0 | 70 | 350 | 184 | 0 | 2 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 160 | 562 | 0 | 0 |  | 6372 | 4088 | 10460 | 3605 | 908 | 2397 | 0 | 1874 | 1252 | 65 | 0 | 221 | 138 | 0 | 0 | 0 | 0
20:00 | 0 | 0 | 150 | 180 | 0 | 6 | 0 | 394 | 352 |  | 0 | 420 | 300 | 17 | 17 | 0 | 44 | 0 | 162 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 20 | 6 | 15 | 19 | 0 | 0 | 35 | 30 | 110 | 0 | 25 | 148 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 24 | 0 | 0 | 0 | 310 | 0 | 183 | 130 | 0 | 47 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 10 | 32 | 12 | 138 | 204 | 0 | 19 | 0 | 43 | 30 | 47 | 47 | 0 | 0 | 61 | 85 | 0 | 0 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 15 | 0 | 0 | 32 | 0 | 17 | 0 | 100 | 104 | 70 | 0 | 85 | 17 | 34 | 0 | 296 | 17 | 34 | 34 | 55 | 90 | 67 | 43 | 0 | 17 | 51 | 0 | 17 | 0 | 54 | 0 | 322 | 36 | 0 | 0 | 0 |  | 909 | 0 | 405 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 32 | 65 | 28 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 209 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 423 | 0 | 0 | 56 | 105 | 103 | 0 | 0 | 100 | 350 | 183 | 0 | 13 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 160 | 556 | 0 | 0 |  | 6304 | 4278 | 10582 | 3609 | 909 | 2397 | 0 | 1989 | 1246 | 65 | 0 | 229 | 138 | 0 | 0 | 0 | 73.22
21:00 | 0 | 0 | 180 | 180 | 0 | 6 | 0 | 397 | 343 |  | 0 | 450 | 313 | 9 | 17 | 0 | 45 | 0 | 200 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 20 | 14 | 15 | 19 | 0 | 0 | 35 | 30 | 108 | 0 | 25 | 149 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 34 | 0 | 0 | 0 | 320 | 0 | 193 | 185 | 0 | 47 | 0 | 0 | 43 | 0 | 47 | 43 | 20 | 10 | 33 | 12 | 146 | 205 | 0 | 19 | 0 | 43 | 30 | 44 | 49 | 0 | 0 | 61 | 85 | 0 | 0 | 18 | 0 | 9 | 315 | 24 | 11 | 0 | 15 | 0 | 0 | 32 | 0 | 17 | 0 | 100 | 104 | 70 | 0 | 85 | 17 | 34 | 0 | 296 | 17 | 34 | 34 | 58 | 90 | 128 | 51 | 0 | 0 | 51 | 0 | 17 | 0 | 54 | 6 | 329 | 18 | 0 | 0 | 0 |  | 908 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 29 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 422 | 0 | 0 | 74 | 105 | 106 | 0 | 0 | 113 | 360 | 140 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 160 | 557 | 0 | 0 |  | 6586 | 4445 | 11031 | 3825 | 908 | 2467 | 0 | 2150 | 1257 | 65 | 0 | 213 | 146 | 0 | 0 | 0 | 73.22
22:00 | 0 | 0 | 180 | 180 | 0 | 5 | 0 | 396 | 312 |  | 0 | 450 | 263 | 8 | 17 | 0 | 217 | 0 | 120 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 20 | 15 | 15 | 19 | 0 | 0 | 30 | 30 | 110 | 0 | 25 | 151 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 34 | 0 | 0 | 0 | 310 | 0 | 183 | 195 | 0 | 47 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 10 | 33 | 20 | 146 | 206 | 0 | 19 | 0 | 43 | 30 | 47 | 49 | 0 | 0 | 62 | 85 | 0 | 80 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 32 | 0 | 17 | 0 | 100 | 104 | 70 | 0 | 85 | 17 | 34 | 0 | 296 | 17 | 34 | 45 | 58 | 90 | 136 | 51 | 0 | 0 | 51 | 0 | 17 | 0 | 54 | 17 | 322 | 18 | 0 | 0 | 0 |  | 907 | 0 | 405 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 29 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 391 | 3 | 0 | 109 | 105 | 106 | 0 | 0 | 113 | 360 | 224 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 160 | 560 | 0 | 0 |  | 6655 | 4543 | 11198 | 3982 | 907 | 2427 | 0 | 2205 | 1260 | 60 | 0 | 211 | 146 | 0 | 0 | 0 | 73.22
23:00 | 0 | 0 | 180 | 180 | 0 | 6 | 0 | 386 | 312 |  | 0 | 450 | 280 | 9 | 15 | 0 | 223 | 0 | 76 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 20 | 15 | 15 | 19 | 0 | 0 | 30 | 0 | 108 | 0 | 25 | 151 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 34 | 0 | 0 | 0 | 310 | 0 | 182 | 195 | 0 | 47 | 0 | 0 | 43 | 0 | 42 | 25 | 20 | 10 | 33 | 0 | 150 | 205 | 0 | 19 | 0 | 43 | 30 | 47 | 49 | 0 | 0 | 62 | 85 | 0 | 110 | 18 | 0 | 10 | 270 | 24 | 11 | 0 | 15 | 0 | 0 | 37 | 0 | 17 | 0 | 100 | 104 | 20 | 0 | 47 | 17 | 34 | 0 | 123 | 17 | 34 | 106 | 33 | 90 | 300 | 53 | 0 | 0 | 51 | 0 | 17 | 0 | 31 | 17 | 322 | 123 | 0 | 0 | 0 |  | 908 | 0 | 410 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 30 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 359 | 17 | 0 | 113 | 105 | 106 | 0 | 0 | 113 | 360 | 226 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 160 | 561 | 0 | 0 |  | 6591 | 4467 | 11058 | 4074 | 908 | 2396 | 0 | 1926 | 1261 | 30 | 0 | 313 | 150 | 0 | 0 | 0 | 73.22
24:00 | 0 | 0 | 180 | 180 | 0 | 6 | 0 | 350 | 311 |  | 0 | 450 | 298 | 8 | 0 | 0 | 222 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 20 | 15 | 15 | 19 | 0 | 0 | 30 | 0 | 110 | 0 | 8 | 151 | 0 | 0 | 0 |  | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 34 | 0 | 0 | 0 | 310 | 0 | 183 | 189 | 0 | 47 | 0 | 0 | 43 | 0 | 44 | 25 | 20 | 10 | 24 | 20 | 148 | 203 | 0 | 19 | 0 | 43 | 30 | 46 | 49 | 0 | 0 | 61 | 85 | 0 | 125 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 100 | 55 | 6 | 0 | 47 | 17 | 34 | 0 | 124 | 17 | 20 | 52 | 9 | 50 | 394 | 53 | 0 | 0 | 51 | 0 | 17 | 0 | 18 | 0 | 322 | 160 | 0 | 0 | 0 |  | 907 | 0 | 405 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 8 | 65 | 31 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 357 | 17 | 0 | 70 | 105 | 70 | 0 | 0 | 70 | 360 | 225 | 0 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 150 | 561 | 0 | 0 |  | 6414 | 4204 | 10618 | 4157 | 907 | 2414 | 0 | 1359 | 1251 | 30 | 0 | 352 | 148 | 0 | 0 | 0 | 73.21
KWH | 0 | 0 | 3235156 | 3244500 | 0 | 190272 | 0 | 8753150 | 7408000 |  | 0 | 9092000 | 6977949 | 336960 | 62690 | 0 | 5333284 | 0 | 3164000 | 67478 | 90864 | 0 | 0 | 0 | 0 | 0 | 247140 | 0 | 81488 | 0 | 480000 | 189180 | 352700 | 460100 | 0 | 469245 | 796140 | 120000 | 2500000 | 0 | 250061 | 3594051 | 0 | 0 | 0 |  | 0 | 708336 | 638409 | 1159920 | 0 | 504000 | 311520 | 787680 | 0 | 0 | 0 | 7343900 | 2713000 | 4554000 | 2107636 | 0 | 590256 | 0 | 0 | 662464 | 0 | 891392 | 230664 | 473242 | 244080 | 680900 | 379410 | 2974080 | 3100800 | 0 | 384804 | 6000 | 1018000 | 687360 | 691200 | 752328 | 1400073 | 0 | 1277373 | 1139520 | 0 | 1303890 | 99000 | 0 | 176940 | 6631180 | 129384 | 264000 | 0 | 115418 | 0 | 0 | 607200 | 0 | 142992 | 133515 | 1641600 | 1638720 | 485090 | 0 | 914400 | 111629 | 533599 | 27723 | 2938145 | 446990 | 540290 | 1377120 | 708960 | 1303680 | 1560800 | 858240 | 165170 | 40320 | 777868 | 0 | 444240 | 56997 | 714240 | 80640 | 6950700 | 623927 | 0 | 18398180 | 0 |  | 21748363 | 0 | 8734752 | 0 | 241920 | 0 | 0 | 0 | 0 | 0 | 162000 | 1532000 | 468050 | 58752 | 0 | 0 | 1540000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169721 | 0 | 0 | 122238 | 0 | 0 | 4411700 | 0 | 0 | 3235691 | 0 | 0 | 0 | 0 | 0 | 4094718 | 0 | 8217272 | 26112 | 0 | 483744 | 511920 | 801225 | 0 | 40652 | 543648 | 7642500 | 4871400 | 0 | 156000 | 460 | 298080 | 665664 | 0 | 0 | 0 | 102524 | 3578200 | 11777000 | 475300 | 0 |  | 148851542 | 86711606 | 235563148 | 85101184 | 21748363 | 51573964 | 0 | 23103631 | 45807580 | 916140 | 0 | 3031785 | 2974080 | 1306421 | 0 | 0
Fuel Cost | 0 | 0 | 4723327.76 | 4834305 | 0 | 253061.76 | 0 | 9190807.5 | 8000640 |  | 0 | 9910280 | 7745523.39 | 3767212.8 | 830642.5 | 0 | 5973278.08 | 0 | 5537000 | 986528.36 | 1278456.48 | 0 | 0 | 0 | 0 | 0 | 3143620.8 | 0 | 1092754.08 | 0 | 360000 | 0 | 0 | 0 | 0 | 1144957.8 | 214957.8 | 32400 | 4725000 | 0 | 4088497.35 | 3737813.04 | 0 | 0 | 0 |  | 0 | 11815044.48 | 10865721.18 | 15670519.2 | 0 | 5831280 | 395630.4 | 2622974.4 | 0 | 0 | 0 | 8151729 | 2957170 | 5282640 | 2718850.44 | 0 | 666989.28 | 0 | 0 | 1106314.88 | 0 | 15394339.84 | 3102430.8 | 648341.54 | 183060 | 1191575 | 284557.5 | 21353894.4 | 3379872 | 0 | 523333.44 | 95640 | 1394660 | 907315.2 | 1202688 | 1301527.44 | 1610083.95 | 0 | 2478103.62 | 2598105.6 | 0 | 1316928.9 | 212850 | 0 | 350341.2 | 6631180 | 97038 | 200640 | 0 | 1575455.7 | 0 | 0 | 8185056 | 0 | 1980439.2 | 1560790.35 | 16941312 | 22384915.2 | 6437144.3 | 0 | 11119104 | 1614155.34 | 6750027.35 | 0 | 34493822.3 | 4867721.1 | 5743282.7 | 18687518.4 | 9138494.4 | 15357350.4 | 1435936 | 11114208 | 2386706.5 | 511660.8 | 8852137.84 | 0 | 5801774.4 | 681114.15 | 10692172.8 | 1062028.8 | 0 | 0 | 0 | 0 | 0 |  | 65245089 | 0 | 9782922.24 | 0 | 2518387.2 | 0 | 0 | 0 | 0 | 0 | 2327940 | 1715840 | 908017 | 640396.8 | 0 | 0 | 3157000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2863193.27 | 0 | 0 | 92534.166 | 0 | 0 | 23337893 | 0 | 0 | 3753401.56 | 0 | 0 | 0 | 0 | 0 | 4749872.88 | 0 | 8135099.28 | 350945.28 | 0 | 5722691.52 | 7397244 | 10175557.5 | 0 | 449204.6 | 6599886.72 | 68858925 | 4968828 | 0 | 1154400 | 5202.6 | 3496478.4 | 10204629.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 425488762.22 | 248611579.136 | 674100341.356 | 95186429.906 | 65245089 | 60063515.34 | 0 | 290193801.54 | 92196818 | 247357.8 | 0 | 40938298.77 | 21353894.4 | 8675136.6 | 0 | 0
Yesterday Day Peak | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 400 | 327 |  | 0 | 420 | 305 | 35 | 0 | 0 | 300 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 15 | 19 | 0 | 0 | 35 | 0 | 108 | 0 | 8 | 149 | 0 | 0 | 0 |  | 0 | 40 | 0 | 46 | 0 | 6 | 13 | 26 | 0 | 0 | 0 | 280 | 0 | 184 | 102 | 0 | 10 | 0 | 0 | 18 | 0 | 44 | 0 | 20 | 10 | 24 | 15 | 122 | 106 | 0 | 20 | 1 | 43 | 30 | 25 | 25 | 112 | 0 | 61 | 60 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 18 | 50 | 63 | 0 | 0 | 24 | 0 | 17 | 3 | 88 | 17 | 17 | 17 | 28 | 50 | 100 | 53 | 19 | 0 | 34 | 0 | 17 | 6 | 17 | 0 | 322 | 54 | 0 | 0 | 0 |  | 904 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 270 | 178 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 14 | 150 | 459 | 64 | 0 |  | 8701 | DayPeak
Yesterday Evening Peak | 0 | 0 | 180 | 180 | 0 | 6 | 0 | 397 | 343 | 0 | 0 | 450 | 313 | 9 | 17 | 0 | 45 | 0 | 200 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 0 | 20 | 14 | 15 | 19 | 0 | 0 | 35 | 30 | 108 | 0 | 25 | 149 | 0 | 0 | 0 | 0 | 0 | 63 | 50 | 69 | 0 | 46 | 13 | 34 | 0 | 0 | 0 | 320 | 0 | 193 | 185 | 0 | 47 | 0 | 0 | 43 | 0 | 47 | 43 | 20 | 10 | 33 | 12 | 146 | 205 | 0 | 19 | 0 | 43 | 30 | 44 | 49 | 0 | 0 | 61 | 85 | 0 | 0 | 18 | 0 | 9 | 315 | 24 | 11 | 0 | 15 | 0 | 0 | 32 | 0 | 17 | 0 | 100 | 104 | 70 | 0 | 85 | 17 | 34 | 0 | 296 | 17 | 34 | 34 | 58 | 90 | 128 | 51 | 0 | 0 | 51 | 0 | 17 | 0 | 54 | 6 | 329 | 18 | 0 | 0 | 0 |  | 908 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 65 | 29 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 214 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 422 | 0 | 0 | 74 | 105 | 106 | 0 | 0 | 113 | 360 | 140 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 160 | 557 | 0 | 0 |  | 11031 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 400 | 330 | 0 | 0 | 450 | 310 | 9 | 100 | 30 | 330 | 0 | 200 | 40 | 42 | 149 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 15 | 20 | 25 | 33 | 33 | 50 | 0 | 60 | 0 | 110 | 0 | 25 | 150 |  | 0 | 0 | 0 | 12 | 70 | 50 | 69 | 0 | 50 | 13 | 35 | 0 | 0 | 0 | 300 | 0 | 200 | 190 | 0 | 46 | 0 | 0 | 43 | 0 | 45 | 43 | 20 | 11 | 32 | 12 | 161 | 200 | 0 | 20 | 0 | 43 | 30 | 50 | 50 | 0 | 0 | 60 | 86 | 0 | 0 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 300 | 300 | 0 | 85 | 0 | 149 | 0 | 100 | 100 | 150 | 250 | 85 | 105 | 51 | 0 | 300 | 17 | 34 | 114 | 55 | 100 | 400 | 72 | 0 | 162 | 51 | 0 | 17 |  | 54 | 35 | 340 | 163 |  | 0 | 10 |  | 934 | 0 | 380 |  | 97 | 200 | 0 | 0 | 28 | 78 | 24 | 65 | 38 | 48 | 0 | 0 | 70 | 30 | 35 | 80 | 0 | 0 | 30 | 8 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 200 |  | 0 | 0 | 0 | 0 | 200 | 0 | 414 | 54 | 200 | 113 | 50 | 113 | 0 | 0 | 113 | 360 | 220 |  | 150 |  |  | 115 | 0 |  | 0 |  | 150 | 550 |  | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 400 | 330 | 0 | 0 | 450 | 310 | 9 | 34 | 15 | 100 | 0 | 150 | 8 | 8 | 64 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 14 | 20 | 25 | 33 | 33 | 8 | 0 | 35 | 0 | 110 | 0 | 8 | 150 |  | 0 | 0 | 0 | 12 | 32 | 50 | 46 | 0 | 6 | 13 | 25 | 0 | 0 | 0 | 300 | 0 | 200 | 190 | 0 | 46 | 0 | 0 | 43 | 0 | 30 | 43 | 20 | 11 | 32 | 12 | 146 | 200 | 0 | 20 | 1.6 | 43 | 30 | 50 | 50 | 0 | 0 | 60 | 86 | 0 | 0 | 17 | 0 | 10 | 300 | 15 | 11 | 0 | 300 | 300 | 0 | 68 | 0 | 149 | 20 | 100 | 50 | 150 | 0 | 24 | 17 | 17 | 5 | 88 | 17 | 17 | 52 | 9 | 100 | 400 | 70 | 50 | 162 | 34 | 0 | 17 | 30 | 18 | 17 | 340 | 163 |  | 0 | 18 |  | 934 | 0 | 350 | 0 | 49 | 200 | 0 | 0 | 20 | 36 | 16 | 65 | 25 | 16 | 0 | 0 | 70 | 30 | 30 | 40 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 414 | 54 | 0 | 70 | 15 | 113 | 0 | 8 | 113 | 360 | 220 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 150 | 550 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 120 | 180 | 0 | 6 | 0 | 365 | 312 | 0 | 0 | 380 | 310 | 9 | 0 | 0 | 108 | 0 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20 | 15 | 15 | 20 | 0 | 0 | 30 | 0 | 107 | 0 | 8 | 147 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 24 | 0 | 6 | 13 | 31 | 0 | 0 | 0 | 340 | 0 | 205 | 200 | 0 | 10 | 0 | 0 | 10 | 0 | 43 | 25 | 20 | 10 | 32 | 20 | 124 | 200 | 0 | 19 | 0 | 43 | 30 | 11 | 10 | 0 | 0 | 40 | 10 | 0 | 0 | 17 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 4 | 70 | 17 | 0 | 0 | 24 | 0 | 17 | 2 | 88 | 17 | 17 | 34 | 0 | 25 | 387 | 17 | 1 | 0 | 17 | 0 | 17 | 2 | 18 | 0 | 348 | 0 | 0 | 124 | 0 | 0 | 915 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 260 | 222 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 2 | 150 | 562 | 22 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 8071 | 8:00
| Highest Generation |  | 11198 | 22:00
| Day Peak Generation |  | 8701 | 12:00
| Evening Peak Generation |  | 11031 | 21:00
| HVDC Max Flow |  | 909 | 20:00
| HVDC EvPeak Flow |  | 908 | 21:00
| Load factor L.F |  | 87.65% | [163 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-07-02
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 8701 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8750
Evening Peak Generation : |  |  | 11031 | MW Hour : | 21:00 | Available Max Generation : |  | 14653
E.P. Demand (at gen end) : |  |  | 11031 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11800
Maximum Generation : |  |  | 11198 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2853
Total Gen. (MKWH) : |  |  | 235.5631 | System Load Factor : | 87.65% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 580 | MW at | 13:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-07-02
Actual : |  | 73.21 | Ft.(MSL) , | Rule curve : | 84.61 | Ft.( MSL )
Gas Consumed : |  | Total = | 1107.47 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 155249945.246
: |  |  | Coal : | 92196818 | Oil : | 331132100.31 | Total : | 578578863.556
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 5083.8668 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1400.0384 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1962.1165 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1706.2972 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1403.5387 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1044.3414 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 584.8911 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 487.8885 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 954.2139 |  |  | 0 | 0%
Total |  | 0 |  | 14627.1926 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,5,7
3) Shajibazar 330 MW
4) Baghabari-100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
8:19 | - | Sylhet CCPP 225 MW was shutdown due to emergency maintenance of gas field.
8:23 | 9:41 | Jhenaidah 132/33kV S/S Transformer T-2 LT Forced S/D Due to T2A incomer Y-Phase DS Red hot maintenance. | [5 empty] | 35.0MW load interrup.
8:23 | 9:40 | Jhenaidah 132/33kV S/S Transformer T-2 HT Forced S/D Due to T2A incomer Y-Phase DS Red hot maintenance.
9:16 | - | SS Power unit-2 tripped due to feed pump trip.
9:38 | 10:50 | Chhatak 132/33kV S/S T-3 HT Scheduled S/D Due to 33kv T3 incoming DS upper clamp red. | [5 empty] | 7.0MW load interrup.
9:38 | 10:51 | Chhatak 132/33kV S/S T-3 LT Scheduled S/D Due to 33kv T3 incoming shutdown for red hot. | [5 empty] | 7.0MW load interrup.
10:01 | - | Sikalbaha 132/33 kV T3 was S/D due to red hot maintenance work by PDB.
10:14 | - | Sirajgonj Gas 210MW Unit-1 tripped due to GT hydraulic oil leakage.
10:17 | 10:45 | Bogura 132/33kV S/S Transformer-4 LT Tripped showing o/c,E/F relays Due to 33kv dupchacia pbs feeder. | [5 empty] | 19.0MW load interrup.
10:59 | - | Ashuganj South 360MW CCPP tripped due to flame monitoring sys. trip.
11:00 | - | Rampal 400/230kV S/S Generator Transformer-1 (GT-1) HT Project Work S/D Due to Maintenance work.
11:12 | 11:54 | Kachua 132/33kV S/S TR-1 LT Forced S/D Due to 33kv breaker high temperature.
11:13 | 11:53 | Kachua 132/33kV S/S TR-1 HT Forced S/D.
- | 11:15 | Bibiyana South 400 MW CCPP ST was sync.
11:57 | 17:44 | Rajshahi 132/33kV S/S 132 kV PPP 50 Mw Forced S/D.
12:00 | - | Day peak Generation : 9026 MW
12:01 | 12:55 | Saidpur 132/33kV S/S TR-4 (414T) HT Forced S/D Due to Due to Redhot T-4 Tr. LT Breaker pole connector (R-ph).
- | 12:26 | Sikalbaha 132/33 kV T3 was switched on.
- | 12:27 | SS Power Unit 2 was sync.
13:45 | 18:39 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to DS maintainance of PDB
13:45 | 18:39 | Kalurghat 132/33kV S/S TRFO-02(516T) LT Forced S/D Due to DS maintainance of PDB
14:00 | - | Bibiyana South 400 MW tripped. | [5 empty] | 124MW generation interrup.
14:01 | 14:17 | Bhulta-Narsingdi 132 kV Ckt-1 Tripped from Bhulta 132/33kV end showing Distance realy relays.
14:02 | 14:31 | Haripur-Narsingdi 132kV Ckt-1 Tripped from Haripur 230/132kV end showing Distance Zone 1, BN relays Due to None.
- | 14:14 | Thakurgao 132/33KV T3 Syn.
- | 14:38 | Sirajgonj Gas 210MW Unit-1 GT was sync.
14:57 | - | Kushiara 163MW tripped. | [5 empty] | 80MW generation interrup.
- | 16:15 | Sirajgonj Gas 210MW Unit-1 ST was sync.
16:57 | - | SS Power Unit 2 was shutdown due to main steam stop valve leakage. | [5 empty] | 270MW generation interrup.
17:02 | - | Siddirganj CCPP 335MW ST tripped. | [5 empty] | 100MW generation interrup.
- | 18:02 | Chowmuhani 132/33kV S/S TR2-425T HT is restored.
- | 18:03 | Bibiyana South 400 MW GT was sync.
- | 19:15 | Siddirganj CCPP 335MW ST was sync.
- | 20:27 | Bibiyana South 400 MW CCPP ST was sync.
20:45 | - | Siddirganj CCPP 335 MW ST tripped.
21:00 | - | Evening peak generation; 11031 MW.
- | 21:07 | Sylhet CCPP 225 MW GT was sync.
21:19 | 22:20 | Jhenaidah 132/33kV S/S Transformer T-1 LT Forced S/D Due to Red Hot maintanance. | [5 empty] | 25.0MW load interrup.
21:20 | 22:20 | Jhenaidah 132/33kV S/S Transformer T-1 HT Forced S/D Due to Red hot maintanance. | [5 empty] | 25.0MW load interrup.
22:28 | 22:47 | Ramganj 132/33kV S/S Transformer -02 HT Tripped showing Trip Relay K32 B phase relays. | [5 empty] | 60.0MW load interrup.
5:40 | - | Kabirpur - Manikganj 132kV Ckt-2 Scheduled S/D from Manikganj 132/33kV end Due to GT-2 Transformer oil centrifuzing.
5:40 | - | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) LT Scheduled S/D.
5:41 | - | Manikganj 132/33kV S/S 132/33 kV Transformer GT-2(35/50 MVA) HT Scheduled S/D.
7:00 | - | Min. Gen. 8750 MW.
7:39 | - | SS Power unit-2 was sync.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 180 | 3235156 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 3244500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 6 | 190272 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 397 | 8753150 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 343 | 7408000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 9092000
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 336960 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 313 | 6977949 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 17 | 62690 | Low Demand
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 20 | 0 | 0
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 0 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 200 | 3164000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 67478 | Low Demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 45 | 5333284 | Load increasing.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 90864 | Low Demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 247140
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 81488 | Low Demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 669180 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 15 | 352700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 19 | 460100 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 0 | 0 | Reserve
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 469245
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 115418 | Low Demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 17 | 142992 | Low Demand
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 17 | 111629 | Low Demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 51 | 858240 | Low Demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 40320 | Reserve
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 56997
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 6 | 80640 | Line problem
| Dhaka area Total |  |  |  | 5867 | 2401 | 51642392
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 108 | 2500000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 250061
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 133515
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 504000
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 65 | 916140 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 149 | 3594051
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 34 | 533599 | Low Demand
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 63 | 708336
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 638409 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 69 | 1159920
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1641600
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 13 | 311520 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 34 | 787680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27723
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 296 | 2938145
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 446990 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 34 | 540290 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 90 | 1303680 | Reserve
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 777868 | Low Demand
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 18 | 623927 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 0 | 18398180 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2545 | 1262 | 38735634
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 193 | 4554000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7343900 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 2713000 | tripped at 10:59
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 329 | 6950700 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 47 | 590256
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 185 | 2107636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 662464 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 485090 | Low Demand
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 891392
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 104 | 1638720 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 473242
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 244080
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 146 | 2974080
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 680900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 230664
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 12 | 379410 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 1377120 | Low Demand
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 58 | 708960 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 714240 | Low Demand
| Cumilla Area Total |  |  |  | 3096 | 1765 | 36164094
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 3100800
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 384804 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 6000
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 32 | 607200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 85 | 914400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 165170
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 0 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 341 | 5178374
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1018000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 687360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 1400073 | tripped at 14:57
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 44 | 691200
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 752328
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000 | Machine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1277373
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 85 | 1139520
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 1303890 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 99000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 129384 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 6631180
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 0 | 0 | Under maint.
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 176940
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 128 | 1560800 | sync at 18:03
| Sylhet Area Total |  |  |  | 2427 | 817 | 17131048
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 908 | 21748363
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 49 | 241920 | Low Demand
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 8734752
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 162000 | Low Demand
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 26112 | Reserve
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 511920 | Low Demand
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 298080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 2901 | 1512 | 31723147
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 58752 | Low Demand
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 29 | 468050 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1532000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 360 | 7642500
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 140 | 4871400 | Frequency control
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 156000 | Low Demand
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 160 | 3578200
| Barisal Area Total |  |  |  | 2265 | 824 | 18306902
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 65 | 1540000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 28 | 0 | 0 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 3235691
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 220 | 4094718
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 422 | 8217272
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 169721 | Low Demand
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 122238 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 0 | Low Demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 0 | Reserve
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Reserve
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 74 | 483744 | Low Demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 543648
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 460
| Adani Power Jharkhanda Ltd |  | Import | 748*1 | 748 | 557 | 11777000
| Rajshahi Area Total |  |  |  | 2905 | 1708 | 30184492
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 180 | 4411700
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 106 | 801225 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40652
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 665664
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 102524
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 475300
| Rangpur Area Total |  |  |  | 750 | 401 | 6497065
| Total |  |  |  | 23370 | 11031 | 235563148
| Eastern Grid Total |  |  |  | 14549 | 6586 | 148851542
| Western Grid Total |  |  |  | 8821 | 4445 | 86711606
| National Grid Total |  |  |  | 23370 | 11031 | 235563148
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-01
| (a) ENTIRE EASTERN GRID : |  | 6464.07 | MW | (b) ENTIRE WESTERN GRID : |  | 4065.6 | MW
| i) Dhaka area |  | 2614.57 | MW | i) Khulna area |  | 1496 | MW
| ii) Chittagong area |  | 1219.5 | MW | ii) Rajshahi area |  | 1224.6 | MW
| iii) Comilla area |  | 1234 | MW | iii) Barisal area |  | 473 | MW
| iv) Mymensingh area |  | 929 | MW | iv) Rangpur area |  | 872 | MW
| v) Sylhet area |  | 467 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 10529.67 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 26 | 00:00 | Kamrangirchar | 23.4 | 13:00 | Natore | 128 | 21:00 | Shitalakhya | 56.4 | 14:00
2 | AKSML | 5 | 00:00 | Chowmuhani | 233 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 50 | 22:00 | Sholosohor | 24 | 19:00
3 | Aftabnagar | 24 | 00:00 | Chuadanga | 88 | 21:00 | Kazla | 38 | 14:00 | Netrakona | 119 | 21:00 | Shyampur | 36 | 14:00
4 | Agargaon | 53 | 14:00 | Coxsbazar | 123 | 19:30 | Keranigonj | 52 | 00:00 | New | 36 | 13:00 | Siddhirganj | 58 | 22:00
5 | Agrabad | 52 | 21:00 | Cumilla(N) | 141 | 09:00 | Khagrachori | 30 | 19:30 | Niamatpur | 81 | 21:00 | Sirajganj | 88 | 19:30
6 | Amnura | 52 | 21:00 | Cumilla(S) | 150 | 23:00 | Khulna | 80 | 22:00 | Noapara | 39 | 21:00 | Sonargaon | 65 | 13:00
7 | Ashuganj | 47 | 00:00 | Daudkandi | 128 | 22:00 | Khulshi | 154 | 18:30 | PHP | 8 | 15:00 | Sreemongol | 51 | 21:00
8 | BIPTC | N/A | N/A | Dhaka | 10 | 12:00 | Kishoreganj | 148 | 22:00 | Pabna | 96 | 22:00 | Sreepur | 31 | 22:00
9 | BSRM | 169 | 12:00 | Dhamrai | 62 | 21:00 | Kodda | 108 | 21:00 | Palashbari | 122 | 22:00 | Srinagar | 42.2 | 14:00
10 | Bagerhat | 86 | 22:00 | Dhanmondi | 58 | 13:00 | Kulaura | 44 | 19:30 | Panchagarh | 51 | 22:00 | Sunamganj | 46 | 22:00
11 | Bakulia | 93 | 20:00 | Dohazari | 96 | 00:00 | Kurigram | 65 | 20:00 | Patuakhali | 114 | 23:00 | Sylhet | 112 | 22:00
12 | Banani | 23.8 | 14:00 | Faridpur | 133 | 22:00 | Kushtia | 96 | 21:00 | Payra | 22.4 | 22:00 | TK | 32.6 | 22:00
13 | Bangabhaban | 4 | 10:00 | Fatullah | 27 | 00:00 | Lalbag | 29 | 13:00 | Postogola | 36 | 13:00 | Tangail | 171 | 20:00
14 | Barapukuria | 57 | 21:00 | Fenchuganj | 42 | 21:00 | Lalmonirhat | 47 | 20:00 | Purbachal | 14 | 13:00 | Thakurgaon | 101 | 23:00
15 | Barguna | 24 | 22:00 | Feni | 116 | 22:00 | Madanganj | 28 | 14:00 | Purbasadipur | 106 | 22:00 | Tongi | 62 | 00:00
16 | Barishal | 105 | 23:00 | GPH | 7 | 13:00 | Madaripur | 102 | 22:00 | Rahanpur_I | 0 | 00:00 | Ullon | 32 | 19:00
17 | Barishal-230 | 92 | 22:00 | Ghorashal | N/A | N/A | Madartek | 60.57 | 14:00 | Rahim | 0 | 00:00 | Uttara | 39 | 13:00
18 | Baroaulia | 52 | 20:00 | Goalpara | 32 | 22:00 | Madunaghat | 52 | 21:00 | Rajbari | 58 | 21:00 | UttaraNew | 34 | 21:00
19 | Baroirhat | 58 | 21:00 | Gollamari | 37 | 22:00 | Magura | 56 | 21:00 | Rajendrapur | 56 | 00:00 | Zigatola | 53 | 13:00
20 | Bashundhara | 94 | 13:00 | Gopalganj | 100 | 22:00 | Mahasthangarh | 70 | 23:00 | Rajshahi | 124 | 23:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 60 | 12:00 | Manikganj | 68 | 22:00 | Rajshahi-230 | 31 | 22:00
22 | Beanibazar | 60 | 00:00 | Halishahar | 55.5 | 21:00 | Maniknagar | 52 | 14:00 | Ramganj | 126 | 21:00
23 | Benapole | 56 | 22:00 | HaripurSBU | 39 | 21:00 | Matarbari | 47 | 20:00 | Rampur | 26 | 00:00
24 | Bhaluka | 74 | 00:00 | Hasnabad | 45 | 13:00 | Matuail | 30 | 18:30 | Rangamati | 18 | 19:00
25 | Bhandaria | 54 | 21:00 | Hathazari | 76 | 21:00 | Millgate | 43 | 23:00 | Rangpur | 124 | 20:00
26 | Bhangura | 34 | 20:00 | Ishurdi | 40 | 20:00 | Mirpur | 84 | 14:00 | Ruppur | 3 | 10:00
27 | Bheramara(GK) | 53 | 21:00 | Jaldhaka | 83 | 21:00 | Mirsorai | 5.5 | 00:00 | SSM | 0 | 00:00
28 | Bhulta | 91 | 22:00 | Jamalpur | 150 | 23:00 | Mithapukur | 38 | 21:00 | Saidpur | 94 | 21:00
29 | Bog-Sherpur | 50 | 21:00 | Jashore | 124 | 21:00 | Modern | 0 | 00:00 | Satkhira | 136 | 22:00
30 | Bogura | 135 | 23:00 | Jhenaidah | 114 | 23:00 | Mogbazar | 68.7 | 14:00 | Satmasjid | 60 | 14:00
31 | Borhanuddin | 76 | 21:00 | Joydebpur | 86 | 22:00 | Mongla | 34 | 19:30 | Savar | 90 | 18:30
32 | Brahmanbaria | 160 | 01:00 | Joypurhat | 57 | 22:00 | Motijheel | 22 | 12:00 | Shahjadpur | 82 | 19:30
33 | Cantonment | 86 | 13:00 | Juldah | 13 | 00:00 | Munshiganj | 85 | 23:00 | Shahjibazar | 95 | 21:00
34 | Chandpur | 68 | 19:30 | KSRM | 10 | 16:00 | Mymensingh | 189 | 21:00 | Shahmirpur | 38 | 23:00
35 | Chandraghona | 33 | 19:30 | Kabirpur | 119 | 19:00 | Naogaon | 116 | 22:00 | Shariatpur | 78 | 22:00
36 | Chapai | 59 | 21:00 | Kachua | 77 | 22:00 | Narail | 56 | 20:00 | Sherpur | 120 | 19:30
37 | Charsaidpur | 18.2 | 13:00 | Kallyanpur | 99 | 16:00 | Narinda | 36 | 13:00 | Shikalbaha | N/A | N/A
38 | Chauddagram | 59 | 21:00 | Kalurghat | 24 | 23:00 | Narshingdi | 122 | 22:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 410 | 16:00 | 399 | 00:00 | Kaliakoir | 400 | 06:00 | 394 | 01:00
| Ashuganj | N/A | N/A | N/A | N/A | Madunaghat_I | 407 | 19:30 | 386 | 10:00
| Bhulta | 407 | 16:00 | 398 | 12:00 | Payra | 417 | 16:00 | 409 | 00:00
| Bibiana | 412 | 16:00 | 400 | 06:00 | Rahanpur_I | 421 | 18:30 | 413 | 00:00
| BIPTC | 398 | 06:00 | 392 | 11:00 | Rampal | 409 | 16:00 | 391 | 00:00
| Gopalganj | 412 | 16:00 | 401 | 00:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 242 | 16:00 | 236 | 00:00 | Hasnabad | 241 | 16:00 | 235 | 11:00
| AKSML | 237 | 18:00 | 219 | 08:00 | Hathazari | 239 | 18:30 | 222 | 09:00
| Aminbazar | 243 | 16:00 | 238 | 0:00 | Ishurdi | 233 | 09:00 | 226 | 00:00
| Ashuganj | 239 | 16:00 | 235 | 01:00 | Jhenaidah | 227 | 16:00 | 217 | 01:00
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | 236 | 05:00 | 233 | 00:00
| Baghabari | 231 | 08:00 | 225 | 21:00 | Keranigonj | 240 | 16:00 | 234 | 13:00
| Barapukuria | 218 | 18:30 | 208 | 01:00 | Khulna(S) | 234 | 16:00 | 224 | 01:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 233 | 19:30 | 222 | 06:00
| Barishal | 242 | 18:30 | 234 | 00:00 | Maniknagar | 241 | 16:00 | 235 | 13:00
| Bheramara | 232 | 18:30 | 223 | 01:00 | Meghnaghat | 245 | 17:00 | 240 | 00:00
| Bhulta | 242 | 16:00 | 236 | 01:00 | Mirsorai | 238 | 18:00 | 223 | 10:00
| Bibiana | 242 | 18:30 | 236 | 00:00 | Rajshahi | 232 | 18:30 | 222 | 00:00
| BIPTC | 233 | 18:30 | 223 | 01:00 | Rampal | 233 | 16:00 | 223 | 00:00
| Bogura | 222 | 18:30 | 215 | 01:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 244 | 18:00 | 234 | 00:00 | Rampura | 240 | 16:00 | 235 | 13:00
| BSRM | 239 | 18:30 | 223 | 11:00 | Shikalbaha | 235 | 19:00 | 220 | 11:00
| Cumilla(N) | 237 | 16:00 | 230 | 01:00 | Shyampur | 240 | 16:00 | 234 | 13:00
| Fenchuganj | 244 | 12:00 | 239 | 17:00 | Siddhirganj | 242 | 16:00 | 238 | 11:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 239 | 18:30 | 231 | 00:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 235 | 09:00 | 231 | 01:00
| GPH | 239 | 18:30 | 221 | 11:00 | Tongi | 237 | 16:00 | 232 | 14:00
| Haripur | 240 | 16:00 | 234 | 23:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 136 | 18:30 | 132 | 13:00 | Lalbag | 137 | 18:30 | 133 | 00:00
| Agargaon | 140 | 16:00 | 137 | 00:00 | Lalmonirhat | 128 | 18:30 | 120 | 01:00
| Agrabad | 138 | 18:00 | 126 | 08:00 | Madanganj | 139 | 16:00 | 134 | 11:00
| AKS | 134 | 18:00 | 126 | 08:00 | Madaripur | 138 | 07:00 | 126 | 00:00
| Aminbazar | 140 | 14:00 | 137 | 00:00 | Madartek | 136 | 16:00 | 132 | 11:00
| Amnura | 132 | 09:00 | 125 | 19:00 | Madunaghat | 139 | 18:30 | 125 | 08:00
| Ashuganj | 141 | 16:00 | 140 | 00:00 | Magura | 134 | 18:30 | 125 | 01:00
| Bagerhat | 130 | 16:00 | 120 | 00:00 | Mahasthangarh | 133 | 18:30 | 123 | 01:00
| Bakulia | 135 | 18:00 | 126 | 09:00 | Manikganj | 136 | 09:00 | 129 | 01:00
| Banani | 137 | 19:00 | 132 | 13:00 | Maniknagar | 138 | 16:00 | 134 | 13:00
| Bangabhaban | 137 | 16:00 | 133 | 13:00 | Matarbari | 125 | 18:30 | 109 | 06:00
| Barapukuria | 135 | 18:00 | 128 | 00:00 | Matuail | 140 | 16:00 | 136.6 | 02:00
| Barguna | 136 | 18:30 | 127 | 01:00 | Millgate | 139 | 16:00 | 134 | 13:00
| Barishal | 134 | 09:00 | 125 | 19:30 | Mirpur | 140 | 16:00 | 135 | 11:00
| Barishal-230 | 133 | 18:00 | 128 | 00:00 | Mithapukur | 131 | 18:00 | 123 | 00:00
| Baroaulia | 138 | 18:00 | 126 | 10:00 | Modern | 139 | 18:30 | 127 | 08:00
| Baroirhat | 134 | 18:00 | 121 | 01:00 | Mogbazar | 136 | 16:00 | 133 | 13:00
| Bashundhara | 138 | 05:00 | 133 | 13:00 | Mongla | 129 | 16:00 | 120 | 00:00
| BashundharaCement | 137 | 18:00 | 134 | 11:00 | Motijheel | 137 | 16:00 | 133 | 12:00
| Beanibazar | 132 | 10:00 | 126 | 19:00 | Munshiganj | 139 | 16:00 | 131 | 17:00
| Benapole | 129 | 07:00 | 122 | 00:00 | Mymensingh | 135 | 18:30 | 122 | 01:00
| Bhaluka | 133 | 10:00 | 126 | 21:00 | Naogaon | 131 | 18:30 | 119 | 00:00
| Bhandaria | 130 | 11:00 | 117 | 01:00 | Narail | 132 | 18:30 | 124 | 00:00
| Bhangura | 138 | 05:00 | 133 | 01:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 18:30 | 131 | 00:00 | Narshingdi | 138 | 16:00 | 126 | 18:00
| Bheramara(GK) | 136 | 16:00 | 131 | 00:00 | Natore | 133 | 18:30 | 125 | 00:00
| Bhulta | 135 | 15:00 | 128 | 00:00 | Nawabganj | 138 | 16:00 | 131 | 03:00
| Bog-Sherpur | 134 | 18:30 | 126 | 01:00 | Netrakona | 135 | 09:00 | 120 | 23:00
| Bogura | 134 | 18:30 | 126 | 01:00 | New | 140 | 16:00 | 135 | 12:00
| Bogura-230 | 134 | 18:30 | 127 | 14:00 | Niamatpur | 129 | 06:00 | 116 | 00:00
| Brahmanbaria | 138 | 17:00 | 133 | 00:00 | Noapara | 132 | 16:00 | 123 | 00:00
| Cantonment | 140 | 16:00 | 135 | 13:00 | Pabna | 135 | 08:00 | 129 | 01:00
| Chandpur | 134 | 18:00 | 115 | 00:00 | Palashbari | 129 | 04:00 | 119 | 00:00
| Chandraghona | 139 | 18:30 | 127 | 08:00 | Panchagarh | 135 | 18:30 | 123 | 00:00
| Chapai | 133 | 18:00 | 127 | 23:00 | Patuakhali | 138 | 12:00 | 131 | 23:00
| Charsaidpur | 140 | 16:00 | 135 | 13:00 | Payra | 140 | 18:30 | 136 | 00:00
| Chauddagram | 134 | 18:00 | 121 | 13:00 | PHP | 133 | 18:30 | 120 | 13:00
| Chhatak | 132 | 06:00 | 125 | 19:00 | Postogola | 141 | 16:00 | 137 | 01:00
| Chowmuhani | 130 | 18:30 | 115 | 00:00 | Purbachal | 139 | 16:00 | 133 | 11:00
| Chuadanga | 130 | 13:00 | 120 | 00:00 | Purbasadipur | 131 | 18:30 | 120 | 00:00
| Coxsbazar | 125 | 18:30 | 109 | 01:00 | Rahim | 140 | 16:00 | 128 | 15:00
| Cumilla(N) | 138 | 18:00 | 129 | 01:00 | Rajbari | 131 | 16:00 | 125 | 00:00
| Cumilla(S) | 138 | 18:30 | 125 | 00:00 | Rajendrapur | 136 | 10:00 | 130 | 02:00
| Daudkandi | 139 | 16:00 | 128 | 00:00 | Rajshahi | 132 | 18:30 | 124 | 00:00
| Dhaka | 137 | 16:00 | 133 | 13:00 | Rajshahi-230 | 130 | 08:00 | 124 | 00:00
| Dhamrai | 138 | 16:00 | 133 | 01:00 | Ramganj | 130 | 18:30 | 111 | 01:00
| Dhanmondi | 140 | 16:00 | 136 | 05:00 | Rampur | 135 | 18:30 | 126 | 10:00
| Dohazari | 135 | 18:30 | 123 | 05:00 | Rampura | 136 | 16:00 | 132 | 13:00
| Faridpur | 131 | 15:00 | 126 | 00:00 | Rangamati | 138 | 18:30 | 126 | 08:00
| Fatullah | 137 | 16:00 | 134 | 00:00 | Rangpur | 127 | 18:00 | 121 | 14:00
| Fenchuganj | 137 | 12:00 | 133 | 19:00 | Ruppur | 136 | 16:00 | 131 | 00:00
| Feni | 135 | 18:30 | 121 | 13:00 | Saidpur | 132 | 09:00 | 121 | 00:00
| Ghorashal | N/A | N/A | N/A | N/A | Satkhira | 129 | 16:00 | 119 | 00:00
| Goalpara | 133 | 16:00 | 126 | 00:00 | Satmasjid | 140 | 16:00 | 135 | 13:00
| Gollamari | 134 | 18:30 | 125 | 01:00 | Savar | 139 | 16:00 | 135 | 00:00
| Gopalganj | 132 | 18:30 | 124 | 00:00 | Shahjadpur | 141 | 08:00 | 135 | 12:00
| Gopalganj-400 | 131 | 16:00 | 127 | 00:00 | Shahjibazar | 137 | 10:00 | 133 | 05:00
| Gulshan | 136 | 16:00 | 132 | 13:00 | Shahmirpur | 134 | 22:00 | 125 | 07:00
| Halishahar | 138 | 18:30 | 126 | 08:00 | Shariatpur | 130 | 16:00 | 125 | 00:00
| Haripur | 140 | 16:00 | 136 | 11:00 | Sherpur | 130 | 09:00 | 112 | 23:00
| HaripurSBU | 140 | 16:00 | 136 | 11:00 | Shikalbaha | N/A | N/A | N/A | N/A
| Hasnabad | 140 | 15:00 | 137 | 11:00 | Shikalbaha-230 | 138 | 12:00 | 127 | 09:00
| Hathazari | 141 | 18:30 | 129 | 07:00 | Shitalakhya | 139.3 | 16:00 | 135.2 | 13:00
| Ishurdi | 136 | 18:30 | 131 | 00:00 | Sholosohor | 136 | 18:00 | 126 | 08:00
| Jaldhaka | 130 | 18:30 | 120 | 00:00 | Shyampur | 137 | 16:00 | 132 | 10:00
| Jamalpur | 131 | 09:00 | 115 | 23:00 | Shyampur-230 | 137 | 16:00 | 133 | 13:00
| Jashore | 131 | 18:30 | 122 | 01:00 | Siddhirganj | 140 | 16:00 | 137 | 05:00
| Jhenaidah | 135 | 16:00 | 127 | 00:00 | Sirajganj | 135 | 08:00 | 128 | 00:00
| Jhenaidah-230 | 134 | 16:00 | 128 | 00:00 | Sonargaon | 137 | 21:00 | 134 | 02:00
| Joydebpur | 142 | 00:00 | 137 | 13:00 | Sreemongol | 136 | 12:00 | 133 | 19:00
| Joypurhat | 130 | 18:00 | 118 | 00:00 | Sreepur | 133 | 10:00 | 130 | 00:00
| Juldah | 139 | 18:30 | 125 | 09:00 | Srinagar | 138 | 16:00 | 132 | 00:00
| Kabirpur | 138 | 09:00 | 132 | 13:00 | SSM | 140 | 18:00 | 130 | 12:00
| Kachua | 136 | 18:00 | 116 | 01:00 | Sunamganj | 130 | 10:00 | 122 | 19:30
| Kaliakoir | 136 | 06:00 | 133 | 00:00 | Sylhet | 134 | 12:00 | 128 | 19:00
| Kallyanpur | 135 | 16:00 | 130 | 12:00 | Tangail | 136 | 09:00 | 123 | 01:00
| Kalurghat | 133 | 22:00 | 127 | 08:00 | Thakurgaon | 133 | 18:30 | 120 | 00:00
| Kamrangirchar | 138 | 16:00 | 129 | 00:00 | TK | 137 | 18:00 | 127 | 07:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 139 | 16:00 | 134 | 23:00
| Kazla | 135 | 00:00 | 135 | 00:00 | Ullon | 136 | 18:30 | 133 | 11:00
| Keranigonj | 138 | 16:00 | 132 | 13:00 | Uttara | 139 | 18:30 | 136 | 00:00
| Khagrachori | 138 | 18:30 | 126 | 08:00 | UttaraNew | 140 | 16:00 | 135 | 21:00
| Khulna | 138 | 22:00 | 124 | 00:00 | Zigatola | 138 | 16:00 | 133 | 00:00
| Khulna(S) | 134 | 18:30 | 126 | 00:00
| Khulshi | 138 | 18:30 | 126 | 08:00
| Kishoreganj | 133 | 10:00 | 128 | 01:00
| Kodda | 139 | 16:00 | 130 | 01:00
| KSRM | 139 | 18:00 | 126 | 10:00
| Kulaura | 136 | 12:00 | 132 | 19:00
| Kurigram | 126 | 18:00 | 118 | 00:00
| Kushtia | 135 | 16:00 | 129 | 00:00

## L-Curve
Date | 2023-07-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 700 | 6414 | 4204 | 10618 |  |  |  | QF-LDC-11
0:30 | 695 | 6131 | 3950 | 10081 | Date: | 2023-07-01
1:00 | 690 | 5848 | 3696 | 9544
1:30 | 685 | 5706 | 3630 | 9336
2:00 | 680 | 5564 | 3564 | 9128
2:30 | 665 | 5529 | 3497.5 | 9026.5 | [5 empty] | Gen. at Eve. Peak | 11031 | 11031 MW (21:00 )
3:00 | 650 | 5494 | 3431 | 8925 | [6 empty] | 21:00
3:30 | 662 | 5459 | 3341 | 8800 | [5 empty] | Gen. at Day Peak | 8701 | 8701 MW (12:00 )
4:00 | 674 | 5424 | 3251 | 8675 | [6 empty] | 12:00
4:30 | 717 | 5392.5 | 3251.5 | 8644 | [5 empty] | Highest Generation | 11198
5:00 | 760 | 5361 | 3252 | 8613 | [6 empty] | 22:00
5:30 | 720 | 5222 | 3212.5 | 8434.5
6:00 | 680 | 5083 | 3173 | 8256
6:30 | 682 | 5053.5 | 3163.5 | 8217
7:00 | 684 | 5024 | 3154 | 8178
7:30 | 722 | 4963.5 | 3161 | 8124.5
8:00 | 760 | 4903 | 3168 | 8071
8:30 | 755 | 4922.5 | 3156 | 8078.5
9:00 | 750 | 4942 | 3144 | 8086
9:30 | 735 | 4908 | 3144.5 | 8052.5
10:00 | 720 | 4874 | 3145 | 8019
10:30 | 745 | 4970.5 | 3129 | 8099.5
11:00 | 770 | 5067 | 3113 | 8180
11:30 | 715 | 5224 | 3216.5 | 8440.5
12:00 | 660 | 5381 | 3320 | 8701
12:30 | 620 | 5550.5 | 3313 | 8863.5
13:00 | 580 | 5720 | 3306 | 9026
13:30 | 595 | 5736.5 | 3298.5 | 9035
14:00 | 610 | 5753 | 3291 | 9044
14:30 | 630 | 5577 | 3268.5 | 8845.5
15:00 | 650 | 5401 | 3246 | 8647
15:30 | 630 | 5232.5 | 3161.5 | 8394
16:00 | 610 | 5064 | 3077 | 8141
16:30 | 665 | 4938.5 | 3109 | 8047.5
17:00 | 720 | 4813 | 3141 | 7954
17:30 | 805 | 4890 | 3235.5 | 8125.5
18:00 | 890 | 4967 | 3330 | 8297
18:30 | 840 | 5361.5 | 3441 | 8802.5
19:00 | 790 | 5756 | 3552 | 9308
19:30 | 640 | 6372 | 4088 | 10460
20:00 | 700 | 6304 | 4278 | 10582 |  |  |  | Executive Engineer
20:30 | 720 | 6445 | 4361.5 | 10806.5 |  |  |  | Network Operation Division
21:00 | 740 | 6586 | 4445 | 11031
21:30 | 755 | 6620.5 | 4494 | 11114.5
22:00 | 770 | 6655 | 4543 | 11198 |  |  |  |  | Page 6 of 7
22:30 | 765 | 6623 | 4505 | 11128
23:00 | 760 | 6591 | 4467 | 11058
23:30 | 730 | 6502.5 | 4335.5 | 10838
24:00 | 700 | 6414 | 4204 | 10618
11031 MW (21:00 )
8701 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-01 |  | Energy |  | 235563148
[15 empty] | 43646 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4157 | 907 | 2414 | 0 | 1359 | 1251 | 30 | 0 | 352 | 148 | 0 | 0 | 0
0:30 | 4021 | 906 | 2235 | 0 | 1157.5 | 1382.5 | 32.5 | 0 | 207.5 | 139 | 0 | 0 | 0 |  |  | Date: | 43646
1:00 | 3885 | 905 | 2056 | 0 | 956 | 1514 | 35 | 0 | 63 | 130 | 0 | 0 | 0
1:30 | 3776.5 | 905 | 2057.5 | 0 | 899 | 1472 | 35 | 0 | 63 | 128 | 0 | 0 | 0 | [9 empty] | 235.5631 | 235.5631 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 235.563 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.563 MKWHr
2:00 | 3668 | 905 | 2059 | 0 | 842 | 1430 | 35 | 0 | 63 | 126 | 0 | 0 | 0 | [9 empty] | 0 | 0
2:30 | 3633.5 | 905 | 2035 | 0 | 798 | 1431 | 35 | 0 | 63 | 126 | 0 | 0 | 0 | [9 empty] | 235.5631 | 235.5631
3:00 | 3599 | 905 | 2011 | 0 | 754 | 1432 | 35 | 0 | 63 | 126 | 0 | 0 | 0
3:30 | 3607.5 | 905 | 2009.5 | 0 | 697.5 | 1356.5 | 35 | 0 | 63 | 126 | 0 | 0 | 0 | [8 empty] | Shortage
4:00 | 3616 | 905 | 2008 | 0 | 641 | 1281 | 35 | 0 | 63 | 126 | 0 | 0 | 0
4:30 | 3613 | 905.5 | 1981 | 0 | 642 | 1280.5 | 35 | 0 | 63 | 124 | 0 | 0 | 0
5:00 | 3610 | 906 | 1954 | 0 | 643 | 1280 | 35 | 0 | 63 | 122 | 0 | 0 | 0
5:30 | 3524.5 | 905.5 | 1921 | 0 | 598.5 | 1282 | 35 | 0 | 46.5 | 119 | 2.5 | 0 | 0
6:00 | 3439 | 905 | 1888 | 0 | 554 | 1284 | 35 | 0 | 30 | 116 | 5 | 0 | 0
6:30 | 3433 | 905.5 | 1866 | 0 | 526.5 | 1282.5 | 35 | 0 | 30 | 113 | 25.5 | 0 | 0 | [7 empty] | Coal
7:00 | 3427 | 906 | 1844 | 0 | 499 | 1281 | 35 | 0 | 30 | 110 | 46 | 0 | 0
7:30 | 3380 | 903 | 1842.5 | 0 | 459 | 1279 | 35 | 0 | 30 | 109 | 87 | 0 | 0 | [6 empty] | Oil
8:00 | 3333 | 900 | 1841 | 0 | 419 | 1277 | 35 | 0 | 30 | 108 | 128 | 0 | 0
8:30 | 3287 | 900.5 | 1875.5 | 0 | 426.5 | 1307 | 35 | 0 | 29 | 112 | 106 | 0 | 0
9:00 | 3241 | 901 | 1910 | 0 | 434 | 1337 | 35 | 0 | 28 | 116 | 84 | 0 | 0
9:30 | 3298.5 | 901.5 | 1933.5 | 0 | 490 | 1160.5 | 35 | 0 | 28 | 116 | 89.5 | 0 | 0
10:00 | 3356 | 902 | 1957 | 0 | 546 | 984 | 35 | 0 | 28 | 116 | 95 | 0 | 0
10:30 | 3298 | 902.5 | 1987 | 0 | 573.5 | 985 | 35 | 0 | 52 | 118 | 148.5 | 0 | 0
11:00 | 3240 | 903 | 2017 | 0 | 601 | 986 | 35 | 0 | 76 | 120 | 202 | 0 | 0
11:30 | 3327 | 903.5 | 2152.5 | 0 | 598 | 1022.5 | 35 | 0 | 107 | 121 | 174 | 0 | 0
12:00 | 3414 | 904 | 2288 | 0 | 595 | 1059 | 35 | 0 | 138 | 122 | 146 | 0 | 0
12:30 | 3433.5 | 904 | 2312.5 | 0 | 608.5 | 1146.5 | 35 | 0 | 146.5 | 125 | 152 | 0 | 0
13:00 | 3453 | 904 | 2337 | 0 | 622 | 1234 | 35 | 0 | 155 | 128 | 158 | 0 | 0
13:30 | 3453 | 904 | 2337 | 0 | 622 | 1234 | 35 | 0 | 155 | 128 | 158 | 0 | 0
14:00 | 3453 | 904 | 2337 | 0 | 622 | 1234 | 35 | 0 | 155 | 128 | 158 | 0 | 0
14:30 | 3307.5 | 904.5 | 2264.5 | 0 | 632.5 | 1273 | 35 | 0 | 169 | 131 | 119.5 | 0 | 0
15:00 | 3162 | 905 | 2192 | 0 | 643 | 1312 | 35 | 0 | 183 | 134 | 81 | 0 | 0
15:30 | 3089 | 905.5 | 2038.5 | 0 | 645.5 | 1301 | 35 | 0 | 173.5 | 130 | 76 | 0 | 0
16:00 | 3016 | 906 | 1885 | 0 | 648 | 1290 | 35 | 0 | 164 | 126 | 71 | 0 | 0
16:30 | 3092 | 906 | 1876 | 0 | 646 | 1160 | 35 | 0 | 162.5 | 103 | 67 | 0 | 0
17:00 | 3168 | 906 | 1867 | 0 | 644 | 1030 | 35 | 0 | 161 | 80 | 63 | 0 | 0 | [11 empty] | 472
17:30 | 3132 | 906 | 1939 | 0 | 710.5 | 1085.5 | 35 | 0 | 175.5 | 96 | 46 | 0 | 0 | [11 empty] | 100
18:00 | 3096 | 906 | 2011 | 0 | 777 | 1141 | 35 | 0 | 190 | 112 | 29 | 0 | 0 | [11 empty] | 20
18:30 | 3192.5 | 906 | 2078.5 | 0 | 1092.5 | 1139.5 | 50 | 0 | 205 | 124 | 14.5 | 0 | 0 | [11 empty] | 592
19:00 | 3289 | 906 | 2146 | 0 | 1408 | 1138 | 65 | 0 | 220 | 136 | 0 | 0 | 0
19:30 | 3605 | 908 | 2397 | 0 | 1874 | 1252 | 65 | 0 | 221 | 138 | 0 | 0 | 0
20:00 | 3609 | 909 | 2397 | 0 | 1989 | 1246 | 65 | 0 | 229 | 138 | 0 | 0 | 0
20:30 | 3717 | 908.5 | 2432 | 0 | 2069.5 | 1251.5 | 65 | 0 | 221 | 142 | 0 | 0 | 0
21:00 | 3825 | 908 | 2467 | 0 | 2150 | 1257 | 65 | 0 | 213 | 146 | 0 | 0 | 0
21:30 | 3903.5 | 907.5 | 2447 | 0 | 2177.5 | 1258.5 | 62.5 | 0 | 212 | 146 | 0 | 0 | 0
22:00 | 3982 | 907 | 2427 | 0 | 2205 | 1260 | 60 | 0 | 211 | 146 | 0 | 0 | 0
22:30 | 4028 | 907.5 | 2411.5 | 0 | 2065.5 | 1260.5 | 45 | 0 | 262 | 148 | 0 | 0 | 0
23:00 | 4074 | 908 | 2396 | 0 | 1926 | 1261 | 30 | 0 | 313 | 150 | 0 | 0 | 0
23:30 | 4115.5 | 907.5 | 2405 | 0 | 1642.5 | 1256 | 30 | 0 | 332.5 | 149 | 0 | 0 | 0 |  |  | Max Temp. in Dhaka |  | 31.8° C
24:00 | 4157 | 907 | 2414 | 0 | 1359 | 1251 | 30 | 0 | 352 | 148 | 0 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 235.563 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.563 MKWHr
Note on W13: Author:

## Generation
g | 2023-07-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 796140
2 | Karnaphuli Hydro PP Unit-4 & 5 | [19 empty] | 30 | 30 | 30 | 30 | 30 | 0 |  | 120000
3 | Chattogram TPP-1 | 104 | 106 | 108 | 108 | 108 | 106 | 102 | 110 | 112 | 110 | 110 | 108 | 110 | 110 | 108 | 107 | 105 | 109 |  | 109 | 109 | 110 | 108 | 110 | 108 | 110 | 2500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 23 | 25 | 25 | 25 | 25 | 25 | 8 | 250061
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 |  | 10 | 15 | 15 | 17 | 18 | 17 |  | 7 | 5 | 4 | 1 | [8 empty] | 133515
6 | Sikalbaha 225MW CCPP (Gas) | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 149 | 149 | 145 | 147 | 149 | 146 | 149 | 148 | 151 | 146 | 151 |  | 147 | 149 | 148 | 149 | 151 | 151 | 151 | 3594051
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 33 | 33 | 33 | 33 | 33 | [7 empty] | 2 | 33 | 32 | 32 | 36 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 638409
12 | Hathazari 100 MW peaking PP | [10 empty] | 4 | 40 | 55 | 55 | 54 | 53 | 48 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 708336
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 533599
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 36 | 44 | 44 | 43 | 43 | 43 | 41 | 41 |  | 43 | 44 | 45 | 47 | 45 | 42 | 44 | 891392
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 206 | 123 | 84 | 81 | 75 | 81 | 81 | 125 | 123 | 158 | 155 | 158 | 127 | 121 | 76 | 77 | 115 | 155 |  | 103 | 201 | 162 | 200 | 120 | 76 | 81 | 3164000
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 270 | 270 | 270 | 240 | 240 | 240 | 240 | 240 | 270 | 300 | 300 | 300 | 260 | 260 | 240 | 44 |  | 45 | 45 | 44 | 45 | 217 | 223 | 222 | 5333284
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 10 | 40 | 15 | 15 | 15 | 15 | 0 | 115418
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 102 | 175 | 185 | 185 | 185 | 120 | 120 |  | 130 | 130 | 130 | 185 | 195 | 195 | 189 | 2107636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 180 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 150 | 150 | 180 | 180 | 180 | 180 | 3235156
23 | Ghorasal TPP Unit-5 | 100 | 100 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 170 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 3244500
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 253 | 295 | 296 | 295 | 294 | 297 | 294 | 291 | 351 |  |  |  | 177 | 266 | 272 | 250 | [9 empty] | 0 | 18398180
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 25 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 25 | 25 | 25 | 45 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 590256
33 | Ashuganj 225 MW CCPP | 187 | 185 | 182 | 191 | 184 | 183 | 183 | 192 | 183 | 183 | 199 | 184 | 196 | 184 | 184 | 184 | 209 | 175 |  | 203 | 188 | 183 | 193 | 183 | 182 | 183 | 4554000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | [15 empty] | 0 | 2713000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 285 | 280 | 280 | 280 | 290 | 280 | 280 | 290 | 280 | 300 | 280 | 280 | 280 | 325 | 280 |  | 345 | 310 | 310 | 320 | 310 | 310 | 310 | 7343900
| Ashuganj 420 MW CCPP(East) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 260 | 401 | 322 | 337 | 323 | 320 | 292 | 333 | 292 |  | 350 | 322 | 322 | 329 | 322 | 322 | 322 | 6950700
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP | 85 | 85 | 85 | 85 | 85 | [21 empty] | 469245
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 357 | 356 | 356 | 356 | 357 | 314 | 307 | 307 | 307 | 363 | 399 | 400 | 381 | 342 | 341 | 343 | 345 | 380 |  | 360 | 396 | 394 | 397 | 396 | 386 | 350 | 8753150
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 380 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 300 | 330 | 420 | 420 | 420 | 400 | 350 | 320 | 370 |  | 380 | 420 | 420 | 450 | 450 | 450 | 450 | 9092000
41 | Haripur 360MW CCPP(HPL) | 282 | 282 | 282 | 282 | 281 | 282 | 282 | 282 | 282 | 327 | 327 | 327 | 327 | 328 | 326 | 287 | 287 | 337 |  | 333 | 354 | 352 | 343 | 312 | 312 | 311 | 7408000
42 | RPCL 210MW CCPP | 71 | 71 | 71 | 70 | 70 | 104 | 104 | 103 | 104 | 104 | 104 | 106 | 134 | 155 | 154 | 158 | 155 | 206 |  | 204 | 202 | 204 | 205 | 206 | 205 | 203 | 3100800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 7 | 7 | 12 | 32 | 19 | 41 | 30 | 10 | 5 | 0 | 0 |  | 0 | [6 empty] | 165170
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1018000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 687360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 60 | 60 | 61 | 61 | 61 | 61 | 40 | 40 | 50 |  | 60 | 60 | 61 | 61 | 62 | 62 | 61 | 1277373
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 40 | 40 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 40 | 60 | 60 | 60 | 60 | 20 | 20 | 20 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1139520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 203 | 203 | 203 | 205 | 204 | 204 | 203 | 84 | [15 empty] | 80 | 110 | 125 | 1303890
51 | Sylhet 20 MW GTPP | 18 | [19 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 99000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | [20 empty] | 9 | 9 | 10 | 10 | 10 | 176940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 11 | 11 | 11 | 11 | 11 | 11 | 25 | 25 | 25 | 25 | 11 | 11 | 11 |  | 29 | 47 | 47 | 44 | 47 | 47 | 46 | 691200
56 | Shahjahanulla 25 MW PP | 24 | [20 empty] | 8 | 24 | 24 | 24 | 24 | 129384
57 | Bibiana-II 341 MW CCPP (Summit) | 80 | 180 | 275 | 285 | 265 | 280 | 290 | 280 | 285 | 280 | 300 | 290 | 280 | 300 | 290 | 260 | 275 | 290 |  | 265 | 310 | 300 | 315 | 290 | 270 | 280 | 6631180
| Bibiyana South 400 MW |  | 15 | 28 | 38 | 50 | 50 | 50 | 50 | 50 | 50 |  | 100 | 120 | 124 | [5 empty] | 15 | 45 | 67 | 128 | 136 | 300 | 394 | 1560800
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 0 | 81488
59 | Tangail Palli Power Gen 22 MW | [25 empty] | 0 | 0
60 | Barabkunda 22 MW PP (Regent) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 311520
61 | Narshingdi 22 MW PP (Doreen) | [25 empty] | 0 | 0
62 | Tangail 22 MW PP (Doreen) | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 20 | 20 | 20 | 22 | 22 | 22 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 384804
63 | Impoprt (Tripura) | 130 | 126 | 126 | 126 | 122 | 116 | 110 | 108 | 116 | 116 | 120 | 122 | 128 | 132 | 134 | 126 | 80 | 112 |  | 136 | 138 | 138 | 146 | 146 | 150 | 148 | 2974080
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 36 | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 26 | 26 | 26 | 26 | 26 | 19 | 19 | 23 |  | 24 | 24 | 24 | 34 | 34 | 34 | 34 | 787680
65 | Feni 22MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 473242
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 244080
67 | Jangalia 33MW PP (Summit) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 32 |  | 32 | 32 | 32 | 33 | 33 | 33 | 24 | 680900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 20 | 20 | 20 | 7 | 0 | 0 |  | 12 | 12 | 12 | 12 | 20 |  | 20 | 379410
69 | Summit Ashulia | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 16 | 16 | 16 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480000
70 | Summit Madhabdi | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 11 | 0 | 0 | 0 | 0 | 0 |  | 6 | 6 | 6 | 14 | 15 | 15 | 15 | 189180
71 | Maona 33 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 5 | 15 | 15 | 15 | 0 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 352700
72 | Rupganj 33 MW PP(Summit) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 7 |  | 7 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 460100
73 | Ghorashal 108MW PP (Regent) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 190272
| Feni Lanka Power | 109 | 106 | 106 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 17 | 17 | 17 | 17 | 17 | 17 | 52 |  | 52 | 52 | 34 | 34 | 45 | 106 | 52 | 1377120
| Chowmuhani 113 MW | 31 | 28 | 29 | 29 | 29 | 21 | 9 | 9 | 9 | 9 | 9 | 28 | 29 | 29 | 36 | 36 | 38 | 38 |  | 56 | 56 | 55 | 58 | 58 | 33 | 9 | 708960
| Manikgonj 162MW PP(MPGL) | [19 empty] | 17 | 17 | 17 |  |  |  | 0 | 40320
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 67478
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150 MW PP | [25 empty] | 0 | 0
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [15 empty] | 1 | 8 | 8 |  | 29 | 43 | 43 | 43 | 43 | 25 | 25 | 230664
| Gazipur 100 MW PP | [19 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 111629
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 4 | 5 | 3 | 3 | 4 | 3 | 2 | 1 | 1 | 0 | [8 empty] | 27723
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 446990
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 20 | 540290
82 | Madanganj 102 PP(Summit) | [19 empty] | 5 | 17 | 17 | 17 | 17 | 15 | 0 | 62690
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 251 | 277 | 295 | 301 | 268 | 290 | 288 | 298 | 273 | 291 | 297 | 305 | 306 | 274 | 287 | 271 | 312 | 289 |  | 313 | 302 | 300 | 313 | 263 | 280 | 298 | 6977949
87 | Meghnaghat 100 MW(IEL) | 9 | [8 empty] | 6 | 24 | 35 | 43 | 42 | 42 | 42 | 18 | 13 |  | 17 | 17 | 17 | 9 | 8 | 9 | 8 | 336960
| Meghnaghat 104 MW PP (OPCL) | 49 | 17 | 17 |  |  |  | 14 | 17 | 32 | 36 | 52 | 53 | 53 | 53 | 54 | 53 | 43 | 17 |  | 32 | 53 | 43 | 51 | 51 | 53 | 53 | 858240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 46 | 46 | 46 | 46 | 46 | 46 | 12 | 12 | 12 | 46 | 46 | 46 | 58 | 58 | 58 | 58 | 58 | 69 |  | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 1159920
92 | Fenchuganj 44MW (Energyprima) | 48 | 49 | 49 | 49 | 48 | 10 | 10 | 10 | 10 | 10 | 10 | 25 | 25 | 25 | 25 | 10 | 10 | 10 |  | 33 | 42 | 47 | 49 | 49 | 49 | 49 | 752328
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 18 | 30 | 30 | 5 | 5 | 5 | 5 |  | 28 | 43 | 43 | 43 | 43 | 43 | 43 | 662464
94 | Gagnagar 102 MW PP (Digital Power) | 16 | [18 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 90864
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 20 | 6 | [5 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 504000
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit)
100 | Manikganj 55 MW PP (Northern) | [25 empty] | 0 | 0
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 80 | 80 | 80 | 80 | 80 | 80 | 112 | 112 | 112 | 112 | 80 | 80 | [11 empty] | 0 | 1400073
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | [8 empty] | 6000
103 | Kamalaghat 54 MW PP(Banco Energy) | [17 empty] | 17 |  | 17 | 54 | 54 | 54 | 35 | 35 | 35 | 247140
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 65 | 66 | 35 | 35 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 32 | 37 | 37 | 607200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 26 | 17 | [17 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 0 | 142992
115 | Juldah 100 MW PP Unit-3 (Acorn) | 88 | 88 | 88 | 88 | 88 | 50 | 50 | 25 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1641600
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 63 | 68 | 68 | 68 | 68 | 69 | 78 |  | 104 | 104 | 104 | 104 | 104 | 104 | 55 | 1638720
117 | Ashuganj 150MW PP (Midland) | 43 | [16 empty] | 5 |  | 25 | 70 | 70 | 70 | 70 | 20 | 6 | 485090
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 47 | 67 | 45 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8 | 8 | 11 |  | 58 | 85 | 85 | 85 | 85 | 47 | 47 | 914400
| Anwara 300 MW PP (United) | 88 | 88 | 83 | 88 | 88 | 88 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 88 | 88 | 120 |  | 170 | 280 | 296 | 296 | 296 | 123 | 124 | 2938145
| Juldah unit-2 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 12 | 12 | 50 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 1303680
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 777868
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 6 | 2 | 7 | 6 | 12 | 6 |  | 1 | 0 | 0 | 0 | 0 | [8 empty] | 56997
| Chandpur 115(Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 18 | 25 | 53 | 56 | 56 |  | 53 | 54 | 54 | 54 | 54 | 31 | 18 | 714240
| Kanchan Purbachal Power Generation Ltd. | [17 empty] | 4 |  | 12 | 17 |  | 6 | 17 | 17 | 0 | 80640
| Mirsharai 150 MW (Oil) | [10 empty] | 36 | 54 | 54 | 54 | 54 | 36 | 36 | 36 |  | 36 | 36 | 36 | 18 | 18 | 123 | 160 | 623927
Mirsharai 150 MW (Gas)
Cox's Bazar Wind
120 | Eastern Zone Total | 5848 | 5564 | 5494 | 5424 | 5361 | 5083 | 5024 | 4903 | 4942 | 4874 | 5067 | 5381 | 5720 | 5753 | 5401 | 5064 | 4813 | 4967 |  | 5756 | 6372 | 6304 | 6586 | 6655 | 6591 | 6414 | 148851542
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [19 empty] | 16 | 20 | 30 | 49 | 64 | 64 | 49 | 241920
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | [23 empty] | 3 | 17 | 17 | 26112
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 26 | 44 | 24 | 26 | 100 | 17 | 12 | 6 | 13 | 19 | 14 | 7 | [8 empty] | 298080
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [20 empty] | 2 | 13 | 54 | 54 | 17 | 0 | 156000
133 | Bhola Nutan Biddut BD LTD (GAS) | 224 | 227 | 225 | 225 | 226 | 227 | 227 | 225 | 226 | 184 | 178 | 178 | 179 | 178 | 181 | 181 | 181 | 181 |  | 184 | 184 | 183 | 140 | 224 | 226 | 225 | 4871400
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [22 empty] | 16 | 16 | 16 | 0 | 58752
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 160 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 160 | 160 | 160 | 160 | 160 | 150 | 3578200
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 55 | 60 | 60 |  | 63 | 65 | 65 | 65 | 65 | 65 | 65 | 1532000
140 | Bhola 33 MW PP (Venture) | 27 | 26 | 25 | 25 | 25 | 24 | 21 | 20 | 18 | 17 | 17 | 18 | 20 | 20 |  |  |  | 13 |  | 23 | 28 | 28 | 29 | 29 | 30 | 31 | 468050
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | [20 empty] | 24 | 32 | 40 | 40 | 40 | 8 | 162000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 35 | 67 | 105 | 105 | 105 | 105 | 105 | 511920
146 | Bheramara HVDC | 905 | 905 | 905 | 905 | 906 | 905 | 906 | 900 | 901 | 902 | 903 | 904 | 904 | 905 | 905 | 906 | 906 | 906 |  | 906 | 908 | 909 | 908 | 907 | 908 | 907 | 21748363
147 | Bheramara 410 MW CCPP | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 260 | 260 | 260 | 290 | 395 | 400 | 410 | 405 | 300 | 300 | 300 |  | 350 | 405 | 405 | 410 | 405 | 410 | 405 | 8734752
148 | Payra 1320 MW | 360 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 270 | 270 | 250 | 250 | 250 | 250 | 250 |  | 250 | 350 | 350 | 360 | 360 | 360 | 360 | 7642500
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 179 | 179 | 179 | 180 | 180 | 179 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4411700
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 70 | 70 | 70 | 60 | 60 | 60 | 60 | 60 | 60 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1540000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 460
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 170 | 170 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  |  |  |  | 8 | 50 | 100 | 130 |  | 138 | 205 | 209 | 214 | 214 | 214 | 214 | 3235691
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 170 | 162 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 166 | 140 | 140 | 140 | 140 | 140 | 140 |  | 149 | 185 | 199 | 220 | 215 | 180 | 180 | 4094718
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 346 | 346 | 303 | 308 | 308 | 308 | 259 | 259 | 287 | 326 | 327 | 376 | 378 | 378 | 376 | 280 | 301 | 336 |  | 313 | 422 | 423 | 422 | 391 | 359 | 357 | 8217272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 8 | 5 | 5 | 5 | 5 | 5 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 122238
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 28 | 28 | 35 | 35 | 35 | 35 | 35 | 169721
169 | Natore 52 MW PP (Rajlanka) | [25 empty] | 0 | 0
170 | Chapainawabganj 100 MW Peaking PP | [25 empty] | 0
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 24 | 45 | 56 | 74 | 109 | 113 | 70 | 483744
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 35 | 70 | 100 | 113 | 113 | 113 | 70 | 543648
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 70 | 34 | 34 | 33 | [12 empty] | 25 |  | 45 | 70 | 103 | 106 | 106 | 106 | 70 | 801225
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 5 | 6 | 5 | 5 | 2 | 1 | [8 empty] | 40652
178 | Energypac Power Venture Thakurgaon Ltd. | 35 | 35 | 35 | [16 empty] | 35 | 35 | 64 | 115 | 115 | 115 | 72 | 665664
| Intraco Solar 30 MW | [5 empty] | 0 | 0 | 2 | 6 | 5 | 6 | 14 | 13 | 11 | 15 | 11 | 12 | 2 |  | 0 | [6 empty] | 102524
| Adani Power Jharkhanda Ltd | 561 | 565 | 566 | 416 | 417 | 418 | 418 | 416 | 416 | 415 | 416 | 459 | 457 | 459 | 460 | 460 | 450 | 561 |  | 558 | 562 | 556 | 557 | 560 | 561 | 561 | 11777000
178 | Teesta Solar Limited | [5 empty] | 2 | 10 | 60 | 18 | 22 | 27 | 64 | 65 | 68 | 28 | 25 | 30 | 18 | [8 empty] | 475300