## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-05-12 | Friday
|  | Date (day): | 2023-05-12 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 12632.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14400 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-05-11 | 2023-05-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 22 | 22 | 22 | 86 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 400 | 390 | 400 | 400
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 252 | 276 | 330 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 400 | 330 | 380 | 380 | 70 |  | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 57 | 50 | 50 | 50 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 280 | 213 | 160 | 160 |  | 175 | GT-2 under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 65 | 65 | 97 | 97 |  | 5 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 15 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | GT-1 Under maint
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 53 | 60 | 55 | 55 | 45 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 90 | 170 | 170 |  | 165 | ST under S/D
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 83 | 40 | 92 |  | 10 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 17 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 150 | 100 | 150
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 50 | 50 | 50 |  | 30 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 19 | 14 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 40 | 41 | 8 | 52 |  |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 97 | 280 | 100 | 285
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 301 | 295 | 300 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 80 | 80 | 70 | 80 | 20 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 75 | 79 | 70 | 80 |  | 20 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 131 | 114 | 35 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 53 | 54 | 54 | 50 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 17 | 54 | 162
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 34 | 34 | 34 | 21 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 3393 | 3336 | 3170 | 3803 | 527 | 1497
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 44 | 6 | 44 | 6 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 223 | 225 | 225
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 69 | 51 | 51 | 54 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 30 | 54 | 48 | 56 |  | 42 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 30 | 68 | 67 | 67 |  | 35 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 8 | 10 | 10 | 10 | 12 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 20 | 20 | 20
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 29 | 0 | 30 | 78 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 88 | 279 | 88 | 300
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 66 | 105 | 92 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 51 | 17 | 51 | 65 |  | Fuel shortage
| Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 0 | 0 | 36 | 144 | 34 | 163 |  |  | On test.
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 826 | 1350 | 937 | 1363 | 731 | 407
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 211 | 200 | 200 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 310 | 330 | 330 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 305 | 300 | 300 |  |  | FGMO
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 36 | 41 | 41 | 41
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  |  | Contract Expired
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 185 | 189 | 180 | 180 | 15
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 18 | 152 | 20 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 37 | 41 | 35 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 70 | 34 | 68 | 132 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 18 | 18 |  | 4 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 7 | 7 | 7 | 7 |  | 4 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 156 | 140 | 129 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 24 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 50 | 50 | 52 | 52
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 0 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 57 | 95 | 26 | 55 | 58 |  | Fuel shortage
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 35 |  | 19 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 90 | 54 | 54 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3159 | 3151 | 1637 | 1919 | 1539 | 1927 | 226 | 620
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 28 | 86 | 30 | 80 | 122 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 18 | 15 | 18 | 4 |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 76 | 93 | 57 | 98 | 102 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 77 | 99 | 57 | 98 | 17 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 10 | 12 | 12 | 12 | 10 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 255 | 308 | 222.6 | 306 | 126 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 28 | 30 | 30 |  | 60 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 46 | 44 | 44
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 10 | 10
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 48 | 59 | 58 | 60
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 83 | 84 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 204 | 207 | 201 | 201 |  | 30 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 17 | 17
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 15 | 15 | 10 |  | Gas shortage
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 280 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 379 | 364 | 400 | 400 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 377 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1574 | 1612 | 1643 | 1665 | 10 | 710
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 804 | 939 | 939
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 61 | 68 | 49 | 98 |  | 17 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 9 | 26 | 20 | 43 |  | 11 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 25 | 80 | 60 | 82 |  | 27 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 24 | 32 | 32 | 40
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 35 | 17 | 35 | 70 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 85 | 105 | 105 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 101 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1239 | 1150 | 1322 | 1342 | 826 | 55
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 16 | 0 | 16 | 94 |  | Fuel shortage
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 25 | 34 | 22 | 32 |  | 8 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 170 | 89 | 74 | 140
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maintenance
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 | 307 |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1566 | 1533 | 1357 | 1582 | 401 | 228
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 28 | 28 | 28 | 28 |  | 24 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 21 | 28 | 15 | 31 |  | 40 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 21 | 21 | 21 | 21
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 40 | 24 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 183 | 173 | 170 | 170 | 40 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 135 | 142 | 140 | 140 | 80 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 341 | 401 | 370 | 390 | 24 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 28 | 27 | 34 | 34 |  | 16 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 39 | 82 | 80 | 83 |  | 21 | Enginr problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 35 | 50 | 35 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 55 | 35 | 55 | 58 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 754 | 710 | 850 | 800 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 1732 | 1837 | 1880 | 1922 | 856 | 122
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 75 | 75 | 75 | 10 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 260 | 250 | 250
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 49 | 34 | 50 |  |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 36 | 72 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 31 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 182 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 614 | 456 | 562 | 490 | 50 | 85
| Total |  |  |  |  | 23332 | 22566 | 12836 | 13501 | 12632.6 | 14400 | 3753 | 3724
A. |  | 2023-05-11 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 13501 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 11368 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14300 | MW
3 | Day peak Generation : |  |  | 12836 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13606.8 | MW
4 | Evening peak Generation : |  |  | 13501 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 763 | MW
5 | Total Energy Generation : |  | 295.776 | MKWHr | By Solar | 3.0559 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 143.8835 | MKWHr |  | By Oil: | 65.8838 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 57.4435 | MKWHr |  | By Hydro: | 0.32274 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3753 | MW | Dhaka | 5136.46 | 5076.46 |  | 60 |  | 18:00 |  | 1112
|  |  | For Plants S/D or M/C prob = |  |  | 3724 | MW | Chittagong | 1382.8 | 1248.8 |  | 134 |  | 19:00 |  | 1198.525
|  |  | Total = |  |  | 7477 | MW | Khulna | 1879 | 1658 |  | 221 |  | 19:30 |  | 1014.21
7 | Total Gas Supplied : |  |  | 1081.59 | MMCFD |  |  | Rajshahi | 1355 | 1257 |  | 98 |  | 20:00 |  | 841.355
8 | Fuel Cost : | i) Gas : | Taka | 164880183.058 | ii) Oil : | Taka | 927266821.13 | Comilla | 1454 | 1204 |  | 250 |  | 21:00 |  | 763.045
|  | iii) Coal : | Taka | 326496511.87 | Total | Taka | 1418643516.058 | Mymensingh | 657 | 657 |  | 0 |  | 22:00 |  | 650.355
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 387 | 387 |  | 0 |  | 23:00 |  | 762.09
| ii) During Peak Demand : |  |  | 350 | MW (E to W) at | 21:00 | hrs | Barisal | 476.54 | 476.54 |  | 0 |  | 24:00 |  | 1184.2
| iii) Maximum : |  |  | 280 | MW at | 20:00 | hrs | Rangpur | 879 | 879 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 38.4° C |  |  | Total | 13606.8 | 12843.8 |  | 763
B. |  | 2023-05-12 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 38.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 14000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 14400 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11800 | MW
4 | Reserve(Generation end) |  |  |  | 400 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 306.7079 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10860 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.4982 | MKWHr. | ii) HVDC Flow at Peak Time |  | 804 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.6883 | MKWHr. | iii) Maximum HVDC Flow : |  | 921 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.35 |  | (b) Today: | 74.23 |  | (c) Rule Curve: |  | 79.91
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-05-11 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 405 | 340 |  | 0 | 450 | 305 | 17 | 53 | 0 | 170 | 0 | 0 | 17 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 26 | 16 | 0 | 0 | 0 | 115 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 45 | 66 | 10 | 0 | 6 | 10 | 19 | 0 | 0 | 0 | 330 | 325 | 210 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 36 | 43 | 18 | 7 | 33 | 20 | 182 | 80 | 0 | 12 | 0 | 43 | 30 | 53 | 49 | 0 | 0 | 57 | 83 | 0 | 200 | 17 | 0 | 10 | 285 | 15 | 5 | 0 | 130 | 301 | 80 | 48 | 75 | 17 | 0 | 12 | 17 | 20 | 379 | 49 | 88 | 55 | 0 | 87 | 17 | 92 | 0 | 13 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 108 | 0 |  | 862 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 72 | 8 | 177 | 29 | 0 | 0 | 0 | 0 | 28 | 0 | 76 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 401 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 843 | 0 | 0 |  | 7350 | 4874 | 12224 | 4076 | 862 | 2300 | 456 | 1370 | 2412 | 0 | 0 | 566 | 182 | 0 | 1582.435 | 74.37
2:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 405 | 340 |  | 0 | 450 | 307 | 17 | 51 | 0 | 166 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 26 | 16 | 0 | 0 | 0 | 115 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 45 | 66 | 10 | 0 | 6 | 10 | 19 | 0 | 0 | 0 | 315 | 310 | 210 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 36 | 43 | 18 | 7 | 33 | 20 | 176 | 80 | 0 | 0 | 0 | 43 | 30 | 53 | 49 | 0 | 0 | 57 | 83 | 0 | 201 | 17 | 0 | 10 | 285 | 15 | 5 | 0 | 115 | 301 | 80 | 48 | 75 | 17 | 0 | 12 | 17 | 18 | 366 | 49 | 88 | 34 | 0 | 87 | 17 | 54 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 108 | 0 |  | 863 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 70 | 8 | 178 | 29 | 0 | 0 | 0 | 0 | 28 | 5 | 76 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 725 | 0 | 0 |  | 7190 | 4775 | 11965 | 4020 | 863 | 2315 | 456 | 1288 | 2294 | 0 | 0 | 553 | 176 | 0 | 1536.595 | 74.37
3:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 405 | 340 |  | 0 | 450 | 306 | 17 | 51 | 0 | 158 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 27 | 33 | 16 | 16 | 0 | 0 | 0 | 115 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 45 | 33 | 10 | 0 | 6 | 10 | 13 | 0 | 0 | 0 | 310 | 305 | 210 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 36 | 52 | 18 | 7 | 33 | 20 | 174 | 80 | 0 | 0 | 0 | 43 | 30 | 53 | 49 | 0 | 0 | 57 | 83 | 0 | 200 | 17 | 0 | 10 | 285 | 15 | 5 | 0 | 105 | 302 | 80 | 48 | 75 | 17 | 0 | 12 | 17 | 20 | 369 | 49 | 88 | 34 | 0 | 87 | 0 | 54 | 0 | 8 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 108 | 0 |  | 919 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 64 | 8 | 178 | 34 | 0 | 0 | 0 | 0 | 28 | 5 | 68 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 73 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 414 | 36 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 751 | 0 | 0 |  | 7107 | 4777 | 11884 | 3996 | 919 | 2313 | 457 | 1201 | 2318 | 0 | 0 | 506 | 174 | 0 | 1445.87 | 74.36
4:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 404 | 340 |  | 0 | 450 | 309 | 17 | 51 | 0 | 149 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 27 | 33 | 28 | 16 | 0 | 0 | 0 | 115 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 45 | 33 | 10 | 0 | 6 | 10 | 17 | 0 | 0 | 0 | 310 | 300 | 210 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 37 | 52 | 18 | 7 | 33 | 20 | 172 | 80 | 0 | 0 | 0 | 43 | 30 | 53 | 49 | 0 | 0 | 57 | 83 | 0 | 200 | 17 | 0 | 10 | 280 | 15 | 5 | 0 | 97 | 261 | 80 | 48 | 75 | 17 | 0 | 12 | 17 | 20 | 378 | 49 | 88 | 34 | 0 | 87 | 0 | 54 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 17 | 17 | 0 | 108 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 60 | 8 | 178 | 33 | 0 | 0 | 0 | 0 | 28 | 5 | 68 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 423 | 36 | 0 | 0 | 105 | 34 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 756 | 0 | 0 |  | 7062 | 4791 | 11853 | 4000 | 920 | 2323 | 416 | 1193 | 2326 | 0 | 0 | 503 | 172 | 0 | 1326.495 | 74.36
5:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 397 | 340 |  | 0 | 450 | 307 | 16 | 51 | 0 | 152 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 27 | 33 | 28 | 16 | 0 | 0 | 0 | 115 | 0 | 25 | 228 | 0 | 0 | 0 |  | 6 | 45 | 33 | 10 | 0 | 6 | 10 | 22 | 0 | 0 | 0 | 315 | 310 | 209 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 37 | 52 | 18 | 7 | 33 | 20 | 170 | 80 | 0 | 0 | 0 | 43 | 30 | 53 | 46 | 0 | 0 | 57 | 83 | 0 | 200 | 17 | 0 | 10 | 280 | 15 | 5 | 0 | 98 | 201 | 80 | 48 | 75 | 17 | 0 | 12 | 17 | 20 | 372 | 49 | 88 | 34 | 0 | 87 | 0 | 54 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 17 | 0 | 17 | 0 | 18 | 17 | 0 | 54 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 60 | 8 | 178 | 31 | 0 | 0 | 0 | 0 | 28 | 15 | 45 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 424 | 36 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 759 | 0 | 0 |  | 6954 | 4747 | 11701 | 4008 | 920 | 2322 | 356 | 1160 | 2329 | 0 | 0 | 436 | 170 | 0 | 1235.77 | 74.35
6:00 | 0 | 0 | 121 | 180 | 0 | 22 | 0 | 398 | 340 |  | 0 | 450 | 304 | 17 | 51 | 0 | 166 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 23 | 27 | 33 | 28 | 8 | 0 | 0 | 0 | 115 | 0 | 25 | 224 | 0 | 0 | 0 |  | 6 | 45 | 33 | 10 | 0 | 6 | 10 | 22 | 0 | 0 | 0 | 350 | 345 | 207 | 189 | 0 | 43 | 0 | 0 | 43 | 0 | 37 | 52 | 18 | 7 | 33 | 20 | 160 | 69 | 0 | 0 | 0 | 43 | 30 | 53 | 43 | 0 | 0 | 56 | 83 | 0 | 204 | 17 | 0 | 10 | 280 | 15 | 5 | 0 | 98 | 0 | 0 | 48 | 0 | 17 | 1 | 12 | 17 | 18 | 413 | 49 | 88 | 20 | 0 | 87 | 5 | 54 | 0 | 9 | 12 | 398 | 17 | 3 | 17 | 17 | 0 | 17 | 2 | 18 | 17 | 0 | 54 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 60 | 8 | 178 | 30 | 0 | 0 | 0 | 0 | 28 | 20 | 45 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 182 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 422 | 0 | 0 | 0 | 105 | 0 | 0 | 0 | 0 | 1244 | 0 | 0 | 17 | 0 | 3 | 36 | 0 | 0 | 0 | 1 | 0 | 742 | 10 | 0 |  | 6684 | 4712 | 11396 | 4125 | 920 | 2313 | 0 | 1106 | 2311 | 0 | 0 | 441 | 160 | 20 | 1099.205 | 74.35
7:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 399 | 335 |  | 0 | 450 | 310 | 17 | 51 | 15 | 170 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 23 | 27 | 33 | 28 | 8 | 0 | 0 | 0 | 115 | 0 | 25 | 226 | 0 | 0 | 0 |  | 6 | 37 | 33 | 10 | 0 | 6 | 10 | 19 | 0 | 0 | 0 | 310 | 305 | 208 | 189 | 0 | 42 | 0 | 0 | 43 | 0 | 38 | 52 | 18 | 7 | 30 | 20 | 156 | 33 | 0 | 0 | 1 | 43 | 30 | 53 | 43 | 0 | 0 | 28 | 80 | 0 | 203 | 17 | 0 | 10 | 285 | 15 | 5 | 0 | 98 | 0 | 0 | 48 | 0 | 17 | 5 | 12 | 17 | 16 | 367 | 49 | 88 | 20 | 1 | 87 | 17 | 54 | 0 | 9 | 12 | 400 | 17 | 10 | 17 | 17 | 0 | 17 | 7 | 17 | 17 | 0 | 54 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 60 | 8 | 180 | 24 | 0 | 0 | 0 | 0 | 28 | 14 | 46 | 21 | 42 | 24 | 0 | 27 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 428 | 0 | 0 | 15 | 105 | 0 | 0 | 2 | 20 | 1244 | 0 | 0 | 17 | 0 | 13 | 36 | 0 | 0 | 0 | 6 | 0 | 768 | 41 | 0 |  | 6546 | 4822 | 11368 | 3945 | 920 | 2313 | 0 | 1182 | 2337 | 0 | 0 | 429 | 156 | 86 | 1150.775 | 74.34
8:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 396 | 310 |  | 0 | 450 | 306 | 17 | 51 | 15 | 196 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 19 | 23 | 27 | 33 | 26 | 8 | 0 | 0 | 0 | 115 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 38 | 33 | 10 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 325 | 320 | 193 | 189 | 0 | 39 | 0 | 0 | 43 | 0 | 37 | 51 | 18 | 7 | 6 | 20 | 156 | 31 | 0 | 0 | 1 | 43 | 30 | 53 | 49 | 0 | 0 | 58 | 80 | 0 | 203 | 17 | 0 | 10 | 280 | 15 | 5 | 0 | 97 | 0 | 0 | 48 | 0 | 17 | 9 | 12 | 17 | 20 | 377 | 58 | 88 | 17 | 2 | 88 | 17 | 54 | 0 | 9 | 12 | 398 | 17 | 20 | 17 | 17 | 0 | 17 | 15 | 18 | 17 | 0 | 36 | 0 |  | 920 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 20 | 59 | 8 | 180 | 23 | 0 | 0 | 0 | 0 | 28 | 14 | 46 | 21 | 42 | 24 | 0 | 28 | 20 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 143 | 0 | 350 | 17 | 0 | 35 | 105 | 33 | 0 | 3 | 35 | 1180 | 0 | 0 | 17 | 2 | 44 | 36 | 0 | 0 | 0 | 13 | 0 | 792 | 86 | 0 |  | 6591 | 4872 | 11463 | 3985 | 920 | 2187 | 0 | 1312 | 2297 | 0 | 0 | 411 | 156 | 195 | 1026.625 | 74.34
9:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 301 |  | 0 | 410 | 313 | 17 | 51 | 15 | 190 | 0 | 0 | 17 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 19 | 23 | 27 | 33 | 19 | 8 | 0 | 0 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 38 | 33 | 10 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 330 | 325 | 207 | 189 | 0 | 37 | 0 | 0 | 43 | 0 | 36 | 50 | 18 | 7 | 32 | 20 | 150 | 28 | 0 | 0 | 1 | 43 | 29 | 53 | 49 | 0 | 0 | 58 | 80 | 0 | 206 | 17 | 0 | 9 | 285 | 15 | 5 | 0 | 97 | 0 | 0 | 49 | 0 | 40 | 14 | 12 | 17 | 18 | 383 | 49 | 88 | 17 | 3 | 88 | 17 | 54 | 0 | 8 | 12 | 391 | 17 | 34 | 17 | 17 | 0 | 17 | 23 | 18 | 17 | 0 | 36 | 0 |  | 921 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 50 | 8 | 175 | 22 | 0 | 0 | 0 | 0 | 28 | 14 | 45 | 21 | 42 | 24 | 0 | 28 | 20 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 381 | 17 | 0 | 35 | 105 | 33 | 0 | 5 | 35 | 1220 | 0 | 0 | 17 | 3 | 45 | 36 | 0 | 0 | 0 | 21 | 0 | 776 | 127 | 0 |  | 6642 | 4949 | 11591 | 4014 | 921 | 2179 | 0 | 1341 | 2320 | 0 | 0 | 390 | 150 | 276 | 1059.095 | 74.33
10:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 271 |  | 0 | 400 | 292 | 17 | 51 | 15 | 180 | 0 | 0 | 24 | 16 | 82 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 22 | 23 | 25 | 33 | 19 | 37 | 0 | 18 | 0 | 115 | 0 | 25 | 220 | 0 | 0 | 0 |  | 9 | 38 | 33 | 22 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 310 | 305 | 182 | 187 | 0 | 38 | 0 | 0 | 43 | 0 | 37 | 50 | 16 | 7 | 33 | 20 | 158 | 29 | 0 | 0 | 2 | 43 | 29 | 53 | 46 | 0 | 0 | 58 | 80 | 0 | 206 | 17 | 0 | 7 | 285 | 8 | 5 | 0 | 97 | 206 | 80 | 67 | 75 | 132 | 10 | 12 | 32 | 18 | 368 | 77 | 88 | 20 | 4 | 88 | 17 | 54 | 0 | 55 | 12 | 391 | 17 | 41 | 68 | 17 | 0 | 17 | 28 | 27 | 17 | 0 | 36 | 0 |  | 916 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 9 | 27 | 24 | 173 | 23 | 27 | 0 | 0 | 0 | 28 | 18 | 39 | 21 | 42 | 24 | 0 | 28 | 19 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 137 | 0 | 368 | 17 | 0 | 35 | 85 | 34 | 0 | 5 | 35 | 1244 | 0 | 0 | 17 | 4 | 91 | 36 | 0 | 0 | 0 | 27 | 0 | 795 | 163 | 0 |  | 7257 | 5081 | 12338 | 3912 | 916 | 2098 | 361 | 1737 | 2364 | 18 | 0 | 399 | 158 | 375 | 918.71 | 74.33
11:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 404 | 273 |  | 0 | 400 | 285 | 22 | 51 | 55 | 185 | 0 | 0 | 45 | 32 | 98 | 0 | 0 | 0 | 0 | 34 | 55 | 35 | 22 | 23 | 25 | 33 | 19 | 40 | 0 | 25 | 0 | 115 | 0 | 25 | 218 | 0 | 0 | 0 |  | 12 | 38 | 33 | 22 | 0 | 6 | 8 | 2 | 0 | 0 | 0 | 325 | 320 | 196 | 187 | 0 | 36 | 0 | 0 | 43 | 0 | 37 | 50 | 17 | 7 | 33 | 20 | 160 | 28 | 0 | 15 | 2 | 43 | 28 | 47 | 43 | 0 | 0 | 55 | 78 | 0 | 206 | 17 | 0 | 7 | 280 | 16 | 5 | 0 | 97 | 294 | 80 | 76 | 75 | 130 | 18 | 25 | 34 | 16 | 382 | 77 | 88 | 51 | 4 | 88 | 17 | 54 | 0 | 56 | 25 | 381 | 17 | 47 | 72 | 17 | 0 | 17 | 31 | 59 | 17 | 0 | 36 | 0 |  | 917 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 9 | 25 | 24 | 175 | 24 | 102 | 0 | 0 | 0 | 28 | 20 | 39 | 21 | 42 | 34 | 0 | 28 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 363 | 17 | 0 | 35 | 85 | 34 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 96 | 36 | 0 | 0 | 0 | 31 | 0 | 686 | 181 | 0 |  | 7644 | 5089 | 12733 | 3983 | 917 | 2072 | 449 | 2026 | 2255 | 25 | 0 | 425 | 160 | 421 | 875.735 | 74.32
12:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 252 |  | 0 | 400 | 280 | 40 | 65 | 55 | 180 | 0 | 0 | 53 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 23 | 25 | 33 | 19 | 40 | 0 | 25 | 0 | 115 | 0 | 25 | 214 | 0 | 0 | 0 |  | 10 | 30 | 30 | 22 | 0 | 6 | 8 | 3 | 0 | 0 | 0 | 330 | 310 | 197 | 185 | 0 | 36 | 0 | 0 | 43 | 0 | 37 | 50 | 17 | 7 | 33 | 20 | 156 | 28 | 0 | 15 | 2 | 40 | 28 | 50 | 43 | 0 | 0 | 48 | 78 | 0 | 204 | 17 | 0 | 9 | 280 | 16 | 5 | 0 | 97 | 301 | 80 | 76 | 75 | 131 | 19 | 25 | 34 | 18 | 379 | 77 | 88 | 51 | 4 | 88 | 17 | 66 | 0 | 57 | 25 | 377 | 17 | 47 | 72 | 17 | 0 | 17 | 32 | 90 | 17 | 0 | 36 | 0 |  | 917 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 9 | 25 | 24 | 170 | 25 | 110 | 0 | 0 | 0 | 28 | 21 | 39 | 21 | 42 | 40 | 0 | 28 | 18 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 341 | 17 | 0 | 35 | 85 | 34 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 101 | 36 | 0 | 0 | 0 | 31 | 0 | 754 | 182 | 0 |  | 7685 | 5151 | 12836 | 3942 | 917 | 2029 | 456 | 2139 | 2322 | 25 | 0 | 421 | 156 | 429 | 1016.12 | 74.32
13:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 397 | 277 |  | 0 | 380 | 265 | 41 | 65 | 55 | 170 | 0 | 0 | 58 | 50 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 23 | 25 | 33 | 19 | 40 | 0 | 25 | 0 | 115 | 0 | 25 | 215 | 0 | 0 | 0 |  | 6 | 32 | 30 | 22 | 0 | 17 | 8 | 3 | 0 | 0 | 0 | 335 | 320 | 198 | 185 | 0 | 34 | 0 | 0 | 43 | 0 | 34 | 43 | 17 | 7 | 32 | 20 | 162 | 26 | 0 | 15 | 2 | 41 | 28 | 52 | 41 | 0 | 0 | 53 | 76 | 0 | 202 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 97 | 301 | 75 | 76 | 75 | 129 | 18 | 25 | 35 | 16 | 372 | 77 | 88 | 51 | 4 | 88 | 17 | 84 | 0 | 57 | 25 | 370 | 46 | 45 | 72 | 22 | 0 | 17 | 31 | 85 | 17 | 0 | 36 | 0 |  | 914 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 20 | 25 | 24 | 170 | 26 | 110 | 0 | 0 | 0 | 28 | 23 | 39 | 21 | 42 | 40 | 0 | 28 | 17 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 134 | 0 | 329 | 17 | 0 | 35 | 105 | 32 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 87 | 36 | 0 | 0 | 0 | 31 | 0 | 741 | 143 | 0 |  | 7737 | 5099 | 12836 | 3928 | 914 | 2016 | 451 | 2225 | 2310 | 25 | 0 | 433 | 162 | 372 | 1111.62 | 74.31
14:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 395 | 263 |  | 0 | 370 | 250 | 42 | 65 | 15 | 165 | 0 | 0 | 60 | 50 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 25 | 33 | 20 | 8 | 0 | 25 | 0 | 115 | 0 | 25 | 210 | 0 | 0 | 0 |  | 11 | 54 | 65 | 22 | 11 | 32 | 8 | 5 | 0 | 0 | 0 | 325 | 310 | 196 | 185 | 0 | 32 | 0 | 0 | 43 | 0 | 40 | 34 | 17 | 7 | 32 | 20 | 154 | 26 | 0 | 15 | 1 | 41 | 28 | 49 | 42 | 0 | 0 | 53 | 75 | 0 | 201 | 17 | 0 | 10 | 285 | 16 | 5 | 0 | 97 | 295 | 74 | 47 | 75 | 55 | 16 | 25 | 35 | 15 | 382 | 48 | 88 | 51 | 4 | 88 | 17 | 72 | 0 | 57 | 25 | 362 | 52 | 32 | 72 | 28 | 0 | 17 | 27 | 94 | 0 | 0 | 36 | 0 |  | 914 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 26 | 21 | 16 | 83 | 25 | 16 | 0 | 0 | 0 | 28 | 30 | 38 | 21 | 42 | 40 | 0 | 27 | 17 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 324 | 17 | 0 | 35 | 105 | 34 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 89 | 36 | 0 | 0 | 0 | 27 | 0 | 744 | 120 | 0 |  | 7441 | 4855 | 12296 | 3802 | 914 | 1965 | 444 | 1849 | 2313 | 25 | 0 | 503 | 154 | 327 | 1436.32 | 74.32
15:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 395 | 254 |  | 0 | 360 | 248 | 52 | 65 | 15 | 150 | 0 | 0 | 60 | 50 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 23 | 25 | 33 | 20 | 8 | 0 | 25 | 0 | 115 | 0 | 25 | 215 | 0 | 0 | 0 |  | 12 | 50 | 65 | 22 | 12 | 38 | 10 | 2 | 0 | 0 | 0 | 330 | 320 | 196 | 183 | 0 | 32 | 0 | 0 | 43 | 0 | 39 | 32 | 17 | 7 | 30 | 20 | 158 | 31 | 0 | 15 | 0 | 42 | 28 | 49 | 41 | 0 | 0 | 54 | 75 | 0 | 201 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 97 | 301 | 74 | 47 | 75 | 36 | 13 | 25 | 34 | 11 | 384 | 48 | 86 | 51 | 3 | 87 | 17 | 72 | 0 | 57 | 25 | 343 | 53 | 12 | 72 | 30 | 0 | 17 | 22 | 94 | 11 | 0 | 36 | 0 |  | 915 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 26 | 23 | 16 | 85 | 28 | 0 | 0 | 0 | 0 | 28 | 24 | 38 | 21 | 42 | 40 | 0 | 28 | 17 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 178 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 323 | 17 | 0 | 35 | 85 | 34 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 3 | 53 | 36 | 25 | 0 | 0 | 21 | 0 | 742 | 120 | 0 |  | 7370 | 4802 | 12172 | 3778 | 915 | 1945 | 450 | 1816 | 2311 | 25 | 25 | 495 | 158 | 254 | 1841.24 | 74.3
16:00 | 0 | 0 | 120 | 180 | 0 | 21 | 0 | 397 | 248 |  | 0 | 360 | 241 | 56 | 65 | 15 | 145 | 0 | 0 | 60 | 56 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 23 | 24 | 33 | 20 | 8 | 0 | 25 | 0 | 115 | 0 | 25 | 217 | 0 | 0 | 0 |  | 12 | 50 | 65 | 22 | 12 | 0 | 10 | 2 | 0 | 0 | 0 | 320 | 310 | 197 | 184 | 0 | 32 | 0 | 0 | 43 | 0 | 30 | 33 | 17 | 7 | 30 | 20 | 132 | 33 | 0 | 15 | 0 | 41 | 28 | 49 | 41 | 0 | 0 | 54 | 76 | 0 | 201 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 97 | 52 | 72 | 37 | 70 | 32 | 8 | 25 | 34 | 11 | 376 | 48 | 86 | 51 | 1 | 87 | 17 | 72 | 0 | 57 | 25 | 360 | 53 | 1 | 72 | 34 | 0 | 27 | 16 | 60 | 18 | 0 | 36 | 0 |  | 914 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 29 | 21 | 16 | 86 | 25 | 0 | 0 | 0 | 0 | 28 | 24 | 63 | 21 | 42 | 32 | 0 | 28 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 340 | 17 | 0 | 35 | 105 | 33 | 0 | 4 | 35 | 1244 | 0 | 0 | 17 | 1 | 46 | 36 | 80 | 0 | 0 | 14 | 0 | 728 | 81 | 0 |  | 6998 | 4836 | 11834 | 3767 | 914 | 1948 | 194 | 1801 | 2297 | 25 | 80 | 504 | 132 | 172 | 1782.03 | 74.3
17:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 260 |  | 0 | 350 | 242 | 57 | 60 | 15 | 90 | 0 | 0 | 60 | 58 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 25 | 33 | 18 | 8 | 0 | 25 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 |  | 14 | 50 | 66 | 22 | 21 | 15 | 10 | 2 | 0 | 0 | 0 | 310 | 305 | 203 | 184 | 0 | 33 | 0 | 0 | 43 | 0 | 24 | 48 | 17 | 7 | 30 | 20 | 132 | 34 | 0 | 15 | 1 | 43 | 28 | 53 | 41 | 0 | 0 | 58 | 80 | 0 | 198 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 97 | 0 | 72 | 37 | 70 | 33 | 3 | 25 | 40 | 11 | 368 | 48 | 88 | 51 | 1 | 87 | 17 | 81 | 0 | 57 | 25 | 330 | 53 | 0 | 72 | 34 | 0 | 35 | 6 | 53 | 22 | 0 | 36 | 0 |  | 914 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 27 | 35 | 16 | 81 | 26 | 0 | 0 | 0 | 0 | 28 | 24 | 71 | 21 | 42 | 32 | 0 | 28 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 341 | 17 | 0 | 35 | 105 | 43 | 0 | 2 | 35 | 1222 | 0 | 0 | 17 | 0 | 24 | 36 | 120 | 0 | 0 | 6 | 0 | 738 | 35 | 0 |  | 6913 | 4811 | 11724 | 3694 | 914 | 1962 | 142 | 1853 | 2285 | 25 | 120 | 519 | 132 | 78 | 1696.08 | 74.29
18:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 366 | 293 |  | 0 | 350 | 243 | 57 | 50 | 15 | 90 | 0 | 0 | 60 | 58 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 26 | 0 | 14 | 11 | 0 | 25 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 54 | 66 | 22 | 29 | 0 | 10 | 7 | 0 | 0 | 0 | 310 | 305 | 204 | 185 | 0 | 33 | 0 | 0 | 43 | 0 | 25 | 47 | 17 | 7 | 24 | 20 | 136 | 35 | 0 | 17 | 0 | 43 | 28 | 52 | 43 | 0 | 0 | 58 | 77 | 0 | 198 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 120 | 0 | 25 | 45 | 25 | 43 | 0 | 25 | 68 | 48 | 367 | 47 | 88 | 51 | 0 | 122 | 17 | 105 | 0 | 56 | 25 | 360 | 53 | 0 | 72 | 35 | 0 | 35 | 1 | 53 | 36 | 0 | 55 | 0 |  | 914 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 52 | 16 | 81 | 24 | 0 | 0 | 0 | 0 | 28 | 28 | 71 | 21 | 8 | 40 | 0 | 28 | 17 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 305 | 17 | 0 | 35 | 105 | 49 | 0 | 1 | 35 | 1160 | 0 | 0 | 137 | 0 | 4 | 80 | 0 | 0 | 0 | 2 | 0 | 731 | 8 | 0 |  | 6985 | 4701 | 11686 | 3653 | 914 | 1951 | 50 | 2155 | 2216 | 25 | 0 | 570 | 136 | 16 | 1112 | 74.29
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 350 | 293 |  | 0 | 350 | 238 | 57 | 55 | 15 | 90 | 0 | 0 | 60 | 82 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 23 | 26 | 33 | 14 | 40 | 0 | 25 | 0 | 115 | 0 | 25 | 225 | 0 | 0 | 0 |  | 12 | 54 | 68 | 22 | 29 | 29 | 10 | 10 | 0 | 0 | 0 | 310 | 305 | 209 | 189 | 0 | 39 | 0 | 0 | 43 | 0 | 34 | 46 | 17 | 7 | 24 | 20 | 138 | 50 | 0 | 17 | 0 | 43 | 28 | 53 | 45 | 0 | 0 | 60 | 82 | 0 | 193 | 18 | 0 | 9 | 275 | 13 | 0 | 0 | 275 | 115 | 71 | 83 | 73 | 86 | 0 | 25 | 68 | 102 | 367 | 91 | 88 | 51 | 0 | 275 | 17 | 104 | 34 | 60 | 25 | 370 | 53 | 0 | 162 | 51 | 0 | 30 | 0 | 54 | 36 | 0 | 90 | 0 |  | 914 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 22 | 60 | 32 | 70 | 32 | 16 | 0 | 0 | 0 | 28 | 36 | 80 | 21 | 34 | 40 | 0 | 28 | 21 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 161 | 0 | 0 | 0 | 0 | 0 | 138 | 0 | 357 | 20 | 0 | 35 | 105 | 49 | 0 | 0 | 55 | 1180 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 670 | 0 | 0 |  | 8072 | 4873 | 12945 | 3653 | 914 | 2019 | 259 | 3062 | 2185 | 25 | 0 | 690 | 138 | 0 | 1198.525 | 74.27
19:30 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 345 | 264 |  | 0 | 340 | 226 | 57 | 65 | 15 | 90 | 0 | 0 | 60 | 83 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 23 | 22 | 33 | 14 | 40 | 0 | 25 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 54 | 68 | 22 | 29 | 44 | 10 | 12 | 0 | 0 | 0 | 310 | 305 | 209 | 189 | 0 | 40 | 0 | 0 | 43 | 0 | 35 | 46 | 17 | 7 | 24 | 20 | 132 | 60 | 0 | 17 | 0 | 43 | 28 | 53 | 45 | 0 | 0 | 60 | 82 | 0 | 200 | 18 | 0 | 9 | 265 | 16 | 0 | 0 | 280 | 52 | 75 | 93 | 79 | 110 | 0 | 25 | 68 | 115 | 318 | 97 | 88 | 51 | 0 | 275 | 17 | 105 | 114 | 75 | 25 | 340 | 53 | 0 | 162 | 51 | 0 | 30 | 0 | 54 | 36 | 0 | 108 | 0 |  | 914 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | 22 | 65 | 32 | 70 | 33 | 16 | 0 | 0 | 0 | 28 | 36 | 80 | 21 | 42 | 40 | 8 | 28 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 303 | 35 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 696 | 0 | 0 |  | 8084 | 4954 | 13038 | 3576 | 914 | 1908 | 206 | 3288 | 2275 | 25 | 0 | 714 | 132 | 0 | 1014.21 | 0
20:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 357 | 264 |  | 0 | 340 | 228 | 56 | 65 | 15 | 90 | 0 | 0 | 60 | 83 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 0 | 23 | 27 | 33 | 14 | 41 | 0 | 25 | 0 | 115 | 0 | 25 | 221 | 0 | 0 | 0 |  | 12 | 54 | 68 | 22 | 29 | 44 | 10 | 11 | 0 | 0 | 0 | 310 | 305 | 207 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 46 | 17 | 7 | 24 | 20 | 128 | 58 | 0 | 18 | 0 | 43 | 28 | 53 | 46 | 0 | 0 | 59 | 83 | 0 | 207 | 18 | 0 | 10 | 265 | 16 | 0 | 0 | 280 | 11 | 79 | 94 | 79 | 114 | 0 | 25 | 68 | 150 | 320 | 99 | 88 | 69 | 0 | 279 | 17 | 103 | 114 | 75 | 25 | 400 | 53 | 0 | 162 | 51 | 0 | 35 | 0 | 54 | 36 | 0 | 126 | 0 |  | 804 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 34 | 72 | 32 | 89 | 34 | 16 | 0 | 0 | 0 | 28 | 38 | 82 | 21 | 42 | 40 | 8 | 28 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 300 | 35 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 142 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 724 | 0 | 0 |  | 8213 | 4906 | 13119 | 3677 | 804 | 1910 | 169 | 3348 | 2303 | 25 | 0 | 755 | 128 | 0 | 841.355 | 74.28
21:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 390 | 276 |  | 0 | 330 | 213 | 57 | 65 | 15 | 90 | 0 | 0 | 60 | 83 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 23 | 27 | 33 | 14 | 41 | 0 | 25 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 |  | 12 | 54 | 68 | 22 | 29 | 44 | 10 | 20 | 0 | 0 | 0 | 310 | 305 | 211 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 41 | 50 | 18 | 7 | 24 | 20 | 140 | 86 | 0 | 18 | 0 | 43 | 28 | 53 | 46 | 0 | 0 | 59 | 83 | 0 | 207 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 280 | 295 | 80 | 93 | 79 | 114 | 0 | 25 | 70 | 152 | 364 | 99 | 88 | 69 | 0 | 279 | 17 | 105 | 114 | 95 | 25 | 400 | 53 | 0 | 17 | 51 | 0 | 35 | 0 | 54 | 34 | 0 | 144 | 0 |  | 804 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 26 | 80 | 32 | 89 | 34 | 16 | 0 | 0 | 0 | 28 | 28 | 82 | 21 | 42 | 40 | 8 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 401 | 35 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | 0 |  | 8525 | 4976 | 13501 | 3817 | 804 | 2022 | 454 | 3182 | 2289 | 25 | 0 | 768 | 140 | 0 | 763.045 | 74.27
22:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 399 | 273 |  | 0 | 330 | 221 | 58 | 65 | 15 | 90 | 0 | 0 | 60 | 83 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 27 | 33 | 14 | 41 | 0 | 25 | 0 | 115 | 0 | 25 | 222 | 0 | 0 | 0 |  | 12 | 55 | 67 | 22 | 29 | 44 | 10 | 23 | 0 | 0 | 0 | 310 | 300 | 211 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 41 | 50 | 18 | 7 | 24 | 20 | 140 | 85 | 0 | 18 | 0 | 43 | 28 | 53 | 46 | 0 | 0 | 59 | 83 | 0 | 207 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 282 | 290 | 83 | 93 | 80 | 115 | 0 | 25 | 98 | 150 | 365 | 99 | 88 | 69 | 0 | 123 | 17 | 105 | 114 | 95 | 25 | 400 | 53 | 0 | 17 | 51 | 0 | 35 | 0 | 54 | 34 | 0 | 144 | 0 |  | 804 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 26 | 77 | 32 | 89 | 36 | 16 | 0 | 0 | 0 | 28 | 28 | 84 | 21 | 42 | 40 | 8 | 28 | 0 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 398 | 35 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 762 | 0 | 0 |  | 8406 | 5013 | 13419 | 3855 | 804 | 2002 | 453 | 3031 | 2341 | 25 | 0 | 768 | 140 | 0 | 650.355 | 74.27
23:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 398 | 283 |  | 0 | 330 | 208 | 30 | 65 | 3 | 140 | 0 | 0 | 32 | 24 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 23 | 28 | 33 | 14 | 41 | 0 | 0 | 0 | 115 | 0 | 25 | 222 | 0 | 0 | 0 |  | 12 | 55 | 67 | 22 | 0 | 44 | 10 | 28 | 0 | 0 | 0 | 350 | 340 | 207 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 45 | 51 | 18 | 7 | 24 | 20 | 148 | 85 | 0 | 18 | 0 | 43 | 28 | 53 | 49 | 0 | 0 | 59 | 83 | 0 | 209 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 295 | 290 | 83 | 93 | 80 | 72 | 0 | 12 | 100 | 150 | 417 | 99 | 88 | 62 | 0 | 87 | 17 | 105 | 114 | 73 | 12 | 400 | 52 | 0 | 17 | 51 | 0 | 35 | 0 | 53 | 34 | 0 | 144 | 0 |  | 803 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 26 | 75 | 32 | 89 | 36 | 0 | 0 | 0 | 0 | 28 | 28 | 84 | 21 | 42 | 40 | 0 | 28 | 0 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 416 | 35 | 0 | 35 | 105 | 49 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 778 | 0 | 0 |  | 8203 | 4949 | 13152 | 4034 | 803 | 2030 | 453 | 2609 | 2357 | 0 | 0 | 718 | 148 | 0 | 762.09 | 74.26
24:00 | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 397 | 284 |  | 0 | 330 | 210 | 25 | 68 | 15 | 142 | 0 | 0 | 25 | 24 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 23 | 28 | 33 | 8 | 8 | 0 | 0 | 0 | 115 | 0 | 25 | 225 | 0 | 0 | 0 |  | 12 | 55 | 67 | 10 | 0 | 15 | 10 | 24 | 0 | 0 | 0 | 310 | 305 | 211 | 189 | 0 | 42 | 0 | 0 | 43 | 0 | 45 | 51 | 18 | 7 | 24 | 20 | 148 | 85 | 0 | 18 | 0 | 43 | 30 | 53 | 50 | 0 | 0 | 60 | 83 | 0 | 208 | 17 | 0 | 10 | 275 | 16 | 5 | 0 | 295 | 300 | 82 | 46 | 75 | 17 | 0 | 12 | 60 | 62 | 367 | 49 | 88 | 62 | 0 | 87 | 17 | 63 | 114 | 16 | 12 | 400 | 50 | 0 | 17 | 17 | 0 | 35 | 0 | 54 | 17 | 0 | 90 | 0 |  | 804 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 26 | 72 | 40 | 89 | 36 | 0 | 0 | 0 | 0 | 28 | 4 | 84 | 21 | 42 | 40 | 0 | 28 | 0 | 0 | 8 | 72 | 0 | 260 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 144 | 0 | 414 | 35 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 839 | 0 | 0 |  | 7525 | 4935 | 12460 | 3911 | 804 | 2023 | 457 | 2065 | 2415 | 0 | 0 | 637 | 148 | 0 | 1184.2 | 74.26
KWH | 0 | 0 | 2913156 | 4284000 | 0 | 524818 | 0 | 9584640 | 7090000 |  | 0 | 8650500 | 6490851 | 807360 | 1279268 | 391658 | 3555802 | 0 | 0 | 873600 | 917136 | 2078880 | 0 | 0 | 0 | 0 | 291240 | 645923 | 634358 | 353304 | 552000 | 588420 | 749880 | 480000 | 561600 | 0 | 322740 | 0 | 2800000 | 0 | 617214 | 5210551 | 0 | 0 | 0 |  | 242880 | 1084224 | 1208208 | 417240 | 207360 | 458880 | 235776 | 298560 | 0 | 0 | 0 | 8211900 | 7774000 | 4922000 | 4533090 | 0 | 900936 | 0 | 0 | 957178 | 0 | 870928 | 1107110 | 406152 | 167040 | 693600 | 459040 | 3688320 | 1198080 | 0 | 231372 | 12300 | 1006000 | 665160 | 1248600 | 1091016 | 0 | 0 | 1316832 | 1920000 | 0 | 4136440 | 402000 | 0 | 245700 | 6849000 | 346368 | 111856 | 0 | 3535309 | 4339111 | 1477882 | 1423200 | 1418407 | 1441584 | 140265 | 438720 | 979680 | 1093963 | 9168000 | 1496400 | 2093827 | 1088109 | 34680 | 2697273 | 379600 | 1808210 | 574560 | 970200 | 447360 | 8978800 | 835200 | 308910 | 1121760 | 672436 | 0 | 588600 | 238027 | 1109760 | 541080 | 0 | 1753018 | 0 |  | 21498181 | 0 | 0 | 0 | 1040640 | 0 | 0 | 0 | 463680 | 1203072 | 434250 | 3252839 | 690663 | 392928 | 0 | 0 | 0 | 676768 | 343665 | 1409176 | 491960 | 912626 | 623490 | 29246 | 643728 | 423360 | 0 | 157284 | 1746327 | 0 | 6118500 | 0 | 0 | 4519709 | 0 | 0 | 0 | 0 | 0 | 3544682 | 0 | 8992582 | 584640 | 0 | 815136 | 2506032 | 804124 | 0 | 58205 | 810816 | 31518700 | 0 | 0 | 1351200 | 33840 | 714240 | 1173120 | 153138 | 0 | 0 | 231959 | 0 | 18060000 | 1283500 | 0 |  | 176067976 | 119708006 | 295775982 | 93877619 | 21498181 | 50005918 | 7235400 | 46136376 | 57443527 | 322740 | 153138 | 12358837 | 3688320 | 3055926 | 0
Fuel Cost | 0 | 0 | 4253207.76 | 6383160 | 0 | 698007.94 | 0 | 10063872 | 7657200 |  | 0 | 9429045 | 7204844.61 | 9026284.8 | 16950301 | 5189468.5 | 3982498.24 | 0 | 0 | 12772032 | 12904103.52 | 33698644.8 | 0 | 0 | 0 | 0 | 3704572.8 | 8719960.5 | 8506740.78 | 264978 | 414000 | 0 | 0 | 0 | 9552816 | 0 | 87139.8 | 0 | 5292000 | 0 | 10091448.9 | 5418973.04 | 0 | 0 | 0 |  | 3169584 | 18084856.32 | 20563700.16 | 5636912.4 | 2629324.8 | 5309241.6 | 299435.52 | 994204.8 | 0 | 0 | 0 | 9115209 | 8473660 | 5709520 | 5847686.1 | 0 | 1018057.68 | 0 | 0 | 1598487.26 | 0 | 15040926.56 | 14890629.5 | 556428.24 | 125280 | 1213800 | 344280 | 26482137.6 | 1305907.2 | 0 | 314665.92 | 196062 | 1378220 | 878011.2 | 2172564 | 1887457.68 | 0 | 0 | 2554654.08 | 4377600 | 0 | 4177804.4 | 864300 | 0 | 486486 | 6849000 | 259776 | 85010.56 | 0 | 48256967.85 | 90947766.56 | 30547820.94 | 19184736 | 29318472.69 | 19965938.4 | 1639697.85 | 4527590.4 | 13382428.8 | 14516889.01 | 8434560 | 18196224 | 30276738.42 | 13764578.85 | 0 | 31665985.02 | 4133844 | 19221272.3 | 7796779.2 | 12505878 | 5269900.8 | 8260496 | 10815840 | 4463749.5 | 14235134.4 | 7652321.68 | 0 | 7687116 | 2844422.65 | 16613107.2 | 7126023.6 | 0 | 0 | 0 |  | 64494543 | 0 | 0 | 0 | 10833062.4 | 0 | 0 | 0 | 8350876.8 | 21655296 | 6240172.5 | 3643179.68 | 1339886.22 | 4282915.2 | 0 | 0 | 0 | 11349399.36 | 6010700.85 | 22039512.64 | 3788092 | 15113086.56 | 10543215.9 | 398622.98 | 10859691.36 | 876355.2 | 0 | 119063.988 | 10146159.87 | 0 | 32366865 | 0 | 0 | 5242862.44 | 0 | 0 | 0 | 0 | 0 | 4111831.12 | 0 | 8902656.18 | 7857561.6 | 0 | 9643058.88 | 36212162.4 | 10212374.8 | 0 | 643165.25 | 9843306.24 | 283983487 | 0 | 0 | 9998880 | 382730.4 | 8378035.2 | 17983929.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 870408460.69 | 657846738.618 | 1528255199.308 | 104558702.068 | 64494543 | 60321480.99 | 150814060.19 | 598255940.19 | 326496511.87 | 87139.8 | 0 | 178196820.75 | 26482137.6 | 18547862.85 | 0
Yesterday Day Peak | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 252 |  | 0 | 400 | 280 | 40 | 65 | 55 | 180 | 0 | 0 | 53 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 23 | 25 | 33 | 19 | 40 | 0 | 25 | 0 | 115 | 0 | 25 | 214 | 0 | 0 | 0 |  | 10 | 30 | 30 | 22 | 0 | 6 | 8 | 3 | 0 | 0 | 0 | 330 | 310 | 197 | 185 | 0 | 36 | 0 | 0 | 43 | 0 | 37 | 50 | 17 | 7 | 33 | 20 | 156 | 28 | 0 | 15 | 2 | 40 | 28 | 50 | 43 | 0 | 0 | 48 | 78 | 0 | 204 | 17 | 0 | 9 | 280 | 16 | 5 | 0 | 97 | 301 | 80 | 76 | 75 | 131 | 19 | 25 | 34 | 18 | 379 | 77 | 88 | 51 | 4 | 88 | 17 | 66 | 0 | 57 | 25 | 377 | 17 | 47 | 72 | 17 | 0 | 17 | 32 | 90 | 17 | 0 | 36 | 0 |  | 917 | 0 | 0 | 0 | 61 | 0 | 0 | 0 | 9 | 25 | 24 | 170 | 25 | 110 | 0 | 0 | 0 | 28 | 21 | 39 | 21 | 42 | 40 | 0 | 28 | 18 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 135 | 0 | 341 | 17 | 0 | 35 | 85 | 34 | 0 | 7 | 35 | 1244 | 0 | 0 | 17 | 4 | 101 | 36 | 0 | 0 | 0 | 31 | 0 | 754 | 182 | 0 |  | 12836 | DayPeak
Yesterday Evening Peak | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 390 | 276 | 0 | 0 | 330 | 213 | 57 | 65 | 15 | 90 | 0 | 0 | 60 | 83 | 150 | 0 | 0 | 0 | 0 | 17 | 55 | 35 | 0 | 23 | 27 | 33 | 14 | 41 | 0 | 25 | 0 | 115 | 0 | 25 | 223 | 0 | 0 | 0 | 0 | 12 | 54 | 68 | 22 | 29 | 44 | 10 | 20 | 0 | 0 | 0 | 310 | 305 | 211 | 189 | 0 | 41 | 0 | 0 | 43 | 0 | 41 | 50 | 18 | 7 | 24 | 20 | 140 | 86 | 0 | 18 | 0 | 43 | 28 | 53 | 46 | 0 | 0 | 59 | 83 | 0 | 207 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 280 | 295 | 80 | 93 | 79 | 114 | 0 | 25 | 70 | 152 | 364 | 99 | 88 | 69 | 0 | 279 | 17 | 105 | 114 | 95 | 25 | 400 | 53 | 0 | 17 | 51 | 0 | 35 | 0 | 54 | 34 | 0 | 144 | 0 |  | 804 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | 26 | 80 | 32 | 89 | 34 | 16 | 0 | 0 | 0 | 28 | 28 | 82 | 21 | 42 | 40 | 8 | 27 | 22 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 173 | 0 | 0 | 0 | 0 | 0 | 142 | 0 | 401 | 35 | 0 | 50 | 105 | 49 | 0 | 0 | 55 | 1244 | 0 | 0 | 150 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 710 | 0 | 0 |  | 13501 | EvPeak
Forecast for Evening | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 330 | 0 | 0 | 380 | 160 | 50 | 97 | 30 | 170 | 0 | 0 | 55 | 92 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 27 | 33 | 33 | 52 | 0 | 0 | 25 | 115 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 56 | 67 | 22 | 30 | 44 | 10 | 20 | 0 | 0 | 0 | 330 | 300 | 200 | 180 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 52 | 18 | 7 | 33 | 20 | 152 | 80 | 0 | 18 | 0 | 43 | 30 | 51 | 44 | 0 | 0 | 60 | 84 | 0 | 201 | 17 | 0 | 10 | 300 | 15 | 10 | 0 | 285 | 300 | 80 | 98 | 80 | 149 | 0 | 25 | 68 | 150 | 400 | 98 | 88 | 51 | 0 | 300 | 17 | 92 | 114 | 55 | 25 | 400 | 54 | 0 | 162 | 51 | 0 | 35 |  | 94 | 34 | 0 | 163 |  |  | 939 | 0 | 0 |  | 98 | 0 | 0 | 0 | 43 | 82 | 40 | 140 | 32 | 16 | 0 | 0 | 0 | 28 | 31 | 83 | 21 | 42 | 40 | 8 | 34 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 170 |  | 0 | 0 | 0 | 0 | 140 | 0 | 390 | 35 | 0 | 50 | 105 | 50 | 0 | 0 | 55 | 1244 | 0 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 800 |  | 0
Forecast for Day | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 400 | 330 | 0 | 0 | 380 | 160 | 50 | 97 | 15 | 170 | 0 | 0 | 55 | 40 | 100 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 22 | 23 | 27 | 33 | 33 | 8 | 0 | 0 | 25 | 115 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 12 | 48 | 67 | 22 | 0 | 6 | 10 | 20 | 0 | 0 | 0 | 330 | 300 | 200 | 180 | 0 | 41 | 0 | 0 | 43 | 0 | 35 | 52 | 18 | 7 | 33 | 20 | 129 | 30 | 0 | 15 | 1.6 | 43 | 30 | 51 | 44 | 0 | 0 | 58 | 84 | 0 | 201 | 17 | 0 | 10 | 280 | 15 | 10 | 0 | 100 | 300 | 70 | 57 | 70 | 35 | 20 | 25 | 34 | 20 | 400 | 57 | 88 | 51 | 5 | 88 | 17 | 92 | 0 | 26 | 25 | 400 | 54 | 50 | 54 | 17 | 0 | 17 | 30 | 54 | 34 | 0 | 34 |  |  | 939 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 20 | 60 | 32 | 74 | 22 | 0 | 0 | 0 | 0 | 28 | 15 | 80 | 21 | 42 | 24 | 0 | 34 | 22 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 370 | 17 | 0 | 35 | 105 | 34 | 0 | 8 | 35 | 1244 | 0 |  | 17 | 6 | 100 | 35 | 0 |  | 0 | 30 | 0 | 850 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 120 | 180 | 0 | 22 | 0 | 372 | 304 | 0 | 0 | 380 | 142 | 25 | 34 | 15 | 155 | 0 | 0 | 25 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 23 | 27 | 33 | 16 | 8 | 0 | 0 | 0 | 115 | 0 | 25 | 226 | 0 | 0 | 0 | 0 | 6 | 55 | 67 | 10 | 0 | 6 | 10 | 29 | 0 | 0 | 0 | 310 | 270 | 182 | 189 | 0 | 33 | 0 | 0 | 43 | 0 | 36 | 51 | 15 | 7 | 25 | 20 | 132 | 31 | 0 | 18 | 1 | 43 | 30 | 50 | 50 | 0 | 0 | 59 | 83 | 0 | 209 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 97 | 0 | 0 | 46 | 0 | 17 | 11 | 12 | 17 | 20 | 367 | 49 | 88 | 17 | 2 | 88 | 17 | 54 | 0 | 9 | 12 | 370 | 17 | 20 | 17 | 17 | 0 | 17 | 9 | 17 | 17 | 0 | 36 | 0 | 0 | 921 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 73 | 8 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 21 | 8 | 0 | 0 | 0 | 21 | 0 | 8 | 75 | 0 | 260 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 146 | 0 | 359 | 17 | 0 | 35 | 53 | 27 | 0 | 3 | 35 | 1244 | 0 | 0 | 17 | 1 | 38 | 0 | 0 | 0 | 0 | 14 | 0 | 855 | 80 | 0 | 0 |  |  |  | 143.8835 | 21.4982 | 65.8838 | 57.4435 | 0.32274 | 3.6883 | 3.0559
295.776
| Minimum Generation |  | 11368 | 7:00
| Highest Generation |  | 13501 | 21:00
| Day Peak Generation |  | 12836 | 12:00
| Evening Peak Generation |  | 13501 | 21:00
| HVDC Max Flow |  | 921 | 9:00
| HVDC EvPeak Flow |  | 804 | 21:00
| Load factor L.F |  | 91.28% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-05-12
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-05-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 12836 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10860
Evening Peak Generation : |  |  | 13501 | MW Hour : | 21:00 | Available Max Generation : |  | 14400
E.P. Demand (at gen end) : |  |  | 14300 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14000
Maximum Generation : |  |  | 13501 | MW Hour : | 21:00 | Reserve(Generation end) |  | 400
Total Gen. (MKWH) : |  |  | 295.776 | System Load Factor : | 91.28% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 280 | MW at | 20:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-05-12
Actual : |  | 74.23 | Ft.(MSL) , | Rule curve : | 79.91 | Ft.( MSL )
Gas Consumed : |  | Total = | 1081.59 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 164880183.058
: |  |  | Coal : | 326496511.87 | Oil : | 927266821.13 | Total : | 1418643516.058
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 60 | 1440:00 | 5098.9131 |  |  | 0 | 0%
Chittagong Area |  | 134 | 3216:00 | 1416.2754 |  |  | 0 | 0%
Khulna Area |  | 221 | 5304:00 | 1862.9675 |  |  | 0 | 0%
Rajshahi Area |  | 98 | 2352:00 | 1645.1712 |  |  | 0 | 0%
Cumilla Area |  | 250 | 6000:00 | 1403.9755 |  |  | 0 | 0%
Mymensingh Area |  | 0 | 0:00 | 1154.9797 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 520.9909 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 420.9926 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 911.984 |  |  | 0 | 0%
Total |  | 763 |  | 14436.25 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3,7
3) Bhula Nuton Biddut
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj- 2
9) Barishal 307 MW
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:10 | 12:55 | Chandpur 132/33kV S/S Bus-B Scheduled S/D Due to Annual maintenance.
09:30 | 15:18 | Rampur 230/132/33 S/S ATR-01 (706T) HT Scheduled S/D Due to On Job Training.
10:33 |  | Adani Power Jharkhand Ltd. unit-2 tripped.
11:02 | 19:14 | BIPTC S/S 20DF44 Forced S/D Due to CB General Fault.
13:01 |  | Bhola CCPP GT1 tripped.
13:06 | 13:41 | GPH-Hathazari 230kV Ckt-1 Tripped from Hathazari 230/132/33kV end showing ABB Distance relay relays.
13:06 | 13:41 | GPH 230/33kV S/S HATHAZARI-2 Tripped showing 86.1 Trip relay optd 86.2 trip relay optd 21.1 relay optd 21.2
realay optd relays Due to Distance Trip distance: 0.5km.
14:26 | 16:24 | Sreepur 230/132/33kV S/S 132/33 kV T-1 HT Scheduled S/D Due to 33kv under frequency relay configure.
14:27 | 16:25 | Sreepur 230/132/33kV S/S 230/132 kV T-1 LT Scheduled S/D Due to Under frequency relay configure.
16:26 | 16:51 | Sreepur 230/132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Shutdown for 33kv incomer -2 under frequency relay configure.
16:27 | 16:41 | Jamalpur-Mymensingh 132kV Ckt-1 Tripped from Jamalpur 132/33kV end showing 1.Distance P443 2.O/C p132 relays.
16:27 | 16:50 | Sreepur 230/132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Shutdown for 33kv under frequency relay configure.
16:31 | 16:38 | Kishoreganj-Mymensingh 132kV Ckt-2 Tripped from Kishoreganj 132/33kV end showing Distance Relay,C-Phase,Z3
relays Due to Distance Relay,C-Phase,Z3 .
16:31 | 16:37 | Kishoreganj-Mymensingh 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing Distance Relay,C-Phase,Z3
relays Due to Distance Relay,C-Phase,Z3.
16:54 | 17:41 | Sholosohor 132/33kV S/S TRAFO-01 HT Forced S/D Due to Due to break bird nest. With the approval of Grid Incharge &
BPDB Authorized person.
17:30 | 19:07 | Kishoreganj-Mymensingh 132kV Ckt-2 Tripped from Kishoreganj 132/33kV end showing Distance Relay,C-Phase,Z3
relays Due to Distance Relay,C-Phase,Z3.
17:30 | 18:28 | Kishoreganj-Mymensingh 132kV Ckt-1 Tripped from Kishoreganj 132/33kV end showing Distance Relay,C-Phase
relays Due to Distance Relay,C-Phase.
18:34 | 18:44 | Jamalpur 132/33kV S/S T-2 LT Tripped showing O/C p132 relays. | [5 empty] | 25 MW loa interrup.
18:34 | 18:44 | Jamalpur 132/33kV S/S T-1 LT Tripped showing O/C p132 relays.
19:45 | 21:12 | Matarbari T1 S/D at 19:45hrs due to pole straight work at 33kv kohelia singapore feeder (PDB). | [5 empty] | 20 MW load interrup.
| 21:23 | Adani Power Jharkhand Ltd. unit-2 was sync.
| 21:50 | Amnura-Chapainawabganj-132kV Ckt-1 is restored.
| 21:50 | C.nawabganj-Rajshahi 132 kV Ckt-1 is restored.
21:54 | 22:40 | Bogura 132/33kV S/S Transformer-3 LT Tripped showing Trip Relay(K31) relays Due to Inst O/C , Ins E/F due to
Thundering and rain fall .
23:04 | 23:26 | Joypurhat-Naogaon 132kV Ckt-1 Tripped from Naogaon 132/33kV end showing Distance relay. relays Due to Stormy | [5 empty] | 24 MW load interrup in
|  | weather and lightning. | [5 empty] | Naogaon 132/33 kV end.
23:43 | 01:25 | Jamalpur 132/33kV S/S T-2 HT Forced S/D Due to 33 kV switching-01 feeder 33kv bus to D.S Loop replace work due to red hot. | [5 empty] | 10 MW load interrup.
23:43 | 01:25 | Jamalpur 132/33kV S/S T-1 HT Forced S/D Due to 33 kV switching-01 feeder 33kv bus to D.S Loop replace work due to red hot.
23:43 | 01:25 | Jamalpur 132/33kV S/S T-1 LT Forced S/D Due to 33 kV switching-01 feeder 33kv bus to D.S Loop replace work due to red hot.
23:43 | 01:25 | Jamalpur 132/33kV S/S T-2 LT Forced S/D Due to 33 kV switching-01 feeder 33kv bus to D.S Loop replace work due to red hot.
01:10 |  | Meghnaghat Summit CCPP 305MW GT2 was forced shutdown. | [5 empty] | 20 MW load interrup.
01:23 |  | Tongi 230/132/33kV S/S T-02 HT Tripped .
01:23 |  | Tongi 230/132/33kV S/S T-02 LT Tripped showing Earth fault protection low voltage side Backup protection trip
circuit -2 supervision relays Due to Tripped .
05:27 | 07:50 | Ghorasal-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Shutdown taken by Ghorashal
substation with concern NLDC.
07:10 |  | Bakulia-Khulshi 132 kV Ckt-1 Tripped from Khulshi 132/33kV end showing Micom(Dist.Relay) relays Due to Fault at Bph.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-05-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 120 | 2913156 | Gas shortage
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 22 | 524818 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 390 | 9584640
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 276 | 7090000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 330 | 8650500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 57 | 807360 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 213 | 6490851 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 65 | 1279268 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 391658 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 353304 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 60 | 873600 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 90 | 3555802 | ST under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 83 | 917136 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 291240 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2078880
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 645923
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 634358 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1140420 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 749880
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 14 | 480000 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 41 | 561600 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 3535309 | Machine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 295 | 4339111
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 80 | 1477882 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 79 | 1418407 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 114 | 1441584 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 2093827 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 835200 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 1121760 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 238027
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 34 | 541080 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 3336 | 71340581
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 617214
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 140265
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 458880 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 322740 | Low Water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 223 | 5210551
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 69 | 1088109
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 54 | 1084224 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1208208 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 417240 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 438720 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 10 | 235776 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 298560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 29 | 207360 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34680
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 279 | 2697273 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 379600 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 105 | 1808210 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 447360 | Engine problem
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 51 | 672436 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 144 | 1753018
| Chattogram area Total |  |  |  | 2382 | 1350 | 22320424
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 4922000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 8211900 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7774000 | FGMO
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 41 | 900936 | Machine problem
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 0 | Contract Expired
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 189 | 4533090
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 957178 | Machine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 152 | 1093963
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 870928 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 70 | 979680 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 406152 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 7 | 167040 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 3688320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 24 | 693600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 50 | 1107110
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 459040 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 574560
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 970200 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 588600 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 54 | 1109760 | Fuel shortage
| Cumilla Area Total |  |  |  | 3151 | 1919 | 40008057
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 86 | 1198080 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 231372 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12300
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 93 | 1423200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 99 | 1496400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 308910
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 12 | 242880 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 308 | 4913142
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1006000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 28 | 665160 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1248600
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 46 | 1091016
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 5 | 111856
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1316832
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1920000
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 207 | 4136440
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 402000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 346368 | Engine problem
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 6849000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 364 | 9168000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245700
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8978800
| Sylhet Area Total |  |  |  | 2427 | 1612 | 37485772
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 804 | 21498181
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 68 | 1040640 | Engine problem
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 463680 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 80 | 1203072 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 32 | 434250
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 584640 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2506032
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 714240
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 153138 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  | 3001 | 1150 | 28597873
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 392928 | Fuel shortage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 690663 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 89 | 3252839 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31518700
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 0 | 0 | Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1351200
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1533 | 37206330
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 28 | 676768 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 343665 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 21 | 491960 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 912626 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 623490 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 173 | 4519709 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 142 | 3544682 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 401 | 8992582 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 643728 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 423360
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 157284 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 29246 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 82 | 1409176 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 815136 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 55 | 810816 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33840
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 710 | 18060000 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 1837 | 42488068
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1746327
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 260 | 6118500
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 49 | 804124 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 58205
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 72 | 1173120 | Fuel shortage
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 231959
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1283500
| Rangpur Area Total |  |  |  | 750 | 456 | 11415735
| Total |  |  |  | 22566 | 13501 | 295775982
| Eastern Grid Total |  |  |  | 14421 | 8525 | 176067976
| Western Grid Total |  |  |  | 8145 | 4976 | 119708006
| National Grid Total |  |  |  | 22566 | 13501 | 295775982
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-05-11
| (a) ENTIRE EASTERN GRID : |  | 8573.26 | MW | (b) ENTIRE WESTERN GRID : |  | 4270.54 | MW
| i) Dhaka area |  | 5076.46 | MW | i) Khulna area |  | 1658 | MW
| ii) Chittagong area |  | 1248.8 | MW | ii) Rajshahi area |  | 1257 | MW
| iii) Comilla area |  | 1204 | MW | iii) Barisal area |  | 476.54 | MW
| iv) Mymensingh area |  | 657 | MW | iv) Rangpur area |  | 879 | MW
| v) Sylhet area |  | 387 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 12843.8 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 7 | 13:00 | Chhatak | 20 | 11:00 | Kamrangirchar | 57 | 13:00 | Natore | 146 | 22:00 | Shitalakhya | 128 | 16:00
2 | AKSML | 7.6 | 22:00 | Chowmuhani | 186 | 22:00 | Kaptai | 4.8 | 19:00 | Nawabganj | 50.4 | 22:00 | Sholosohor | 30 | 19:00
3 | Aftabnagar | 62 | 17:00 | Chuadanga | 98 | 21:00 | Kazla | 97 | 12:00 | Netrakona | 90 | 00:00 | Shyampur | 178 | 10:00
4 | Agargaon | 96 | 15:00 | Coxsbazar | 122 | 18:30 | Keranigonj | 70 | 19:30 | New | 87 | 12:00 | Siddhirganj | 114 | 19:00
5 | Agrabad | 84 | 18:00 | Cumilla(N) | 205 | 19:30 | Khagrachori | 28 | 19:30 | Niamatpur | 92 | 22:00 | Sirajganj | 96 | 21:00
6 | Amnura | 60 | 21:00 | Cumilla(S) | 182 | 01:00 | Khulna | 105 | 20:00 | Noapara | 41 | 23:00 | Sonargaon | 91 | 21:00
7 | Ashuganj | 81 | 23:00 | Daudkandi | 152 | 19:30 | Khulshi | 179 | 18:30 | PHP | 5 | 19:30 | Sreemongol | 69 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 40 | 11:00 | Kishoreganj | 90 | 12:00 | Pabna | 106 | 19:00 | Sreepur | 66.1 | 12:00
9 | BSRM | 112 | 15:00 | Dhamrai | 110 | 18:00 | Kodda | 319 | 19:30 | Palashbari | 121 | 20:00 | Srinagar | 47.6 | 20:00
10 | Bagerhat | 103 | 22:00 | Dhanmondi | 161 | 13:00 | Kulaura | 50 | 19:00 | Panchagarh | 59 | 20:00 | Sunamganj | 34 | 00:00
11 | Bakulia | 111 | 18:00 | Dohazari | 86 | 21:00 | Kurigram | 60 | 20:00 | Patuakhali | 117 | 22:00 | Sylhet | 153 | 17:00
12 | Banani | 86 | 15:00 | Faridpur | 148 | 21:00 | Kushtia | 118 | 21:00 | Payra | 22 | 22:00 | TK | 30.6 | 23:00
13 | Bangabhaban | 24 | 10:00 | Fatullah | 73 | 15:00 | Lalbag | 81 | 13:00 | Postogola | 61 | 19:00 | Tangail | 198 | 12:00
14 | Barapukuria | 63 | 21:00 | Fenchuganj | 49 | 18:30 | Lalmonirhat | 47 | 20:00 | Purbachal | 22 | 15:00 | Thakurgaon | 93 | 20:00
15 | Barguna | 22 | 21:00 | Feni | 129 | 19:30 | Madanganj | 46 | 18:30 | Purbasadipur | 131 | 20:00 | Tongi | 105 | 00:00
16 | Barishal | 115 | 18:30 | GPH | 76 | 19:30 | Madaripur | 112 | 22:00 | Rahanpur_I | 0 | 00:00 | Ullon | 45 | 00:00
17 | Barishal-230 | 104 | 19:30 | Ghorashal | 78 | 00:00 | Madartek | 92 | 00:00 | Rahim | 45 | 10:00 | Uttara | 80 | 16:00
18 | Baroaulia | 70 | 12:00 | Goalpara | 38 | 23:00 | Madunaghat | 54 | 18:30 | Rajbari | 66 | 23:00 | UttaraNew | 58 | 14:00
19 | Baroirhat | 69 | 20:00 | Gollamari | 56 | 22:00 | Magura | 56 | 21:00 | Rajendrapur | 86 | 21:00 | Zigatola | 88 | 15:00
20 | Bashundhara | 194 | 15:00 | Gopalganj | 105.4 | 22:00 | Mahasthangarh | 58 | 04:00 | Rajshahi | 164 | 22:00
21 | BashundharaCement | 6 | 11:00 | Gulshan | 84 | 13:00 | Manikganj | 117 | 22:00 | Rajshahi-230 | 37 | 21:00
22 | Beanibazar | 62 | 18:30 | Halishahar | 90.5 | 11:00 | Maniknagar | 102 | 15:00 | Ramganj | 132 | 19:30
23 | Benapole | 64 | 20:00 | HaripurSBU | 158 | 21:00 | Matarbari | 38 | 00:00 | Rampur | 35 | 21:00
24 | Bhaluka | 148 | 16:00 | Hasnabad | 101 | 20:00 | Matuail | 74 | 13:00 | Rangamati | 12 | 22:00
25 | Bhandaria | 53 | 22:00 | Hathazari | 76 | 18:30 | Millgate | 106 | 12:00 | Rangpur | 155 | 20:00
26 | Bhangura | 42 | 08:00 | Ishurdi | 57 | 21:00 | Mirpur | 164 | 15:00 | Ruppur | 6.4 | 16:00
27 | Bheramara(GK) | 59 | 23:00 | Jaldhaka | 74 | 20:00 | Mirsorai | 6 | 19:00 | SSM | 16 | 11:00
28 | Bhulta | 252 | 23:00 | Jamalpur | 114 | 12:00 | Mithapukur | 38 | 20:00 | Saidpur | 109 | 20:00
29 | Bog-Sherpur | 54 | 05:00 | Jashore | 126 | 12:00 | Modern | 0 | 00:00 | Satkhira | 141 | 22:00
30 | Bogura | 143 | 04:00 | Jhenaidah | 134 | 19:00 | Mogbazar | 148 | 15:00 | Satmasjid | 128 | 19:00
31 | Borhanuddin | 70 | 01:00 | Joydebpur | 168 | 21:00 | Mongla | 32 | 10:00 | Savar | 198 | 18:00
32 | Brahmanbaria | 188 | 19:30 | Joypurhat | 59 | 19:00 | Motijheel | 47 | 16:00 | Shahjadpur | 99 | 07:00
33 | Cantonment | 150 | 15:00 | Juldah | 28 | 00:00 | Munshiganj | 110 | 23:00 | Shahjibazar | 109 | 13:00
34 | Chandpur | 75 | 19:30 | KSRM | 29 | 10:00 | Mymensingh | 164 | 13:00 | Shahmirpur | 50 | 00:00
35 | Chandraghona | 32 | 21:00 | Kabirpur | 312 | 19:00 | Naogaon | 128 | 22:00 | Shariatpur | 74 | 22:00
36 | Chapai | 70 | 22:00 | Kachua | 91 | 19:30 | Narail | 54 | 22:00 | Sherpur | 100 | 11:00
37 | Charsaidpur | 45 | 00:00 | Kallyanpur | 105 | 22:00 | Narinda | 81 | 13:00 | Shikalbaha | 31 | 23:00
38 | Chauddagram | 71 | 19:30 | Kalurghat | 36 | 19:00 | Narshingdi | 177 | 00:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-05-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 399 | 19:00 | 386 | 12:00 | Kaliakoir | 385 | 01:00 | 374 | 11:00
| Bhulta | 387 | 21:00 | 370 | 12:00 | Madunaghat_I | 416 | 21:00 | 375 | 09:00
| Bibiana | 406 | 19:00 | 395 | 09:00 | Payra | 412 | 00:00 | 406 | 20:00
| BIPTC | 397 | 06:00 | 39 | 19:30 | Rahanpur_I | 419 | 00:00 | 412 | 04:00
| Gopalganj | 405 | 00:00 | 392 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 255 | 23:00 | 219 | 12:00 | Hathazari | 238 | 21:00 | 217 | 11:00
| AKSML | 236 | 21:00 | 206 | 11:00 | Ishurdi | 233 | 15:00 | 224 | 04:00
| Aminbazar | 232 | 19:00 | 222 | 09:00 | Jhenaidah | 227 | 00:00 | 216 | 12:00
| Ashuganj | 238 | 19:30 | 223 | 12:00 | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 232 | 18:00 | 224 | 12:00 | Keranigonj | 229 | 19:30 | 220 | 09:00
| Barapukuria | 222 | 15:00 | 212 | 20:00 | Khulna(S) | 235 | 00:00 | 222 | 12:00
| Barishal | 239 | 07:00 | 223 | 22:00 | Madunaghat_I | 239 | 21:00 | 217 | 09:00
| Bheramara | 233 | 19:30 | 222 | 01:00 | Maniknagar | 229 | 21:00 | 219 | 09:00
| Bhulta | 231 | 21:00 | 221 | 12:00 | Meghnaghat | 234 | 22:00 | 226 | 11:00
| Bibiana | 240 | 19:30 | 231 | 09:00 | Mirsorai | 239 | 21:00 | 218 | 11:00
| BIPTC | 255 | 11:00 | 221 | 12:00 | Rajshahi | 234 | 16:00 | 222 | 20:00
| Bogura | 226 | 16:00 | 219 | 07:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 13:00 | 230 | 02:00 | Rampura | 229 | 21:00 | 218 | 09:00
| BSRM | 240 | 21:00 | 218 | 11:00 | Shikalbaha | 235 | 19:30 | 218 | 10:00
| Cumilla(N) | 233 | 21:00 | 221 | 09:00 | Shyampur | 229 | 05:00 | 221 | 09:00
| Fenchuganj | 242 | 21:00 | 236 | 01:00 | Siddhirganj | 232 | 21:00 | 223 | 09:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 237 | 16:00 | 232 | 11:00
| GPH | 238 | 21:00 | 218 | 11:00 | Sreepur | 233 | 19:30 | 226 | 12:00
| Haripur | 229 | 21:00 | 219 | 12:00 | Tongi | 228 | 20:00 | 214 | 10:00
| Hasnabad | 230 | 00:00 | 221 | 09:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 136 | 21:00 | 127 | 11:00 | Lalbag | 137 | 03:00 | 130 | 09:00
| Agargaon | 130 | 04:00 | 123 | 12:00 | Lalmonirhat | 130 | 14:00 | 118 | 20:00
| Agrabad | 139 | 19:00 | 125 | 09:00 | Madanganj | 133 | 21:00 | 125 | 09:00
| AKS | 135 | 18:30 | 124 | 10:00 | Madaripur | 130 | 07:00 | 123 | 22:00
| Aminbazar | 132 | 19:00 | 124 | 13:00 | Madartek | 136 | 04:00 | 126 | 12:00
| Amnura | 136 | 17:00 | 128 | 12:00 | Madunaghat | 139 | 19:00 | 128 | 11:00
| Ashuganj | 139 | 19:30 | 133 | 11:00 | Magura | 133 | 00:00 | 122 | 20:00
| Bagerhat | 135 | 00:00 | 123 | 06:00 | Mahasthangarh | 134 | 00:00 | 126 | 06:00
| Bakulia | 139 | 19:30 | 127 | 11:00 | Manikganj | 136 | 18:00 | 125 | 23:00
| Banani | 139 | 19:30 | 125 | 12:00 | Maniknagar | 132 | 03:00 | 124 | 11:00
| Bangabhaban | 131 | 03:00 | 124 | 11:00 | Matarbari | 130 | 20:00 | 113 | 18:30
| Barapukuria | 137 | 15:00 | 128 | 21:00 | Matuail | 133 | 21:00 | 127 | 09:00
| Barguna | 138 | 18:00 | 131 | 14:00 | Millgate | 130 | 19:00 | 121 | 12:00
| Barishal | 138 | 18:00 | 120 | 23:00 | Mirpur | 129 | 19:30 | 122 | 12:00
| Barishal-230 | 132 | 07:00 | 122 | 22:00 | Mithapukur | 132 | 16:00 | 121 | 20:00
| Baroaulia | 139 | 19:00 | 126 | 09:00 | Modern | 139 | 21:00 | 126 | 11:00
| Baroirhat | 135 | 19:00 | 122 | 09:00 | Mogbazar | 136 | 00:00 | 128 | 12:00
| Bashundhara | 130 | 22:00 | 120 | 12:00 | Mongla | 133 | 03:00 | 123 | 20:00
| BashundharaCement | 133 | 21:00 | 125 | 09:00 | Motijheel | 131 | 05:00 | 124 | 11:00
| Beanibazar | 135 | 20:00 | 128 | 18:00 | Munshiganj | 132 | 19:30 | 126 | 09:00
| Benapole | 132 | 19:30 | 120 | 12:00 | Mymensingh | 136 | 17:00 | 108 | 11:00
| Bhaluka | 135 | 17:00 | 112 | 12:00 | Naogaon | 131 | 18:00 | 123 | 06:00
| Bhandaria | 135 | 16:00 | 125 | 05:00 | Narail | 133 | 16:00 | 123 | 20:00
| Bhangura | 136 | 18:00 | 131 | 03:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 131 | 16:00 | 126 | 01:00 | Narshingdi | 129 | 18:30 | 121 | 09:00
| Bheramara(GK) | 131 | 07:00 | 126 | 01:00 | Natore | 132 | 16:00 | 126 | 03:00
| Bhulta | 124 | 03:00 | 118 | 09:00 | Nawabganj | 136 | 00:00 | 131 | 09:00
| Bog-Sherpur | 134 | 16:00 | 129 | 03:00 | Netrakona | 134 | 18:00 | 116 | 12:00
| Bogura | 138 | 23:00 | 129 | 12:00 | New | 130 | 05:00 | 121 | 12:00
| Bogura-230 | 136 | 15:00 | 130 | 01:00 | Niamatpur | 130 | 03:00 | 118 | 13:00
| Brahmanbaria | 134 | 18:30 | 128 | 11:00 | Noapara | 134 | 16:00 | 125 | 20:00
| Cantonment | 130 | 03:00 | 123 | 12:00 | Pabna | 133 | 19:30 | 126 | 03:00
| Chandpur | 135 | 21:00 | 118 | 09:00 | Palashbari | 131 | 16:00 | 121 | 20:00
| Chandraghona | 139 | 19:00 | 127 | 09:00 | Panchagarh | 136 | 18:00 | 119 | 20:00
| Chapai | 134 | 00:00 | 130 | 23:00 | Patuakhali | 138 | 02:00 | 134 | 13:00
| Charsaidpur | 134 | 21:00 | 128 | 09:00 | Payra | 140 | 18:00 | 136 | 12:00
| Chauddagram | 135 | 21:00 | 121 | 09:00 | PHP | 136 | 21:00 | 122 | 03:00
| Chhatak | 134 | 19:00 | 129 | 07:00 | Postogola | 133 | 19:00 | 126 | 08:00
| Chowmuhani | 133 | 21:00 | 119 | 02:00 | Purbachal | 128 | 04:00 | 120 | 12:00
| Chuadanga | 129 | 16:00 | 118 | 12:00 | Purbasadipur | 137 | 04:00 | 117 | 20:00
| Coxsbazar | 129 | 19:00 | 111 | 18:30 | Rahim | 134 | 21:00 | 128 | 09:00
| Cumilla(N) | 137 | 21:00 | 127 | 08:00 | Rajbari | 128 | 07:00 | 122 | 22:00
| Cumilla(S) | 137 | 21:00 | 124 | 09:00 | Rajendrapur | 138 | 19:30 | 130 | 02:00
| Daudkandi | 133 | 21:00 | 125 | 12:00 | Rajshahi | 133 | 16:00 | 126 | 12:00
| Dhaka | 136 | 03:00 | 127 | 11:00 | Rajshahi-230 | 132 | 16:00 | 126 | 12:00
| Dhamrai | 133 | 19:30 | 127 | 11:00 | Ramganj | 134 | 21:00 | 116 | 07:00
| Dhanmondi | 133 | 21:00 | 126 | 12:00 | Rampur | 138 | 20:00 | 125 | 11:00
| Dohazari | 137 | 19:00 | 123 | 11:00 | Rampura | 136 | 03:00 | 127 | 11:00
| Faridpur | 129 | 16:00 | 124 | 12:00 | Rangamati | 137 | 19:00 | 126 | 12:00
| Fatullah | 134 | 21:00 | 126 | 09:00 | Rangpur | 133 | 16:00 | 120 | 20:00
| Fenchuganj | 138 | 20:00 | 134 | 01:00 | Ruppur | 133 | 16:00 | 127 | 12:00
| Feni | 137 | 21:00 | 122 | 06:00 | Saidpur | 131 | 15:00 | 119 | 21:00
| Ghorashal | 139 | 18:00 | 131 | 04:00 | Satkhira | 133 | 00:00 | 120 | 20:00
| Goalpara | 138 | 00:00 | 127 | 20:00 | Satmasjid | 130 | 04:00 | 123 | 12:00
| Gollamari | 133 | 07:00 | 126 | 12:00 | Savar | 130 | 19:00 | 122 | 09:00
| Gopalganj | 133 | 00:00 | 127 | 12:00 | Shahjadpur | 140 | 19:00 | 135 | 01:00
| Gopalganj-400 | 130 | 00:00 | 125 | 22:00 | Shahjibazar | 134 | 03:00 | 130 | 11:00
| Gulshan | 135 | 04:00 | 127 | 11:00 | Shahmirpur | 139 | 19:00 | 127 | 11:00
| Halishahar | 138 | 19:00 | 125 | 09:00 | Shariatpur | 129 | 08:00 | 122 | 20:00
| Haripur | 134 | 21:00 | 128 | 09:00 | Sherpur | 140 | 17:00 | 117 | 12:00
| HaripurSBU | 137 | 02:00 | 128 | 09:00 | Shikalbaha | 141 | 19:00 | 129 | 11:00
| Hasnabad | 133 | 21:00 | 129 | 16:00 | Shikalbaha-230 | 140 | 19:30 | 128 | 12:00
| Hathazari | 139 | 21:00 | 128 | 09:00 | Shitalakhya | 133 | 22:00 | 126 | 09:00
| Ishurdi | 134 | 18:00 | 128 | 01:00 | Sholosohor | 139 | 21:00 | 126 | 11:00
| Jaldhaka | 131 | 18:00 | 117 | 20:00 | Shyampur | 133 | 20:00 | 125 | 09:00
| Jamalpur | 140 | 17:00 | 120 | 06:00 | Shyampur-230 | 133 | 20:00 | 125 | 09:00
| Jashore | 131 | 00:00 | 122 | 12:00 | Siddhirganj | 133 | 21:00 | 127 | 09:00
| Jhenaidah | 134 | 00:00 | 125 | 20:00 | Sirajganj | 136 | 18:00 | 128 | 10:00
| Jhenaidah-230 | 134 | 00:00 | 126 | 12:00 | Sonargaon | 133 | 21:00 | 126 | 07:00
| Joydebpur | 140 | 19:00 | 132 | 11:00 | Sreemongol | 136 | 19:30 | 129 | 12:00
| Joypurhat | 129 | 23:00 | 119 | 03:00 | Sreepur | 132 | 19:30 | 128 | 10:00
| Juldah | 140 | 21:00 | 126 | 11:00 | Srinagar | 138 | 09:00 | 130 | 09:00
| Kabirpur | 139 | 19:30 | 118 | 12:00 | SSM | 143 | 01:00 | 130 | 07:00
| Kachua | 135 | 21:00 | 120 | 09:00 | Sunamganj | 132 | 19:00 | 126 | 12:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 133 | 19:00 | 130 | 11:00
| Kallyanpur | 131 | 02:00 | 125 | 12:00 | Tangail | 137 | 18:00 | 123 | 12:00
| Kalurghat | 140 | 21:00 | 126 | 11:00 | Thakurgaon | 135 | 18:00 | 117 | 21:00
| Kamrangirchar | 129 | 07:00 | 123 | 12:00 | TK | 140 | 21:00 | 128 | 09:00
| Kaptai | 136 | 21:00 | 125 | 09:00 | Tongi | 132 | 01:00 | 124 | 10:00
| Kazla | 131 | 08:00 | 125 | 14:00 | Ullon | 136 | 23:00 | 126 | 12:00
| Keranigonj | 137 | 02:00 | 130 | 09:00 | Uttara | 130 | 19:30 | 121 | 12:00
| Khagrachori | 136 | 19:30 | 126 | 12:00 | UttaraNew | 129 | 19:30 | 122 | 09:00
| Khulna | 135 | 00:00 | 129 | 20:00 | Zigatola | 138 | 22:00 | 130 | 10:00
| Khulna(S) | 138 | 00:00 | 129 | 06:00
| Khulshi | 138 | 19:00 | 125 | 09:00
| Kishoreganj | 135 | 18:00 | 118 | 11:00
| Kodda | 140 | 18:00 | 128 | 23:00
| KSRM | 139 | 21:00 | 125 | 11:00
| Kulaura | 138 | 20:00 | 132 | 12:00
| Kurigram | 132 | 18:00 | 117 | 20:00
| Kushtia | 132 | 16:00 | 125 | 04:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-05-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 990 | 7525 | 4935 | 12460 |  |  |  | QF-LDC-11
0:30 | 940 | 7437.5 | 4904.5 | 12342 | Date: | 2023-05-11
1:00 | 890 | 7350 | 4874 | 12224
1:30 | 875 | 7270 | 4824.5 | 12094.5
2:00 | 860 | 7190 | 4775 | 11965
2:30 | 850 | 7148.5 | 4776 | 11924.5 | [5 empty] | Gen. at Eve. Peak | 13501 | 13501 MW (21:00 )
3:00 | 840 | 7107 | 4777 | 11884 | [6 empty] | 21:00
3:30 | 825 | 7084.5 | 4784 | 11868.5 | [5 empty] | Gen. at Day Peak | 12836 | 12836 MW (12:00 )
4:00 | 810 | 7062 | 4791 | 11853 | [6 empty] | 12:00
4:30 | 830 | 7008 | 4769 | 11777 | [5 empty] | Highest Generation | 13501
5:00 | 850 | 6954 | 4747 | 11701 | [6 empty] | 21:00
5:30 | 850 | 6819 | 4729.5 | 11548.5
6:00 | 850 | 6684 | 4712 | 11396
6:30 | 950 | 6615 | 4767 | 11382
7:00 | 1050 | 6546 | 4822 | 11368
7:30 | 1108 | 6568.5 | 4847 | 11415.5
8:00 | 1166 | 6591 | 4872 | 11463
8:30 | 1218 | 6616.5 | 4910.5 | 11527
9:00 | 1270 | 6642 | 4949 | 11591
9:30 | 1285 | 6949.5 | 5015 | 11964.5
10:00 | 1300 | 7257 | 5081 | 12338
10:30 | 1215 | 7450.5 | 5085 | 12535.5
11:00 | 1130 | 7644 | 5089 | 12733
11:30 | 1105 | 7664.5 | 5120 | 12784.5
12:00 | 1080 | 7685 | 5151 | 12836
12:30 | 1120 | 7711 | 5125 | 12836
13:00 | 1160 | 7737 | 5099 | 12836
13:30 | 1170 | 7589 | 4977 | 12566
14:00 | 1180 | 7441 | 4855 | 12296
14:30 | 1225 | 7405.5 | 4828.5 | 12234
15:00 | 1270 | 7370 | 4802 | 12172
15:30 | 1305 | 7184 | 4819 | 12003
16:00 | 1340 | 6998 | 4836 | 11834
16:30 | 1255 | 6955.5 | 4823.5 | 11779
17:00 | 1170 | 6913 | 4811 | 11724
17:30 | 1097 | 6949 | 4756 | 11705
18:00 | 1024 | 6985 | 4701 | 11686
18:30 | 812 | 7528.5 | 4787 | 12315.5
19:00 | 600 | 8072 | 4873 | 12945
19:30 | 540 | 8084 | 4954 | 13038
20:00 | 280 | 8213 | 4906 | 13119 |  |  |  | Executive Engineer
20:30 | 315 | 8369 | 4941 | 13310 |  |  |  | Network Operation Division
21:00 | 350 | 8525 | 4976 | 13501
21:30 | 450 | 8465.5 | 4994.5 | 13460
22:00 | 550 | 8406 | 5013 | 13419 |  |  |  |  | Page 6 of 7
22:30 | 675 | 8304.5 | 4981 | 13285.5
23:00 | 800 | 8203 | 4949 | 13152
23:30 | 895 | 7864 | 4942 | 12806
24:00 | 990 | 7525 | 4935 | 12460
13501 MW (21:00 )
12836 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-05-11 |  | Energy |  | 295775982
[13 empty] | 2023-05-11 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3911 | 804 | 2023 | 457 | 2065 | 2415 | 0 | 0 | 637 | 148 | 0 | 0
0:30 | 3993.5 | 833 | 2161.5 | 456.5 | 1717.5 | 2413.5 | 0 | 0 | 601.5 | 165 | 0 | 791.2175 |  | Date: | 43595
1:00 | 4076 | 862 | 2300 | 456 | 1370 | 2412 | 0 | 0 | 566 | 182 | 0 | 1582.435
1:30 | 4048 | 862.5 | 2307.5 | 456 | 1329 | 2353 | 0 | 0 | 559.5 | 179 | 0 | 1559.515 | [7 empty] | Total Energy | 295.776 |  | Total Energy Gen MKWHr Energy Not Served MKWHr Energy Requirement MKWHr | Total Energy Gen 295.776 MKWHr Energy Not Served 27.534 MKWHr Energy Requirement 323.310 MKWHr
2:00 | 4020 | 863 | 2315 | 456 | 1288 | 2294 | 0 | 0 | 553 | 176 | 0 | 1536.595 | [7 empty] | Energy not Served | 27.5337
2:30 | 4008 | 891 | 2314 | 456.5 | 1244.5 | 2306 | 0 | 0 | 529.5 | 175 | 0 | 1491.2325 | [7 empty] | Energy Requirement | 323.3097
3:00 | 3996 | 919 | 2313 | 457 | 1201 | 2318 | 0 | 0 | 506 | 174 | 0 | 1445.87
3:30 | 3998 | 919.5 | 2318 | 436.5 | 1197 | 2322 | 0 | 0 | 504.5 | 173 | 0 | 1386.1825
4:00 | 4000 | 920 | 2323 | 416 | 1193 | 2326 | 0 | 0 | 503 | 172 | 0 | 1326.495
4:30 | 4004 | 920 | 2322.5 | 386 | 1176.5 | 2327.5 | 0 | 0 | 469.5 | 171 | 0 | 1281.1325
5:00 | 4008 | 920 | 2322 | 356 | 1160 | 2329 | 0 | 0 | 436 | 170 | 0 | 1235.77
5:30 | 4066.5 | 920 | 2317.5 | 178 | 1133 | 2320 | 0 | 0 | 438.5 | 165 | 10 | 1167.4875
6:00 | 4125 | 920 | 2313 | 0 | 1106 | 2311 | 0 | 0 | 441 | 160 | 20 | 1099.205
6:30 | 4035 | 920 | 2313 | 0 | 1144 | 2324 | 0 | 0 | 435 | 158 | 53 | 1124.99 | [6 empty] | Coal
7:00 | 3945 | 920 | 2313 | 0 | 1182 | 2337 | 0 | 0 | 429 | 156 | 86 | 1150.775
7:30 | 3965 | 920 | 2250 | 0 | 1247 | 2317 | 0 | 0 | 420 | 156 | 140.5 | 1088.7 | [5 empty] | Oil
8:00 | 3985 | 920 | 2187 | 0 | 1312 | 2297 | 0 | 0 | 411 | 156 | 195 | 1026.625
8:30 | 3999.5 | 920.5 | 2183 | 0 | 1326.5 | 2308.5 | 0 | 0 | 400.5 | 153 | 235.5 | 1042.86
9:00 | 4014 | 921 | 2179 | 0 | 1341 | 2320 | 0 | 0 | 390 | 150 | 276 | 1059.095
9:30 | 3963 | 918.5 | 2138.5 | 180.5 | 1539 | 2342 | 9 | 0 | 394.5 | 154 | 325.5 | 988.9025
10:00 | 3912 | 916 | 2098 | 361 | 1737 | 2364 | 18 | 0 | 399 | 158 | 375 | 918.71
10:30 | 3947.5 | 916.5 | 2085 | 405 | 1881.5 | 2309.5 | 21.5 | 0 | 412 | 159 | 398 | 897.2225
11:00 | 3983 | 917 | 2072 | 449 | 2026 | 2255 | 25 | 0 | 425 | 160 | 421 | 875.735
11:30 | 3962.5 | 917 | 2050.5 | 452.5 | 2082.5 | 2288.5 | 25 | 0 | 423 | 158 | 425 | 945.9275
12:00 | 3942 | 917 | 2029 | 456 | 2139 | 2322 | 25 | 0 | 421 | 156 | 429 | 1016.12
12:30 | 3935 | 915.5 | 2022.5 | 453.5 | 2182 | 2316 | 25 | 0 | 427 | 159 | 400.5 | 1226.22
13:00 | 3928 | 914 | 2016 | 451 | 2225 | 2310 | 25 | 0 | 433 | 162 | 372 | 1436.32
13:30 | 3928 | 914 | 2016 | 451 | 2225 | 2310 | 25 | 0 | 433 | 162 | 372 | 1436.32
14:00 | 3928 | 914 | 2016 | 451 | 2225 | 2310 | 25 | 0 | 433 | 162 | 372 | 1436.32
14:30 | 3853 | 914.5 | 1980.5 | 450.5 | 2020.5 | 2310.5 | 25 | 12.5 | 464 | 160 | 313 | 1638.78
15:00 | 3778 | 915 | 1945 | 450 | 1816 | 2311 | 25 | 25 | 495 | 158 | 254 | 1841.24
15:30 | 3772.5 | 914.5 | 1946.5 | 322 | 1808.5 | 2304 | 25 | 52.5 | 499.5 | 145 | 213 | 1811.635
16:00 | 3767 | 914 | 1948 | 194 | 1801 | 2297 | 25 | 80 | 504 | 132 | 172 | 1782.03
16:30 | 3730.5 | 914 | 1955 | 168 | 1827 | 2291 | 25 | 100 | 511.5 | 132 | 125 | 1739.055
17:00 | 3694 | 914 | 1962 | 142 | 1853 | 2285 | 25 | 120 | 519 | 132 | 78 | 1696.08 | [9 empty] | 472
17:30 | 3673.5 | 914 | 1956.5 | 96 | 2004 | 2250.5 | 25 | 60 | 544.5 | 134 | 47 | 1404.04 | [9 empty] | 100
18:00 | 3653 | 914 | 1951 | 50 | 2155 | 2216 | 25 | 0 | 570 | 136 | 16 | 1112 | [9 empty] | 20
18:30 | 3653 | 914 | 1985 | 154.5 | 2608.5 | 2200.5 | 25 | 0 | 630 | 137 | 8 | 1155.2625 | [9 empty] | 592
19:00 | 3653 | 914 | 2019 | 259 | 3062 | 2185 | 25 | 0 | 690 | 138 | 0 | 1198.525
19:30 | 3576 | 914 | 1908 | 206 | 3288 | 2275 | 25 | 0 | 714 | 132 | 0 | 1019.94
20:00 | 3677 | 804 | 1910 | 169 | 3348 | 2303 | 25 | 0 | 755 | 128 | 0 | 841.355
20:30 | 3747 | 804 | 1966 | 311.5 | 3265 | 2296 | 25 | 0 | 761.5 | 134 | 0 | 802.2
21:00 | 3817 | 804 | 2022 | 454 | 3182 | 2289 | 25 | 0 | 768 | 140 | 0 | 763.045
21:30 | 3836 | 804 | 2012 | 453.5 | 3106.5 | 2315 | 25 | 0 | 768 | 140 | 0 | 706.7
22:00 | 3855 | 804 | 2002 | 453 | 3031 | 2341 | 25 | 0 | 768 | 140 | 0 | 650.355
22:30 | 3944.5 | 803.5 | 2016 | 453 | 2820 | 2349 | 12.5 | 0 | 743 | 144 | 0 | 706.2225
23:00 | 4034 | 803 | 2030 | 453 | 2609 | 2357 | 0 | 0 | 718 | 148 | 0 | 762.09
23:30 | 3972.5 | 803.5 | 2026.5 | 455 | 2337 | 2386 | 0 | 0 | 677.5 | 148 | 0 | 973.145 |  | Max Temp. in Dhaka |  | 38.4° C
24:00 | 3911 | 804 | 2023 | 457 | 2065 | 2415 | 0 | 0 | 637 | 148 | 0 | 1184.2
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 295.776 MKWHr Energy Not Served 27.534 MKWHr Energy Requirement 323.310 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-05-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [9 empty] | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 322740
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 617214
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 9 | 14 | 10 | 18 | 19 | 18 | 16 | 13 | 8 | 3 | 0 | [8 empty] | 140265
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 225 | 225 | 228 | 224 | 226 | 221 | 223 | 220 | 218 | 214 | 215 | 210 | 215 | 217 | 223 | 223 |  | 225 | 223 | 221 | 223 | 222 | 222 | 225 | 5210551
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 66 | 66 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 30 | 65 | 65 | 65 | 66 | 66 |  | 68 | 68 | 68 | 68 | 67 | 67 | 67 | 1208208
12 | Hathazari 100 MW peaking PP | 45 | 45 | 45 | 45 | 45 | 45 | 37 | 38 | 38 | 38 | 38 | 30 | 32 | 54 | 50 | 50 | 50 | 54 |  | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 1084224
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 55 | 34 | 34 | 34 | 34 | 20 | 20 | 17 | 17 | 20 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 69 | 69 | 69 | 62 | 62 | 1088109
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 36 | 36 | 36 | 37 | 37 | 37 | 38 | 37 | 36 | 37 | 37 | 37 | 34 | 40 | 39 | 30 | 24 | 25 |  | 34 | 35 | 35 | 41 | 41 | 45 | 45 | 870928
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 170 | 166 | 158 | 149 | 152 | 166 | 170 | 196 | 190 | 180 | 185 | 180 | 170 | 165 | 150 | 145 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 140 | 142 | 3555802
18 | Kodda 300 MW PP Unit-2 (Summit) | 130 | 115 | 105 | 97 | 98 | 98 | 98 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 120 |  | 275 | 280 | 280 | 280 | 282 | 295 | 295 | 3535309
19 | Ashuganj 195MW PP (APSCL-United) | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 187 | 187 | 185 | 185 | 185 | 183 | 184 | 184 | 185 |  | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 4533090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 120 | 120 | 120 | 120 | 120 | 121 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2913156
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 40 | 40 | 40 | 40 | 40 | 43 | 42 | 39 | 37 | 38 | 36 | 36 | 34 | 32 | 32 | 32 | 33 | 33 |  | 39 | 40 | 41 | 41 | 41 | 41 | 42 | 900936
33 | Ashuganj 225 MW CCPP | 210 | 210 | 210 | 210 | 209 | 207 | 208 | 193 | 207 | 182 | 196 | 197 | 198 | 196 | 196 | 197 | 203 | 204 |  | 209 | 209 | 207 | 211 | 211 | 207 | 211 | 4922000
34 | Ashuganj 450 MW CCPP(South) | 325 | 310 | 305 | 300 | 310 | 345 | 305 | 320 | 325 | 305 | 320 | 310 | 320 | 310 | 320 | 310 | 305 | 305 |  | 305 | 305 | 305 | 305 | 300 | 340 | 305 | 7774000
| Ashuganj 450 MW CCPP(North) | 330 | 315 | 310 | 310 | 315 | 350 | 310 | 325 | 330 | 310 | 325 | 330 | 335 | 325 | 330 | 320 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 350 | 310 | 8211900
Ashuganj 420 MW CCPP(East)
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 405 | 405 | 405 | 404 | 397 | 398 | 399 | 396 | 400 | 400 | 404 | 400 | 397 | 395 | 395 | 397 | 400 | 366 |  | 350 | 345 | 357 | 390 | 399 | 398 | 397 | 9584640
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 410 | 400 | 400 | 400 | 380 | 370 | 360 | 360 | 350 | 350 |  | 350 | 340 | 340 | 330 | 330 | 330 | 330 | 8650500
41 | Haripur 360MW CCPP(HPL) | 340 | 340 | 340 | 340 | 340 | 340 | 335 | 310 | 301 | 271 | 273 | 252 | 277 | 263 | 254 | 248 | 260 | 293 |  | 293 | 264 | 264 | 276 | 273 | 283 | 284 | 7090000
42 | RPCL 210MW CCPP | 80 | 80 | 80 | 80 | 80 | 69 | 33 | 31 | 28 | 29 | 28 | 28 | 26 | 26 | 31 | 33 | 34 | 35 |  | 50 | 60 | 58 | 86 | 85 | 85 | 85 | 1198080
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 10 | 20 | 34 | 41 | 47 | 47 | 45 | 32 | 12 | 1 | 0 | [9 empty] | 308910
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 41 | 41 | 42 | 41 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1006000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 30 | 665160
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 57 | 57 | 56 | 28 | 58 | 58 | 58 | 55 | 48 | 53 | 53 | 54 | 54 | 58 | 58 |  | 60 | 60 | 59 | 59 | 59 | 59 | 60 | 1316832
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 83 | 83 | 83 | 83 | 83 | 80 | 80 | 80 | 80 | 78 | 78 | 76 | 75 | 75 | 76 | 80 | 77 |  | 82 | 82 | 83 | 83 | 83 | 83 | 83 | 1920000
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 200 | 201 | 200 | 200 | 200 | 204 | 203 | 203 | 206 | 206 | 206 | 204 | 202 | 201 | 201 | 201 | 198 | 198 |  | 193 | 200 | 207 | 207 | 207 | 209 | 208 | 4136440
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 402000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 7 | 7 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 245700
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 111856
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 47 | 50 | 52 | 49 | 49 | 49 | 53 | 52 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1248600
56 | Shahjahanulla 25 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 13 | 16 | 16 | 16 | 16 | 16 | 16 | 346368
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 285 | 280 | 280 | 280 | 285 | 280 | 285 | 285 | 280 | 280 | 290 | 285 | 290 | 290 | 290 | 280 |  | 275 | 265 | 265 | 280 | 275 | 280 | 275 | 6849000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 398 | 400 | 398 | 391 | 391 | 381 | 377 | 370 | 362 | 343 | 360 | 330 | 360 |  | 370 | 340 | 400 | 400 | 400 | 400 | 400 | 8978800
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 634358
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 9 | 12 | 10 | 6 | 11 | 12 | 12 | 14 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 242880
60 | Barabkunda 22 MW PP (Regent) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 235776
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 0 | 0 | 22 | 22 |  | 0 |  |  | 0 | 22 | 22 | 22 | 353304
62 | Tangail 22 MW PP (Doreen) | 12 | [9 empty] | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 231372
63 | Impoprt (Tripura) | 182 | 176 | 174 | 172 | 170 | 160 | 156 | 156 | 150 | 158 | 160 | 156 | 162 | 154 | 158 | 132 | 132 | 136 |  | 138 | 132 | 128 | 140 | 140 | 148 | 148 | 3688320
64 | Malancha, Ctg. EPZ (United) | 19 | 19 | 13 | 17 | 22 | 22 | 19 | 2 | 2 | 2 | 2 | 3 | 3 | 5 | 2 | 2 | 2 | 7 |  | 10 | 12 | 11 | 20 | 23 | 28 | 24 | 298560
65 | Feni 22MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 406152
66 | Feni 11 MW PP (Doreen) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 167040
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 6 | 32 | 33 | 33 | 33 | 32 | 32 | 30 | 30 | 30 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 693600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 459040
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 552000
70 | Summit Madhabdi | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 26 |  | 26 | 22 | 27 | 27 | 27 | 28 | 28 | 588420
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 749880
72 | Rupganj 33 MW PP(Summit) | 26 | 26 | 16 | 28 | 28 | 28 | 28 | 26 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 18 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 8 | 480000
73 | Ghorashal 108MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 524818
| Feni Lanka Power | [17 empty] | 0 |  | 34 | 114 | 114 | 114 | 114 | 114 | 114 | 574560
| Chowmuhani 113 MW | 13 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 8 | 55 | 56 | 57 | 57 | 57 | 57 | 57 | 57 | 56 |  | 60 | 75 | 75 | 95 | 95 | 73 | 16 | 970200
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 68 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 162 | 162 | 162 | 17 | 17 | 17 | 17 | 1121760
77 | Siddhirganj 100 PP(Dutch Bangla) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 45 | 53 | 58 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 32 | 25 | 873600
78 | Gazipur 52 MW PP | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 37 | 40 | 40 | 40 | 8 | 8 | 8 | 8 | 11 |  | 40 | 40 | 41 | 41 | 41 | 41 | 8 | 561600
79 | Kodda 150 MW PP | 64 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 82 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 |  | 150 | 150 | 150 | 150 | 150 | 98 | 98 | 2078880
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 52 | 52 | 52 | 52 | 52 | 51 | 50 | 50 | 50 | 50 | 43 | 34 | 32 | 33 | 48 | 47 |  | 46 | 46 | 46 | 50 | 50 | 51 | 51 | 1107110
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 86 | 86 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2093827
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | 1 | 0 | [8 empty] | 34680
| Jodiac Power | 17 | 17 |  |  |  | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 379600
| Karnaphuli Power Ltd. | 92 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 66 | 84 | 72 | 72 | 72 | 81 | 105 |  | 104 | 105 | 103 | 105 | 105 | 105 | 63 | 1808210
82 | Madanganj 102 PP(Summit) | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 65 | 65 | 65 | 65 | 65 | 60 | 50 |  | 55 | 65 | 65 | 65 | 65 | 65 | 68 | 1279268
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 305 | 307 | 306 | 309 | 307 | 304 | 310 | 306 | 313 | 292 | 285 | 280 | 265 | 250 | 248 | 241 | 242 | 243 |  | 238 | 226 | 228 | 213 | 221 | 208 | 210 | 6490851
87 | Meghnaghat 100 MW(IEL) | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 22 | 40 | 41 | 42 | 52 | 56 | 57 | 57 |  | 57 | 57 | 56 | 57 | 58 | 30 | 25 | 807360
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 46 | 52 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 52 | 50 | 835200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 10 | 417240
92 | Fenchuganj 44MW (Energyprima) | 49 | 49 | 49 | 49 | 46 | 43 | 43 | 49 | 49 | 46 | 43 | 43 | 41 | 42 | 41 | 41 | 41 | 43 |  | 45 | 45 | 46 | 46 | 46 | 49 | 50 | 1091016
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 957178
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 50 | 50 | 50 | 56 | 58 | 58 |  | 82 | 83 | 83 | 83 | 83 | 24 | 24 | 917136
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 17 | 32 | 38 | 0 | 15 | 0 |  | 29 | 44 | 44 | 44 | 44 | 44 | 15 | 458880
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 11 | 12 | 12 | 21 | 29 |  | 29 | 29 | 29 | 29 | 29 |  | 0 | 207360
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 15 | 15 | 15 | 15 | 55 | 55 | 55 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 3 | 15 | 391658
100 | Manikganj 55 MW PP (Northern) | [6 empty] | 17 | 35 | 35 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 35 |  | 0 | 645923
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 1 | 0 | [8 empty] | 12300
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 34 | 54 | 54 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 291240
104 | Keranigonj 300 MW PP (APR) | 301 | 301 | 302 | 261 | 201 |  |  |  |  | 206 | 294 | 301 | 301 | 295 | 301 | 52 | 0 | 0 |  | 115 | 52 | 11 | 295 | 290 | 290 | 300 | 4339111
105 | Bramhangoan 100 MW PP (Aggreko) | 80 | 80 | 80 | 80 | 80 |  |  |  |  | 80 | 80 | 80 | 75 | 74 | 74 | 72 | 72 | 25 |  | 71 | 75 | 79 | 80 | 83 | 83 | 82 | 1477882
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 67 | 76 | 76 | 76 | 47 | 47 | 37 | 37 | 45 |  | 83 | 93 | 94 | 93 | 93 | 93 | 46 | 1423200
112 | Aurahati 100MW PP (Aggreko) | 75 | 75 | 75 | 75 | 75 |  |  |  |  | 75 | 75 | 75 | 75 | 75 | 75 | 70 | 70 | 25 |  | 73 | 79 | 79 | 79 | 80 | 80 | 75 | 1418407
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 132 | 130 | 131 | 129 | 55 | 36 | 32 | 33 | 43 |  | 86 | 110 | 114 | 114 | 115 | 72 | 17 | 1441584
115 | Juldah 100 MW PP Unit-3 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 438720
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 32 | 34 | 34 | 35 | 35 | 34 | 34 | 40 | 68 |  | 68 | 68 | 68 | 70 | 98 | 100 | 60 | 979680
117 | Ashuganj 150MW PP (Midland) | 20 | 18 | 20 | 20 | 20 | 18 | 16 | 20 | 18 | 18 | 16 | 18 | 16 | 15 | 11 | 11 | 11 | 48 |  | 102 | 115 | 150 | 152 | 150 | 150 | 62 | 1093963
118 | Bibiyana-III 400 MW CCPP | 379 | 366 | 369 | 378 | 372 | 413 | 367 | 377 | 383 | 368 | 382 | 379 | 372 | 382 | 384 | 376 | 368 | 367 |  | 367 | 318 | 320 | 364 | 365 | 417 | 367 | 9168000
| Jamalpur 115 MW PP (United) | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 58 | 49 | 77 | 77 | 77 | 77 | 48 | 48 | 48 | 48 | 47 |  | 91 | 97 | 99 | 99 | 99 | 99 | 49 | 1496400
| Anwara 300 MW PP (United) | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 87 | 122 |  | 275 | 275 | 279 | 279 | 123 | 87 | 87 | 2697273
| Juldah unit-2 (Acorn) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 12 | 12 | 447360
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 28 | 30 | 34 | 34 | 35 |  | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 672436
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 27 | 35 | 35 |  | 30 | 30 | 35 | 35 | 35 | 35 | 35 | 588600
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 7 | 15 | 23 | 28 | 31 | 32 | 31 | 27 | 22 | 16 | 6 | 1 |  | 0 | [6 empty] | 238027
| Chandpur 115(Doreen) | 18 | 18 | 18 | 17 | 18 | 18 | 17 | 18 | 18 | 27 | 59 | 90 | 85 | 94 | 94 | 60 | 53 | 53 |  | 54 | 54 | 54 | 54 | 54 | 53 | 54 | 1109760
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 11 | 18 | 22 | 36 |  | 36 | 36 | 36 | 34 | 34 | 34 | 17 | 541080
| Mirsharai 150 MW (Oil) | 108 | 108 | 108 | 108 | 54 | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 55 |  | 90 | 108 | 126 | 144 | 144 | 144 | 90 | 1753018
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 7350 | 7190 | 7107 | 7062 | 6954 | 6684 | 6546 | 6591 | 6642 | 7257 | 7644 | 7685 | 7737 | 7441 | 7370 | 6998 | 6913 | 6985 |  | 8072 | 8084 | 8213 | 8525 | 8406 | 8203 | 7525 | 176067976
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 53 | 61 | 61 | 61 | 30 | 30 | 30 | 30 | 35 |  | 62 | 62 | 63 | 68 | 63 | 65 | 65 | 1040640
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [13 empty] | 0 | 25 | 80 | 120 | 0 | [8 empty] | 153138
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 9 | 9 | 9 | 20 | 26 | 26 | 29 | 27 | 25 |  | 22 | 22 | 34 | 26 | 26 | 26 | 26 | 463680
Khulna 225 MW CCPP
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 584640
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 3 | 13 | 44 | 45 | 91 | 96 | 101 | 87 | 89 | 53 | 46 | 24 | 4 |  | 0 | [6 empty] | 714240
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 137 |  | 150 | 150 | 142 | 150 | 150 | 150 | 150 | 1351200
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [9 empty] | 27 | 102 | 110 | 110 | 16 | 0 |  |  | 0 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 392928
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 177 | 178 | 178 | 178 | 178 | 178 | 180 | 180 | 175 | 173 | 175 | 170 | 170 | 83 | 85 | 86 | 81 | 81 |  | 70 | 70 | 89 | 89 | 89 | 89 | 89 | 3252839
140 | Bhola 33 MW PP (Venture) | 29 | 29 | 34 | 33 | 31 | 30 | 24 | 23 | 22 | 23 | 24 | 25 | 26 | 25 | 28 | 25 | 26 | 24 |  | 32 | 33 | 34 | 34 | 36 | 36 | 36 | 690663
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 |  | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 434250
143 | Gopalganj 100 MW Peaking PP | 72 | 70 | 64 | 60 | 60 | 60 | 60 | 59 | 50 | 27 | 25 | 25 | 25 | 21 | 23 | 21 | 35 | 52 |  | 60 | 65 | 72 | 80 | 77 | 75 | 72 | 1203072
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 85 | 85 | 105 | 105 | 85 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2506032
146 | Bheramara HVDC | 862 | 863 | 919 | 920 | 920 | 920 | 920 | 920 | 921 | 916 | 917 | 917 | 914 | 914 | 915 | 914 | 914 | 914 |  | 914 | 914 | 804 | 804 | 804 | 803 | 804 | 21498181
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1180 | 1220 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1222 | 1160 |  | 1180 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 31518700
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 73 | 76 | 76 | 75 | 75 | 75 | 74 | 75 | 75 | 74 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 72 | 1746327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6118500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 676768
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | 0 | 0 | [8 empty] | 33840
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 181 | 181 | 181 | 181 | 181 | 182 | 183 | 183 | 184 | 184 | 184 | 183 | 181 | 178 | 178 | 177 | 177 | 176 |  | 161 | 150 | 150 | 173 | 186 | 183 | 181 | 4519709
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 134 | 135 | 136 | 137 | 138 | 140 | 143 | 143 | 137 | 137 | 134 | 135 | 134 | 132 | 133 | 133 | 132 | 135 |  | 138 | 141 | 142 | 142 | 142 | 144 | 144 | 3544682
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 401 | 414 | 414 | 423 | 424 | 422 | 428 | 350 | 381 | 368 | 363 | 341 | 329 | 324 | 323 | 340 | 341 | 305 |  | 357 | 303 | 300 | 401 | 398 | 416 | 414 | 8992582
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP |  | 5 | 5 | 5 | 15 | 20 | 14 | 14 | 14 | 18 | 20 | 21 | 23 | 30 | 24 | 24 | 24 | 28 |  | 36 | 36 | 38 | 28 | 28 | 28 | 4 | 343665
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 19 | 18 | 18 | 17 | 17 | 17 | 18 | 18 | 17 |  | 21 | 22 | 22 | 22 |  | 0 | 0 | 423360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 157284
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 491960
166 | Katakhali 50 MW PP (Northern) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 8 |  | 34 | 42 | 42 | 42 | 42 | 42 | 42 | 912626
167 | Katakhali 50 MW Peaking PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 34 | 40 | 40 | 40 | 40 | 32 | 32 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 623490
168 | Santahar 50 MW Peaking PP | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 28 | 28 | 27 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 27 | 28 | 28 | 28 | 643728
169 | Natore 52 MW PP (Rajlanka) | [19 empty] | 0 | 8 | 8 | 8 | 8 |  | 0 | 29246
170 | Chapainawabganj 100 MW Peaking PP | 76 | 76 | 68 | 68 | 45 | 45 | 46 | 46 | 45 | 39 | 39 | 39 | 39 | 38 | 38 | 63 | 71 | 71 |  | 80 | 80 | 82 | 82 | 84 | 84 | 84 | 1409176
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 |  |  |  |  | 15 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 50 | 50 | 50 | 50 | 35 | 35 | 815136
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 |  |  |  |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 810816
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 |  |  |  | 33 | 33 | 34 | 34 | 34 | 32 | 34 | 34 | 33 | 43 | 49 |  | 49 | 49 | 49 | 49 | 49 | 49 | 34 | 804124
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 2 | 3 | 5 | 5 | 7 | 7 | 7 | 7 | 7 | 4 | 2 | 1 |  | 0 | [6 empty] | 58205
178 | Energypac Power Venture Thakurgaon Ltd. | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 80 |  | 114 | 114 | 114 | 72 | 72 | 35 | 0 | 1173120
| Intraco Solar 30 MW | [5 empty] | 1 | 6 | 13 | 21 | 27 | 31 | 31 | 31 | 27 | 21 | 14 | 6 | 2 |  | 0 | [6 empty] | 231959
| Adani Power Jharkhanda Ltd | 843 | 725 | 751 | 756 | 759 | 742 | 768 | 792 | 776 | 795 | 686 | 754 | 741 | 744 | 742 | 728 | 738 | 731 |  | 670 | 696 | 724 | 710 | 762 | 778 | 839 | 18060000
178 | Teesta Solar Limited | [5 empty] | 10 | 41 | 86 | 127 | 163 | 181 | 182 | 143 | 120 | 120 | 81 | 35 | 8 |  | 0 | [6 empty] | 1283500