## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-07-20 | Friday
|  | Date (day): | 2018-07-20 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10863 | MW |  |  | (b) At Evening Peak Hour : |  | 12241 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-07-19 | 2018-07-20 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 70 | 70 |  | 13
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 | 170 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 0 | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365 | 0
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 71 | 72 | 72 | 6 |  | Gas shortage
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 70 | 83 | 85 | 100 | 8 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 345 | 409 | 412 | 412 | 0 |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 96 | 96 | 98 | 98 |  | 12
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 275 | 271 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 430 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 93 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 250 | 305 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 80 | 80 | 42 | 81 |  | 19 | Engine problem
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 47 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 17 | 22 | 22 | 22 | 0
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 97 | 100 | 100 | 110 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 44 | 100 | 100 | 100 | 0
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 84 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 0 | 0 | 0 | 0 | 217 |  | Under maint.
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 49 | 50 | 50 | 50 | 0
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 102 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 39 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 149 MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 149 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 79 | 78 | 97 | 97 |  | 11 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 30 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 50 | 51 | 51
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 220 | 280 | 100 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
35 | Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 98 | 98 | 0 | 100
36 | Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 53 | 99 | 100 | 100 |  |  | line shut down
| Summit Gazipur-1 150MW |  | HFO | IPP | 149 MW | 0 | 0 | 146 | 145 | 135 | 145
| Dhaka area Total |  |  |  |  | 5635 | 5399 | 3585 | 3977 | 3941 | 4305 | 666 | 570
37 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
38 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
39 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 33 | 50 | 50
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 160 | 160 | 160 | 160 |  | 70 | # 3 under maint
41 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
42 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 210 | 227 | 213 | 213
43 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 135 | 135 | 135
44 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 32 | 40 | 51 | 51
45 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 74 | 71 | 74 | 74
46 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 32 | 46 | 51 | 51
47 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 80 | 80 |  | 20 | Engine problem
48 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 14 | 30 | 30
49 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 91 | 106 | 101 | 101 |  | 7 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 974 | 1067 | 1100 | 1100 | 240 | 149
50 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 |  | 135 | Under shut down
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 100 | 100
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34 |  | Gas shortage
51 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 118 | 225 | 225 |  |  | FGMO
52 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 320 | 360 | 360 |  |  | FGMO
53 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 298 | 360 | 360
54 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 20 | 43 | 43 |  | 2 | Engine problem
55 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
56 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 10 | 5 | 10 |  |  | Gas shortage
57 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 160 | 80 | 172 | 23 |  | Gas shortage
58 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
59 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 85 | 85 | 85
60 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 0 | 40
61 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  | 63 | ST under maint.
62 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 18 | 22 | 22
63 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 122 | 74 | 102 | 118
64 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
65 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 10 | 52 | 52 | 52
66 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 22 | 15 | 22 | 22 |  | 3 | Engine problem
67 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 100 | 170 | 100 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1583 | 1776 | 1851 | 2104 | 57 | 258
68 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 47 | 47 | 48 | 48 | 154 |  | Gas shortage
69 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
70 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 90 | 95 | 95 | 95
71 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 2 | 0
72 | United Mymensingh PPL |  | HFO | IPP | 200 | 200 | 200 | 163 | 161 | 170 | 170
| Mymensingh Area Total |  |  |  |  | 530 | 522 | 322.4 | 323 | 335 | 333 | 154 | 0
73 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 65 | 67 | 68 | 68
74 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 66 | 65 | 74 | 74
75 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
76 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 320 | 298 | 330 | 330
77 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 51 | 53 | 53
78 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 48 | 50 | 50 | 50
79 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
80 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 59 | 59 | 60 | 60
81 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 86 | 86 | 86
82 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 45 | 45 | 45
83 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 130 | 98 | 130 | 130 | 12 |  | Gas shortage
84 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
85 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 44 | 47 | 47 |  | 3 | Engine problem
86 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 13 | 14 | 23 | 23 |  | 2
87 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 341 | 341 |  |  | FGMO
88 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1382 | 1340 | 1491 | 1491 | 12 | 25
89 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 30 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 463 | 464 | 476 | 476
90 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 27 | 30 | 100 |  |  | Engine problem
91 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 82 | 99 | 99 |  | 16 | Engine problem
92 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 48
93 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 147 | 158 | 158 |  | 72 | Engine problem.
94 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 68 | 0 | 90
95 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 284 | 240 | 280 | 255 | 155 |  | Gas shortage
96 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 0 | 40
97 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 55 | 55 | 0 | 55
98 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 85 | 93 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 913 | 1289 | 1043 | 1453 | 155 | 88
99 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 110 | 110 | 110 | 110
100 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 10 | 0 | 30
101 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 20 | 33 | 33
102 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 90 | 154 | 160 | 165
103 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 96 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 320 | 390 | 398 | 433 | 0 | 0
104 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
105 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 48 | 0 | 50
106 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 0 | 37
107 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 40 | 50 | 50
108 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 35 | 43 | 43 | 43 |  | 7 | Engine problem
109 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 0 | 40
110 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 214 | 130 | 214
111 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 220 | 130 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 40 | 0 | 0 | 0 |  |  | Under maint.
112 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Transformer problem.
113 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 14 | 18 | 18 | 18
114 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 7 | 10 | 10 | 10
115 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
116 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 51 | 50 | 52 | 52
117 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 100 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 518 | 833 | 544 | 845 | 71 | 157
118 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
119 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 138 | 120 | 142 | 142 |  | 132 | Machine problem
120 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 17
121 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 14 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 138 | 149 | 160 | 177 | 0 | 302
| Total |  |  |  |  | 15953 | 15410 | 9735.4 | 11144 | 10863 | 12241 | 1355 | 1549
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9179.7903 | 10508 | 10243.037 | 11542.393
A. |  | 2018-07-19 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 11203 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 8659.6 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11144 | MW
3 | Day peak Generation : |  |  | 9735.4 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10508 | MW
4 | Evening peak Generation : |  |  | 11144 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 240.6369 | MKWHr | By Solar | 0.0175 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 127.4155 | MKWHr |  | By Oil: | 92.5959 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.2771 | MKWHr |  | By Hydro: | 3.655 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1355 | MW | Dhaka | 4141 | 4141 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1549 | MW | Chittagong | 1071 | 1071 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2904 | MW | Khulna | 1238 | 1238 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1046.61 | MMCFD |  |  | Rajshahi | 1103 | 1103 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 93231572.438 | ii) Oil : | Taka | 913403583.18 | Comilla | 894 | 894 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 12649606 | Total | Taka | 1019284761.618 | Mymensingh | 701 | 701 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 13.6145 | MKWHr. | Sylhet | 493 | 493 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -790 | MW at | 21:00 | hrs | Barisal | 282 | 282 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -1140 | MW at | 1:00 | hrs | Rangpur | 585 | 585 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 37.6° C |  |  | Total | 10508 | 10508 |  | 0
B. |  | 2018-07-20 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 36° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12241 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9200 | MW
4 | Reserve(Generation end) |  |  |  | 941 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 242.7204 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8451 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.128 | MKWHr. | ii) HVDC Flow at Peak Time |  | 464 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5478 | MKWHr. | iii) Maximum HVDC Flow : |  | 469 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.82 |  | (b) Today: | 103.56 |  | (c) Rule Curve: |  | 86.88
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-07-19
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 149 MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | Summit Gazipur-1 150MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 400 | 301 | 96 | 0 | 420 | 305 | 100 | 81 | 44 | 0 | 0 | 102 | 34 | 85 | 102 | 149 | 100 | 87 | 51 | 40 | 54 | 56 | 55 | 0 | 25 | 32 | 25 | 33 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 203 | 0 | 135 | 0 | 50 | 74 | 48 | 80 | 106 | 50 | 19 | 36 | 0 | 100 | 110 | 258 | 300 | 155 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 41 | 34 | 22 | 11 | 33 | 21 | 121 | 49 | 89 | 20 | 0 | 68 | 66 | 53 | 50 | 163 | 317 | 61 | 86 | 45 | 135 | 0 | 47 | 7 | 300 | 22 | 11 | 150 | 285 | 0 | 61 | 168 | 70 | 146 |  | 464 | 0 | 262 | 10 | 22 | 20 | 0 | 51 | 47 | 69 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 36 | 100 | 50 | 43 | 37 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 132 | 15 | 15 | 0 | 130 | 0 | 130 | 95 | 98 | 0 | 0 |  | 8511 | 2195 | 10706 | 3566 | 464 | 1882 | 3082 | 132 | 160 | 1299 | 121 | 0 | 0 | 103.92
2:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 350 | 321 | 96 | 0 | 450 | 200 | 100 | 81 | 55 | 0 | 0 | 101 | 34 | 85 | 102 | 149 | 100 | 88 | 51 | 40 | 54 | 56 | 55 | 0 | 25 | 32 | 25 | 33 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 201 | 0 | 70 | 0 | 50 | 74 | 48 | 80 | 106 | 50 | 19 | 30 | 0 | 100 | 110 | 268 | 300 | 174 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 41 | 34 | 22 | 11 | 33 | 21 | 121 | 48 | 90 | 20 | 0 | 68 | 66 | 53 | 50 | 130 | 302 | 60 | 86 | 45 | 135 | 0 | 47 | 9 | 275 | 22 | 11 | 80 | 285 | 0 | 36 | 168 | 50 | 146 |  | 464 | 0 | 267 | 10 | 16 | 30 | 0 | 37 | 47 | 69 | 0 | 95 | 34 | 110 | 0 | 0 | 0 | 50 | 36 | 100 | 50 | 43 | 37 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 130 | 15 | 15 | 0 | 130 | 0 | 130 | 95 | 98 | 0 | 0 |  | 8186 | 2199 | 10385 | 3542 | 464 | 1871 | 2855 | 130 | 160 | 1242 | 121 | 0 | 0 | 103.9
3:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 345 | 322 | 96 | 0 | 450 | 200 | 100 | 81 | 55 | 0 | 0 | 101 | 34 | 80 | 102 | 149 | 100 | 87 | 11 | 40 | 54 | 56 | 55 | 0 | 25 | 32 | 25 | 33 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 203 | 0 | 50 | 0 | 50 | 74 | 47 | 80 | 50 | 50 | 19 | 39 | 0 | 100 | 110 | 268 | 305 | 168 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 41 | 34 | 22 | 11 | 33 | 21 | 121 | 48 | 90 | 20 | 0 | 68 | 66 | 53 | 50 | 130 | 306 | 60 | 86 | 45 | 135 | 0 | 47 | 9 | 295 | 22 | 11 | 0 | 285 | 0 | 0 | 166 | 0 | 146 |  | 464 | 0 | 267 | 10 | 16 | 40 | 0 | 37 | 47 | 63 | 0 | 95 | 30 | 110 | 0 | 0 | 0 | 50 | 36 | 100 | 50 | 43 | 37 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 127 | 15 | 15 | 0 | 130 | 0 | 130 | 95 | 50 | 0 | 0 |  | 7925 | 2148 | 10073 | 3540 | 464 | 1897 | 2537 | 127 | 160 | 1227 | 121 | 0 | 0 | 103.88
4:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 370 | 348 | 13 | 0 | 450 | 200 | 100 | 81 | 55 | 0 | 0 | 101 | 0 | 80 | 30 | 100 | 60 | 88 | 0 | 39 | 54 | 56 | 55 | 0 | 25 | 32 | 25 | 33 | 51 | 0 | 81 | 80 | 120 | 0 | 16 | 0 | 222 | 0 | 50 | 0 | 50 | 74 | 47 | 80 | 95 | 50 | 19 | 39 | 0 | 100 | 110 | 270 | 345 | 160 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 49 | 73 | 20 | 0 | 68 | 66 | 53 | 50 | 130 | 338 | 59 | 86 | 45 | 135 | 0 | 47 | 9 | 320 | 22 | 11 | 0 | 285 | 0 | 0 | 166 | 0 | 147 |  | 464 | 0 | 286 | 10 | 16 | 30 | 0 | 37 | 47 | 51 | 0 | 93 | 28 | 110 | 0 | 0 | 0 | 50 | 36 | 100 | 50 | 43 | 37 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 131 | 15 | 15 | 0 | 130 | 0 | 130 | 94 | 0 | 0 | 0 |  | 7751 | 2094 | 9845 | 3648 | 464 | 1945 | 2242 | 131 | 161 | 1134 | 120 | 0 | 0 | 103.86
5:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 360 | 350 | 13 | 0 | 450 | 305 | 100 | 81 | 55 | 0 | 0 | 102 | 0 | 81 | 30 | 100 | 60 | 88 | 0 | 40 | 54 | 56 | 55 | 17 | 25 | 32 | 25 | 33 | 51 | 0 | 81 | 80 | 120 | 0 | 16 | 0 | 202 | 0 | 100 | 0 | 50 | 74 | 47 | 80 | 91 | 50 | 19 | 39 | 0 | 100 | 110 | 268 | 300 | 169 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 48 | 72 | 20 | 0 | 68 | 66 | 53 | 50 | 130 | 306 | 60 | 86 | 45 | 135 | 0 | 47 | 9 | 310 | 22 | 11 | 0 | 285 | 0 | 0 | 166 | 0 | 147 |  | 464 | 0 | 308 | 10 | 16 | 50 | 0 | 37 | 47 | 46 | 0 | 95 | 28 | 110 | 0 | 0 | 0 | 50 | 36 | 100 | 50 | 43 | 37 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 138 | 15 | 15 | 0 | 130 | 0 | 130 | 95 | 0 | 0 | 0 |  | 7809 | 2141 | 9950 | 3610 | 464 | 1938 | 2344 | 138 | 161 | 1179 | 116 | 0 | 0 | 103.84
6:00 | 65 | 120 | 0 | 0 | 340 | 0 | 0 | 340 | 334 | 0 | 0 | 450 | 200 | 60 | 65 | 55 | 0 | 0 | 97 | 0 | 40 | 7 | 48 | 10 | 88 | 0 | 40 | 54 | 56 | 55 | 17 | 25 | 32 | 25 | 33 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 203 | 0 | 50 | 0 | 40 | 74 | 17 | 80 | 91 | 50 | 19 | 39 | 0 | 100 | 110 | 268 | 300 | 171 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 50 | 48 | 20 | 0.1 | 68 | 66 | 53 | 50 | 130 | 302 | 61 | 86 | 45 | 135 | 0 | 47 | 7 | 270 | 22 | 11 | 0 | 268 | 0 | 0 | 168 | 0 | 147 |  | 464 | 0 | 315 | 10 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 72 | 27 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 40 | 43 | 0 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 125 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 0 | 0 | 0 |  | 7219.1 | 1818 | 9037.1 | 3545 | 464 | 1879 | 1960 | 125 | 160 | 802 | 102 | 0.1 | 0 | 103.82
7:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 365 | 331 | 0 | 0 | 450 | 230 | 16 | 15 | 15 | 0 | 0 | 97 | 0 | 14 | 7 | 16 | 10 | 40 | 0 | 12 | 18 | 56 | 55 | 17 | 25 | 32 | 25 | 33 | 51 | 0 | 80 | 80 | 130 | 0 | 16 | 0 | 206 | 0 | 80 | 0 | 40 | 74 | 17 | 80 | 92 | 50 | 19 | 26 | 0 | 100 | 110 | 288 | 320 | 166 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 22 | 11 | 33 | 21 | 90 | 47 | 8 | 20 | 0.6 | 68 | 66 | 49 | 50 | 100 | 321 | 60 | 86 | 45 | 135 | 0 | 47 | 9 | 270 | 22 | 11 | 0 | 150 | 0 | 0 | 166 | 0 | 147 |  | 464 | 0 | 309 | 10 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 94 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 43 | 0 | 51 | 0 | 18 | 10 | 11 | 0 | 0 | 125 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 0 | 0 | 0 |  | 6869.6 | 1790 | 8659.6 | 3671 | 464 | 1828 | 1568 | 125 | 160 | 753 | 90 | 0.6 | 0 | 103.81
8:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 380 | 293 | 0 | 0 | 450 | 270 | 9 | 22 | 15 | 0 | 0 | 99 | 0 | 16 | 7 | 16 | 40 | 90 | 0 | 21 | 36 | 55 | 55 | 17 | 25 | 32 | 25 | 25 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 216 | 0 | 135 | 0 | 40 | 74 | 17 | 80 | 85 | 50 | 19 | 10 | 0 | 100 | 100 | 288 | 305 | 168 | 77 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 93 | 47 | 8 | 20 | 1.2 | 68 | 66 | 50 | 50 | 163 | 331 | 59 | 86 | 45 | 130 | 0 | 46 | 9 | 330 | 22 | 11 | 0 | 160 | 0 | 0 | 165 | 0 | 147 |  | 464 | 0 | 308 | 10 | 16 | 50 | 0 | 0 | 0 | 0 | 0 | 93 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 43 | 0 | 51 | 0 | 18 | 10 | 11 | 0 | 0 | 109 | 0 | 0 | 0 | 130 | 0 | 130 | 96 | 0 | 0 | 0 |  | 7135.2 | 1773 | 8908.2 | 3647 | 464 | 1898 | 1718 | 109 | 160 | 818 | 93 | 1.2 | 0 | 103.81
9:00 | 65 | 120 | 0 | 0 | 365 | 0 | 0 | 360 | 292 | 26 | 0 | 430 | 305 | 65 | 42 | 43 | 0 | 0 | 99 | 5 | 35 | 48 | 100 | 100 | 89 | 50 | 34 | 54 | 55 | 55 | 17 | 25 | 31 | 25 | 25 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 200 | 0 | 100 | 0 | 40 | 74 | 17 | 80 | 86 | 50 | 19 | 2 | 0 | 100 | 100 | 285 | 272 | 178 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 106 | 47 | 24 | 20 | 1.6 | 68 | 66 | 50 | 50 | 130 | 309 | 59 | 84 | 45 | 134 | 0 | 46 | 9 | 300 | 22 | 11 | 50 | 221 | 0 | 51 | 166 | 51 | 145 |  | 464 | 0 | 295 | 10 | 16 | 50 | 0 | 52 | 0 | 0 | 0 | 89 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 43 | 0 | 51 | 0 | 18 | 8 | 11 | 0 | 0 | 120 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 50 | 0 | 0 |  | 7622.6 | 1866 | 9488.6 | 3565 | 464 | 1802 | 2419 | 120 | 160 | 851 | 106 | 1.6 | 0 | 103.8
10:00 | 65 | 0 | 0 | 0 | 365 | 0 | 0 | 370 | 276 | 42 | 0 | 430 | 305 | 92 | 75 | 48 | 0 | 0 | 99 | 23 | 60 | 50 | 110 | 0 | 88 | 48 | 34 | 54 | 55 | 55 | 17 | 25 | 26 | 25 | 25 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 205 | 0 | 135 | 0 | 40 | 74 | 17 | 80 | 92 | 50 | 19 | 3 | 0 | 100 | 100 | 285 | 279 | 179 | 78 | 100 | 43 | 0 | 5 | 51 | 84 | 0 | 8 | 19 | 11 | 25 | 22 | 112 | 47 | 24 | 20 | 1.9 | 65 | 66 | 50 | 47 | 163 | 304 | 59 | 84 | 45 | 133 | 0 | 45 | 9 | 300 | 16 | 11 | 90 | 221 | 0 | 50 | 166 | 100 | 146 |  | 464 | 0 | 284 | 10 | 16 | 50 | 0 | 54 | 0 | 0 | 0 | 92 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 44 | 40 | 43 | 0 | 51 | 0 | 18 | 7 | 11 | 0 | 0 | 127 | 0 | 0 | 0 | 130 | 0 | 130 | 93 | 75 | 0 | 0 |  | 7687.9 | 1871 | 9558.9 | 3427 | 464 | 1810 | 2562 | 127 | 160 | 895 | 112 | 1.9 | 0 | 103.79
11:00 | 72 | 0 | 0 | 0 | 365 | 70 | 0 | 345 | 275 | 96 | 0 | 430 | 250 | 93 | 80 | 47 | 0 | 0 | 97 | 44 | 70 | 85 | 149 | 0 | 79 | 49 | 39 | 54 | 55 | 55 | 17 | 25 | 26 | 25 | 25 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 210 | 0 | 100 | 0 | 32 | 74 | 32 | 80 | 91 | 37 | 19 | 3 | 0 | 100 | 100 | 295 | 230 | 190 | 78 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 10 | 19 | 11 | 25 | 22 | 122 | 47 | 90 | 20 | 2.4 | 65 | 66 | 48 | 48 | 163 | 320 | 59 | 82 | 45 | 130 | 0 | 43 | 9 | 280 | 13 | 11 | 100 | 220 | 0 | 98 | 163 | 53 | 146 |  | 463 | 0 | 284 | 10 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 35 | 0 | 51 | 0 | 14 | 7 | 11 | 0 | 0 | 138 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 85 | 40 | 0 |  | 7846.4 | 1889 | 9735.4 | 3424 | 463 | 1856 | 2695 | 138 | 160 | 875 | 122 | 2.4 | 0 | 103.79
12:00 | 72 | 0 | 0 | 0 | 365 | 75 | 50 | 355 | 276 | 96 | 0 | 400 | 200 | 99 | 80 | 48 | 0 | 0 | 95 | 52 | 70 | 102 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 17 | 25 | 31 | 25 | 25 | 50 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 198 | 0 | 100 | 0 | 32 | 74 | 32 | 80 | 91 | 37 | 19 | 4 | 0 | 100 | 100 | 335 | 238 | 184 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 44 | 16 | 19 | 11 | 33 | 15 | 112 | 46 | 56 | 20 | 2.3 | 65 | 66 | 48 | 48 | 130 | 302 | 68 | 81 | 45 | 128 | 0 | 42 | 9 | 260 | 14 | 0 | 10 | 220 | 0 | 50 | 117 | 51 | 136 |  | 464 | 0 | 260 | 10 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 82 | 26 | 110 | 0 | 0 | 0 | 48 | 0 | 50 | 50 | 35 | 0 | 50 | 0 | 14 | 7 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 150 | 0 | 165 | 95 | 85 | 0 | 0 |  | 7635.3 | 1933 | 9568.3 | 3389 | 464 | 1829 | 2452 | 150 | 160 | 1010 | 112 | 2.3 | 0 | 103.78
13:00 | 72 | 0 | 0 | 0 | 363 | 82 | 70 | 350 | 270 | 96 | 0 | 400 | 200 | 99 | 80 | 48 | 0 | 0 | 95 | 61 | 63 | 94 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 17 | 25 | 31 | 25 | 25 | 48 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 203 | 0 | 100 | 0 | 32 | 72 | 31 | 80 | 90 | 42 | 19 | 8 | 0 | 100 | 100 | 360 | 235 | 183 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 49 | 16 | 18 | 11 | 33 | 15 | 112 | 46 | 90 | 20 | 2.3 | 65 | 66 | 49 | 47 | 130 | 316 | 58 | 83 | 45 | 128 | 0 | 42 | 9 | 270 | 14 | 5 | 10 | 220 | 0 | 50 | 125 | 51 | 131 |  | 464 | 0 | 248 | 10 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 92 | 26 | 110 | 0 | 0 | 0 | 48 | 0 | 50 | 50 | 43 | 0 | 50 | 0 | 16 | 7 | 11 | 0 | 0 | 156 | 0 | 0 | 0 | 214 | 0 | 220 | 94 | 85 | 0 | 100 |  | 7734.3 | 2165 | 9899.3 | 3409 | 464 | 1867 | 2493 | 156 | 160 | 1236 | 112 | 2.3 | 0 | 0
14:00 | 72 | 0 | 0 | 0 | 365 | 83 | 69 | 365 | 271 | 96 | 0 | 400 | 250 | 99 | 77 | 47 | 0 | 0 | 98 | 50 | 63 | 92 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 17 | 25 | 30 | 25 | 25 | 48 | 0 | 78 | 80 | 120 | 0 | 16 | 0 | 202 | 0 | 130 | 0 | 32 | 72 | 31 | 80 | 94 | 44 | 19 | 2 | 0 | 100 | 100 | 355 | 231 | 161 | 78 | 100 | 43 | 0 | 5 | 51 | 84 | 49 | 14 | 18 | 11 | 33 | 15 | 92 | 46 | 90 | 20 | 2.3 | 65 | 65 | 47 | 47 | 163 | 286 | 56 | 83 | 45 | 98 | 0 | 44 | 9 | 280 | 14 | 8 | 10 | 260 | 0 | 10 | 100 | 51 | 131 |  | 464 | 0 | 235 | 10 | 16 | 0 | 0 | 51 | 0 | 0 | 0 | 90 | 27 | 110 | 0 | 0 | 0 | 48 | 0 | 50 | 40 | 43 | 0 | 50 | 0 | 15 | 7 | 11 | 0 | 0 | 157 | 0 | 0 | 0 | 214 | 0 | 220 | 93 | 85 | 0 | 100 |  | 7718.3 | 2136 | 9854.3 | 3322 | 464 | 1903 | 2491 | 157 | 158 | 1265 | 92 | 2.3 | 0 | 0
15:00 | 72 | 0 | 0 | 0 | 365 | 83 | 68 | 375 | 271 | 96 | 0 | 400 | 300 | 97 | 77 | 48 | 0 | 0 | 94 | 50 | 63 | 92 | 149 | 0 | 77 | 49 | 40 | 54 | 55 | 55 | 17 | 25 | 28 | 25 | 25 | 48 | 0 | 78 | 80 | 120 | 0 | 16 | 0 | 210 | 0 | 130 | 0 | 32 | 64 | 14 | 80 | 92 | 44 | 19 | 2 | 0 | 100 | 100 | 340 | 257 | 176 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 48 | 21 | 18 | 11 | 33 | 15 | 96 | 46 | 90 | 20 | 1.9 | 65 | 65 | 47 | 47 | 163 | 282 | 48 | 79 | 45 | 98 | 0 | 44 | 9 | 300 | 14 | 8 | 100 | 278 | 0 | 97 | 130 | 100 | 125 |  | 464 | 0 | 224 | 10 | 16 | 15 | 0 | 48 | 0 | 0 | 0 | 89 | 24 | 112 | 0 | 0 | 0 | 48 | 0 | 50 | 40 | 43 | 41 | 50 | 0 | 16 | 8 | 11 | 0 | 0 | 150 | 0 | 15 | 0 | 214 | 0 | 220 | 94 | 91 | 0 | 100 |  | 8057.9 | 2193 | 10250.9 | 3328 | 464 | 1919 | 2816 | 150 | 158 | 1318 | 96 | 1.9 | 0 | 0
16:00 | 72 | 0 | 0 | 0 | 363 | 83 | 69 | 358 | 271 | 96 | 0 | 400 | 200 | 98 | 78 | 48 | 0 | 0 | 92 | 50 | 63 | 92 | 149 | 0 | 55 | 49 | 40 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 25 | 48 | 0 | 78 | 80 | 120 | 0 | 16 | 0 | 207 | 0 | 100 | 0 | 32 | 51 | 14 | 80 | 97 | 44 | 19 | 2 | 0 | 100 | 100 | 325 | 276 | 173 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 48 | 28 | 18 | 11 | 33 | 15 | 96 | 46 | 95 | 20 | 1.2 | 66 | 65 | 47 | 47 | 163 | 290 | 48 | 79 | 45 | 98 | 0 | 41 | 9 | 270 | 14 | 8 | 100 | 262 | 0 | 95 | 130 | 100 | 125 |  | 464 | 32 | 220 | 10 | 16 | 15 | 0 | 52 | 0 | 5 | 0 | 88 | 28 | 110 | 8 | 0 | 0 | 48 | 9 | 50 | 40 | 43 | 44 | 50 | 0 | 6 | 8 | 11 | 0 | 0 | 133 | 0 | 13 | 0 | 214 | 0 | 220 | 93 | 91 | 0 | 173 |  | 7849.2 | 2294 | 10143.2 | 3314 | 464 | 1880 | 2697 | 133 | 158 | 1400 | 96 | 1.2 | 0 | 0
17:00 | 72 | 0 | 0 | 0 | 364 | 83 | 69 | 364 | 270 | 96 | 0 | 400 | 300 | 94 | 78 | 55 | 0 | 0 | 92 | 50 | 63 | 92 | 149 | 0 | 45 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 25 | 48 | 0 | 78 | 80 | 120 | 0 | 16 | 0 | 204 | 0 | 130 | 0 | 32 | 51 | 14 | 80 | 100 | 37 | 19 | 6 | 0 | 0 | 100 | 300 | 250 | 204 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 48 | 8 | 18 | 11 | 33 | 15 | 96 | 46 | 95 | 20 | 0.7 | 66 | 65 | 47 | 47 | 163 | 290 | 59 | 81 | 45 | 96 | 0 | 42 | 9 | 280 | 14 | 11 | 150 | 261 | 0 | 93 | 130 | 100 | 134 |  | 463 | 32 | 220 | 10 | 16 | 10 | 0 | 54 | 0 | 30 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 48 | 34 | 50 | 40 | 43 | 44 | 50 | 0 | 16 | 8 | 11 | 0 | 0 | 146 | 15 | 13 | 0 | 214 | 0 | 208 | 94 | 91 | 0 | 0 |  | 7918.7 | 2185 | 10103.7 | 3217 | 463 | 1904 | 2825 | 146 | 158 | 1294 | 96 | 0.7 | 0 | 0
18:00 | 72 | 0 | 0 | 0 | 365 | 83 | 70 | 346 | 272 | 96 | 0 | 400 | 200 | 99 | 78 | 55 | 0 | 0 | 92 | 50 | 70 | 102 | 149 | 0 | 66 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 30 | 48 | 0 | 78 | 80 | 120 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 40 | 72 | 14 | 80 | 99 | 37 | 19 | 2 | 0 | 0 | 100 | 300 | 272 | 212 | 78 | 100 | 43 | 0 | 5 | 51 | 86 | 48 | 8 | 18 | 11 | 33 | 15 | 100 | 47 | 95 | 20 | 0.2 | 68 | 65 | 50 | 48 | 163 | 276 | 42 | 84 | 45 | 96 | 0 | 43 | 9 | 260 | 14 | 11 | 150 | 282 | 0 | 50 | 130 | 51 | 125 |  | 463 | 24 | 230 | 10 | 16 | 15 | 0 | 55 | 13 | 50 | 0 | 78 | 25 | 110 | 0 | 0 | 0 | 48 | 34 | 50 | 33 | 43 | 45 | 50 | 0 | 16 | 10 | 11 | 0 | 0 | 140 | 15 | 13 | 0 | 130 | 0 | 140 | 99 | 50 | 0 | 0 |  | 7709.2 | 2016 | 9725.2 | 3205 | 463 | 1899 | 2648 | 140 | 158 | 1112 | 100 | 0.2 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 72 | 0 | 0 | 0 | 350 | 83 | 70 | 365 | 282 | 96 | 0 | 400 | 280 | 98 | 80 | 55 | 0 | 0 | 93 | 80 | 75 | 102 | 149 | 0 | 80 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 30 | 25 | 30 | 40 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 221 | 0 | 120 | 0 | 40 | 71 | 31 | 80 | 105 | 25 | 19 | 3 | 0 | 22 | 100 | 320 | 327 | 205 | 78 | 100 | 43 | 0 | 5 | 51 | 85 | 40 | 22 | 18 | 11 | 33 | 15 | 108 | 45 | 95 | 20 | 0 | 68 | 65 | 50 | 49 | 163 | 320 | 57 | 82 | 45 | 108 | 0 | 43 | 9 | 260 | 14 | 11 | 150 | 278 | 0 | 72 | 127 | 93 | 133 |  | 464 | 24 | 243 | 27 | 16 | 30 | 0 | 55 | 47 | 55 | 25 | 86 | 34 | 110 | 10 | 0 | 0 | 48 | 34 | 59 | 40 | 43 | 45 | 50 | 0 | 16 | 10 | 11 | 0 | 0 | 130 | 12 | 13 | 0 | 145 | 0 | 145 | 98 | 75 | 0 | 0 |  | 8184 | 2200 | 10384 | 3390 | 464 | 1916 | 2917 | 130 | 160 | 1299 | 108 | 0 | 0 | 0
19:30 | 72 | 0 | 0 | 0 | 350 | 83 | 70 | 410 | 281 | 96 | 0 | 400 | 305 | 100 | 80 | 55 | 0 | 0 | 97 | 100 | 84 | 102 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 30 | 45 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 221 | 0 | 135 | 0 | 40 | 71 | 31 | 80 | 105 | 24 | 19 | 7 | 0 | 0 | 110 | 345 | 300 | 181 | 105 | 100 | 43 | 0 | 5 | 51 | 85 | 40 | 43 | 19 | 11 | 33 | 15 | 124 | 48 | 95 | 20 | 0 | 68 | 65 | 50 | 49 | 163 | 278 | 59 | 84 | 45 | 100 | 0 | 44 | 9 | 260 | 14 | 11 | 150 | 279 | 0 | 100 | 125 | 100 | 140 |  | 464 | 24 | 240 | 53 | 16 | 40 | 0 | 54 | 46 | 70 | 25 | 86 | 37 | 110 | 10 | 0 | 0 | 48 | 34 | 100 | 40 | 43 | 46 | 50 | 0 | 16 | 10 | 11 | 0 | 0 | 142 | 15 | 14 | 0 | 214 | 0 | 220 | 95 | 91 | 0 | 0 |  | 8340 | 2464 | 10804 | 3359 | 464 | 1949 | 3078 | 142 | 160 | 1528 | 124 | 0 | 0 | 0
20:00 | 72 | 0 | 0 | 0 | 365 | 83 | 71 | 406 | 270 | 96 | 0 | 400 | 240 | 98 | 81 | 55 | 0 | 0 | 82 | 100 | 84 | 102 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 30 | 47 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 221 | 0 | 86 | 0 | 40 | 71 | 46 | 80 | 105 | 24 | 19 | 8 | 0 | 60 | 110 | 350 | 301 | 181 | 132 | 100 | 43 | 0 | 30 | 51 | 85 | 40 | 43 | 19 | 11 | 33 | 15 | 122 | 48 | 95 | 20 | 0 | 68 | 65 | 48 | 50 | 163 | 255 | 50 | 84 | 45 | 98 | 0 | 45 | 9 | 260 | 14 | 11 | 150 | 279 | 0 | 98 | 150 | 100 | 145 |  | 463 | 32 | 240 | 100 | 36 | 120 | 0 | 54 | 46 | 68 | 40 | 75 | 37 | 110 | 10 | 0 | 0 | 48 | 34 | 100 | 40 | 43 | 47 | 49 | 0 | 18 | 10 | 11 | 0 | 0 | 129 | 15 | 15 | 0 | 214 | 0 | 220 | 96 | 92 | 0 | 0 |  | 8339 | 2612 | 10951 | 3376 | 463 | 1995 | 3124 | 129 | 160 | 1582 | 122 | 0 | 0 | 0
21:00 | 72 | 0 | 0 | 0 | 365 | 83 | 71 | 409 | 271 | 96 | 0 | 400 | 305 | 100 | 80 | 55 | 0 | 0 | 97 | 100 | 84 | 102 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 30 | 50 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 40 | 71 | 46 | 80 | 106 | 33 | 19 | 14 | 0 | 100 | 100 | 320 | 298 | 118 | 160 | 100 | 20 | 0 | 10 | 51 | 85 | 41 | 52 | 18 | 11 | 33 | 15 | 74 | 47 | 95 | 20 | 0 | 67 | 65 | 51 | 50 | 163 | 298 | 59 | 86 | 45 | 98 | 0 | 44 | 9 | 280 | 14 | 11 | 170 | 280 | 0 | 98 | 161 | 99 | 145 |  | 464 | 30 | 240 | 27 | 82 | 147 | 0 | 55 | 43 | 68 | 40 | 154 | 20 | 110 | 10 | 0 | 0 | 48 | 34 | 100 | 40 | 43 | 45 | 50 | 0 | 18 | 10 | 11 | 0 | 0 | 120 | 15 | 14 | 0 | 214 | 0 | 220 | 96 | 93 | 0 | 0 |  | 8483 | 2661 | 11144 | 3433 | 464 | 2017 | 3219 | 120 | 160 | 1657 | 74 | 0 | 0 | 0
22:00 | 72 | 0 | 0 | 0 | 365 | 84 | 72 | 408 | 272 | 96 | 0 | 400 | 305 | 100 | 81 | 55 | 0 | 0 | 97 | 100 | 83 | 102 | 149 | 0 | 79 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 31 | 50 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 228 | 0 | 135 | 0 | 50 | 71 | 45 | 80 | 106 | 39 | 19 | 26 | 0 | 100 | 100 | 300 | 280 | 192 | 85 | 100 | 20 | 0 | 5 | 51 | 85 | 40 | 52 | 18 | 11 | 33 | 15 | 98 | 48 | 95 | 20 | 0 | 67 | 65 | 51 | 50 | 163 | 278 | 50 | 86 | 44 | 100 | 0 | 44 | 9 | 290 | 20 | 11 | 170 | 285 | 0 | 95 | 170 | 100 | 146 |  | 468 | 30 | 230 | 27 | 115 | 160 | 0 | 55 | 46 | 47 | 40 | 149 | 32 | 110 | 10 | 0 | 0 | 50 | 34 | 96 | 40 | 43 | 44 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 136 | 15 | 14 | 0 | 214 | 0 | 220 | 97 | 94 | 0 | 0 |  | 8496 | 2707 | 11203 | 3434 | 468 | 1974 | 3285 | 136 | 160 | 1648 | 98 | 0 | 0 | 0
23:00 | 72 | 0 | 0 | 0 | 365 | 85 | 72 | 406 | 272 | 96 | 0 | 400 | 305 | 100 | 81 | 55 | 0 | 0 | 97 | 100 | 82 | 102 | 149 | 0 | 79 | 51 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 31 | 50 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 229 | 0 | 130 | 0 | 51 | 71 | 33 | 80 | 106 | 44 | 19 | 26 | 0 | 100 | 100 | 302 | 335 | 179 | 78 | 100 | 20 | 0 | 5 | 35 | 85 | 40 | 52 | 18 | 11 | 32 | 15 | 88 | 47 | 95 | 20 | 0 | 67 | 66 | 52 | 50 | 163 | 306 | 59 | 86 | 45 | 130 | 0 | 44 | 9 | 260 | 20 | 11 | 170 | 219 | 0 | 91 | 168 | 100 | 146 |  | 469 | 32 | 230 | 27 | 115 | 160 | 0 | 55 | 46 | 46 | 0 | 148 | 35 | 110 | 10 | 0 | 0 | 50 | 34 | 97 | 40 | 43 | 44 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 142 | 14 | 15 | 0 | 214 | 0 | 220 | 96 | 94 | 0 | 0 |  | 8462 | 2677 | 11139 | 3541 | 469 | 1926 | 3179 | 142 | 160 | 1634 | 88 | 0 | 0 | 0
24:00 | 72 | 0 | 0 | 0 | 364 | 86 | 72 | 405 | 301 | 96 | 0 | 410 | 305 | 100 | 81 | 55 | 0 | 0 | 97 | 100 | 82 | 102 | 149 | 0 | 78 | 51 | 39 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 32 | 47 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 51 | 71 | 45 | 80 | 106 | 44 | 19 | 30 | 0 | 100 | 100 | 302 | 320 | 184 | 78 | 100 | 20 | 0 | 5 | 35 | 85 | 40 | 52 | 19 | 11 | 32 | 15 | 90 | 47 | 95 | 20 | 0 | 67 | 66 | 52 | 50 | 163 | 293 | 59 | 86 | 45 | 130 | 0 | 43 | 9 | 295 | 20 | 11 | 170 | 200 | 0 | 96 | 168 | 100 | 136 |  | 468 | 0 | 236 | 27 | 115 | 160 | 0 | 55 | 46 | 45 | 0 | 147 | 36 | 110 | 10 | 0 | 0 | 50 | 30 | 97 | 40 | 43 | 44 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 135 | 14 | 15 | 0 | 214 | 0 | 220 | 97 | 94 | 0 | 0 |  | 8505 | 2639 | 11144 | 3523 | 468 | 2006 | 3150 | 135 | 160 | 1612 | 90 | 0 | 0 | 0
KWH | 1416000 | 1078875 | 0 | 0 | 8650363 | 1053818 | 871808 | 8958970 | 6962000 | 1639300 | 0 | 9297000 | 6270051 | 2161920 | 1772160 | 1195191 | 0 | 0 | 2386000 | 1156800 | 1702080 | 1898064 | 3026880 | 688404 | 1830720 | 915500 | 927552 | 1242360 | 1328587 | 1286000 | 316152 | 600000 | 692820 | 566131 | 717600 | 1173204 | 0 | 1742000 | 1913000 | 2900000 | 0 | 365220 | 0 | 4993107 | 0 | 2513426 | 0 | 986400 | 1690136 | 745135 | 1843320 | 2265600 | 1035360 | 452208 | 388320 | 0 | 2097740 | 2484464 | 7507300 | 7082250 | 4269000 | 2057454 | 2389800 | 931176 | 0 | 150000 | 1049200 | 1772160 | 676408 | 539741 | 460620 | 242640 | 775600 | 407490 | 2547840 | 1134560 | 1786560 | 447228 | 17500 | 1548000 | 1574646 | 1195800 | 1175000 | 3463486 | 6898209 | 1355000 | 2016000 | 1022040 | 2839410 | 0 | 1058320 | 211320 | 7321500 | 431760 | 234960 | 1994880 | 5954070 | 0 | 1295557 | 3609600 | 1442465 | 3388320 |  | 11128000 | 218000 | 6377760 | 393120 | 739200 | 1170240 | 0 | 1043920 | 513600 | 721920 | 117375 | 2379667 | 653319 | 2668800 | 60255 | 0 | 0 | 868888 | 451254 | 1704136 | 1068510 | 953328 | 609541 | 1214880 | 0 | 284480 | 205740 | 249354 | 0 | 0 | 3277100 | 182000 | 222000 | 0 | 4156736 | 0 | 4199745 | 2289530 | 1575360 | 63500 | 403000 |  | 188472616 | 52164258 | 240636874 | 82917253 | 11128000 | 44498295 | 63469479 | 3277100 | 3655000 | 29126407 | 2547840 | 17500 | 0
Fuel Cost | 1217760 | 927832.5 | 0 | 0 | 5536232.32 | 853592.58 | 819499.52 | 5464971.7 | 4246820 | 15753673 | 0 | 6228990 | 95242074.69 | 13576857.6 | 11838028.8 | 7302617.01 | 0 | 0 | 2648460 | 17999808 | 10638000 | 12508241.76 | 29269929.6 | 4385133.48 | 10966012.8 | 14638845 | 6186771.84 | 8858026.8 | 8303668.75 | 8063220 | 237114 | 450000 | 0 | 0 | 0 | 11098509.84 | 0 | 0 | 0 | 3190000 | 0 | 3458633.4 | 0 | 68155910.55 | 0 | 55069163.66 | 0 | 8670456 | 18202764.72 | 7250163.55 | 11410150.8 | 14635776 | 6771254.4 | 384376.8 | 0 | 0 | 1908943.4 | 2260862.24 | 4654526 | 4886752.5 | 2988300 | 1419643.26 | 2294208 | 623887.92 | 0 | 138000 | 860344 | 1683552 | 7332262.72 | 4004878.22 | 354677.4 | 181980 | 597212 | 305617.5 | 17427225.6 | 850920 | 16418486.4 | 344365.56 | 0 | 1609920 | 1637631.84 | 1147968 | 1057500 | 2701519.08 | 4828746.3 | 1544700 | 2157120 | 1124244 | 3236927.4 | 0 | 984237.6 | 196527.6 | 4685760 | 323820 | 178569.6 | 34571270.4 | 43226548.2 | 0 | 22089246.85 | 25808640 | 24594028.25 | 0 |  | 56752800 | 6354700 | 4273099.2 | 3148891.2 | 6127968 | 18817459.2 | 0 | 16660963.2 | 5783136 | 8504217.6 | 924915 | 1641970.23 | 646785.81 | 19749120 | 2029388.4 | 0 | 0 | 9948767.6 | 4837442.88 | 15269058.56 | 9242611.5 | 8484619.2 | 6491611.65 | 12051609.6 | 0 | 312928 | 193395.6 | 188760.978 | 0 | 0 | 12649606 | 5865860 | 5942940 | 0 | 0 | 0 | 61568261.7 | 0 | 27300988.8 | 0 | 0 |  | 761700911.31 | 331763875.908 | 1093464787.218 | 61773145.388 | 56752800 | 31458427.05 | 576710544.79 | 12649606 | 0 | 336693038.39 | 17427225.6 | 0 | 0
Yesterday Day Peak | 72 | 0 | 0 | 0 | 365 | 70 | 0 | 345 | 275 | 96 | 0 | 430 | 250 | 93 | 80 | 47 | 0 | 0 | 97 | 44 | 70 | 85 | 149 | 0 | 79 | 49 | 39 | 54 | 55 | 55 | 17 | 25 | 26 | 25 | 25 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 210 | 0 | 100 | 0 | 32 | 74 | 32 | 80 | 91 | 37 | 19 | 3 | 0 | 100 | 100 | 295 | 230 | 190 | 78 | 100 | 40 | 0 | 5 | 51 | 85 | 0 | 10 | 19 | 11 | 25 | 22 | 122 | 47 | 90 | 20 | 2.4 | 65 | 66 | 48 | 48 | 163 | 320 | 59 | 82 | 45 | 130 | 0 | 43 | 9 | 280 | 13 | 11 | 100 | 220 | 0 | 98 | 163 | 53 | 146 |  | 463 | 0 | 284 | 10 | 16 | 0 | 0 | 55 | 0 | 0 | 0 | 90 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 35 | 0 | 51 | 0 | 14 | 7 | 11 | 0 | 0 | 138 | 0 | 0 | 0 | 130 | 0 | 130 | 95 | 85 | 40 | 0 |  | 9735.4 | DayPeak
Yesterday Evening Peak | 72 | 0 | 0 | 0 | 365 | 83 | 71 | 409 | 271 | 96 | 0 | 400 | 305 | 100 | 80 | 55 | 0 | 0 | 97 | 100 | 84 | 102 | 149 | 0 | 78 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 32 | 25 | 30 | 50 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 227 | 0 | 135 | 0 | 40 | 71 | 46 | 80 | 106 | 33 | 19 | 14 | 0 | 100 | 100 | 320 | 298 | 118 | 160 | 100 | 20 | 0 | 10 | 51 | 85 | 41 | 52 | 18 | 11 | 33 | 15 | 74 | 47 | 95 | 20 | 0 | 67 | 65 | 51 | 50 | 163 | 298 | 59 | 86 | 45 | 98 | 0 | 44 | 9 | 280 | 14 | 11 | 170 | 280 | 0 | 98 | 161 | 99 | 145 |  | 464 | 30 | 240 | 27 | 82 | 147 | 0 | 55 | 43 | 68 | 40 | 154 | 20 | 110 | 10 | 0 | 0 | 48 | 34 | 100 | 40 | 43 | 45 | 50 | 0 | 18 | 10 | 11 | 0 | 0 | 120 | 15 | 14 | 0 | 214 | 0 | 220 | 96 | 93 | 0 | 0 |  | 11144 | EvPeak
Forecast for Evening | 70 | 0 | 0 | 0 | 365 | 100 | 72 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 81 | 55 | 0 | 0 | 100 | 100 | 93 | 102 | 149 | 100 | 97 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 213 | 0 | 135 | 0 | 51 | 74 | 51 | 80 | 101 | 50 | 19 | 30 | 0 | 100 | 100 | 360 | 360 | 225 | 172 | 100 | 43 | 0 | 10 | 51 | 85 | 40 | 52 | 22 | 11 | 33 | 22 | 118 | 48 | 95 | 20 | 0 | 68 | 74 | 53 | 50 | 163 | 330 | 60 | 86 | 45 | 130 | 0 | 47 | 10 | 341 | 23 | 11 | 200 | 300 | 0 | 100 | 170 | 100 | 145 |  | 476 | 32 | 255 | 100 | 99 | 158 | 0 | 55 | 48 | 90 | 40 | 165 | 33 | 110 | 30 | 0 | 0 | 50 | 37 | 100 | 50 | 43 | 40 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 142 | 17 | 18 | 0 | 214 | 0 | 220 | 95 | 100
Forecast for Day | 70 | 0 | 0 | 0 | 365 | 85 | 72 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 42 | 55 | 0 | 0 | 100 | 100 | 93 | 102 | 149 | 100 | 97 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 80 | 80 | 120 | 0 | 16 | 0 | 213 | 0 | 135 | 0 | 51 | 74 | 51 | 80 | 101 | 50 | 19 | 30 | 0 | 100 | 100 | 360 | 360 | 225 | 80 | 100 | 43 | 0 | 5 | 51 | 85 | 0 | 52 | 22 | 11 | 33 | 22 | 102 | 48 | 95 | 20 | 2 | 68 | 74 | 53 | 50 | 163 | 330 | 60 | 86 | 45 | 130 | 0 | 47 | 10 | 341 | 23 | 11 | 100 | 100 | 0 | 0 | 170 | 100 | 135 |  | 476 | 0 | 280 | 30 | 99 | 158 | 0 | 0 | 0 | 0 | 0 | 160 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 0 | 52 | 0 | 18 | 10 | 11 | 0 | 0 | 142 |  | 18 | 0 | 130 | 0 | 130 | 95 | 0
Generation at 08:00(Today) | 70 | 0 | 0 | 0 | 270 | 84 | 73 | 350 | 300 | 13 | 0 | 370 | 200 | 50 | 81 | 55 | 0 | 0 | 102 | 0 | 7 | 102 | 115 | 0 | 80 | 0 | 27 | 54 | 55 | 55 | 22 | 25 | 22 | 25 | 33 | 25 | 0 | 81 | 80 | 120 | 0 | 16 | 0 | 194 | 0 | 50 | 0 | 40 | 8 | 16 | 80 | 99 | 30 | 19 | 31 | 0 | 100 | 100 | 302 | 280 | 180 | 80 | 100 | 20 | 0 | 5 | 51 | 50 | 0 | 0 | 19 | 11 | 33 | 15 | 102 | 48 | 64 | 20 | 1 | 68 | 66 | 53 | 50 | 130 | 279 | 59 | 50 | 45 | 80 | 0 | 41 | 9 | 290 | 21 | 8 | 0 | 67 | 0 | 0 | 156 | 0 | 17 | 0 | 427 | 0 | 285 | 10 | 98 | 70 | 0 | 0 | 0 | 36 | 0 | 139 | 25 | 80 | 0 | 0 | 0 | 0 | 0 | 72 | 40 | 43 | 0 | 50 | 0 | 15 | 9 | 11 | 0 | 0 | 130 | 0 | 0 | 0 | 130 | 0 | 130 | 11 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8659.6 | 7:00
| Highest Generation |  | 11203 | 22:00
| Day Peak Generation |  | 9735.4 | 11:00
| Evening Peak Generation |  | 11144 | 21:00
| HVDC Max Flow |  | 469 | 23:00
| HVDC EvPeak Flow |  | 464 | 21:00
| Load factor L.F |  | 89.5%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-07-20
Till now the maximum generation is : - |  |  | 11387 | 22:00 | Hrs on | 2018-07-18
The Summary of Yesterday's |  | 2018-07-19 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9735.4 | MW Hour : | 11:00 | Min. Gen. at | 8:00 | 8451 | MW
Evening Peak Generation : |  | 11144 | MW Hour : | 21:00 | Available Max Generation : |  | 12241 | MW
E.P. Demand (at gen end) : |  | 11144 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11300 | MW
Maximum Generation : |  | 11203 | MW Hour : | 22:00 | Reserve(Generation end) |  | 941 | MW
Total Gen. (MKWH) : |  | 240.6369 | System Load Factor : | 89.5% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -1140 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-07-20
Actual : | 103.56 | Ft.(MSL) , | Rule curve : | 86.88 | Ft.( MSL )
Gas Consumed : | Total = | 1046.61 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 93231572.438
|  | Coal : | 12649606 | Oil : | 913403583.18 | Total : | 1019284761.618
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3968.0746 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1349.5109 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1209.1431 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1092.572 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 987.3364 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 796.7459 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 445.3133 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 205.1357 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 614.4909 |  |  | 0 | 0%
Total | 0 |  | 10668.3227 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1,2 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
|  |  |  | 3) Ghorasal Unit-3,4,5 |  | 12) Santahar Peaking
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Kamrangirchar-Lalbagh 132 kV Ckt was shut down from 09:10 to 10:11 for maint by DPDC.
b) Kamrangirchar-Hasnabad 132 kV Ckt tripped at 09:51 showing dist B,C phase Z2 from Hasnabad end & No signal
at Kamrangirchar end.
c) Ghorasal-Ishurdi 230 kV Ckt-1 tripped at 10:36 showing DT,PT3,PTAW at Ishurdi end & PT3,PTAW from Ghorasal
end and was switched on at 11:43.
d) Ghorasal-Ishurdi 230 kV Ckt-2 tripped at 11:15 showing DT,PT3,PTAW at Ishurdi end & PT3,PTAW from Ghorasal
end and was switched on at 11:35.
e) Mymensing -Jamalpur 132 kV Ckt-2 tripped at 11:05 from both end showing C phase Z1 and was switched on at 11:13.
again tripped at 12:18 showing same relay and was switched on at 17:58.
f) Ghorasal-Ishurdi 230 kV Ckt-1 tripped at 12:12 from both end showing DT,DTRH2,PD3 relay and was switched on at
16:00.
g) Ghorasal-Ishurdi 230 kV Ckt-2 tripped at 13:14 from both end showing DT,DTRH2,PD3 relay and was switched on at
14:05.
h) Bheramara-Faridpur 132 kV Ckt -2 tripped at 13:44 showing dist Z2,ABC phase relay and was switched on at 14:18.
i) Ghorasal # 3 was under shut down at 09:24 due to Gas line maint work.
j) Ashuganj-Sirajganj 230 kV Ckt-2 shifted on Bus-1 due to Bus-2 Isolator problem.
k) Ashuganj #4 tripped at 16:30 due to vacuumed fall and was synchronized at 19:50.
l) Madaripur-Barisal 132 kV Ckt-1 tripped at 15:01 from both end showing dist Z1 from both end and was switched on at
15:24.
m) Ashuganj-Kishoreganj 132 kV Ckt-1 was shut down from 14:27 to 23:03 due to CT burst at Kishoreganj S/S under |  |  |  | About 30 MW power interruption occurred under Kishoreganj S/S
T3 transformer 33 kV side. |  |  |  | areas from 14:27 to 23:03.
n) Barisal(S)-Barisal(N) 132 kV Ckt-2 tripped at 01:23 from both end showing dist C phase at Barisal(S) end & dist
lockout at Barisal (N) end and was switched on at 02:11(20/7/18) again tripped showing dist C phase ,SOTF due to
conductor tear off tower # 726 C phase disk and was switched on at 07:50(20/7/18).
o) Faridpur-Madaripur 132 kV Ckt-1 tripped at 04:30 from both end showing dist A phase from both end and was
switched on at 05:54(20/7/18) again tripped showing same relay and was switched on at 07:55.
p) Mymensing T-1 & T2 transformer tripped at 05:51 showing E/F,O/C relay at 33 kV side and was switched on at 05:54. |  |  |  | About 120 MW power interruption occurred under Mymensing S/S
areas from 05:51 to 05:54.
q) Halishahar 132/33 kV T-1 transformer is under shut down since 07:03(20/7/18) due to C/M.
r) Hasnabad-Meghnaghat 230 kV Ckt1 is under shut down since 07:05(20/7/18) due to C/M.
s) Sirajganj-Bogra 132 kV Ckt-1 is under shut down since 07:18(20/7/18) due to D/W.
t) Hathazari 132/33 kV T-1 transformer is under shut down since 07:43(20/7/18) due to D/W.
u) Tongi(N) 132/33 kV T-1 transformer was under shut down since 21:58 due to D/W. |  |  |  | About 120 MW power interruption occurred under Tongi S/S
areas since 21:58.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-07-19 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 72 | 1416000 | Gas shortage
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 1078875 | Shut down
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8650363
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 71 | 871808 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 83 | 1053818 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 409 | 8958970 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 96 | 1639300 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 271 | 6962000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 9297000 | Gas shortage
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2161920
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 6270051 | FGMO
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 80 | 1772160 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1195191
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 0 | 688404 | Line problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 316152
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 97 | 2386000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 1156800
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 84 | 1702080 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 0 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 50 | 915500
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 102 | 1898064
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 927552 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1242360
25 | Kodda 149 MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 3026880
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 1328587
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1286000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 78 | 1830720 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1292820 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 25 | 566131 | Engine problem
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 30 | 717600
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 1173204
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 280 | 5954070
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
35 | Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 100 | 98 | 1295557
36 | Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 100 | 99 | 1442465
| Summit Gazipur-1 150MW |  | IPP | 149 MW | 0 | 145 | 3388320
| Dhaka area Total |  |  |  | 5399 | 3977 | 85862722
37 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
| Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
38 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 365220 | Engine problem
39 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 33 | 1035360 | Engine problem
40 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 160 | 3655000 | # 3 under maint.
41 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
42 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 227 | 4993107 | FGMO
43 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2513426
44 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 40 | 986400
45 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 71 | 1690136
46 | Dohazari Peaking |  | PDB | 6*17 | 102 | 46 | 745135 | Engine problem
47 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1843320 | Engine problem
48 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 452208
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 14 | 388320
49 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 106 | 2265600
| Chittagong area Total |  |  |  | 1561 | 1067 | 23833232
50 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Under shut down
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2097740
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2484464 | Gas shortage
51 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 118 | 4269000 | FGMO
52 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 7507300 | FGMO
53 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 298 | 7082250 | FGMO
54 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 20 | 931176
55 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
56 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 10 | 150000 | Gas shortage
57 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 160 | 2057454 | Gas shortage
58 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 1049200
59 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1772160
60 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 41 | 676408
61 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2389800 | ST S/D
62 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 18 | 460620
63 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 242640
** | Tripura |  | Imported power | 0 | 160 | 74 | 2547840 | Restriction from NLDC Delhi
64 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 775600
65 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 52 | 539741
66 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 407490 | Engine problem
67 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 170 | 1994880 | Line problem
| Comilla Area Total |  |  |  | 2541 | 1776 | 39435763
68 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 47 | 1134560 | Gas shortage
69 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 447228
70 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1786560
71 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 17500
72 | United Mymensingh PPL |  | IPP | 200 | 200 | 161 | 3609600 | Engine problem
| Mymensingh Area Total |  |  |  | 522 | 323 | 6995448
73 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 67 | 1548000
74 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 65 | 1574646
75 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3463486
76 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 298 | 6898209 | FGMO
77 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 51 | 1195800
78 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 1175000
79 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 234960
80 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 59 | 1355000 | FGMO
81 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 2016000
82 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 45 | 1022040 | Engine problem
83 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 98 | 2839410
84 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
85 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 44 | 1058320
86 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 14 | 431760 | Engine problem
87 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 280 | 7321500 | FGMO
88 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 211320
| Sylhet Area Total |  |  |  | 1549 | 1340 | 32345451
89 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 30 | 218000 | Engine problem
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 464 | 11128000
90 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 27 | 393120 | Fuel shortage
91 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 82 | 739200 | Fuel shortage
92 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 43 | 513600
93 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 147 | 1170240 | Machine problem
94 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 68 | 721920
95 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 240 | 6377760 | Gas shortage
96 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 117375
97 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 55 | 1043920
98 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 93 | 1575360
| Khulna Area Total |  |  |  | 1769 | 1289 | 23998495
99 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2668800
100 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 10 | 60255
101 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 20 | 653319
102 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 154 | 2379667
103 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 96 | 2289530
| Barisal Area Total |  |  |  | 462 | 390 | 8051571
104 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
105 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 48 | 868888
106 | Bera Peaking |  | PDB | 9*8.29 | 71 | 34 | 451254
107 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 1068510 | Engine problem
108 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 953328 | Engine problem
109 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 609541
110 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 214 | 0
111 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 220 | 0
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 63500 | Under maint.
112 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 0 | 0 | Under maint.
113 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 284480 | Engine problem
114 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 205740
115 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 249354
116 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 50 | 1214880
117 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 1704136
| Rajshahi Area Total |  |  |  | 1123 | 833 | 7673611
118 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
119 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 120 | 3277100
120 | Rangpur GT |  | PDB | 1*20 | 20 | 15 | 182000
121 | Saidpur GT |  | PDB | 1*20 | 20 | 14 | 222000
| Rangpur Area Total |  |  |  | 484 | 149 | 3681100
| Total |  |  |  | 15410 | 11144 | 231877393
| Eastern Grid Total |  |  |  | 11572 | 8483 | 188472616
| Western Grid Total |  |  |  | 3838 | 2661 | 43404777
| National Grid Total |  |  |  | 15410 | 11144 | 231877393
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-07-19 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7300 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3208 | MW
i) Dhaka area |  |  | 4141 | MW | i) Khulna area |  |  | 1238 | MW
ii) Chittagong area |  |  | 1071 | MW | ii) Rajshahi area |  |  | 1103 | MW
iii) Comilla area |  |  | 894 | MW | iii) Barisal area |  |  | 282 | MW
iv) Mymensingh area |  |  | 701 | MW | iv) Rangpur area |  |  | 585 | MW
v) Sylhet area |  |  | 493 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10508 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 142 | 1400 | Kishorganj | 84 | 100 | Goalpara | 40 | 1930
Munsiganj | 118 | 2000 | Netrokona | 84 | 2200 | Central s/s | 78 | 2100
Sonargaon | 43 | 2100 | Jamalpur | 108 | 100 | Noapara | 90 | 2200
Shyampur | 170 | 1100 | Sherpur | 80 | 2300 | Jessore | 147 | 2200
Bhulta | 194 | 1200 | Srimongal | 42 | 2000 | Jhenida | 90 | 1930
Madanganj | 58 | 2300 | Shahjibazar | 113 | 2200 | Bottail | 116 | 100
Shitalakhya | 118 | 2400 | Fenchuganj | 52 | 2000 | G.K Project | 52 | 2300
Rahim steel | 10 | 1400 | Kulawara | 45 | 1830 | Faridpur | 140 | 2300
Matuail | 92 | 1600 | Sylhet | 160 | 1830 | Madaripur | 138 | 2300
Ghorasal | 86 | 2300 | Chatak | 30 | 2000 | Gopalganj | 86 | 2200
Narsingdi | 124 | 2000 | Sunamganj | 37 | 2100 | Bagerhat | 77 | 2300
Haripur (SBU) | 95 | 1700 | Biani Bazar | 49 | 2100 | Mongla | 36 | 900
Ullon | 105 | 1900 | Comilla (S) | 124 | 1930 | Satkhira | 103 | 2100
Hasnabad | 226 | 2100 | Comilla(N) | 147 | 1930 | Gallamari | 48 | 1300
Magbazar | 162 | 1500 | Chandpur | 109 | 2300 | Magura | 48 | 1900
Maniknagar | 108 | 1200 | Feni | 130 | 2200 | Chuadanga | 70 | 100
Bangabhaban | 44 | 1300 | Chowmuhani | 176 | 2200 | Barisal | 124 | 2100
Narinda | 96 | 1300 | Ashuganj | 63 | 2200 | Patuakhali | 51 | 2000
Dhanmondi | 151 | 1300 | Daudkandi | 84 | 2300 | Bhandaria | 48 | 2100
Lalbag | 83 | 2100 | B.Baria | 138 | 2100 | Ishurdi | 51 | 100
Madartek | 56 | 1400 | Ramganj | 37 | 2100 | Ruppur Paromanobik | 2 | 1600
Mirpur | 113 | 1930 | Madunaghat | 52 | 2000 | Natore | 107 | 100
Kalyanpur | 129 | 1500 | Hathazari | 96 | 2000 | Bogra | 228 | 100
Gulshan | 166 | 1300 | Khulshi | 208 | 1500 | Noagaon | 97 | 100
Uttara | 99 | 100 | Halishahar | 246 | 1500 | Rajshahi | 161 | 2000
Kamrangirchar | 87 | 2000 | Baraulia | 163 | 300 | C.Nawabganj | 77 | 2100
Savar | 143 | 1500 | Sikalbaha | 37 | 2000 | Amnura | 46 | 2100
Bhasantec | 177 | 1500 | Dohazari | 86 | 2000 | Pabna | 108 | 2000
Agargaon | 51 | 2000 | Cox'sbazar | 94 | 2000 | Shahjadpur | 100 | 2100
Satmosjid | 111 | 1500 | Chandraghona | 34 | 2100 | Serajganj | 79 | 2000
Tongi | 147 | 1500 | Kaptai | 4 | 2100 | Niyamatpur | 60 | 600
Kabirpur | 216 | 1400 | A. Khaer Stl. | 10 | 100 | Joypurhat | 40 | 2000
Basundhara | 132 | 2100 | Bakulia | 114 | 2000 | Rangpur | 115 | 1900
Manikganj | 115 | 2000 | Julda | 20 | 1900 | Lalmonirhat | 80 | 2000
Joydevpur | 236 | 1000 | TK chemical | 2 | 1200 | Saidpur | 94 | 1900
New Tongi | 110 | 1900 | Modern Steel | 12 | 1000 | Purbasadipur | 91 | 100
Korda | 268 | 2100 | Shahmirpur | 29 | 100 | Thakurgaon | 76 | 2100
Dhamrai | 26 | 2300 | Abul Khair 230 | 190 | 1300 | Palashbari | 99 | 100
Tangail | 172 | 2100 | BSRM | 112 | 1200 | Barapukuria | 53 | 2100
Mymensing | 260 | 2100 | Khagrachhari | 18 | 1900 | Panchagar | 34 | 100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
Date: | 2018-07-19
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 393 | 6:00 | 380 | 22:00 | Kaliakoir | 373 | 6:00 | 360 | 16:00
Bheramara | 398 | 6:00 | 382 | 20:00 | Bhulta | 385 | 20:00 | 372 | 11:00
Ashuganj(N) | 390 | 19:00 | 380 | 8:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 224 | 11:00 | Tongi | 223 | 4:00 | 212 | 13:00
Ishurdi | 235 | 12:00 | 225 | 1:00 | Comilla (N) | 231 | 2:00 | 226 | 11:00
Ashuganj | 236 | 20:00 | 230 | 1:00 | Hathazari | 221 | 22:00 | 210 | 13:00
Serajganj | 226 | 16:00 | 215 | 1:00 | Megnaghat | 228 | 1:00 | 220 | 12:00
Baghabari | 225 | 16:00 | 218 | 1:00 | Fenchuganj | 238 | 20:00 | 232 | 23:00
Barapukuria | 232 | 15:00 | 216 | 6:00 | Siddhirganj | 224 | 1:00 | 218 | 15:00
Bogra | 216 | 16:00 | 198 | 1:00 | Maniknagar | 223 | 1:00 | 215 | 16:00
Khulna South | 236 | 16:00 | 222 | 19:00 | Old Airport | 224 | 1:00 | 214 | 16:00
Rampura | 222 | 6:00 | 216 | 12:00 | Barisal | 234 | 20:00 | 222 | 13:00
Haripur | 222 | 1:00 | 218 | 15:00 | AKSML | 220 | 6:00 | 211 | 13:00
Hasnabad | 225 | 20:00 | 218 | 12:00 | BSRM | 222 | 6:00 | 215 | 12:00
Aminbazar | 225 | 1:00 | 216 | 16:00 | Bibiyana | 235 | 20:00 | 229 | 16:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1830 | 131 | 800 | B.Baria | 134 | 700 | 132 | 1900
Munsiganj | 136 | 100 | 132 | 1600 | Ramganj | 130 | 2300 | 119 | 1600
Megnaghat | 134 | 2000 | 131 | 1830 | Madanhat | 136 | 1700 | 129 | 1400
Shyampur | 133 | 1830 | 126 | 700 | Hathazari | 130 | 1400 | 127 | 1900
Bhulta | 129 | 1800 | 125 | 1600 | Khulshi | 127 | 700 | 123 | 1500
Madanganj | 139 | 2000 | 130 | 700 | Halishahar | 131 | 700 | 125 | 1500
Shitalakhya | 140 | 100 | 131 | 800 | Baraulia | 129 | 700 | 124 | 1500
Rahim steal | 135 | 2000 | 131 | 700 | Sikalbaha | 131 | 700 | 126 | 1500
Matuail | 134 | 2000 | 130 | 1600 | Dohazari | 130 | 700 | 123 | 2100
Ghorasal | 135 | 1800 | 133 | 1700 | Cox'sbazar | 119 | 500 | 110 | 900
Narsinghdi | 131 | 200 | 126 | 1600 | Chandraghona | 131 | 800 | 128 | 1400
Haripur (SBU) | 135 | 100 | 131 | 700 | Kaptai | 132 | 100 | 129 | 1500
Ullon | 133 | 200 | 126 | 1100 | A. Khaer Stl. | 127 | 700 | 125 | 2100
Hasnabad | 139 | 100 | 132 | 1200 | Bakulia | 129 | 700 | 124 | 1500
Magbazar | 135 | 600 | 124 | 1600 | Julda | 130 | 500 | 125 | 1400
Maniknagar | 133 | 100 | 129 | 1600 | TK Chemical | 132 | 500 | 129 | 1100
Bangabhaban | 133 | 100 | 129 | 1600 | Modern Steel | 129 | 400 | 125 | 1200
Narinda | 133 | 100 | 129 | 1600 | Shahmirpur | 128 | 1900 | 124 | 1500
Dhanmondi | 133 | 100 | 129 | 1600 | Khagrachhari | 132 | 600 | 126 | 1600
Lalbag | 138 | 2000 | 130 | 1200 | Goalpara | 137 | 1700 | 129 | 1300
Madartek | 133 | 200 | 124 | 1600 | Central s/s | 137 | 1700 | 128 | 1300
Mirpur | 134 | 100 | 128 | 1300 | Noapara | 135 | 900 | 126 | 1300
Kalyanpur | 137 | 700 | 127 | 1600 | Jessore | 129 | 1600 | 122 | 1300
Gulshan | 132 | 100 | 124 | 1600 | Jhenida | 128 | 1800 | 119 | 100
Uttara | 137 | 100 | 122 | 1500 | Bottail | 135 | 1600 | 129 | 100
Kamrangirchar | 133 | 100 | 122 | 1500 | G.K.Project | 140 | 900 | 135 | 100
Savar | 134 | 200 | 124 | 1600 | Faridpur | 133 | 1930 | 125 | 2200
Bhasantec | 133 | 600 | 124 | 1200 | Madaripur | 135 | 1930 | 124 | 700
Agargaon | 133 | 200 | 125 | 1200 | Gopalganj | 139 | 2000 | 122 | 1100
Satmosjid | 133 | 600 | 124 | 1600 | Bagerhat | 135 | 1700 | 129 | 1100
Tongi | 134 | 1930 | 128 | 1500 | Mongla | 134 | 1800 | 126 | 100
Kabirpur | 135 | 500 | 127 | 1500 | Satkhira | 135 | 900 | 126 | 1300
Basundhara | 131 | 300 | 126 | 1500 | Gallamari | 138 | 1930 | 130 | 100
Manikganj | 137 | 300 | 130 | 2100 | Magura | 127 | 1800 | 117 | 2300
Joydevpur | 138 | 1400 | 130 | 800 | Chuadanga | 124 | 1800 | 111 | 100
New Tongi | 134 | 100 | 128 | 1600 | Barisal | 138 | 1930 | 131 | 1300
Kodda | 135 | 2100 | 128 | 800 | Patuakhali | 135 | 1930 | 126 | 1300
Dhamrai | 136 | 600 | 128 | 1500 | Bhandaria | 136 | 1800 | 126 | 1300
Tangail | 132 | 400 | 126 | 2200 | Ishurdi | 140 | 600 | 135 | 100
Mymensing | 128 | 600 | 121 | 100 | Ruppur Paromanobik | 140 | 1600 | 132 | 100
Kishorganj | 135 | 1500 | 122 | 100 | Natore | 137 | 1200 | 128 | 100
Netrokona | 125 | 1000 | 115 | 2100 | Bogra | 133 | 1600 | 119 | 100
Jamalpur | 138 | 1700 | 125 | 800 | Noagaon | 124 | 1500 | 108 | 100
Sherpur | 138 | 1700 | 123 | 1830 | Rajshahi | 134 | 1500 | 125 | 2100
Srimongal | 138 | 600 | 133 | 1900 | C.Nawabganj | 134 | 1200 | 124 | 2100
Shahjibazar | 136 | 600 | 132 | 2100 | Amnura | 137 | 1500 | 127 | 2100
Fenchuganj | 136 | 400 | 133 | 1930 | Pabna | 134 | 1600 | 127 | 100
Khulawara | 135 | 600 | 132 | 1900 | Shahjadpur | 139 | 1200 | 134 | 100
Sylhet | 135 | 500 | 131 | 1900 | Serajganj | 132 | 1500 | 123 | 100
Chatak | 135 | 600 | 129 | 1930 | Niyamatpur | 123 | 1500 | 106 | 100
Sunamganj | 133 | 400 | 129 | 2200 | Joypurhat | 123 | 1600 | 108 | 100
Biani Bazar | 134 | 600 | 128 | 2100 | Rangpur | 119 | 1600 | 101 | 100
Comilla(s) | 126 | 700 | 119 | 2100 | Lalmonirhat | 112 | 1600 | 96 | 1000
Comilla(n) | 138 | 1000 | 130 | 1500 | Saidpur | 119 | 1500 | 100 | 100
Chandpur | 127 | 1930 | 120 | 2300 | Purbasadipur | 128 | 1500 | 113 | 100
Feni | 120 | 700 | 115 | 2200 | Thakurgaon | 120 | 1500 | 102 | 400
Chowmuhani | 122 | 1000 | 116 | 2200 | Palashbari | 118 | 1700 | 102 | 100
Ashuganj | 136 | 1800 | 132 | 100 | Barapukuria | 132 | 1500 | 116 | 600
Daudkandi | 139 | 2000 | 127 | 800 | Panchagar | 120 | 1700 | 102 | 100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division

## L-Curve
Date | 2018-07-19
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 840 | 8505 | 2639 | 11144 |  |  |  | QF-LDC-12
0:30 | 990 | 8508 | 2417 | 10925 | Date: | 2018-07-19
1:00 | 1140 | 8511 | 2195 | 10706
1:30 | 1130 | 8348.5 | 2197 | 10545.5
2:00 | 1120 | 8186 | 2199 | 10385
2:30 | 1100 | 8055.5 | 2173.5 | 10229 | [5 empty] | Gen. at Eve. Peak | 11144 | 11144 MW (21:00 )
3:00 | 1080 | 7925 | 2148 | 10073 | [6 empty] | 21:00
3:30 | 1065 | 7838 | 2121 | 9959 | [5 empty] | Gen. at Day Peak | 9735.4 | 9735.4 MW (11:00 )
4:00 | 1050 | 7751 | 2094 | 9845 | [6 empty] | 11:00
4:30 | 1025 | 7780 | 2117.5 | 9897.5 | [5 empty] | Highest Generation | 11203
5:00 | 1000 | 7809 | 2141 | 9950 | [6 empty] | 22:00
5:30 | 920 | 7514.05 | 1979.5 | 9493.55
6:00 | 840 | 7219.1 | 1818 | 9037.1
6:30 | 840 | 7044.35 | 1804 | 8848.35
7:00 | 840 | 6869.6 | 1790 | 8659.6
7:30 | 840 | 7002.4 | 1781.5 | 8783.9
8:00 | 840 | 7135.2 | 1773 | 8908.2
8:30 | 820 | 7378.9 | 1819.5 | 9198.4
9:00 | 800 | 7622.6 | 1866 | 9488.6
9:30 | 790 | 7655.25 | 1868.5 | 9523.75
10:00 | 780 | 7687.9 | 1871 | 9558.9
10:30 | 910 | 7767.15 | 1880 | 9647.15
11:00 | 1040 | 7846.4 | 1889 | 9735.4
11:30 | 790 | 7740.85 | 1911 | 9651.85
12:00 | 540 | 7635.3 | 1933 | 9568.3
12:30 | 630 | 7684.8 | 2049 | 9733.8
13:00 | 720 | 7734.3 | 2165 | 9899.3
13:30 | 505 | 7726.3 | 2150.5 | 9876.8
14:00 | 290 | 7718.3 | 2136 | 9854.3
14:30 | 350 | 7888.1 | 2164.5 | 10052.6
15:00 | 410 | 8057.9 | 2193 | 10250.9
15:30 | 385 | 7953.55 | 2243.5 | 10197.05
16:00 | 360 | 7849.2 | 2294 | 10143.2
16:30 | 440 | 7883.95 | 2239.5 | 10123.45
17:00 | 520 | 7918.7 | 2185 | 10103.7
17:30 | 605 | 7813.95 | 2100.5 | 9914.45
18:00 | 690 | 7709.2 | 2016 | 9725.2
18:30 | 745 | 7946.6 | 2108 | 10054.6
19:00 | 800 | 8184 | 2200 | 10384
19:30 | 820 | 8340 | 2464 | 10804
20:00 | 780 | 8339 | 2612 | 10951 |  |  |  | Executive Engineer
20:30 | 785 | 8411 | 2636.5 | 11047.5 |  |  |  | Network Operation Division
21:00 | 790 | 8483 | 2661 | 11144
21:30 | 815 | 8489.5 | 2684 | 11173.5
22:00 | 840 | 8496 | 2707 | 11203 |  |  |  |  | Page 6 of 7
22:30 | 830 | 8479 | 2692 | 11171
23:00 | 820 | 8462 | 2677 | 11139
23:30 | 830 | 8483.5 | 2658 | 11141.5
24:00 | 840 | 8505 | 2639 | 11144
11144 MW (21:00 )
9735.4 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-07-19 |  | Energy | 240636874
[10 empty] | 2018-07-19 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3523 | 468 | 2006 | 3150 | 135 | 160 | 1612 | 0 | 90
0:30 | 3544.5 | 466 | 1944 | 3116 | 133.5 | 160 | 1455.5 | 0 | 105.5 | Date: | 2018-07-19
1:00 | 3566 | 464 | 1882 | 3082 | 132 | 160 | 1299 | 0 | 121
1:30 | 3554 | 464 | 1876.5 | 2968.5 | 131 | 160 | 1270.5 | 0 | 121 | [7 empty] | Total Energy | 240.6369 | Total Energy Gen 240.637 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 240.637 MKWHr
2:00 | 3542 | 464 | 1871 | 2855 | 130 | 160 | 1242 | 0 | 121 | [7 empty] | Energy not Served | 0
2:30 | 3541 | 464 | 1884 | 2696 | 128.5 | 160 | 1234.5 | 0 | 121 | [7 empty] | Energy Requirement | 240.6369
3:00 | 3540 | 464 | 1897 | 2537 | 127 | 160 | 1227 | 0 | 121
3:30 | 3594 | 464 | 1921 | 2389.5 | 129 | 160.5 | 1180.5 | 0 | 120.5 | [6 empty] | Shortage
4:00 | 3648 | 464 | 1945 | 2242 | 131 | 161 | 1134 | 0 | 120
4:30 | 3629 | 464 | 1941.5 | 2293 | 134.5 | 161 | 1156.5 | 0 | 118
5:00 | 3610 | 464 | 1938 | 2344 | 138 | 161 | 1179 | 0 | 116
5:30 | 3577.5 | 464 | 1908.5 | 2152 | 131.5 | 160.5 | 990.5 | 0 | 109
6:00 | 3545 | 464 | 1879 | 1960 | 125 | 160 | 802 | 0 | 102
6:30 | 3608 | 464 | 1853.5 | 1764 | 125 | 160 | 777.5 | 0 | 96 |  |  |  |  | Coal
7:00 | 3671 | 464 | 1828 | 1568 | 125 | 160 | 753 | 0 | 90
7:30 | 3659 | 464 | 1863 | 1643 | 117 | 160 | 785.5 | 0 | 91.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3647 | 464 | 1898 | 1718 | 109 | 160 | 818 | 0 | 93
8:30 | 3606 | 464 | 1850 | 2068.5 | 114.5 | 160 | 834.5 | 0 | 99.5
9:00 | 3565 | 464 | 1802 | 2419 | 120 | 160 | 851 | 0 | 106
9:30 | 3496 | 464 | 1806 | 2490.5 | 123.5 | 160 | 873 | 0 | 109
10:00 | 3427 | 464 | 1810 | 2562 | 127 | 160 | 895 | 0 | 112
10:30 | 3425.5 | 463.5 | 1833 | 2628.5 | 132.5 | 160 | 885 | 0 | 117
11:00 | 3424 | 463 | 1856 | 2695 | 138 | 160 | 875 | 0 | 122
11:30 | 3406.5 | 463.5 | 1842.5 | 2573.5 | 144 | 160 | 942.5 | 0 | 117
12:00 | 3389 | 464 | 1829 | 2452 | 150 | 160 | 1010 | 0 | 112
12:30 | 3399 | 464 | 1848 | 2472.5 | 153 | 160 | 1123 | 0 | 112
13:00 | 3409 | 464 | 1867 | 2493 | 156 | 160 | 1236 | 0 | 112
13:30 | 3409 | 464 | 1867 | 2493 | 156 | 160 | 1236 | 0 | 112
14:00 | 3409 | 464 | 1867 | 2493 | 156 | 160 | 1236 | 0 | 112
14:30 | 3368.5 | 464 | 1893 | 2654.5 | 153 | 159 | 1277 | 0 | 104
15:00 | 3328 | 464 | 1919 | 2816 | 150 | 158 | 1318 | 0 | 96
15:30 | 3321 | 464 | 1899.5 | 2756.5 | 141.5 | 158 | 1359 | 0 | 96
16:00 | 3314 | 464 | 1880 | 2697 | 133 | 158 | 1400 | 0 | 96
16:30 | 3265.5 | 463.5 | 1892 | 2761 | 139.5 | 158 | 1347 | 0 | 96
17:00 | 3217 | 463 | 1904 | 2825 | 146 | 158 | 1294 | 0 | 96
17:30 | 3211 | 463 | 1901.5 | 2736.5 | 143 | 158 | 1203 | 0 | 98
18:00 | 3205 | 463 | 1899 | 2648 | 140 | 158 | 1112 | 0 | 100
18:30 | 3297.5 | 463.5 | 1907.5 | 2782.5 | 135 | 159 | 1205.5 | 0 | 104
19:00 | 3390 | 464 | 1916 | 2917 | 130 | 160 | 1299 | 0 | 108
19:30 | 3359 | 464 | 1949 | 3078 | 142 | 160 | 1528 | 0 | 124
20:00 | 3376 | 463 | 1995 | 3124 | 129 | 160 | 1582 | 0 | 122
20:30 | 3404.5 | 463.5 | 2006 | 3171.5 | 124.5 | 160 | 1619.5 | 0 | 98
21:00 | 3433 | 464 | 2017 | 3219 | 120 | 160 | 1657 | 0 | 74
21:30 | 3433.5 | 466 | 1995.5 | 3252 | 128 | 160 | 1652.5 | 0 | 86
22:00 | 3434 | 468 | 1974 | 3285 | 136 | 160 | 1648 | 0 | 98
22:30 | 3487.5 | 468.5 | 1950 | 3232 | 139 | 160 | 1641 | 0 | 93
23:00 | 3541 | 469 | 1926 | 3179 | 142 | 160 | 1634 | 0 | 88
23:30 | 3532 | 468.5 | 1966 | 3164.5 | 138.5 | 160 | 1623 | 0 | 89 | Max Temp. in Dhaka |  | 37.6° C
24:00 | 3523 | 468 | 2006 | 3150 | 135 | 160 | 1612 | 0 | 90
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 240.637 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 240.637 MKWHr
Note on W13: Author:

## Generation
2018-07-19
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 80 | 80 | 80 | 81 | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 78 | 78 | 78 | 78 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1742000
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913000
3 | Chittagong ST-1 (Raozan) | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 365220
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 203 | 201 | 203 | 222 | 202 | 203 | 206 | 216 | 200 | 205 | 210 | 198 | 203 | 202 | 210 | 207 | 204 | 202 |  | 221 | 221 | 221 | 227 | 228 | 229 | 227 | 4993107
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 135 | 70 | 50 | 50 | 100 | 50 | 80 | 135 | 100 | 135 | 100 | 100 | 100 | 130 | 130 | 100 | 130 | 50 |  | 120 | 135 | 86 | 135 | 135 | 130 | 135 | 2513426
| Dohazari Peaking | 48 | 48 | 47 | 47 | 47 | 17 | 17 | 17 | 17 | 17 | 32 | 32 | 31 | 31 | 14 | 14 | 14 | 14 |  | 31 | 31 | 46 | 46 | 45 | 33 | 45 | 745135
12 | Hathazari peaking | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 64 | 51 | 51 | 72 |  | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 1690136
| Daudkandi bangla trak | 150 | 80 | 0 | [5 empty] | 50 | 90 | 100 | 10 | 10 | 10 | 100 | 100 | 150 | 150 |  | 150 | 150 | 150 | 170 | 170 | 170 | 170 | 1994880
14 | Daudkandi Peaking 52MW | 41 | 41 | 41 | 0 | 0 | 0 | 0 |  |  |  | 0 | 44 | 49 | 49 | 48 | 48 | 48 | 48 |  | 40 | 40 | 40 | 41 | 40 | 40 | 40 | 676408
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 102 | 101 | 101 | 101 | 102 | 97 | 97 | 99 | 99 | 99 | 97 | 95 | 95 | 98 | 94 | 92 | 92 | 92 |  | 93 | 97 | 82 | 97 | 97 | 97 | 97 | 2386000
17 | Siddhirganj CCPP-335 MW
18 | Summit Gazipur | 285 | 285 | 285 | 285 | 285 | 268 | 150 | 160 | 221 | 221 | 220 | 220 | 220 | 260 | 278 | 262 | 261 | 282 |  | 278 | 279 | 279 | 280 | 285 | 219 | 200 | 5954070
19 | Ashuganj 195MW Modular | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 105 | 132 | 160 | 85 | 78 | 78 | 2057454
20 | Ghorasal ST: Unit-1,2 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1416000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 0 | 0 | [15 empty] | 1078875
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 365 | 365 | 365 | 365 | 365 | 340 | 365 | 365 | 365 | 365 | 365 | 365 | 363 | 365 | 365 | 363 | 364 | 365 |  | 350 | 350 | 365 | 365 | 365 | 365 | 364 | 8650363
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 |  |  | 22 | 0 | 60 | 100 | 100 | 100 | 100 | 2097740
30 | Ashuganj ST: Unit- 5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 110 | 110 | 100 | 100 | 100 | 100 | 2484464
32 | Ashuganj Engines TSK | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 20 | 20 | 20 | 20 | 931176
33 | Ashuganj CCPP 225 MW | 155 | 174 | 168 | 160 | 169 | 171 | 166 | 168 | 178 | 179 | 190 | 184 | 183 | 161 | 176 | 173 | 204 | 212 |  | 205 | 181 | 181 | 118 | 192 | 179 | 184 | 4269000
34 | Ashuganj CCPP(South) | 300 | 300 | 305 | 345 | 300 | 300 | 320 | 305 | 272 | 279 | 230 | 238 | 235 | 231 | 257 | 276 | 250 | 272 |  | 327 | 300 | 301 | 298 | 280 | 335 | 320 | 7082250
| Ashuganj CCPP(North) | 258 | 268 | 268 | 270 | 268 | 268 | 288 | 288 | 285 | 285 | 295 | 335 | 360 | 355 | 340 | 325 | 300 | 300 |  | 320 | 345 | 350 | 320 | 300 | 302 | 302 | 7507300
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2389800
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 400 | 350 | 345 | 370 | 360 | 340 | 365 | 380 | 360 | 370 | 345 | 355 | 350 | 365 | 375 | 358 | 364 | 346 |  | 365 | 410 | 406 | 409 | 408 | 406 | 405 | 8958970
40 | Meghnaghat CCPP 450MW | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 430 | 430 | 430 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 410 | 9297000
41 | Haripur Power CCPP 360MW | 301 | 321 | 322 | 348 | 350 | 334 | 331 | 293 | 292 | 276 | 275 | 276 | 270 | 271 | 271 | 271 | 270 | 272 |  | 282 | 281 | 270 | 271 | 272 | 272 | 301 | 6962000
42 | Mymensingh RPCL 210MW | 49 | 48 | 48 | 49 | 48 | 50 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 46 | 46 | 46 | 47 |  | 45 | 48 | 48 | 47 | 48 | 47 | 47 | 1134560
43 | Haripur NEPC 110MW | 96 | 96 | 96 | 13 | 13 | 0 | 0 | 0 | 26 | 42 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 1639300
44 | Fenchugonj CCPP-1 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 65 | 65 | 65 | 65 | 65 | 65 | 66 | 66 | 68 |  | 68 | 68 | 68 | 67 | 67 | 67 | 67 | 1548000
45 | Fenchugonj CCPP-2 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 66 | 66 | 1574646
46 | Shajibazar 330 MW | 317 | 302 | 306 | 338 | 306 | 302 | 321 | 331 | 309 | 304 | 320 | 302 | 316 | 286 | 282 | 290 | 290 | 276 |  | 320 | 278 | 255 | 298 | 278 | 306 | 293 | 6898209
47 | Shahjibazar GT: Unit- 8, 9 | 61 | 60 | 60 | 59 | 60 | 61 | 60 | 59 | 59 | 59 | 59 | 68 | 58 | 56 | 48 | 48 | 59 | 42 |  | 57 | 59 | 50 | 59 | 50 | 59 | 59 | 1355000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 84 | 84 | 82 | 81 | 83 | 83 | 79 | 79 | 81 | 84 |  | 82 | 84 | 84 | 86 | 86 | 86 | 86 | 2016000
49 | Shahjibazar (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 44 | 45 | 45 | 1022040
50 | Sylhet GT 150 MW | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 130 | 134 | 133 | 130 | 128 | 128 | 98 | 98 | 98 | 96 | 96 |  | 108 | 100 | 98 | 98 | 100 | 130 | 130 | 2839410
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 45 | 43 | 42 | 42 | 44 | 44 | 41 | 42 | 43 |  | 43 | 44 | 45 | 44 | 44 | 44 | 43 | 1058320
53 | Sylhet (Desh) 10MW | 7 | 9 | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 211320
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 5 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234960
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 53 | 49 | 50 | 50 | 50 | 48 | 48 | 49 | 47 | 47 | 47 | 47 | 50 |  | 50 | 50 | 48 | 51 | 51 | 52 | 52 | 1195800
56 | Shahjahanulla 25 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 16 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 20 | 20 | 20 | 431760
57 | Summit Bibiana- 2 | 300 | 275 | 295 | 320 | 310 | 270 | 270 | 330 | 300 | 300 | 280 | 260 | 270 | 280 | 300 | 270 | 280 | 260 |  | 260 | 260 | 260 | 280 | 290 | 260 | 295 | 7321500
58 | Southern 55MW | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1286000
59 | Sikalbaha (Energis) | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 40 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 40 |  | 40 | 40 | 40 | 40 | 50 | 51 | 51 | 986400
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 452208
61 | Narshingdi (Doreen) | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 316152
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 447228
63 | Tripura | 121 | 121 | 121 | 120 | 116 | 102 | 90 | 93 | 106 | 112 | 122 | 112 | 112 | 92 | 96 | 96 | 96 | 100 |  | 108 | 124 | 122 | 74 | 98 | 88 | 90 | 2547840
64 | Malancha, Ctg. EPZ (United) | 36 | 30 | 39 | 39 | 39 | 39 | 26 | 10 | 2 | 3 | 3 | 4 | 8 | 2 | 2 | 2 | 6 | 2 |  | 3 | 7 | 8 | 14 | 26 | 26 | 30 | 388320
65 | Feni (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 18 | 18 | 18 | 19 | 460620
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 242640
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 775600
68 | Summit Comilla 25MW | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 407490
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 31 | 26 | 26 | 31 | 31 | 30 | 28 | 28 | 30 | 30 |  | 30 | 32 | 32 | 32 | 32 | 32 | 32 | 692820
71 | Summit Maona | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 566131
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 |  | 30 | 30 | 30 | 30 | 31 | 31 | 32 | 717600
73 | Ghorashal (Regent) | [10 empty] | 70 | 75 | 82 | 83 | 83 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 84 | 85 | 86 | 1053818
76 | Siddhirganj (Desh) | 34 | 34 | 34 | 0 |  |  |  |  | 5 | 23 | 44 | 52 | 61 | 50 | 50 | 50 | 50 | 50 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 1156800
77 | Siddhirganj (Dutch Bangla) | 85 | 85 | 80 | 80 | 81 | 40 | 14 | 16 | 35 | 60 | 70 | 70 | 63 | 63 | 63 | 63 | 63 | 70 |  | 75 | 84 | 84 | 84 | 83 | 82 | 82 | 1702080
78 | Gazipur (RPCL) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 50 | 48 | 48 | 48 | 48 | 48 | 48 |  | 40 | 45 | 47 | 50 | 50 | 50 | 47 | 1173204
79 | Kodda 149 MW | 149 | 149 | 149 | 100 | 100 | 48 | 16 | 16 | 100 | 110 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3026880
80 | Jamalpur 95MW | 89 | 90 | 90 | 73 | 72 | 48 | 8 | 8 | 24 | 24 | 90 | 56 | 90 | 90 | 90 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1786560
81 | Lakdhanvi 52 MW | 34 | 34 | 34 | 0 | [5 empty] | 8 | 10 | 16 | 16 | 14 | 21 | 28 | 8 | 8 |  | 22 | 43 | 43 | 52 | 52 | 52 | 52 | 539741
82 | Madanganj 102MW | 81 | 81 | 81 | 81 | 81 | 65 | 15 | 22 | 42 | 75 | 80 | 80 | 80 | 77 | 77 | 78 | 78 | 78 |  | 80 | 80 | 81 | 80 | 81 | 81 | 81 | 1772160
83 | Pagla (DPA ) | 51 | 51 | 11 | 0 | 0 | 0 | 0 |  | 50 | 48 | 49 | 50 | 50 | 50 | 49 | 49 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 915500
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 84 | 85 | 85 | 85 | 84 | 85 | 85 | 85 | 86 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1772160
85 | Keraniganj (Powerpac) 100MW | 100 | 100 | 100 | 60 | 60 | 10 | 10 | 40 | 100 | 0 | 0 | 0 | [14 empty] | 688404
86 | Meghnaghat CCPP(Summit) | 305 | 200 | 200 | 200 | 305 | 200 | 230 | 270 | 305 | 305 | 250 | 200 | 200 | 250 | 300 | 200 | 300 | 200 |  | 280 | 305 | 240 | 305 | 305 | 305 | 305 | 6270051
87 | Meghnaghat (IEL) | 100 | 100 | 100 | 100 | 100 | 60 | 16 | 9 | 65 | 92 | 93 | 99 | 99 | 99 | 97 | 98 | 94 | 99 |  | 98 | 100 | 98 | 100 | 100 | 100 | 100 | 2161920
88 | Ghorashal 78MW (MAX) | [10 empty] | 0 | 50 | 70 | 69 | 68 | 69 | 69 | 70 |  | 70 | 70 | 71 | 71 | 72 | 72 | 72 | 871808
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 30 | 10 | 5 | 5 | 5 | 150000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1843320
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 48 |  | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 1175000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 35 | 35 | 1049200
94 | Gagnagar (Orion) | 102 | 102 | 102 | 30 | 30 | 7 | 7 | 7 | 48 | 50 | 85 | 102 | 94 | 92 | 92 | 92 | 92 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1898064
95 | Patenga 50MW | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 37 | 37 | 42 | 44 | 44 | 44 | 37 | 37 |  | 25 | 24 | 24 | 33 | 39 | 44 | 44 | 1035360
96 | Chittagong ECPV 108 MW | 106 | 106 | 50 | 95 | 91 | 91 | 92 | 85 | 86 | 92 | 91 | 91 | 90 | 94 | 92 | 97 | 100 | 99 |  | 105 | 105 | 105 | 106 | 106 | 106 | 106 | 2265600
97 | Katpotti 51 MW | 40 | 40 | 40 | 39 | 40 | 40 | 12 | 21 | 34 | 34 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 927552
98 | Bosila 108MW | 87 | 88 | 87 | 88 | 88 | 88 | 40 | 90 | 89 | 88 | 79 | 78 | 78 | 78 | 77 | 55 | 45 | 66 |  | 80 | 78 | 78 | 78 | 79 | 79 | 78 | 1830720
99 | Madanganj-55 MW | 44 | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 43 | 48 | 47 | 48 | 48 | 47 | 48 | 48 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1195191
100 | Northern 55 MW | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1328587
101 | Kushiara 163 MW CCPP GT | 163 | 130 | 130 | 130 | 130 | 130 | 100 | 163 | 130 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3463486
102 | Sarishabari (Solar) |  |  |  |  | 0 | 0.1 | 0.6 | 1.2 | 1.6 | 1.9 | 2.4 | 2.3 | 2.3 | 2.3 | 1.9 | 1.2 | 0.7 | 0.2 |  | 0 | 0 | 0 |  |  |  |  | 17500
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 54 | 54 | 18 | 36 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1242360
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | 61 | 36 | 0 | [5 empty] | 51 | 50 | 98 | 50 | 50 | 10 | 97 | 95 | 93 | 50 |  | 72 | 100 | 98 | 98 | 95 | 91 | 96 | 1295557
106 | United Mymensingh PPL | 168 | 168 | 166 | 166 | 166 | 168 | 166 | 165 | 166 | 166 | 163 | 117 | 125 | 100 | 130 | 130 | 130 | 130 |  | 127 | 125 | 150 | 161 | 170 | 168 | 168 | 3609600
112 | Aggreko Aurahati 100MW | 70 | 50 | [6 empty] | 51 | 100 | 53 | 51 | 51 | 51 | 100 | 100 | 100 | 51 |  | 93 | 100 | 100 | 99 | 100 | 100 | 100 | 1442465
114 | Summit Gazipur-1 150MW | 146 | 146 | 146 | 147 | 147 | 147 | 147 | 147 | 145 | 146 | 146 | 136 | 131 | 131 | 125 | 125 | 134 | 125 |  | 133 | 140 | 145 | 145 | 146 | 146 | 136 | 3388320
115
116
117
118
120 | Eastern Zone Total | 8511 | 8186 | 7925 | 7751 | 7809 | 7219.1 | 6869.6 | 7135.2 | 7622.6 | 7687.9 | 7846.4 | 7635.3 | 7734.3 | 7718.3 | 8057.9 | 7849.2 | 7918.7 | 7709.2 | 0 | 8184 | 8340 | 8339 | 8483 | 8496 | 8462 | 8505 | 188472616
121
122
123 | Khulna 60MW
124 | Khulna (KPCL-1 & 3) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 27 | 53 | 100 | 27 | 27 | 27 | 27 | 393120
125 | Khulna (KPCL-2) | 22 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 36 | 82 | 115 | 115 | 115 | 739200
126
127 | Khulna (Aggreko) 55MW | 51 | 37 | 37 | 37 | 37 |  |  |  | 52 | 54 | 55 | 55 | 55 | 51 | 48 | 52 | 54 | 55 |  | 55 | 54 | 54 | 55 | 55 | 55 | 55 | 1043920
128 | Faridpur Peaking | 47 | 47 | 47 | 47 | 47 | [12 empty] | 13 |  | 47 | 46 | 46 | 43 | 46 | 46 | 46 | 513600
129 | Khulna CCPP 225MW | 20 | 30 | 40 | 30 | 50 | 50 | 50 | 50 | 50 | 50 | 0 |  |  | 0 | 15 | 15 | 10 | 15 |  | 30 | 40 | 120 | 147 | 160 | 160 | 160 | 1170240
130
131
132
133
| Summit Barisal 110 MW | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 112 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2668800
136 | Barisal GT: Unit-1, 2 | [15 empty] | 8 | 0 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 60255
137 | Bhola Aggreko 95MW | 95 | 95 | 95 | 94 | 95 | 95 | 95 | 96 | 95 | 93 | 95 | 95 | 94 | 93 | 94 | 93 | 94 | 99 |  | 98 | 95 | 96 | 96 | 97 | 96 | 97 | 2289530
| Bhola CCPP 194MW | 85 | 95 | 95 | 93 | 95 | 72 | 94 | 93 | 89 | 92 | 90 | 82 | 92 | 90 | 89 | 88 | 90 | 78 |  | 86 | 86 | 75 | 154 | 149 | 148 | 147 | 2379667
140 | Bhola (Venture) 33MW | 33 | 34 | 30 | 28 | 28 | 27 | 24 | 24 | 24 | 22 | 25 | 26 | 26 | 27 | 24 | 28 | 25 | 25 |  | 34 | 37 | 37 | 20 | 32 | 35 | 36 | 653319
141 | Bangla Trak Noapara | 98 | 98 | 50 | [5 empty] | 50 | 75 | 85 | 85 | 85 | 85 | 91 | 91 | 91 | 50 |  | 75 | 91 | 92 | 93 | 94 | 94 | 94 | 1575360
142 | Noapara (KZA) 40MW | [19 empty] | 25 | 25 | 40 | 40 | 40 |  |  | 117375
143 | Gopalganj Peaking | 69 | 69 | 63 | 51 | 46 | [10 empty] | 5 | 30 | 50 |  | 55 | 70 | 68 | 68 | 47 | 46 | 45 | 721920
144 | Bheramara GT-1,2,3 | [15 empty] | 32 | 32 | 24 |  | 24 | 24 | 32 | 30 | 30 | 32 |  | 218000
145
146 | Bheramara HVDC | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 463 | 464 | 464 | 464 | 464 | 464 | 463 | 463 |  | 464 | 464 | 463 | 464 | 468 | 469 | 468 | 11128000
147 | Bheramara 360 MW | 262 | 267 | 267 | 286 | 308 | 315 | 309 | 308 | 295 | 284 | 284 | 260 | 248 | 235 | 224 | 220 | 220 | 230 |  | 243 | 240 | 240 | 240 | 230 | 230 | 236 | 6377760
148
149
150 | Barapukuria Unit-1
151 | Barapukuria Unit-2
152 | Barapukuria Unit-3 | 132 | 130 | 127 | 131 | 138 | 125 | 125 | 109 | 120 | 127 | 138 | 150 | 156 | 157 | 150 | 133 | 146 | 140 |  | 130 | 142 | 129 | 120 | 136 | 142 | 135 | 3277100
153 | Baghabari GT 71MW
156 | Baghabari GT 100MW
| Baghabari Peaking 50MW | 50 | 50 | 50 | 50 | 50 | 0 |  |  |  |  | 0 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 50 | 50 | 50 | 868888
157 | Sirajgonj Unit-1 225MW (Gas)
158 | Sirajgonj Unit-1 225MW (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 150 | 214 | 214 | 214 | 214 | 214 | 130 |  | 145 | 214 | 214 | 214 | 214 | 214 | 214 | 4156736
| Sirajgonj Unit-2 225MW (Gas) | [26 empty] | 0
| Sirajgonj Unit-2 225MW (Oil) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 165 | 220 | 220 | 220 | 220 | 208 | 140 |  | 145 | 220 | 220 | 220 | 220 | 220 | 220 | 4199745
159 | Sirajgonj Unit-3 225 MW(Gas) | [10 empty] | 40 | 100 | 0 | 0 | [12 empty] | 63500
160 | Sirajgonj Unit-3 225 MW(Oil) | [11 empty] | 0 | 100 | 100 | 100 | 173 | 0 | 0 | [8 empty] | 403000
161 | Bera Peaking | 36 | 36 | 36 | 36 | 36 | [9 empty] | 0 | 9 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 30 | 451254
162 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 14 | 14 | 16 | 15 | 16 | 6 | 16 | 16 |  | 16 | 16 | 18 | 18 | 18 | 18 | 18 | 284480
163 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 7 | 7 | 7 | 7 | 7 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 205740
164 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 249354
165 | Amnura 50MW | 50 | 50 | 50 | 50 | 50 | 40 | 50 | 50 | 50 | 40 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 33 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 1068510
166 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 953328
167 | Katakhali Peaking | 37 | 37 | 37 | 37 | 37 | [9 empty] | 41 | 44 | 44 | 45 |  | 45 | 46 | 47 | 45 | 44 | 44 | 44 | 609541
168 | Santahar Peaking
169 | Rajlanka 52 MW | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 49 | 50 | 52 | 52 | 52 | 1214880
170 | Chapainawabganj-100 MW | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 44 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 59 | 100 | 100 | 100 | 96 | 97 | 97 | 1704136
171
172
173 | Rangpur GT | 15 | 15 | 15 | 15 | 15 | [11 empty] | 15 | 15 |  | 12 | 15 | 15 | 15 | 15 | 14 | 14 | 182000
175 | Saidpur GT | 15 | 15 | 15 | 15 | 15 | [9 empty] | 15 | 13 | 13 | 13 |  | 13 | 14 | 15 | 14 | 14 | 15 | 15 | 222000
176
177
178
178 | Western Zone Total | 2195 | 2199 | 2148 | 2094 | 2141 | 1818 | 1790 | 1773 | 1866 | 1871 | 1889 | 2033 | 2165 | 2136 | 2193 | 2294 | 2185 | 2016 | 0 | 2200 | 2464 | 2612 | 2661 | 2707 | 2677 | 2639 | 52164258
176
177