## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-05-30 | Wednesday
|  | Date (day): | 2018-05-30 |  | Wednesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10945 | MW |  |  | (b) At Evening Peak Hour : |  | 11978 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-05-29 | 2018-05-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | # 1 under maint.
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 130 | 130 | 130 | 130 | 40 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190 | 0
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 165 | 165 | 165 |  |  | On test
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 376 | 300 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 55 | 84 | 84 |  | 26 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 301 | 292 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 305 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 100 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55 |  | 0
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 30 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 100 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 86 | 88 | 88 |  | 12 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 170 | 0 | 170 | 170 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 21 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 94 | 94 | 94
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 6 | 48 | 48 | 48 |  | 3 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 37 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 99 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 45 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 14 | 285 | 100 | 285
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 MW | 0 | 0 | 0 | 82 | 0 | 100 |  |  | On test
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2425 | 3609 | 3749 | 4034 | 513 | 396
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 25 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 36 | 44 | 44 | 44 |  | 6 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 103 | 102 | 134 | 140
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 209 | 195 | 203 | 203
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 130 | 135 | 130
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 51 | 42 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 80 | 85 | 85
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 47 | 50 | 50
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 90 | 90 | 90
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 16 | 20 | 20 |  | 2 | Engine problem
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 2 | 24
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 98 | 90 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 741 | 885 | 937 | 960 | 360 | 58
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 100 | 100
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 120 | 100 | 120 | 120
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under Maint.
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 183 | 221 | 221
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 321 | 360 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 231 | 360 | 360
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 42 | 42 | 42
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | 132 kV Cable fault
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 10 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 144 | 105 | 150 | 150 | 45 |  | Gas shortage
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 51 | 85 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 48
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 154 | 154 | 154 | 154
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 136 | 188 | 144 | 188
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 25 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 15 | 21 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 180 | 0 | 200 |  |  | On test
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1394 | 1907 | 1934 | 2226 | 88 | 189
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 89 | 83 | 89 | 89 | 113 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 95 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.3 | 0 | 2 | 0
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 107.3 | 200 | 208 | 206 | 113 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 51 | 58 | 60 | 60
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 74 | 74 | 74 | 74
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 163 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 318 | 301 | 330 | 330 |  | 0
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 39 | 53 | 50 | 50
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 39 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 49 | 66 | 66
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 86 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 50 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 100 | 118 | 130 | 130
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 41 | 46 | 48 | 48
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 255 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1339 | 1346 | 1492 | 1492 | 0 | 20
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 33 | 0 | 33
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 479 | 479 | 482 | 482
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 108 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 82 | 102 | 115 | 115
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 42 | 0 | 42
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 130 | 211 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 5 | 61 | 40 | 60
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 340 | 318 | 318 | 318
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 33 | 33 | 33 | 33
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 53 | 0 | 55
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 1079 | 1540 | 1323 | 1573 | 0 | 0
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 110 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 9 | 35 | 33 | 33
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 129 | 120 | 170 | 170
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 95 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 297 | 360 | 408 | 438 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 0 | 41
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 25 | 40 | 43 | 43
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 47 | 48 | 48
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Fuel shortage
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 223 | 220 | 220 |  |  | FGMO
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 36 | 0 | 36
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 8 | 10 | 10 | 10
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 44 | 44
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 34 | 102 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 296 | 657 | 537 | 657 | 281 | 107
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 77 | 77 | 77
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 260 | 280 | 280 |  |  | on test
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 355 | 371 | 357 | 392 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 8033.3 | 10875 | 10945 | 11978 | 1355 | 855
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7615.9377 | 10310 | 10376.3632 | 11355.6947
A. |  | 2018-05-29 | (Yesterday) |  |  |  |  | Tuesday
1 | Highest Generation : |  |  | 10875 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 5950.4 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10875 | MW
3 | Day peak Generation : |  |  | 8033.3 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10310 | MW
4 | Evening peak Generation : |  |  | 10875 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 204.9011 | MKWHr | By Solar | 0.016235 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 115.6846 | MKWHr |  | By Oil: | 63.3089 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 8.5009 | MKWHr |  | By Hydro: | 2.4245 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1355 | MW | Dhaka | 3928 | 3928 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 855 | MW | Chittagong | 1019 | 1019 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2210 | MW | Khulna | 1373 | 1373 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1034.97 | MMCFD |  |  | Rajshahi | 1032 | 1032 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 88431177 | ii) Oil : | Taka | 578393651.34 | Comilla | 973 | 973 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 11087571.26 | Total | Taka | 677912399.6 | Mymensingh | 675 | 675 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 3.838 | MKWHr. | Sylhet | 412 | 412 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -640 | MW at | 21:00 | hrs | Barisal | 261 | 261 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -640 | MW at | 19:00 | hrs | Rangpur | 637 | 637 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 35.4° C |  |  | Total | 10310 | 10310 |  | 0
B. |  | 2018-05-30 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 36.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11978 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8800 | MW
4 | Reserve(Generation end) |  |  |  | 978 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 207.2563 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7679.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.5571 | MKWHr. | ii) HVDC Flow at Peak Time |  | 479 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.409 | MKWHr. | iii) Maximum HVDC Flow : |  | 479 | MW at | 12:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.19 |  | (b) Today: | 81.19 |  | (c) Rule Curve: |  | 76.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-05-29
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 130 | 0 | 190 | 80 | 0 | 0 | 345 | 303 | 13 | 0 | 320 | 200 | 50 | 15 | 55 | 170 | 0 | 0 | 0 | 50 | 7 | 149 | 10 | 51 | 10 | 6 | 54 | 37 | 55 | 19 | 25 | 32 | 33 | 33 | 51 | 0 | 87 | 33 | 0 | 0 | 25 | 0 | 196 | 0 | 70 | 0 | 51 | 82 | 47 | 90 | 97 | 45 | 18 | 30 | 100 | 100 | 0 | 270 | 279 | 182 | 128 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 162 | 70 | 56 | 0 | 0 | 60 | 75 | 50 | 50 | 163 | 147 | 59 | 86 | 49 | 96 | 0 | 45 | 9 | 280 | 23 | 11 | 12 | 200 | 0 | 98 |  | 473 | 0 | 310 | 27 | 99 | 180 | 0 | 0 | 0 | 44 | 33 | 0 | 34 | 80 | 0 | 0 | 0 | 0 | 0 | 51 | 12 | 8 | 0 | 8 | 0 | 2 | 0 | 0 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 165 | 50 | 0 | 0 | 0 |  | 6681 | 1933 | 8614 | 3173 | 473 | 1740 | 1605 | 357 | 120 | 984 | 162 | 0 | 0 | 81.34
2:00 | 37 | 130 | 0 | 190 | 138 | 0 | 0 | 344 | 281 | 0 | 0 | 320 | 200 | 7 | 15 | 15 | 170 | 0 | 0 | 0 | 7 | 7 | 110 | 10 | 8 | 10 | 6 | 54 | 36 | 55 | 19 | 0 | 32 | 33 | 33 | 51 | 0 | 87 | 31 | 0 | 0 | 25 | 0 | 195 | 0 | 70 | 0 | 51 | 50 | 47 | 80 | 97 | 45 | 18 | 30 | 100 | 100 | 0 | 240 | 250 | 182 | 108 | 153 | 42 | 0 | 5 | 51 | 60 | 0 | 0 | 19 | 11 | 33 | 21 | 170 | 72 | 8 | 0 | 0 | 60 | 75 | 50 | 50 | 163 | 149 | 52 | 60 | 50 | 78 | 0 | 45 | 9 | 260 | 23 | 11 | 12 | 137 | 0 | 26 |  | 473 | 0 | 250 | 45 | 99 | 160 | 0 | 0 | 0 | 44 | 33 | 0 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 51 | 12 | 8 | 0 | 8 | 0 | 5 | 0 | 0 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 165 | 95 | 0 | 0 | 0 |  | 6079 | 1948 | 8027 | 3065 | 473 | 1676 | 1277 | 356 | 118 | 892 | 170 | 0 | 0 | 81.31
3:00 | 37 | 130 | 0 | 190 | 200 | 0 | 0 | 344 | 281 | 0 | 0 | 290 | 200 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 60 | 10 | 8 | 10 | 6 | 54 | 36 | 55 | 19 | 25 | 23 | 33 | 16 | 8 | 0 | 84 | 31 | 0 | 0 | 26 | 0 | 195 | 0 | 71 | 0 | 51 | 50 | 47 | 90 | 97 | 44 | 18 | 32 | 100 | 100 | 0 | 230 | 250 | 180 | 78 | 152 | 42 | 0 | 5 | 51 | 60 | 0 | 0 | 19 | 11 | 33 | 21 | 180 | 87 | 8 | 0 | 0 | 60 | 75 | 50 | 50 | 100 | 150 | 42 | 40 | 20 | 77 | 0 | 43 | 9 | 270 | 23 | 0 | 12 | 13 | 0 | 0 |  | 473 | 0 | 250 | 69 | 99 | 160 | 0 | 0 | 0 | 44 | 33 | 0 | 34 | 110 | 10 | 0 | 0 | 0 | 0 | 51 | 12 | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 165 | 95 | 0 | 0 | 0 |  | 5713 | 1977 | 7690 | 3087 | 473 | 1508 | 1118 | 356 | 115 | 853 | 180 | 0 | 0 | 81.28
4:00 | 37 | 130 | 0 | 190 | 200 | 0 | 0 | 345 | 281 | 0 | 0 | 290 | 200 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 48 | 10 | 8 | 10 | 6 | 54 | 18 | 55 | 19 | 25 | 23 | 33 | 16 | 8 | 0 | 84 | 31 | 0 | 0 | 26 | 0 | 195 | 0 | 70 | 0 | 51 | 50 | 47 | 80 | 90 | 44 | 18 | 32 | 100 | 100 | 0 | 220 | 250 | 181 | 78 | 153 | 42 | 0 | 5 | 40 | 20 | 0 | 0 | 19 | 11 | 33 | 0 | 90 | 92 | 8 | 0 | 0 | 40 | 75 | 22 | 20 | 100 | 164 | 50 | 20 | 1 | 77 | 0 | 43 | 9 | 270 | 21 | 0 | 11 | 13 | 0 | 0 |  | 473 | 0 | 200 | 69 | 83 | 160 | 0 | 0 | 0 | 44 | 33 | 0 | 33 | 110 | 10 | 0 | 0 | 0 | 0 | 51 | 12 | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 170 | 95 | 0 | 0 | 0 |  | 5403 | 1915 | 7318 | 3014 | 473 | 1359 | 1066 | 356 | 115 | 845 | 90 | 0 | 0 | 81.25
5:00 | 37 | 130 | 0 | 190 | 160 | 0 | 0 | 345 | 281 | 0 | 0 | 290 | 200 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 25 | 10 | 8 | 10 | 6 | 18 | 18 | 36 | 19 | 25 | 32 | 33 | 29 | 8 | 0 | 85 | 31 | 0 | 0 | 25 | 0 | 195 | 0 | 70 | 0 | 51 | 0 | 17 | 80 | 51 | 45 | 19 | 13 | 100 | 100 | 0 | 285 | 0 | 182 | 78 | 153 | 3 | 0 | 5 | 6 | 5 | 0 | 0 | 19 | 11 | 8 | 0 | 60 | 93 | 8 | 0 | 0 | 40 | 75 | 4 | 2 | 100 | 185 | 52 | 5 | 1 | 79 | 0 | 5 | 9 | 270 | 21 | 0 | 0 | 14 | 0 | 0 |  | 473 | 0 | 135 | 69 | 83 | 140 | 0 | 0 | 0 | 39 | 33 | 0 | 29 | 110 | 12 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 170 | 95 | 0 | 0 | 0 |  | 4771 | 1799 | 6570 | 2710 | 473 | 1198 | 962 | 357 | 116 | 694 | 60 | 0 | 0 | 81.22
6:00 | 37 | 130 | 0 | 190 | 160 | 0 | 0 | 300 | 232 | 0 | 0 | 240 | 200 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 15 | 10 | 8 | 10 | 6 | 18 | 18 | 36 | 19 | 25 | 32 | 33 | 29 | 8 | 0 | 85 | 31 | 0 | 0 | 0 | 0 | 196 | 0 | 60 | 0 | 8 | 0 | 17 | 80 | 12 | 8 | 0 | 17 | 100 | 100 | 0 | 250 | 0 | 160 | 68 | 153 | 3 | 0 | 5 | 6 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 58 | 93 | 8 | 0 | 0.1 | 40 | 66 | 4 | 2 | 100 | 271 | 50 | 5 | 1 | 78 | 0 | 5 | 0 | 270 | 23 | 0 | 0 | 14 | 0 | 0 |  | 473 | 0 | 135 | 69 | 83 | 120 | 0 | 0 | 0 | 39 | 33 | 0 | 7 | 110 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 140 | 41 | 0 | 0 | 0 |  | 4417.1 | 1661 | 6078.1 | 2635 | 473 | 1008 | 818 | 357 | 116 | 613 | 58 | 0.1 | 0 | 81.19
7:00 | 37 | 130 | 0 | 190 | 160 | 0 | 0 | 300 | 262 | 0 | 0 | 270 | 200 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 15 | 10 | 8 | 21 | 6 | 18 | 18 | 17 | 19 | 25 | 24 | 33 | 29 | 8 | 0 | 84 | 32 | 0 | 0 | 0 | 0 | 204 | 0 | 71 | 0 | 8 | 0 | 17 | 80 | 12 | 8 | 0 | 2 | 0 | 0 | 0 | 250 | 0 | 183 | 68 | 153 | 3 | 0 | 5 | 6 | 5 | 0 | 0 | 0 | 11 | 8 | 0 | 78 | 72 | 8 | 0 | 0.4 | 40 | 66 | 5 | 2 | 100 | 316 | 53 | 5 | 1 | 78 | 0 | 6 | 0 | 270 | 23 | 0 | 0 | 14 | 0 | 0 |  | 472 | 0 | 135 | 10 | 83 | 120 | 0 | 0 | 0 | 39 | 33 | 0 | 3 | 90 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 8 | 0 | 0 | 0 | 3 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 160 | 42 | 0 | 0 | 0 |  | 4348.4 | 1602 | 5950.4 | 2491 | 472 | 1052 | 731 | 358 | 116 | 652 | 78 | 0.4 | 0 | 81.16
8:00 | 37 | 130 | 0 | 190 | 200 | 0 | 0 | 365 | 355 | 0 | 0 | 270 | 200 | 7 | 15 | 18 | 150 | 0 | 0 | 0 | 7 | 8 | 48 | 10 | 8 | 21 | 6 | 18 | 18 | 17 | 0 | 25 | 24 | 33 | 33 | 8 | 0 | 84 | 31 | 0 | 0 | 0 | 0 | 206 | 0 | 80 | 0 | 8 | 0 | 16 | 90 | 12 | 6 | 0 | 2 | 0 | 0 | 0 | 260 | 0 | 181 | 68 | 154 | 42 | 0 | 5 | 6 | 5 | 0 | 0 | 0 | 11 | 8 | 0 | 98 | 74 | 8 | 0 | 0.9 | 60 | 66 | 5 | 2 | 100 | 318 | 64 | 5 | 1 | 77 | 0 | 6 | 0 | 325 | 23 | 0 | 0 | 14 | 0 | 0 |  | 473 | 0 | 200 | 10 | 82 | 120 | 0 | 0 | 0 | 7 | 33 | 85 | 5 | 64 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 0 | 0 | 8 | 0 | 11 | 0 | 3 | 0 | 75 | 280 | 0 | 0 | 0 | 0 | 0 | 160 | 41 | 0 | 0 | 0 |  | 4742.9 | 1694 | 6436.9 | 2813 | 473 | 1212 | 708 | 355 | 115 | 662 | 98 | 0.9 | 0 | 81.13
9:00 | 37 | 130 | 0 | 190 | 305 | 0 | 0 | 365 | 345 | 0 | 0 | 350 | 200 | 7 | 15 | 30 | 170 | 0 | 0 | 0 | 7 | 24 | 82 | 30 | 8 | 21 | 6 | 18 | 18 | 17 | 0 | 25 | 23 | 33 | 33 | 8 | 0 | 83 | 32 | 0 | 0 | 0 | 0 | 196 | 0 | 70 | 0 | 8 | 0 | 8 | 90 | 14 | 6 | 18 | 2 | 0 | 0 | 0 | 305 | 0 | 197 | 126 | 154 | 42 | 0 | 10 | 6 | 5 | 0 | 0 | 0 | 11 | 22 | 15 | 112 | 103 | 8 | 0 | 1.7 | 56 | 66 | 5 | 13 | 100 | 314 | 64 | 5 | 1 | 80 | 0 | 42 | 0 | 320 | 23 | 0 | 0 | 14 | 0 | 0 |  | 472 | 0 | 360 | 10 | 82 | 120 | 0 | 0 | 0 | 7 | 33 | 82 | 10 | 64 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 8 | 0 | 11 | 8 | 3 | 0 | 62 | 280 | 0 | 0 | 0 | 0 | 0 | 160 | 61 | 0 | 0 | 0 |  | 5244.7 | 1879 | 7123.7 | 3226 | 472 | 1420 | 766 | 342 | 115 | 669 | 112 | 1.7 | 0 | 81.11
10:00 | 37 | 130 | 0 | 190 | 310 | 0 | 0 | 360 | 346 | 0 | 0 | 450 | 200 | 7 | 15 | 38 | 170 | 0 | 0 | 0 | 7 | 24 | 100 | 30 | 8 | 21 | 6 | 18 | 56 | 17 | 19 | 25 | 23 | 33 | 33 | 34 | 0 | 83 | 32 | 0 | 0 | 0 | 0 | 202 | 0 | 100 | 0 | 22 | 0 | 16 | 90 | 91 | 16 | 19 | 2 | 13 | 75 | 0 | 285 | 0 | 190 | 144 | 154 | 34 | 0 | 10 | 6 | 20 | 0 | 0 | 10 | 11 | 33 | 15 | 114 | 102 | 8 | 0 | 2 | 54 | 63 | 22 | 20 | 100 | 314 | 62 | 20 | 20 | 80 | 0 | 41 | 0 | 320 | 23 | 0 | 0 | 14 | 0 | 0 |  | 472 | 0 | 344 | 10 | 81 | 120 | 0 | 0 | 0 | 5 | 33 | 86 | 14 | 64 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 8 | 0 | 18 | 8 | 3 | 0 | 68 | 280 | 0 | 0 | 0 | 0 | 0 | 180 | 71 | 0 | 0 | 0 |  | 5759 | 1911 | 7670 | 3300 | 472 | 1632 | 938 | 348 | 115 | 749 | 114 | 2 | 0 | 81.09
11:00 | 37 | 130 | 0 | 190 | 309 | 0 | 0 | 346 | 343 | 0 | 0 | 450 | 200 | 7 | 15 | 55 | 170 | 0 | 0 | 0 | 7 | 24 | 100 | 30 | 8 | 21 | 6 | 18 | 56 | 17 | 22 | 25 | 23 | 33 | 33 | 51 | 0 | 70 | 32 | 0 | 0 | 17 | 0 | 202 | 0 | 100 | 0 | 47 | 0 | 17 | 90 | 96 | 29 | 19 | 2 | 80 | 100 | 0 | 285 | 0 | 193 | 144 | 154 | 35 | 0 | 10 | 38 | 22 | 0 | 0 | 16 | 11 | 33 | 15 | 130 | 89 | 8 | 0 | 2.2 | 56 | 66 | 22 | 20 | 100 | 330 | 61 | 20 | 20 | 80 | 0 | 40 | 0 | 285 | 23 | 0 | 0 | 14 | 0 | 0 |  | 478 | 0 | 345 | 10 | 82 | 120 | 0 | 0 | 0 | 5 | 33 | 128 | 9 | 64 | 0 | 0 | 0 | 0 | 0 | 26 | 12 | 8 | 0 | 8 | 0 | 17 | 8 | 5 | 0 | 72 | 280 | 0 | 0 | 0 | 0 | 0 | 170 | 96 | 0 | 0 | 0 |  | 5949.2 | 1976 | 7925.2 | 3442 | 478 | 1646 | 1033 | 352 | 102 | 740 | 130 | 2.2 | 0 | 81.07
12:00 | 37 | 130 | 0 | 190 | 0 | 0 | 0 | 376 | 301 | 0 | 0 | 450 | 200 | 7 | 15 | 55 | 170 | 0 | 0 | 0 | 7 | 24 | 115 | 30 | 8 | 21 | 6 | 18 | 56 | 17 | 22 | 25 | 23 | 33 | 33 | 42 | 0 | 70 | 33 | 0 | 0 | 17 | 0 | 209 | 0 | 120 | 0 | 51 | 0 | 0 | 90 | 98 | 36 | 15 | 2 | 100 | 120 | 0 | 310 | 0 | 204 | 144 | 154 | 39 | 0 | 10 | 51 | 51 | 0 | 0 | 16 | 11 | 33 | 15 | 136 | 89 | 16 | 0 | 2.3 | 51 | 74 | 39 | 39 | 140 | 318 | 60 | 84 | 45 | 100 | 0 | 41 | 0 | 325 | 23 | 0 | 0 | 14 | 0 | 0 |  | 479 | 0 | 340 | 10 | 82 | 130 | 0 | 0 | 0 | 5 | 33 | 129 | 9 | 64 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 8 | 0 | 8 | 0 | 18 | 8 | 5 | 0 | 75 | 280 | 0 | 0 | 0 | 0 | 0 | 190 | 95 | 0 | 0 | 0 |  | 6006.3 | 2027 | 8033.3 | 3245 | 479 | 1852 | 1058 | 355 | 103 | 803 | 136 | 2.3 | 0 | 81.05
13:00 | 37 | 130 | 0 | 190 | 0 | 0 | 0 | 363 | 302 | 13 | 0 | 450 | 200 | 50 | 15 | 54 | 170 | 0 | 0 | 0 | 20 | 50 | 149 | 90 | 100 | 21 | 13 | 54 | 56 | 36 | 22 | 25 | 23 | 33 | 0 | 47 | 0 | 70 | 33 | 0 | 0 | 17 | 0 | 202 | 0 | 110 | 0 | 13 | 0 | 0 | 78 | 98 | 39 | 18 | 2 | 100 | 100 | 0 | 290 | 0 | 183 | 144 | 154 | 39 | 0 | 10 | 51 | 85 | 0 | 0 | 16 | 11 | 33 | 0 | 144 | 90 | 41 | 22 | 2.2 | 51 | 74 | 47 | 50 | 163 | 303 | 44 | 84 | 45 | 130 | 0 | 41 | 0 | 270 | 15 | 11 | 0 | 13 | 0 | 0 |  | 478 | 0 | 338 | 98 | 81 | 180 | 0 | 0 | 0 | 5 | 33 | 125 | 9 | 110 | 0 | 0 | 0 | 0 | 0 | 34 | 33 | 25 | 0 | 25 | 0 | 16 | 8 | 5 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 175 | 96 | 0 | 0 | 0 |  | 6249.2 | 2230 | 8479.2 | 3145 | 478 | 1873 | 1523 | 356 | 103 | 855 | 144 | 2.2 | 0 | 81.03
14:00 | 37 | 130 | 0 | 190 | 50 | 0 | 0 | 372 | 291 | 26 | 0 | 420 | 250 | 97 | 48 | 55 | 170 | 0 | 0 | 0 | 70 | 93 | 149 | 100 | 100 | 21 | 47 | 54 | 56 | 36 | 22 | 25 | 23 | 33 | 33 | 42 | 0 | 67 | 31 | 0 | 0 | 17 | 0 | 204 | 0 | 111 | 0 | 42 | 0 | 0 | 90 | 97 | 39 | 17 | 2 | 100 | 100 | 0 | 290 | 0 | 198 | 144 | 154 | 42 | 0 | 30 | 51 | 86 | 0 | 0 | 16 | 11 | 33 | 20 | 146 | 88 | 72 | 22 | 1.9 | 49 | 74 | 49 | 50 | 163 | 317 | 60 | 86 | 45 | 130 | 0 | 41 | 9 | 260 | 23 | 11 | 0 | 88 | 0 | 0 |  | 478 | 0 | 340 | 96 | 81 | 160 | 0 | 0 | 0 | 5 | 24 | 130 | 10 | 110 | 0 | 0 | 0 | 0 | 0 | 34 | 33 | 35 | 0 | 25 | 0 | 18 | 8 | 5 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 180 | 96 | 0 | 0 | 0 |  | 6816.9 | 2224 | 9040.9 | 3315 | 478 | 1859 | 1944 | 356 | 98 | 843 | 146 | 1.9 | 0 | 81.01
15:00 | 37 | 130 | 0 | 190 | 80 | 0 | 0 | 350 | 292 | 26 | 0 | 420 | 250 | 98 | 65 | 55 | 170 | 0 | 0 | 0 | 80 | 93 | 149 | 100 | 98 | 20 | 49 | 54 | 55 | 36 | 22 | 25 | 0 | 33 | 33 | 48 | 0 | 64 | 30 | 0 | 0 | 16 | 0 | 202 | 0 | 120 | 0 | 42 | 0 | 0 | 90 | 97 | 44 | 18 | 4 | 100 | 100 | 0 | 290 | 0 | 196 | 144 | 153 | 42 | 0 | 30 | 51 | 86 | 0 | 4 | 16 | 11 | 33 | 21 | 168 | 88 | 82 | 0 | 1.6 | 56 | 74 | 50 | 49 | 163 | 315 | 60 | 86 | 47 | 126 | 0 | 41 | 9 | 300 | 23 | 11 | 0 | 83 | 0 | 0 |  | 478 | 0 | 330 | 97 | 83 | 160 | 0 | 0 | 0 | 5 | 24 | 129 | 18 | 110 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 35 | 0 | 25 | 0 | 18 | 8 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 175 | 96 | 0 | 0 | 0 |  | 6894.6 | 2228 | 9122.6 | 3267 | 478 | 1912 | 1999 | 358 | 94 | 845 | 168 | 1.6 | 0 | 80.99
16:00 | 37 | 130 | 0 | 190 | 123 | 0 | 0 | 360 | 284 | 55 | 0 | 420 | 200 | 98 | 73 | 55 | 170 | 0 | 0 | 0 | 84 | 93 | 149 | 100 | 98 | 20 | 48 | 54 | 56 | 36 | 22 | 25 | 32 | 33 | 33 | 48 | 0 | 65 | 30 | 0 | 0 | 25 | 0 | 200 | 0 | 120 | 0 | 42 | 0 | 0 | 90 | 97 | 38 | 18 | 3 | 100 | 100 | 0 | 290 | 95 | 158 | 144 | 153 | 41 | 0 | 30 | 51 | 85 | 0 | 8 | 16 | 11 | 33 | 21 | 156 | 88 | 95 | 22 | 1 | 56 | 74 | 49 | 49 | 163 | 314 | 47 | 84 | 48 | 108 | 0 | 41 | 9 | 275 | 23 | 11 | 0 | 149 | 0 | 0 |  | 479 | 0 | 320 | 96 | 81 | 150 | 0 | 0 | 0 | 9 | 33 | 123 | 19 | 110 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 35 | 0 | 8 | 0 | 16 | 8 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 175 | 98 | 0 | 0 | 0 |  | 7052 | 2196 | 9248 | 3382 | 479 | 1876 | 2065 | 357 | 95 | 837 | 156 | 1 | 0 | 80.97
17:00 | 37 | 130 | 0 | 190 | 173 | 0 | 0 | 345 | 281 | 55 | 0 | 350 | 200 | 75 | 70 | 55 | 170 | 0 | 0 | 0 | 84 | 93 | 149 | 50 | 98 | 20 | 48 | 54 | 56 | 36 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 67 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 80 | 0 | 42 | 0 | 0 | 90 | 97 | 40 | 16 | 8 | 100 | 100 | 0 | 290 | 69 | 182 | 76 | 153 | 42 | 0 | 30 | 51 | 51 | 0 | 8 | 19 | 0 | 33 | 21 | 138 | 83 | 95 | 22 | 0.3 | 56 | 74 | 53 | 50 | 100 | 308 | 61 | 60 | 48 | 78 | 0 | 44 | 9 | 275 | 23 | 11 | 0 | 152 | 0 | 0 |  | 479 | 0 | 270 | 39 | 88 | 120 | 0 | 0 | 0 | 33 | 24 | 128 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 35 | 0 | 8 | 0 | 16 | 8 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 165 | 61 | 0 | 0 | 0 |  | 6676.3 | 2046 | 8722.3 | 3334 | 479 | 1597 | 1937 | 357 | 97 | 783 | 138 | 0.3 | 0 | 80.95
18:00 | 37 | 130 | 0 | 190 | 170 | 0 | 0 | 345 | 280 | 55 | 0 | 350 | 200 | 60 | 70 | 55 | 170 | 0 | 0 | 0 | 84 | 94 | 149 | 50 | 98 | 20 | 48 | 54 | 56 | 36 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 67 | 33 | 0 | 0 | 25 | 0 | 202 | 0 | 50 | 0 | 42 | 8 | 0 | 90 | 97 | 44 | 18 | 10 | 100 | 100 | 0 | 290 | 121 | 183 | 76 | 153 | 42 | 0 | 10 | 51 | 51 | 28 | 8 | 19 | 11 | 33 | 21 | 144 | 79 | 95 | 22 | 0 | 56 | 74 | 53 | 49 | 100 | 302 | 50 | 40 | 20 | 78 | 0 | 22 | 9 | 285 | 23 | 11 | 0 | 160 | 0 | 0 |  | 479 | 0 | 250 | 39 | 99 | 120 | 0 | 0 | 20 | 35 | 24 | 122 | 25 | 110 | 0 | 0 | 0 | 0 | 18 | 34 | 40 | 35 | 17 | 8 | 0 | 18 | 8 | 8 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 165 | 61 | 0 | 0 | 0 |  | 6651 | 2092 | 8743 | 3353 | 479 | 1518 | 1946 | 357 | 100 | 846 | 144 | 0 | 0 | 80.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.57
19:00 | 37 | 130 | 0 | 190 | 170 | 0 | 0 | 300 | 260 | 55 | 0 | 360 | 200 | 85 | 75 | 55 | 140 | 0 | 0 | 30 | 84 | 94 | 149 | 100 | 98 | 21 | 48 | 54 | 37 | 55 | 22 | 25 | 22 | 33 | 28 | 50 | 0 | 68 | 32 | 0 | 0 | 25 | 0 | 201 | 0 | 80 | 0 | 42 | 80 | 49 | 90 | 98 | 44 | 18 | 22 | 100 | 100 | 0 | 250 | 161 | 183 | 76 | 153 | 42 | 0 | 10 | 51 | 30 | 49 | 8 | 19 | 11 | 33 | 21 | 164 | 73 | 95 | 22 | 0 | 58 | 74 | 53 | 49 | 100 | 307 | 64 | 86 | 20 | 96 | 0 | 45 | 9 | 265 | 23 | 5 | 158 | 286 | 0 | 74 |  | 479 | 32 | 205 | 102 | 98 | 160 | 0 | 12 | 48 | 50 | 33 | 128 | 34 | 110 | 0 | 0 | 0 | 43 | 49 | 64 | 40 | 43 | 37 | 43 | 36 | 18 | 10 | 11 | 0 | 77 | 250 | 16 | 0 | 0 | 0 | 0 | 150 | 61 | 10 | 0 | 0 |  | 7279 | 2449 | 9728 | 3254 | 479 | 1559 | 2552 | 327 | 100 | 1293 | 164 | 0 | 0 | 80.91
19:30 | 37 | 130 | 0 | 190 | 170 | 0 | 0 | 350 | 292 | 55 | 0 | 360 | 250 | 100 | 85 | 55 | 170 | 0 | 0 | 100 | 84 | 94 | 149 | 100 | 98 | 51 | 48 | 54 | 37 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 68 | 32 | 0 | 0 | 25 | 0 | 201 | 0 | 125 | 0 | 42 | 80 | 47 | 90 | 97 | 44 | 18 | 16 | 100 | 100 | 0 | 240 | 161 | 183 | 77 | 153 | 42 | 0 | 10 | 51 | 85 | 48 | 12 | 19 | 11 | 33 | 21 | 176 | 72 | 95 | 20 | 0 | 58 | 74 | 53 | 49 | 163 | 307 | 43 | 86 | 46 | 97 | 0 | 46 | 9 | 265 | 23 | 8 | 155 | 286 | 0 | 88 |  | 478 | 31 | 310 | 103 | 99 | 190 | 0 | 53 | 48 | 50 | 33 | 120 | 35 | 110 | 0 | 0 | 0 | 43 | 49 | 102 | 40 | 43 | 37 | 43 | 37 | 18 | 10 | 11 | 0 | 77 | 262 | 16 | 0 | 0 | 0 | 0 | 170 | 95 | 83 | 0 | 0 |  | 7759 | 2796 | 10555 | 3416 | 478 | 1766 | 2857 | 339 | 100 | 1423 | 176 | 0 | 0 | 0
20:00 | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 300 | 291 | 60 | 0 | 360 | 200 | 100 | 98 | 55 | 170 | 0 | 0 | 100 | 84 | 94 | 149 | 100 | 98 | 51 | 48 | 54 | 37 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 69 | 32 | 0 | 0 | 25 | 0 | 202 | 0 | 120 | 0 | 42 | 80 | 47 | 90 | 97 | 44 | 16 | 16 | 100 | 100 | 0 | 230 | 161 | 183 | 77 | 154 | 42 | 0 | 10 | 51 | 85 | 48 | 17 | 19 | 11 | 33 | 21 | 172 | 85 | 95 | 20 | 0 | 58 | 74 | 53 | 49 | 163 | 301 | 41 | 86 | 49 | 96 | 0 | 45 | 7 | 260 | 23 | 8 | 157 | 286 | 0 | 89 |  | 478 | 33 | 280 | 103 | 99 | 206 | 0 | 53 | 48 | 50 | 33 | 120 | 35 | 110 | 0 | 0 | 0 | 43 | 49 | 102 | 40 | 43 | 39 | 43 | 37 | 18 | 10 | 11 | 0 | 76 | 273 | 16 | 0 | 0 | 0 | 0 | 165 | 95 | 98 | 0 | 0 |  | 7660 | 2806 | 10466 | 3324 | 478 | 1760 | 2848 | 349 | 101 | 1434 | 172 | 0 | 0 | 80.89
21:00 | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 300 | 292 | 55 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 86 | 94 | 149 | 100 | 99 | 51 | 48 | 54 | 37 | 55 | 22 | 25 | 32 | 33 | 33 | 45 | 0 | 69 | 33 | 0 | 0 | 25 | 0 | 195 | 0 | 130 | 0 | 42 | 80 | 47 | 90 | 90 | 44 | 16 | 24 | 100 | 100 | 0 | 321 | 231 | 183 | 105 | 154 | 42 | 0 | 10 | 51 | 85 | 48 | 25 | 19 | 11 | 33 | 21 | 188 | 83 | 95 | 22 | 0 | 58 | 74 | 53 | 50 | 163 | 301 | 49 | 86 | 50 | 118 | 0 | 46 | 9 | 255 | 23 | 11 | 180 | 285 | 0 | 82 |  | 479 | 33 | 318 | 108 | 102 | 211 | 0 | 53 | 42 | 61 | 33 | 120 | 35 | 110 | 0 | 0 | 0 | 43 | 41 | 102 | 40 | 43 | 47 | 43 | 36 | 18 | 10 | 11 | 0 | 77 | 260 | 16 | 18 | 0 | 0 | 0 | 223 | 95 | 100 | 0 | 0 |  | 7947 | 2928 | 10875 | 3386 | 479 | 1887 | 2974 | 337 | 102 | 1522 | 188 | 0 | 0 | 80.87
22:00 | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 350 | 293 | 70 | 0 | 430 | 250 | 100 | 98 | 55 | 0 | 0 | 0 | 100 | 85 | 94 | 149 | 100 | 99 | 21 | 48 | 54 | 37 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 70 | 33 | 0 | 0 | 25 | 0 | 189 | 0 | 131 | 0 | 42 | 80 | 47 | 90 | 90 | 45 | 16 | 24 | 100 | 100 | 0 | 300 | 300 | 181 | 105 | 153 | 42 | 0 | 10 | 51 | 85 | 48 | 25 | 19 | 11 | 33 | 21 | 184 | 83 | 95 | 22 | 0 | 58 | 74 | 53 | 50 | 163 | 301 | 64 | 86 | 50 | 118 | 0 | 45 | 9 | 255 | 23 | 11 | 105 | 285 | 0 | 9 |  | 479 | 33 | 310 | 109 | 115 | 160 | 0 | 53 | 43 | 52 | 33 | 121 | 38 | 110 | 0 | 0 | 0 | 43 | 41 | 102 | 40 | 43 | 44 | 43 | 36 | 18 | 10 | 11 | 0 | 75 | 260 | 16 | 18 | 0 | 0 | 0 | 170 | 95 | 100 | 0 | 0 |  | 7815 | 2821 | 10636 | 3489 | 479 | 1870 | 2774 | 335 | 103 | 1402 | 184 | 0 | 0 | 80.85
23:00 | 37 | 130 | 0 | 190 | 163 | 0 | 0 | 346 | 293 | 70 | 0 | 430 | 250 | 100 | 97 | 55 | 80 | 0 | 0 | 100 | 85 | 93 | 149 | 100 | 99 | 21 | 47 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 70 | 33 | 0 | 0 | 25 | 0 | 195 | 0 | 80 | 0 | 42 | 80 | 45 | 90 | 90 | 44 | 16 | 30 | 100 | 100 | 0 | 330 | 360 | 136 | 68 | 153 | 42 | 0 | 10 | 20 | 85 | 48 | 25 | 19 | 11 | 33 | 22 | 176 | 80 | 95 | 22 | 0 | 56 | 74 | 53 | 50 | 163 | 316 | 66 | 86 | 50 | 117 | 0 | 44 | 9 | 270 | 23 | 11 | 32 | 285 | 0 | 0 |  | 478 | 0 | 311 | 107 | 115 | 120 | 0 | 53 | 47 | 52 | 33 | 122 | 36 | 110 | 0 | 0 | 0 | 43 | 41 | 102 | 40 | 43 | 44 | 43 | 36 | 18 | 10 | 11 | 0 | 78 | 259 | 16 | 18 | 0 | 0 | 0 | 170 | 96 | 100 | 0 | 0 |  | 7776 | 2752 | 10528 | 3622 | 478 | 1821 | 2705 | 337 | 103 | 1286 | 176 | 0 | 0 | 80.83
24:00 | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 349 | 294 | 70 | 0 | 430 | 200 | 100 | 97 | 55 | 130 | 0 | 0 | 100 | 85 | 94 | 133 | 100 | 99 | 10 | 47 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 70 | 33 | 0 | 0 | 25 | 0 | 189 | 0 | 80 | 0 | 42 | 80 | 45 | 80 | 91 | 44 | 19 | 29 | 100 | 100 | 0 | 300 | 300 | 151 | 53 | 154 | 42 | 0 | 5 | 20 | 85 | 48 | 16 | 19 | 11 | 33 | 22 | 176 | 80 | 95 | 22 | 0 | 56 | 74 | 53 | 50 | 163 | 302 | 58 | 86 | 50 | 118 | 0 | 45 | 9 | 280 | 23 | 11 | 0 | 302 | 0 | 0 |  | 479 | 0 | 300 | 108 | 115 | 120 | 0 | 33 | 47 | 49 | 33 | 138 | 35 | 110 | 0 | 0 | 0 | 43 | 41 | 102 | 40 | 43 | 44 | 43 | 36 | 18 | 10 | 11 | 0 | 77 | 259 | 16 | 18 | 0 | 0 | 0 | 170 | 96 | 70 | 0 | 0 |  | 7615 | 2704 | 10319 | 3590 | 479 | 1811 | 2563 | 336 | 103 | 1261 | 176 | 0 | 0 | 80.81
KWH | 782000 | 2921310 | 0 | 4454100 | 3814136 | 0 | 0 | 8425852 | 7047000 | 561600 | 0 | 8590936 | 5549440 | 1253760 | 1207248 | 1039035 | 3607238 | 0 | 0 | 610560 | 1119360 | 1264608 | 2625600 | 1316847 | 1276800 | 498050 | 645792 | 1011240 | 966269 | 948860 | 417888 | 575000 | 599220 | 594513 | 717300 | 878916 | 0 | 1663287 | 761200 | 0 | 0 | 428580 | 0 | 4768610 | 0 | 2221464 | 0 | 901440 | 706544 | 591257 | 2010840 | 1926720 | 850560 | 371328 | 337440 | 2006858 | 2028475 | 0 | 6976900 | 2908750 | 4453000 | 2458909 | 3460199 | 822888 | 0 | 270000 | 890669 | 1207248 | 298672 | 151472 | 348732 | 229140 | 693400 | 452430 | 3408960 | 1944330 | 1218808 | 225252 | 16235 | 1231000 | 1717760 | 902400 | 865000 | 3427874 | 6197724 | 1272000 | 1333440 | 756000 | 2288250 | 0 | 807960 | 146520 | 7316770 | 537840 | 138432 | 773760 | 2857853 | 0 | 445052 |  | 11557090 | 144700 | 6901920 | 1391520 | 2160000 | 3646080 | 0 | 271580 | 336720 | 704896 | 727875 | 2241057 | 529490 | 2365440 | 32651 | 0 | 0 | 243744 | 257369 | 1179510 | 645610 | 511184 | 242566 | 442080 | 188529 | 278160 | 140148 | 118350 | 0 | 1826618 | 6674300 | 90000 | 57000 | 0 | 0 | 0 | 4261318 | 1904024 | 482880 | 0 | 0 |  | 152346710 | 52554409 | 204901119 | 76474572 | 11557090 | 39209988 | 40711639 | 8500918 | 2424487 | 22597230 | 3408960 | 16235 | 0
Fuel Cost | 672520 | 2512326.6 | 0 | 3830526 | 3280156.96 | 0 | 0 | 5139769.72 | 4298670 | 5396976 | 0 | 5755927.12 | 84295993.6 | 7873612.8 | 8064416.64 | 6348503.85 | 2344704.7 | 0 | 0 | 9500313.6 | 6996000 | 8333766.72 | 25389552 | 8388315.39 | 7648032 | 7963819.5 | 4307432.64 | 7210141.2 | 6039181.25 | 5949352.2 | 313416 | 431250 | 0 | 0 | 0 | 8314545.36 | 0 | 0 | 0 | 0 | 0 | 4058652.6 | 0 | 65091526.5 | 0 | 48672276.24 | 0 | 7923657.6 | 7609478.88 | 5752930.61 | 12447099.6 | 12446611.2 | 5562662.4 | 315628.8 | 0 | 1826240.78 | 1845912.25 | 0 | 6348979 | 2007037.5 | 3117100 | 1696647.21 | 3321791.04 | 551334.96 | 0 | 248400 | 730348.58 | 1134813.12 | 3237604.48 | 1123922.24 | 268523.64 | 171855 | 533918 | 339322.5 | 23317286.4 | 1458247.5 | 11200845.52 | 173444.04 | 0 | 1280240 | 1786470.4 | 866304 | 778500 | 4421957.46 | 4338406.8 | 1450080 | 1426780.8 | 831600 | 2608605 | 0 | 751402.8 | 136263.6 | 4682732.8 | 403380 | 105208.32 | 13409260.8 | 0 | 0 | 0 |  | 58941159 | 4218005 | 4624286.4 | 9184032 | 14472000 | 58628966.4 | 0 | 4334416.8 | 3791467.2 | 8303674.88 | 4636563.75 | 2218646.43 | 524195.1 | 14618419.2 | 1099685.68 | 0 | 0 | 2790868.8 | 2758995.68 | 10568409.6 | 5584526.5 | 4549537.6 | 2583327.9 | 4385433.6 | 2030457.33 | 305976 | 131739.12 | 89590.95 | 0 | 11087571.26 | 0 | 2076300 | 1222080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 520410512.82 | 239760332.18 | 760170845 | 59708919.29 | 58941159 | 28722257.71 | 322568044.16 | 11087571.26 | 0 | 255825607.18 | 23317286.4 | 0 | 0
Yesterday Day Peak | 37 | 130 | 0 | 190 | 0 | 0 | 0 | 376 | 301 | 0 | 0 | 450 | 200 | 7 | 15 | 55 | 170 | 0 | 0 | 0 | 7 | 24 | 115 | 30 | 8 | 21 | 6 | 18 | 56 | 17 | 22 | 25 | 23 | 33 | 33 | 42 | 0 | 70 | 33 | 0 | 0 | 17 | 0 | 209 | 0 | 120 | 0 | 51 | 0 | 0 | 90 | 98 | 36 | 15 | 2 | 100 | 120 | 0 | 310 | 0 | 204 | 144 | 154 | 39 | 0 | 10 | 51 | 51 | 0 | 0 | 16 | 11 | 33 | 15 | 136 | 89 | 16 | 0 | 2.3 | 51 | 74 | 39 | 39 | 140 | 318 | 60 | 84 | 45 | 100 | 0 | 41 | 0 | 325 | 23 | 0 | 0 | 14 | 0 | 0 |  | 479 | 0 | 340 | 10 | 82 | 130 | 0 | 0 | 0 | 5 | 33 | 129 | 9 | 64 | 0 | 0 | 0 | 0 | 0 | 34 | 25 | 8 | 0 | 8 | 0 | 18 | 8 | 5 | 0 | 75 | 280 | 0 | 0 | 0 | 0 | 0 | 190 | 95 | 0 | 0 | 0 |  | 8033.3 | DayPeak
Yesterday Evening Peak | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 300 | 292 | 55 | 0 | 450 | 305 | 100 | 100 | 55 | 0 | 0 | 0 | 100 | 86 | 94 | 149 | 100 | 99 | 51 | 48 | 54 | 37 | 55 | 22 | 25 | 32 | 33 | 33 | 45 | 0 | 69 | 33 | 0 | 0 | 25 | 0 | 195 | 0 | 130 | 0 | 42 | 80 | 47 | 90 | 90 | 44 | 16 | 24 | 100 | 100 | 0 | 321 | 231 | 183 | 105 | 154 | 42 | 0 | 10 | 51 | 85 | 48 | 25 | 19 | 11 | 33 | 21 | 188 | 83 | 95 | 22 | 0 | 58 | 74 | 53 | 50 | 163 | 301 | 49 | 86 | 50 | 118 | 0 | 46 | 9 | 255 | 23 | 11 | 180 | 285 | 0 | 82 |  | 479 | 33 | 318 | 108 | 102 | 211 | 0 | 53 | 42 | 61 | 33 | 120 | 35 | 110 | 0 | 0 | 0 | 43 | 41 | 102 | 40 | 43 | 47 | 43 | 36 | 18 | 10 | 11 | 0 | 77 | 260 | 16 | 18 | 0 | 0 | 0 | 223 | 95 | 100 | 0 | 0 |  | 10875 | EvPeak
Forecast for Evening | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 412 | 360 | 84 | 0 | 450 | 305 | 100 | 100 | 55 | 170 | 0 | 0 | 100 | 88 | 94 | 149 | 100 | 100 | 50 | 48 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 90 | 50 | 0 | 0 | 25 | 0 | 203 | 0 | 130 | 0 | 51 | 85 | 50 | 90 | 98 | 44 | 20 | 24 | 100 | 120 | 0 | 360 | 360 | 221 | 150 | 154 | 42 | 0 | 10 | 51 | 85 | 48 | 52 | 19 | 11 | 33 | 22 | 188 | 89 | 95 | 22 | 0 | 60 | 74 | 50 | 50 | 163 | 330 | 66 | 86 | 50 | 130 | 0 | 48 | 10 | 341 | 23 | 11 | 200 | 285 | 0 | 100 |  | 482 | 33 | 318 | 110 | 115 | 225 | 0 | 55 | 42 | 60 | 33 | 170 | 33 | 110 | 30 | 0 | 0 | 43 | 41 | 100 | 43 | 43 | 48 | 44 | 36 | 18 | 10 | 11 | 0 | 77 | 280 | 17 | 18 | 0 | 0 | 0 | 220 | 95 | 100
Forecast for Day | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 412 | 360 | 84 | 0 | 450 | 305 | 100 | 100 | 55 | 170 | 0 | 0 | 100 | 88 | 94 | 149 | 100 | 100 | 50 | 48 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 84 | 50 | 0 | 0 | 25 | 0 | 203 | 0 | 135 | 0 | 51 | 85 | 50 | 90 | 98 | 44 | 20 | 2 | 100 | 120 | 0 | 360 | 360 | 221 | 150 | 154 | 42 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 11 | 33 | 22 | 144 | 89 | 95 | 22 | 2 | 60 | 74 | 50 | 50 | 163 | 330 | 66 | 86 | 50 | 130 | 0 | 48 | 10 | 341 | 23 | 11 | 0 | 100 | 0 | 0 |  | 482 | 0 | 318 | 110 | 115 | 225 | 0 | 0 | 0 | 40 | 33 | 170 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 43 | 43 | 48 | 44 | 0 | 18 | 10 | 11 | 0 | 77 | 280 |  | 0 | 0 | 0 | 0 | 220 | 95
Generation at 08:00(Today) | 37 | 130 | 0 | 190 | 165 | 0 | 0 | 360 | 332 | 0 | 0 | 380 | 110 | 7 | 15 | 30 | 110 | 0 | 0 | 0 | 15 | 7 | 48 | 10 | 60 | 0 | 0 | 18 | 37 | 17 | 19 | 0 | 32 | 33 | 33 | 27 | 0 | 66 | 32 | 0 | 0 | 17 | 0 | 203 | 0 | 70 | 0 | 24 | 24 | 14 | 90 | 91 | 44 | 19 | 2 | 100 | 100 | 0 | 335 | 320 | 164 | 53 | 154 | 42 | 0 | 5 | 20 | 31 | 0 | 0 | 19 | 11 | 33 | 22 | 140 | 85 | 56 | 22 | 0.7 | 56 | 74 | 11 | 10 | 100 | 314 | 61 | 30 | 20 | 118 | 0 | 45 | 9 | 305 | 23 | 11 | 0 | 95 | 0 | 0 | 0 | 479 | 0 | 300 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 8 | 142 | 23 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 25 | 0 | 8 | 0 | 18 | 11 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 180 | 95 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 5950.4 | 7:00
| Highest Generation |  | 10875 | 21:00
| Day Peak Generation |  | 8033.3 | 12:00
| Evening Peak Generation |  | 10875 | 21:00
| HVDC Max Flow |  | 479 | 12:00
| HVDC EvPeak Flow |  | 479 | 21:00
| Load factor L.F |  | 78.51%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-05-30
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-05-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8033.3 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7679.4 | MW
Evening Peak Generation : |  | 10875 | MW Hour : | 21:00 | Available Max Generation : |  | 11978 | MW
E.P. Demand (at gen end) : |  | 10875 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10875 | MW Hour : | 21:00 | Reserve(Generation end) |  | 978 | MW
Total Gen. (MKWH) : |  | 204.9011 | System Load Factor : | 78.51% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -640 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-05-30
Actual : | 81.19 | Ft.(MSL) , | Rule curve : | 76.6 | Ft.( MSL )
Gas Consumed : | Total = | 1034.97 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 88431177
|  | Coal : | 11087571.26 | Oil : | 578393651.34 | Total : | 677912399.6
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3884.355 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1320.4347 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1182.9835 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1068.8963 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 965.9622 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 779.4961 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 436.4491 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 200.715 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 601.1833 |  |  | 0 | 0%
Total | 0 |  | 10440.4751 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj ST: Unit- 5
| Nil |  |  | 2) Sylhet 20 MW |  | 11) Haripur GT-1,2
|  |  |  | 3) Khulna ST 110 MW | (04/11/14) | 12) Sirajgonj Unit-1 225 MW
|  |  |  | 4) Ghorasal Unit-2,4 |  | 13) Ashuganj 55 MW
5) Baghabari 100 MW
6) Tongi GT
7) Chittagong Unit-1,2
8) Baghabari-71 MW
9) Siddhirganj 210 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Aminbazar-Savar 132 kV Ckt-1 was under shut down from 07:26 to 16:38 for C/M.
b) Shunamganj 132/33 kV T2 transformer tripped at 09:20 showing differential 3-phase.
c) Ashuganj Unit-3 & 4 were synchronized at 09:53 & 09:28 respectively.
d) Ishurdi 132/33 kV T2 transformer was under shut down from 09:58 to 11:10 due to Y-phase Bushing temperature high.
e) Sikalbaha-Dohazari 132 kV Ckt-2 was under shut down from 10:45 to 13:09 for wave trap loop maintenance.
f) Modunaghat-TK Chemical -Sikalbaha 132 kV Ckt tripped at 12:10 from Modunaghat & Sikalbaha end showing dist B-phase
Z1 ABC, O/C and was switched on at 13:01.
g) Haripur-Bhulta 132 kV Ckt tripped at 12:33 showing dist Z1 ,CN and was switched on at 12:43. |  |  |  | About 98 MW power interruption occurred under Bhulta S/S
area from 12:33 to 12:43.
h) Ghorasal Unit-7 tripped at 11:53 due to gas problem and GT & ST were synchronized at 13:53 & 15:45 respectively.
i) Goalpara 132/33 kV TR-5 transformer was under shut down from 09:18 to 18:18 for painting work.
j) Satkhira 132/33 kV T2 transformer was under shut down from 11:29 to 16:28 for CB maintenance.
k) Rangpur 33 kV bus-2 & 3 were under shut down from 12:12 to 13:20 for red hot maintenance. |  |  |  | About 25 MW power interruption occurred under Rangpur S/S
area from 12:12 to 13:20.
l) After maintenance Ashuganj(S) 450 MW GT & ST were synchronized at 15:05 & 17:23 respectively.
m) Aminbazar-Savar 132 kV Ckt-1 was shut down at 06:46(30/05/2018) for C/M..
n) Satkhira 132/33 kV T1 transformer tripped at 15:04 showing O/C 3-phase and was switched on at 15:08. |  |  |  | About 64 MW power interruption occurred under Satkhira S/S
area from 15:04 to 15:08.
o) Madunaghat 132/33 kV T1 transformer was shut down at 12:11 (30/05/2018) for D/W. |  |  |  | About 5 MW power interruption occurred under Madunaghat S/S
area from 00:11(30/05/2018) to till now.
p) Bagerhat 132/33 kV T3 transformer was shut down from 07:02 to 09:25(30/05/2018) due to problem at 33 kV
Y-phase isolator clamp.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-05-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 37 | 782000 | #1 Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 130 | 2921310 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 190 | 4454100
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 165 | 3814136 | On test.
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 300 | 8425852 | Gas shortage.
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 55 | 561600 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 292 | 7047000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8590936
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1253760
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 305 | 5549440
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 100 | 1207248
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1039035
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1316847
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 417888
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 610560
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 86 | 1119360 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 0 | 3607238 | On test.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 498050
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 94 | 1264608
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 48 | 645792
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1011240
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2625600
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 37 | 966269 | Engine problem
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 948860
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 99 | 1276800
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1174220 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 594513
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 717300
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 45 | 878916 | Engine problem
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 285 | 2857853 | On test.
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 MW | 0 | 82 | 445052
| Dhaka area Total |  |  |  | 5199 | 3609 | 68623383
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 25 | 428580
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 44 | 850560 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 102 | 2424487
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 195 | 4768610
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2221464 | FGMO
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 42 | 901440 | Engine problem
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 80 | 706544
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 47 | 591257
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 2010840 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 371328 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 337440
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 90 | 1926720 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 885 | 17539270
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2006858 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2028475 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 183 | 4453000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 321 | 6976900 | FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 231 | 2908750 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 42 | 822888
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 10 | 270000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 105 | 2458909 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 890669
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 85 | 1207248
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 48 | 298672
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 154 | 3460199
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 348732
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 229140
** | Tripura |  | Imported power | 0 | 160 | 188 | 3408960
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 693400
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 25 | 151472 | Low demand
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 452430
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 180 | 773760
| Comilla Area Total |  |  |  | 2541 | 1907 | 33840462
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 83 | 1944330 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 225252
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1218808
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 16235
| Mymensingh Area Total |  |  |  | 322 | 200 | 3404625
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 58 | 1231000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 74 | 1717760
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3427874
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 301 | 6197724 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 902400
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 865000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 138432
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 49 | 1272000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1333440
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 50 | 756000
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 118 | 2288250
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 807960
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 537840
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 255 | 7316770 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 146520
| Sylhet Area Total |  |  |  | 1549 | 1346 | 28938970
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 33 | 144700
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 479 | 11557090
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 108 | 1391520
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 102 | 2160000 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 42 | 336720
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 211 | 3646080
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 61 | 704896
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 318 | 6901920 | Gas shortage
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 33 | 727875 | Engine problem
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 53 | 271580
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 100 | 482880 | On test.
| Khulna Area Total |  |  |  | 1769 | 1540 | 28325261
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 2365440
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 32651 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 35 | 529490
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 120 | 2241057
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 1904024
| Barisal Area Total |  |  |  | 462 | 360 | 7072662
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 243744
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 41 | 257369
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 645610
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 511184 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 47 | 242566
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 223 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 36 | 188529
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 18 | 278160 | Engine problem
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 140148
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 118350
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 442080 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 1179510
| Rajshahi Area Total |  |  |  | 1123 | 657 | 4247250
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 77 | 1826618
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 260 | 6674300
117 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 90000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 57000
| Rangpur Area Total |  |  |  | 484 | 371 | 8647918
| Total |  |  |  | 15010 | 10875 | 200639801
| Eastern Grid Total |  |  |  | 11172 | 7947 | 152346710
| Western Grid Total |  |  |  | 3838 | 2928 | 48293091
| National Grid Total |  |  |  | 15010 | 10875 | 200639801
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-05-29 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 7007 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3303 | MW
i) Dhaka area |  |  | 3928 | MW | i) Khulna area |  |  | 1373 | MW
ii) Chittagong area |  |  | 1019 | MW | ii) Rajshahi area |  |  | 1032 | MW
iii) Comilla area |  |  | 973 | MW | iii) Barisal area |  |  | 261 | MW
iv) Mymensingh area |  |  | 675 | MW | iv) Rangpur area |  |  | 637 | MW
v) Sylhet area |  |  | 412 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 10310 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 1000 | Kishorganj | 92 | 2100 | Central s/s | 76 | 1900
Munsiganj | 120 | 2100 | Netrokona | 68 | 1900 | Noapara | 95 | 1930
Megnaghat | 58 | 2100 | Jamalpur | 92 | 2300 | Jessore | 147 | 2100
Shyampur | 152 | 100 | Sherpur | 66 | 2200 | Jhenida | 92 | 2100
Bhulta | 168 | 100 | Srimongal | 42 | 1900 | Bottail | 124 | 2100
Madanganj | 43 | 100 | Shahjibazar | 94 | 2200 | G.K Project | 54 | 2000
Shitalakhya | 107 | 1600 | Fenchuganj | 47 | 2100 | Faridpur | 150 | 2000
Rahim steel | 10 | 700 | Kulawara | 41 | 1900 | Madaripur | 134 | 2100
Matuail | 94 | 1400 | Sylhet | 155 | 2100 | Gopalganj | 87 | 2100
Ghorasal | 81 | 2100 | Chatak | 27 | 2100 | Bagerhat | 85 | 1930
Narsingdi | 120 | 2000 | Sunamganj | 27 | 2100 | Mongla | 32 | 1100
Haripur (SBU) | 97 | 1600 | Comilla (S) | 188 | 2100 | Satkhira | 91 | 2100
Ullon | 98 | 1930 | Comilla(N) | 93 | 2100 | Gallamari | 60 | 2000
Hasnabad | 209 | 2100 | Chandpur | 128 | 1900 | Magura | 46 | 2100
Magbazar | 117 | 1500 | Feni | 109 | 2100 | Chuadanga | 81 | 2100
Maniknagar | 80 | 1000 | Chowmuhani | 196 | 2100 | Barisal | 116 | 1930
Bangabhaban | 36 | 1100 | Ashuganj | 56 | 2200 | Patuakhali | 87 | 2100
Narinda | 84 | 1930 | Daudkandi | 100 | 2200 | Bhandaria | 47 | 2200
Dhanmondi | 163 | 1300 | B.Baria | 123 | 2100 | Ishurdi | 53 | 2000
Lalbag | 89 | 1600 | Madunaghat | 71 | 2000 | Ruppur Paromanobik | 1 | 100
Madartek | 52 | 2100 | Hathazari | 77 | 1930 | Natore | 93 | 2000
Mirpur | 109 | 2100 | Khulshi | 194 | 1000 | Bogra | 112 | 1930
Kalyanpur | 129 | 2100 | Halishahar | 136 | 1400 | Noagaon | 92 | 1930
Gulshan | 92 | 2100 | Baraulia | 140 | 1000 | Rajshahi | 137 | 2100
Uttara | 78 | 1930 | Sikalbaha | 43 | 1930 | C.Nawabganj | 64 | 2100
Kamrangirchar | 78 | 1930 | Dohazari | 88 | 1900 | Amnura | 30 | 2000
Savar | 148 | 1930 | Cox'sbazar | 94 | 2000 | Pabna | 106 | 2000
Bhasantec | 155 | 2000 | Chandraghona | 33 | 1900 | Shahjadpur | 84 | 2100
Agargaon | 46 | 1930 | Kaptai | 4 | 1830 | Serajganj | 81 | 2100
Satmosjid | 94 | 2100 | A. Khaer Stl. | 9 | 500 | Niyamatpur | 46 | 2000
Tongi | 142 | 1900 | Bakulia | 114 | 2000 | Joypurhat | 49 | 2000
Kabirpur | 187 | 1600 | Julda | 23 | 200 | Rangpur | 115 | 2100
Basundhara | 134 | 2100 | TK chemical | 105.4 | 1100 | Lalmonirhat | 86 | 1930
Manikganj | 104 | 2000 | Modern Steel | 12 | 200 | Saidpur | 111 | 2000
Joydevpur | 213 | 1930 | Shahmirpur | 30 | 2100 | Purbasadipur | 95 | 2100
New Tongi | 109 | 1200 | Abul Khair 230 | 14 | 100 | Thakurgaon | 61 | 2100
Korda | 212 | 2000 | BSRM | 107 | 200 | Palashbari | 100 | 2100
Tangail | 167 | 2100 | Khagrachhari | 18 | 1930 | Barapukuria | 49 | 2100
Mymensing | 217 | 2100 | Goalpara | 41 | 1930 | Panchagar | 34 | 1930
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-05-29
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 391 | 19:00 | 381 | 12:00 | Kaliakoir | 375 | 1:00 | 356 | 12:00
Bheramara | 407 | 6:00 | 399 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 222 | 15:00 | Tongi | 220 | 18:00 | 209 | 12:00
Ishurdi | 237 | 6:00 | 224 | 21:00 | Comilla (N) | 233 | 19:30 | 223 | 13:00
Ashuganj | 235 | 1:00 | 225 | 11:00 | Hathazari | 215 | 1:00 | 205 | 14:00
Serajganj | 225 | 2:00 | 215 | 21:00 | Megnaghat | 230 | 18:30 | 219 | 12:00
Baghabari | 230 | 5:00 | 218 | 22:00 | Fenchuganj | 238 | 5:00 | 232 | 9:00
Barapukuria | 242 | 5:00 | 227 | 21:00 | Siddhirganj | 224 | 6:00 | 215 | 12:00
Bogra | 230 | 6:00 | 210 | 21:00 | Maniknagar | 224 | 18:30 | 213 | 12:00
Khulna South | 235 | 6:00 | 224 | 1:00 | Old Airport | 222 | 6:00 | 210 | 12:00
Rampura | 222 | 6:00 | 216 | 12:00 | Barisal | 239 | 4:00 | 218 | 1:00
Haripur | 223 | 19:00 | 215 | 11:00 | AKSML | 218 | 20:00 | 207 | 1:00
Hasnabad | 225 | 18:30 | 212 | 12:00 | BSRM | 220 | 20:00 | 210 | 14:00
Aminbazar | 224 | 1:00 | 213 | 11:00 | Bibiyana | 233 | 2:00 | 227 | 13:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 1830 | 127 | 1200 | Madanhat | 131 | 100 | 125 | 1400
Munsiganj | 136 | 1830 | 127 | 1100 | Hathazari | 128 | 100 | 123 | 1500
Megnaghat | 136 | 1900 | 126 | 1200 | Khulshi | 137 | 400 | 121 | 700
Shyampur | 132 | 1930 | 122 | 1200 | Halishahar | 130 | 400 | 122 | 900
Bhulta | 135 | 2000 | 120 | 1100 | Baraulia | 127 | 400 | 121 | 900
Madanganj | 136 | 1830 | 126 | 1200 | Sikalbaha | 129 | 300 | 124 | 900
Shitalakhya | 139 | 1900 | 125 | 1200 | Dohazari | 126 | 300 | 122 | 1500
Rahim steal | 136 | 1900 | 128 | 1100 | Cox'sbazar | 126 | 1300 | 114 | 1900
Matuail | 136 | 1900 | 125 | 1200 | Chandraghona | 130 | 300 | 125 | 1300
Ghorasal | 138 | 100 | 130 | 1500 | Kaptai | 130 | 300 | 127 | 1300
Narsinghdi | 134 | 1900 | 123 | 1200 | A. Khaer Stl. | 127 | 1800 | 124 | 1300
Haripur (SBU) | 137 | 1800 | 127 | 1200 | Bakulia | 127 | 200 | 122 | 800
Ullon | 136 | 300 | 128 | 1200 | Julda | 128 | 200 | 123 | 1500
Hasnabad | 136 | 200 | 126 | 1200 | TK Chemical | 130 | 100 | 126 | 1500
Magbazar | 136 | 500 | 126 | 1200 | Modern Steel | 127 | 300 | 121 | 1500
Maniknagar | 135 | 600 | 128 | 1200 | Shahmirpur | 128 | 300 | 124 | 1500
Bangabhaban | 131 | 100 | 128 | 1200 | Khagrachhari | 130 | 500 | 123 | 1500
Narinda | 137 | 600 | 128 | 1200 | Goalpara | 139 | 600 | 133 | 100
Dhanmondi | 135 | 600 | 128 | 1200 | Central s/s | 138 | 600 | 132 | 100
Lalbag | 131 | 100 | 119 | 1200 | Noapara | 136 | 700 | 127 | 100
Madartek | 137 | 600 | 128 | 1200 | Jessore | 132 | 700 | 121 | 2100
Mirpur | 134 | 100 | 124 | 1200 | Jhenida | 134 | 600 | 118 | 2100
Kalyanpur | 133 | 600 | 126 | 1200 | Bottail | 136 | 700 | 127 | 2100
Gulshan | 136 | 500 | 128 | 1200 | G.K.Project | 144 | 600 | 134 | 2100
Uttara | 129 | 600 | 121 | 1200 | Faridpur | 132 | 600 | 122 | 2100
Kamrangirchar | 133 | 600 | 124 | 1200 | Madaripur | 133 | 300 | 123 | 1900
Savar | 130 | 200 | 121 | 1200 | Gopalganj | 134 | 300 | 123 | 2100
Bhasantec | 128 | 600 | 118 | 1200 | Bagerhat | 133 | 800 | 129 | 100
Agargaon | 129 | 600 | 120 | 1200 | Mongla | 132 | 800 | 125 | 2100
Satmosjid | 128 | 600 | 119 | 1200 | Satkhira | 135 | 700 | 129 | 2100
Tongi | 132 | 1800 | 125 | 1300 | Gallamari | 139 | 600 | 132 | 100
Kabirpur | 136 | 200 | 122 | 2000 | Magura | 132 | 500 | 115 | 2100
Basundhara | 130 | 1830 | 122 | 1400 | Chuadanga | 129 | 600 | 110 | 2100
Manikganj | 140 | 200 | 132 | 2100 | Barisal | 138 | 700 | 133 | 1500
Joydevpur | 140 | 200 | 128 | 1500 | Patuakhali | 138 | 700 | 133 | 1500
New Tongi | 134 | 600 | 124 | 1400 | Bhandaria | 140 | 700 | 120 | 100
Kodda | 141 | 200 | 128 | 1500 | Ishurdi | 143 | 600 | 133 | 2100
Tangail | 139 | 100 | 121 | 2000 | Ruppur Paromanobik | 139 | 900 | 135 | 100
Mymensing | 138 | 100 | 110 | 2100 | Natore | 140 | 500 | 130 | 2100
Kishorganj | 135 | 200 | 118 | 2100 | Bogra | 140 | 600 | 122 | 2100
Netrokona | 135 | 500 | 110 | 1900 | Noagaon | 137 | 500 | 120 | 2100
Jamalpur | 137 | 100 | 111 | 2300 | Rajshahi | 137 | 1830 | 128 | 2100
Sherpur | 138 | 100 | 109 | 2300 | C.Nawabganj | 135 | 500 | 128 | 1300
Srimongal | 136 | 1830 | 127 | 1200 | Amnura | 140 | 500 | 130 | 1100
Shahjibazar | 136 | 1830 | 127 | 1100 | Pabna | 135 | 600 | 127 | 2100
Fenchuganj | 136 | 1900 | 126 | 1200 | Shahjadpur | 143 | 400 | 133 | 2100
Khulawara | 132 | 1930 | 122 | 1200 | Serajganj | 138 | 400 | 126 | 2100
Sylhet | 135 | 2000 | 120 | 1100 | Niyamatpur | 139 | 100 | 114 | 2100
Chatak | 136 | 1830 | 126 | 1200 | Joypurhat | 138 | 500 | 115 | 2100
Sunamganj | 139 | 1900 | 125 | 1200 | Rangpur | 135 | 700 | 110 | 2100
Comilla(s) | 132 | 600 | 129 | 2100 | Lalmonirhat | 135 | 600 | 105 | 2100
Comilla(n) | 137 | 1830 | 129 | 700 | Saidpur | 136 | 500 | 108 | 2100
Chandpur | 130 | 700 | 125 | 1900 | Purbasadipur | 140 | 700 | 120 | 2100
Feni | 121 | 700 | 115 | 1400 | Thakurgaon | 138 | 500 | 115 | 2100
Chowmuhani | 129 | 600 | 116 | 100 | Palashbari | 136 | 100 | 111 | 2100
Ashuganj | 140 | 300 | 131 | 2400 | Barapukuria | 142 | 500 | 127 | 2100
Daudkandi | 138 | 1830 | 125 | 1200 | Panchagar | 134 | 500 | 108 | 2100
B.Baria | 140 | 300 | 126 | 2300
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-05-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 570 | 7615 | 2704 | 10319 |  |  |  | QF-LDC-12
0:30 | 485 | 7148 | 2318.5 | 9466.5 | Date: | 2018-05-29
1:00 | 400 | 6681 | 1933 | 8614
1:30 | 385 | 6380 | 1940.5 | 8320.5
2:00 | 370 | 6079 | 1948 | 8027
2:30 | 385 | 5896 | 1962.5 | 7858.5 | [5 empty] | Gen. at Eve. Peak | 10875 | 10875 MW (21:00 )
3:00 | 400 | 5713 | 1977 | 7690 | [6 empty] | 21:00
3:30 | 370 | 5558 | 1946 | 7504 | [5 empty] | Gen. at Day Peak | 8033.3 | 8033.3 MW (12:00 )
4:00 | 340 | 5403 | 1915 | 7318 | [6 empty] | 12:00
4:30 | 240 | 5087 | 1857 | 6944 | [5 empty] | Highest Generation | 10875
5:00 | 140 | 4771 | 1799 | 6570 | [6 empty] | 21:00
5:30 | 70 | 4594.05 | 1730 | 6324.05
6:00 | 0 | 4417.1 | 1661 | 6078.1
6:30 | 60 | 4382.75 | 1631.5 | 6014.25
7:00 | 120 | 4348.4 | 1602 | 5950.4
7:30 | 90 | 4545.65 | 1648 | 6193.65
8:00 | 60 | 4742.9 | 1694 | 6436.9
8:30 | 65 | 4993.8 | 1786.5 | 6780.3
9:00 | 70 | 5244.7 | 1879 | 7123.7
9:30 | 50 | 5501.85 | 1895 | 7396.85
10:00 | 30 | 5759 | 1911 | 7670
10:30 | 75 | 5854.1 | 1943.5 | 7797.6
11:00 | 120 | 5949.2 | 1976 | 7925.2
11:30 | 130 | 5977.75 | 2001.5 | 7979.25
12:00 | 140 | 6006.3 | 2027 | 8033.3
12:30 | 160 | 6127.75 | 2128.5 | 8256.25
13:00 | 180 | 6249.2 | 2230 | 8479.2
13:30 | 210 | 6533.05 | 2227 | 8760.05
14:00 | 240 | 6816.9 | 2224 | 9040.9
14:30 | 290 | 6855.75 | 2226 | 9081.75
15:00 | 340 | 6894.6 | 2228 | 9122.6
15:30 | 310 | 6973.3 | 2212 | 9185.3
16:00 | 280 | 7052 | 2196 | 9248
16:30 | 350 | 6864.15 | 2121 | 8985.15
17:00 | 420 | 6676.3 | 2046 | 8722.3
17:30 | 450 | 6663.65 | 2069 | 8732.65
18:00 | 480 | 6651 | 2092 | 8743
18:30 | 560 | 6965 | 2270.5 | 9235.5
19:00 | 640 | 7279 | 2449 | 9728
19:30 | 560 | 7759 | 2796 | 10555
20:00 | 540 | 7660 | 2806 | 10466 |  |  |  | Executive Engineer
20:30 | 590 | 7803.5 | 2867 | 10670.5 |  |  |  | Network Operation Division
21:00 | 640 | 7947 | 2928 | 10875
21:30 | 625 | 7881 | 2874.5 | 10755.5
22:00 | 610 | 7815 | 2821 | 10636 |  |  |  |  | Page 6 of 7
22:30 | 595 | 7795.5 | 2786.5 | 10582
23:00 | 580 | 7776 | 2752 | 10528
23:30 | 575 | 7695.5 | 2728 | 10423.5
24:00 | 570 | 7615 | 2704 | 10319
10875 MW (21:00 )
8033.3 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-05-29 |  | Energy | 204901119
[10 empty] | 2018-05-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3590 | 479 | 1811 | 2563 | 336 | 103 | 1261 | 0 | 176
0:30 | 3381.5 | 476 | 1775.5 | 2084 | 346.5 | 111.5 | 1122.5 | 0 | 169 | Date: | 2018-05-29
1:00 | 3173 | 473 | 1740 | 1605 | 357 | 120 | 984 | 0 | 162
1:30 | 3119 | 473 | 1708 | 1441 | 356.5 | 119 | 938 | 0 | 166 | [7 empty] | Total Energy | 204.9011 | Total Energy Gen 204.901 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 204.901 MKWHr
2:00 | 3065 | 473 | 1676 | 1277 | 356 | 118 | 892 | 0 | 170 | [7 empty] | Energy not Served | 0
2:30 | 3076 | 473 | 1592 | 1197.5 | 356 | 116.5 | 872.5 | 0 | 175 | [7 empty] | Energy Requirement | 204.9011
3:00 | 3087 | 473 | 1508 | 1118 | 356 | 115 | 853 | 0 | 180
3:30 | 3050.5 | 473 | 1433.5 | 1092 | 356 | 115 | 849 | 0 | 135 | [6 empty] | Shortage
4:00 | 3014 | 473 | 1359 | 1066 | 356 | 115 | 845 | 0 | 90
4:30 | 2862 | 473 | 1278.5 | 1014 | 356.5 | 115.5 | 769.5 | 0 | 75
5:00 | 2710 | 473 | 1198 | 962 | 357 | 116 | 694 | 0 | 60
5:30 | 2672.5 | 473 | 1103 | 890 | 357 | 116 | 653.5 | 0 | 59
6:00 | 2635 | 473 | 1008 | 818 | 357 | 116 | 613 | 0 | 58
6:30 | 2563 | 472.5 | 1030 | 774.5 | 357.5 | 116 | 632.5 | 0 | 68 |  |  |  |  | Coal
7:00 | 2491 | 472 | 1052 | 731 | 358 | 116 | 652 | 0 | 78
7:30 | 2652 | 472.5 | 1132 | 719.5 | 356.5 | 115.5 | 657 | 0 | 88 |  |  |  | Oil |  |  |  | ,
8:00 | 2813 | 473 | 1212 | 708 | 355 | 115 | 662 | 0 | 98
8:30 | 3019.5 | 472.5 | 1316 | 737 | 348.5 | 115 | 665.5 | 0 | 105
9:00 | 3226 | 472 | 1420 | 766 | 342 | 115 | 669 | 0 | 112
9:30 | 3263 | 472 | 1526 | 852 | 345 | 115 | 709 | 0 | 113
10:00 | 3300 | 472 | 1632 | 938 | 348 | 115 | 749 | 0 | 114
10:30 | 3371 | 475 | 1639 | 985.5 | 350 | 108.5 | 744.5 | 0 | 122
11:00 | 3442 | 478 | 1646 | 1033 | 352 | 102 | 740 | 0 | 130
11:30 | 3343.5 | 478.5 | 1749 | 1045.5 | 353.5 | 102.5 | 771.5 | 0 | 133
12:00 | 3245 | 479 | 1852 | 1058 | 355 | 103 | 803 | 0 | 136
12:30 | 3195 | 478.5 | 1862.5 | 1290.5 | 355.5 | 103 | 829 | 0 | 140
13:00 | 3145 | 478 | 1873 | 1523 | 356 | 103 | 855 | 0 | 144
13:30 | 3145 | 478 | 1873 | 1523 | 356 | 103 | 855 | 0 | 144
14:00 | 3145 | 478 | 1873 | 1523 | 356 | 103 | 855 | 0 | 144
14:30 | 3206 | 478 | 1892.5 | 1761 | 357 | 98.5 | 850 | 0 | 156
15:00 | 3267 | 478 | 1912 | 1999 | 358 | 94 | 845 | 0 | 168
15:30 | 3324.5 | 478.5 | 1894 | 2032 | 357.5 | 94.5 | 841 | 0 | 162
16:00 | 3382 | 479 | 1876 | 2065 | 357 | 95 | 837 | 0 | 156
16:30 | 3358 | 479 | 1736.5 | 2001 | 357 | 96 | 810 | 0 | 147
17:00 | 3334 | 479 | 1597 | 1937 | 357 | 97 | 783 | 0 | 138
17:30 | 3343.5 | 479 | 1557.5 | 1941.5 | 357 | 98.5 | 814.5 | 0 | 141
18:00 | 3353 | 479 | 1518 | 1946 | 357 | 100 | 846 | 0 | 144
18:30 | 3303.5 | 479 | 1538.5 | 2249 | 342 | 100 | 1069.5 | 0 | 154
19:00 | 3254 | 479 | 1559 | 2552 | 327 | 100 | 1293 | 0 | 164
19:30 | 3416 | 478 | 1766 | 2857 | 339 | 100 | 1423 | 0 | 176
20:00 | 3324 | 478 | 1760 | 2848 | 349 | 101 | 1434 | 0 | 172
20:30 | 3355 | 478.5 | 1823.5 | 2911 | 343 | 101.5 | 1478 | 0 | 180
21:00 | 3386 | 479 | 1887 | 2974 | 337 | 102 | 1522 | 0 | 188
21:30 | 3437.5 | 479 | 1878.5 | 2874 | 336 | 102.5 | 1462 | 0 | 186
22:00 | 3489 | 479 | 1870 | 2774 | 335 | 103 | 1402 | 0 | 184
22:30 | 3555.5 | 478.5 | 1845.5 | 2739.5 | 336 | 103 | 1344 | 0 | 180
23:00 | 3622 | 478 | 1821 | 2705 | 337 | 103 | 1286 | 0 | 176
23:30 | 3606 | 478.5 | 1816 | 2634 | 336.5 | 103 | 1273.5 | 0 | 176 | Max Temp. in Dhaka |  | 35.4° C
24:00 | 3590 | 479 | 1811 | 2563 | 336 | 103 | 1261 | 0 | 176
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 204.901 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 204.901 MKWHr
Note on W13: Author:

## Generation
2018-05-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 87 | 87 | 84 | 84 | 85 | 85 | 84 | 84 | 83 | 83 | 70 | 70 | 70 | 67 | 64 | 65 | 67 | 67 |  | 68 | 68 | 69 | 69 | 70 | 70 | 70 | 1663287
2 | Kaptai Unit-4 & 5 | 33 | 31 | 31 | 31 | 31 | 31 | 32 | 31 | 32 | 32 | 32 | 33 | 33 | 31 | 30 | 30 | 30 | 33 |  | 32 | 32 | 32 | 33 | 33 | 33 | 33 | 761200
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 25 | 26 | 26 | 25 | 0 |  |  |  |  | 17 | 17 | 17 | 17 | 16 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 428580
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 196 | 195 | 195 | 195 | 195 | 196 | 204 | 206 | 196 | 202 | 202 | 209 | 202 | 204 | 202 | 200 | 202 | 202 |  | 201 | 201 | 202 | 195 | 189 | 195 | 189 | 4768610
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 70 | 70 | 71 | 70 | 70 | 60 | 71 | 80 | 70 | 100 | 100 | 120 | 110 | 111 | 120 | 120 | 80 | 50 |  | 80 | 125 | 120 | 130 | 131 | 80 | 80 | 2221464
| Dohazari Peaking | 47 | 47 | 47 | 47 | 17 | 17 | 17 | 16 | 8 | 16 | 17 | 0 | [5 empty] | 0 |  | 49 | 47 | 47 | 47 | 47 | 45 | 45 | 591257
12 | Hathazari peaking | 82 | 50 | 50 | 50 | 0 | [12 empty] | 8 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 706544
| Daudkandi bangla trak | 12 | 12 | 12 | 11 | 0 | [12 empty] | 0 |  | 158 | 155 | 157 | 180 | 105 | 32 | 0 | 773760
14 | Daudkandi Peaking 52MW | [17 empty] | 28 |  | 49 | 48 | 48 | 48 | 48 | 48 | 48 | 298672
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 170 | 170 | 150 | 150 | 150 | 150 | 150 | 150 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 140 | 170 | 170 | 0 | 0 | 80 | 130 | 3607238
18 | Summit Gazipur | 200 | 137 | 13 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 13 | 88 | 83 | 149 | 152 | 160 |  | 286 | 286 | 286 | 285 | 285 | 285 | 302 | 2857853
19 | Ashuganj 195MW Modular | 128 | 108 | 78 | 78 | 78 | 68 | 68 | 68 | 126 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 76 | 76 |  | 76 | 77 | 77 | 105 | 105 | 68 | 53 | 2458909
20 | Ghorasal ST: Unit-1,2 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 782000
21 | Ghorasal ST: Unit-3 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2921310
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4454100
24
25 | Ghorasal ST: Unit-7 | 80 | 138 | 200 | 200 | 160 | 160 | 160 | 200 | 305 | 310 | 309 | 0 |  | 50 | 80 | 123 | 173 | 170 |  | 170 | 170 | 165 | 165 | 165 | 163 | 165 | 3814136
26
28 | Ashuganj ST: Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 0 |  | 0 | 13 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2006858
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 0 |  | 0 | 75 | 100 | 120 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2028475
30 | Ashuganj ST: Unit- 5
32 | Ashuganj Engines TSK | 42 | 42 | 42 | 42 | 3 | 3 | 3 | 42 | 42 | 34 | 35 | 39 | 39 | 42 | 42 | 41 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 822888
33 | Ashuganj CCPP 225 MW | 182 | 182 | 180 | 181 | 182 | 160 | 183 | 181 | 197 | 190 | 193 | 204 | 183 | 198 | 196 | 158 | 182 | 183 |  | 183 | 183 | 183 | 183 | 181 | 136 | 151 | 4453000
34 | Ashuganj CCPP(South) | 279 | 250 | 250 | 250 | 0 | [9 empty] | 0 | 95 | 69 | 121 |  | 161 | 161 | 161 | 231 | 300 | 360 | 300 | 2908750
| Ashuganj CCPP(North) | 270 | 240 | 230 | 220 | 285 | 250 | 250 | 260 | 305 | 285 | 285 | 310 | 290 | 290 | 290 | 290 | 290 | 290 |  | 250 | 240 | 230 | 321 | 300 | 330 | 300 | 6976900
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 153 | 153 | 152 | 153 | 153 | 153 | 153 | 154 | 154 | 154 | 154 | 154 | 154 | 154 | 153 | 153 | 153 | 153 |  | 153 | 153 | 154 | 154 | 153 | 153 | 154 | 3460199
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 345 | 344 | 344 | 345 | 345 | 300 | 300 | 365 | 365 | 360 | 346 | 376 | 363 | 372 | 350 | 360 | 345 | 345 |  | 300 | 350 | 300 | 300 | 350 | 346 | 349 | 8425852
40 | Meghnaghat CCPP 450MW | 320 | 320 | 290 | 290 | 290 | 240 | 270 | 270 | 350 | 450 | 450 | 450 | 450 | 420 | 420 | 420 | 350 | 350 |  | 360 | 360 | 360 | 450 | 430 | 430 | 430 | 8590936
41 | Haripur Power CCPP 360MW | 303 | 281 | 281 | 281 | 281 | 232 | 262 | 355 | 345 | 346 | 343 | 301 | 302 | 291 | 292 | 284 | 281 | 280 |  | 260 | 292 | 291 | 292 | 293 | 293 | 294 | 7047000
42 | Mymensingh RPCL 210MW | 70 | 72 | 87 | 92 | 93 | 93 | 72 | 74 | 103 | 102 | 89 | 89 | 90 | 88 | 88 | 88 | 83 | 79 |  | 73 | 72 | 85 | 83 | 83 | 80 | 80 | 1944330
43 | Haripur NEPC 110MW | 13 | 0 | [10 empty] | 13 | 26 | 26 | 55 | 55 | 55 |  | 55 | 55 | 60 | 55 | 70 | 70 | 70 | 561600
44 | Fenchugonj CCPP-1 | 60 | 60 | 60 | 40 | 40 | 40 | 40 | 60 | 56 | 54 | 56 | 51 | 51 | 49 | 56 | 56 | 56 | 56 |  | 58 | 58 | 58 | 58 | 58 | 56 | 56 | 1231000
45 | Fenchugonj CCPP-2 | 75 | 75 | 75 | 75 | 75 | 66 | 66 | 66 | 66 | 63 | 66 | 74 | 74 | 74 | 74 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1717760
46 | Shajibazar 330 MW | 147 | 149 | 150 | 164 | 185 | 271 | 316 | 318 | 314 | 314 | 330 | 318 | 303 | 317 | 315 | 314 | 308 | 302 |  | 307 | 307 | 301 | 301 | 301 | 316 | 302 | 6197724
47 | Shahjibazar GT: Unit- 8, 9 | 59 | 52 | 42 | 50 | 52 | 50 | 53 | 64 | 64 | 62 | 61 | 60 | 44 | 60 | 60 | 47 | 61 | 50 |  | 64 | 43 | 41 | 49 | 64 | 66 | 58 | 1272000
48 | Shahjibazar 86MW | 86 | 60 | 40 | 20 | 5 | 5 | 5 | 5 | 5 | 20 | 20 | 84 | 84 | 86 | 86 | 84 | 60 | 40 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1333440
49 | Shahjibazar (EPL) 50MW | 49 | 50 | 20 | 1 | 1 | 1 | 1 | 1 | 1 | 20 | 20 | 45 | 45 | 45 | 47 | 48 | 48 | 20 |  | 20 | 46 | 49 | 50 | 50 | 50 | 50 | 756000
50 | Sylhet GT 150 MW | 96 | 78 | 77 | 77 | 79 | 78 | 78 | 77 | 80 | 80 | 80 | 100 | 130 | 130 | 126 | 108 | 78 | 78 |  | 96 | 97 | 96 | 118 | 118 | 117 | 118 | 2288250
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 45 | 45 | 43 | 43 | 5 | 5 | 6 | 6 | 42 | 41 | 40 | 41 | 41 | 41 | 41 | 41 | 44 | 22 |  | 45 | 46 | 45 | 46 | 45 | 44 | 45 | 807960
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 9 | 0 | [7 empty] | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 146520
54 | Hobiganj 11MW | 11 | 11 | 0 | [9 empty] | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 138432
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 22 | 4 | 4 | 5 | 5 | 5 | 22 | 22 | 39 | 47 | 49 | 50 | 49 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 902400
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 21 | 21 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 15 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 537840
57 | Summit Bibiana- 2 | 280 | 260 | 270 | 270 | 270 | 270 | 270 | 325 | 320 | 320 | 285 | 325 | 270 | 260 | 300 | 275 | 275 | 285 |  | 265 | 265 | 260 | 255 | 255 | 270 | 280 | 7316770
58 | Southern 55MW | 55 | 55 | 55 | 55 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 36 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 948860
59 | Sikalbaha (Energis) | 51 | 51 | 51 | 51 | 51 | 8 | 8 | 8 | 8 | 22 | 47 | 51 | 13 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 901440
60 | Barabkunda (Regent) | 18 | 18 | 18 | 18 | 19 | 0 |  |  | 18 | 19 | 19 | 15 | 18 | 17 | 18 | 18 | 16 | 18 |  | 18 | 18 | 16 | 16 | 16 | 16 | 19 | 371328
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 417888
62 | Tangail (Doreen) 22MW | [12 empty] | 22 | 22 | 0 | 22 | 22 | 22 |  | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 225252
63 | Tripura | 162 | 170 | 180 | 90 | 60 | 58 | 78 | 98 | 112 | 114 | 130 | 136 | 144 | 146 | 168 | 156 | 138 | 144 |  | 164 | 176 | 172 | 188 | 184 | 176 | 176 | 3408960
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 32 | 32 | 13 | 17 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 4 | 3 | 8 | 10 |  | 22 | 16 | 16 | 24 | 24 | 30 | 29 | 337440
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 0 |  |  |  | 10 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 348732
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 229140
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 22 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 693400
68 | Summit Comilla 25MW | 21 | 21 | 21 | 0 |  |  |  |  | 15 | 15 | 15 | 15 |  | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 452430
69 | Summit Ashulia | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 32 | 32 | 23 | 23 | 32 | 32 | 24 | 24 | 23 | 23 | 23 | 23 | 23 | 23 | 0 | 32 | 32 | 32 |  | 22 | 32 | 32 | 32 | 32 | 32 | 32 | 599220
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 594513
72 | Summit Rupganj | 33 | 33 | 16 | 16 | 29 | 29 | 29 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 717300
73 | Ghorashal (Regent)
76 | Siddhirganj (Desh) | [17 empty] | 0 |  | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 610560
77 | Siddhirganj (Dutch Bangla) | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 20 | 70 | 80 | 84 | 84 | 84 |  | 84 | 84 | 84 | 86 | 85 | 85 | 85 | 1119360
78 | Gazipur (RPCL) | 51 | 51 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 34 | 51 | 42 | 47 | 42 | 48 | 48 | 50 | 50 |  | 50 | 50 | 50 | 45 | 51 | 51 | 51 | 878916
79 | Kodda 150MW | 149 | 110 | 60 | 48 | 25 | 15 | 15 | 48 | 82 | 100 | 100 | 115 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 133 | 2625600
80 | Jamalpur 95MW | 56 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 41 | 72 | 82 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1218808
81 | Lakdhanvi 52 MW | [13 empty] | 0 | 4 | 8 | 8 | 8 |  | 8 | 12 | 17 | 25 | 25 | 25 | 16 | 151472
82 | Madanganj 102MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 48 | 65 | 73 | 70 | 70 |  | 75 | 85 | 98 | 100 | 98 | 97 | 97 | 1207248
83 | Pagla (DPA ) | 10 | 10 | 10 | 10 | 10 | 10 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 |  | 21 | 51 | 51 | 51 | 21 | 21 | 10 | 498050
84 | B.Baria (Aggreko) 85MW | 85 | 60 | 60 | 20 | 5 | 5 | 5 | 5 | 5 | 20 | 22 | 51 | 85 | 86 | 86 | 85 | 51 | 51 |  | 30 | 85 | 85 | 85 | 85 | 85 | 85 | 1207248
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 90 | 100 | 100 | 100 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1316847
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 200 | 200 | 200 |  | 200 | 250 | 200 | 305 | 250 | 250 | 200 | 5549440
87 | Meghnaghat (IEL) | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 50 | 97 | 98 | 98 | 75 | 60 |  | 85 | 100 | 100 | 100 | 100 | 100 | 100 | 1253760
88 | Ghorashal 78MW (MAX)
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 270000
91 | Juldah (Acorn) | 90 | 80 | 90 | 80 | 80 | 80 | 80 | 90 | 90 | 90 | 90 | 90 | 78 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 2010840
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 20 | 2 | 2 | 2 | 2 | 13 | 20 | 20 | 39 | 50 | 50 | 49 | 49 | 50 | 49 |  | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 865000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 40 | 6 | 6 | 6 | 6 | 6 | 6 | 38 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 20 | 20 | 890669
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 24 | 24 | 24 | 24 | 50 | 93 | 93 | 93 | 93 | 94 |  | 94 | 94 | 94 | 94 | 94 | 93 | 94 | 1264608
95 | Patenga 50MW | 45 | 45 | 44 | 44 | 45 | 8 | 8 | 6 | 6 | 16 | 29 | 36 | 39 | 39 | 44 | 38 | 40 | 44 |  | 44 | 44 | 44 | 44 | 45 | 44 | 44 | 850560
96 | Chittagong ECPV 108 MW | 97 | 97 | 97 | 90 | 51 | 12 | 12 | 12 | 14 | 91 | 96 | 98 | 98 | 97 | 97 | 97 | 97 | 97 |  | 98 | 97 | 97 | 90 | 90 | 90 | 91 | 1926720
97 | Katpotti 51 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 13 | 47 | 49 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 645792
98 | Bosila 108MW | 51 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 100 | 100 | 98 | 98 | 98 | 98 |  | 98 | 98 | 98 | 99 | 99 | 99 | 99 | 1276800
99 | Madanganj-55 MW | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 30 | 38 | 55 | 55 | 54 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1039035
100 | Northern 55 MW | 37 | 36 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 56 | 56 |  | 37 | 37 | 37 | 37 | 37 | 56 | 56 | 966269
101 | Kushiara 163 MW CCPP GT | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 163 | 163 | 163 | 163 | 100 | 100 |  | 100 | 163 | 163 | 163 | 163 | 163 | 163 | 3427874
102 | Sarishabari (Solar) | [5 empty] | 0.1 | 0.4 | 0.9 | 1.7 | 2 | 2.2 | 2.3 | 2.2 | 1.9 | 1.6 | 1 | 0.3 | [9 empty] | 16235
103 | Banco Energy 54MW | 54 | 54 | 54 | 54 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1011240
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | 98 | 26 | 0 | [16 empty] | 74 | 88 | 89 | 82 | 9 | 0 | 0 | 445052
106
112
113
114
115
116
117
118 | Eastern Zone Total | 6681 | 6079 | 5713 | 5403 | 4771 | 4417.1 | 4348.4 | 4742.9 | 5244.7 | 5759 | 5949.2 | 6006.3 | 6249.2 | 6816.9 | 6894.6 | 7052 | 6676.3 | 6651 | 0 | 7279 | 7759 | 7660 | 7947 | 7815 | 7776 | 7615
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 27 | 45 | 69 | 69 | 69 | 69 | 10 | 10 | 10 | 10 | 10 | 10 | 98 | 96 | 97 | 96 | 39 | 39 |  | 102 | 103 | 103 | 108 | 109 | 107 | 108 | 1391520
124 | Khulna (KPCL-2) | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 82 | 82 | 81 | 82 | 82 | 81 | 81 | 83 | 81 | 88 | 99 |  | 98 | 99 | 99 | 102 | 115 | 115 | 115 | 2160000
125
126 | Khulna (Aggreko) 55MW | [17 empty] | 0 |  | 12 | 53 | 53 | 53 | 53 | 53 | 33 | 271580
127 | Faridpur Peaking | [17 empty] | 20 |  | 48 | 48 | 48 | 42 | 43 | 47 | 47 | 336720
128 | Khulna CCPP 225MW | 180 | 160 | 160 | 160 | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 180 | 160 | 160 | 150 | 120 | 120 |  | 160 | 190 | 206 | 211 | 160 | 120 | 120 | 3646080
129
130
131
132
133
| Summit Barisal 110 MW | 80 | 110 | 110 | 110 | 110 | 110 | 90 | 64 | 64 | 64 | 64 | 64 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2365440
| Barisal GT: Unit-1, 2 |  |  | 10 | 10 | 12 | [21 empty] | 32651
136 | Bhola Aggreko 95MW | 50 | 95 | 95 | 95 | 95 | 41 | 42 | 41 | 61 | 71 | 96 | 95 | 96 | 96 | 96 | 98 | 61 | 61 |  | 61 | 95 | 95 | 95 | 95 | 96 | 96 | 1904024
137 | Bhola CCPP 194MW | [7 empty] | 85 | 82 | 86 | 128 | 129 | 125 | 130 | 129 | 123 | 128 | 122 |  | 128 | 120 | 120 | 120 | 121 | 122 | 138 | 2241057
| Bhola (Venture) 33MW | 34 | 34 | 34 | 33 | 29 | 7 | 3 | 5 | 10 | 14 | 9 | 9 | 9 | 10 | 18 | 19 | 26 | 25 |  | 34 | 35 | 35 | 35 | 38 | 36 | 35 | 529490
140 | Bangla Trak Noapara | [17 empty] | 0 |  | 10 | 83 | 98 | 100 | 100 | 100 | 70 | 482880
141 | Noapara (KZA) 40MW | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 24 | 33 | 24 | 24 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 727875
142 | Gopalganj Peaking | 44 | 44 | 44 | 44 | 39 | 39 | 39 | 7 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 33 | 35 |  | 50 | 50 | 50 | 61 | 52 | 52 | 49 | 704896
143 | Bheramara GT-1,2,3 | [17 empty] | 0 |  | 32 | 31 | 33 | 33 | 33 | 0 |  | 144700
144
145 |  | 473 | 473 | 473 | 473 | 473 | 473 | 472 | 473 | 472 | 472 | 478 | 479 | 478 | 478 | 478 | 479 | 479 | 479 |  | 479 | 478 | 478 | 479 | 479 | 478 | 479 | 11557090
146 | Bheramara 360 MW | 310 | 250 | 250 | 200 | 135 | 135 | 135 | 200 | 360 | 344 | 345 | 340 | 338 | 340 | 330 | 320 | 270 | 250 |  | 205 | 310 | 280 | 318 | 310 | 311 | 300 | 6901920
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 77 | 76 | 76 | 76 | 77 | 77 | 78 | 75 | 62 | 68 | 72 | 75 | 76 | 76 | 78 | 77 | 77 | 77 |  | 77 | 77 | 76 | 77 | 75 | 78 | 77 | 1826618
151 | Barapukuria Unit-3 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 250 | 262 | 273 | 260 | 260 | 259 | 259 | 6674300
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | [17 empty] | 0 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 243744
Sirajgonj Unit-1 225MW (Gas)
157 | Sirajgonj Unit-1 225MW (Oil)
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 165 | 165 | 165 | 170 | 170 | 140 | 160 | 160 | 160 | 180 | 170 | 190 | 175 | 180 | 175 | 175 | 165 | 165 |  | 150 | 170 | 165 | 223 | 170 | 170 | 170 | 4261318
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | [16 empty] | 0 | 18 |  | 49 | 49 | 49 | 41 | 41 | 41 | 41 | 257369
161 | Bogra (GBB) | 2 | 5 | 0 |  |  |  |  | 11 | 11 | 18 | 17 | 18 | 16 | 18 | 18 | 16 | 16 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 278160
162 | Bogra (EPL) | [8 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 140148
163 | Ullapara (Summit) | [5 empty] | 0 | 3 | 3 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 118350
164 | Amnura 50MW | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 25 | 33 | 33 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 645610
165 | Katakhali (Northern) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 25 | 35 | 35 | 35 | 35 | 35 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 511184
166 | Katakhali Peaking | [17 empty] | 17 |  | 37 | 37 | 39 | 47 | 44 | 44 | 44 | 242566
167 | Santahar Peaking | [19 empty] | 36 | 37 | 37 | 36 | 36 | 36 | 36 | 188529
168 | Rajlanka 52 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 25 | 25 | 8 | 8 | 8 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 442080
169 | Chapainawabganj-100 MW | 51 | 51 | 51 | 51 | 26 | 26 | 26 | 25 | 26 | 26 | 26 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 64 | 102 | 102 | 102 | 102 | 102 | 102 | 1179510
170
171
172 | Rangpur GT | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 90000
173 | Saidpur GT | [21 empty] | 0 | 18 | 18 | 18 | 18 | 57000
175
176
177
178 | Western Zone Total | 0 | 1933 | 1948 | 1977 | 1915 | 1799 | 1661 | 1694 | 1879 | 1911 | 1976 | 2027 | 2230 | 2224 | 2228 | 2196 | 2046 | 2092 | 0 | 2449 | 2796 | 2806 | 2928 | 2821 | 2821 | 2752 | 2704
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953