## Daily Gen
Hourly Generation & Demand
Date: | 2016-07-01
Time | Generation | Demand | Loadshed | Remarks
Hour | MW | MW | MW
1:00 | 8795 | 8795 | 0
2:00 | 8725 | 8725 | 0
3:00 | 8650 | 8650 | 0
4:00 | 8547 | 8547 | 0
5:00 | 7799 | 7799 | 0
6:00 | 7365 | 7365 | 0
7:00 | 7139 | 7139 | 0
8:00 | 6958 | 6958 | 0
9:00 | 6985 | 6985 | 0
10:00 | 7320 | 7320 | 0 | Day Peak
11:00 | 7184 | 7184 | 0
12:00 | 7155 | 7155 | 0
13:00 | 6866 | 6866 | 0
14:00 | 6742 | 6742 | 0
15:00 | 7164 | 7164 | 0
16:00 | 7004 | 7004 | 0
17:00 | 6744 | 6744 | 0
18:00 | 6900 | 6900 | 0
18:30 | 7091 | 7091 | 0
19:00 | 7659 | 7659 | 0
19:30 | 8489 | 8489 | 0
20:00 | 8541 | 8541 | 0
21:00 | 8588 | 8588 | 0 | Evening peak
22:00 | 8612 | 8612 | 0
23:00 | 8633 | 8633 | 0
24:00 | 8398 | 8398 | 0

## forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [7 empty] | 2016-07-02 | Saturday
|  | Date (day): | 2016-07-02 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8255 | MW |  |  | (b) At Evening Peak Hour : |  | 9435 | MW
Sl. No. | Name of the Power Stations |  | Fuel | Producer | Installed Capacity |  | Present Capacity | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
[8 empty] | On | 2016-07-01 | 2016-07-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Nos. of Unit X Capacity (MW) | MW | MW | MW | MW | MW | MW | MW | MW
1 | a) Ghorasal ST: Unit-1, 2 |  | Gas | PDB | 2*55 | 110 | 85 | 72 | 72 | 72 | 72
| b) Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 110 | 170 | 170 | 170
| c) Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120
| d) Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| e) Ghorasal ST: Unit-6 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | (18/07/2010) |  | Long term maint.
2 | Ghorashal 100MW(Aggreko) |  | Gas | QRPP | 128*0.85 | 100 | 100 | 99 | 95 | 95 | 100
3 | Ghorashal 45MW (Aggreko) |  | Gas | QRPP | 58*0.85 | 45 | 45 | 45 | 45 | 46 | 45
4 | Ghorashal 78.5MW (MAX) |  | Gas | QRPP | 4*21.5 | 78 | 78 | 65 | 70 | 44 | 70
5 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 86 | 74 | 94 |  | 22 | Engine problem
6 | Haripur GT: Unit-1, 2, 3 |  | Gas | PDB | 3*32 | 96 | 60 | 40 | 40 | 40 | 40 |  | 20 | #3 Under maint.
7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 411 | 417 | 413 | 412
8 | Haripur NEPC (HFO) |  | HFO | IPP | 8*15 | 110 | 110 | 68 | 110 | 110 | 110 |  |  | Engine problem
9 | Haripur Power CCPP |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 216 | 300 | 316 | 300 | 60 |  | Gas shortage
10 | Meghnaghat CCPP |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint.
11 | Meghnaghat (IEL) |  | HFO | RPP | 12*8.9 | 100 | 100 | 90 | 99 | 98 | 100
12 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 230 | 200 | 305 | 305
13 | Madanganj (Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 63 | 97 | 95 | 100
14 | Madanganj-55 MW |  | HFO | IPP | 5*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
15 | Keraniganj (Powerpac) |  | HFO | RPP | 8*13.45 | 100 | 100 | 93 | 100 | 93 | 93 |  | 7 | Engine problem
16 | Narshingdi (Doreen) |  | Gas | SIPP,REB | 8*2.90 | 22 | 22 | 12 | 10 | 19 | 22
17 | Siddhirgonj ST |  | Gas | PDB | 1*210 | 210 | 150 | 110 | 110 | 110 | 110 | 40 |  | Gas shortage
18 | Siddhirgonj GT: Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 37 | 97 | 125 | 85 | 113 |  | Gas shortage.
19 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 96 | 98 | 0 | 10 | 60 | 60 |  | 88 | Transformer problem
20 | Siddhirganj (Dutch Bangla) |  | HFO | RPP | 12*8.9 | 100 | 100 | 79 | 97 | 100 | 100 |  | 3 | Engine problem
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 0 | 10 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 80 | 97 | 85 |  | 22 | Engine problem
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 36 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Kodda Peaking |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 149
| Southern Power |  | HFO | RPP |  |  |  | 18 | 36 | 36 | 36 |  |  | On test
| CLCPC Keranigonj 108 MW |  | HFO | RPP |  |  |  | 0 | 0 | 0 | 0 |  |  | On test
25 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 6*3.67+7*8.73 | 80 | 80 | 47 | 56 | 55 | 56 |  | 24 | Engine problem
26 | Summit Power, Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
27 | Summit Power, Rupganj |  | Gas | SIPP,REB | 4*8.74 | 33 | 33 | 33 | 25 | 33 | 33
28 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 42 | 41 | 42 |  | 10 | Engine problem
29 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas Shortage
| Dhaka Area Total |  |  |  |  | 4664 | 4433 | 2722 | 3042 | 3265 | 3257 | 318 | 847
30 | a) Chittagong ST: Unit-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 120 | 100 | 80 |  | Gas shortage
| b) Chittagong ST: Unit-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
31 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 26 | 26 | 0 | 25
32 | Patenga 50MW (Barakatullah) |  | HFO | IPP | 8*6.984 | 50 | 50 | 35 | 51 | 47 | 50
33 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40, 3*50 | 230 | 230 | 85 | 120 | 40 | 120 |  | 50 | # 5 Under maint.
34 | Sikalbaha ST |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
35 | Sikalbaha Peaking GT |  | Gas | PDB | 1*150 | 150 | 150 | 120 | 120 | 135 | 120 | 30 |  | Gas shortage
36 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 43 | 43 | 34 | 34 | 34 | 34
37 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 76 | 0 | 80
38 | Dohazari-Kalaish Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 16 | 39 | 16 | 85
39 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 101 | 90 | 100 |  | 10 | Engine problem
40 | Barabkunda (Regent) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 20 | 21 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  |  | 16 | 32 | 5 | 32
41 | Chittagong ECPV 108 MW |  | HFO | IPP |  | 108 | 108 | 82 | 96 | 95 | 96
| Chittagong area Total |  |  |  |  | 1408 | 1328 | 734 | 936 | 722 | 982 | 170 | 100
42 | a) Ashuganj ST: Unit- 1 & 2 |  | Gas | APSCL | 2*64 | 128 | 97 | 0 | 0 | 0 | 0 |  | 97 | Under maint.
| b) Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 132 | 132 | 132 | 132
| c) Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 150 | 150 | 150 | 150
| d) Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 135 | 135 | 135 | 135
| e) Ashuganj : GT-2 |  | Gas | APSCL | 1*56 | 56 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
43 | a) Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 217 | 217 | 0 | 0 | 0 | 0 |  | 217 | 2016-08-04
| b) Ashuganj CCPP 450 MW |  | Gas | APSCL |  |  |  | 0 | 200 | 200 | 395 |  |  | On test
44 | Ashuganj Engines |  | Gas | APSCL | 14*3.968 | 53 | 45 | 18 | 18 | 18 | 18 | 27 |  | Gas shortage
45 | Ashuganj (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 52 | 50 | 52
46 | Ashuganj (Aggrekko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 97 | 42 | 95
47 | Ashuganj (United) |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 53 | 53 | 53
48 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.7+1*16 | 195 | 195 | 160 | 175 | 179 | 175 | 20 |  | Gas shortage
49 | Ashuganj (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 20 | 40 | 40 | 40 |  | 20 | Engine problem
50 | Brahmanbaria (Aggreko) |  | Gas | QRPP | 86*1.10 | 85 | 85 | 81 | 85 | 22 | 85
51 | Titas (Daudkandi) Peaking |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 45
52 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 | 73 |  | Gas shortage
53 | Feni (Doreen) |  | Gas | SIPP,PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16
54 | Feni, Mohipal (Doreen) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
** | Tripura |  |  | Imported Power |  | 100 | 100 | 68 | 98 | 60 | 100
55 | Jangalia (Summit) |  | Gas | SIPP,PDB | 4*8.73 | 33 | 33 | 30 | 30 | 30 | 30
56 | Lakdhanvi-52 MW |  | HFO | (IPP) |  | 52 | 52 | 43 | 34 | 52 | 52
57 | Summit Power, Comilla |  | Gas | SIPP,REB | 3*3.6+2*6.9 | 25 | 25 | 22 | 20 | 18 | 22
| Comilla Area Total |  |  |  |  | 1896 | 1789 | 1047 | 1484 | 1298 | 1696 | 120 | 374
58 | RPCL CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 137 | 153 | 154 | 150 | 49 |  | Gas shortage
59 | Tangail (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 13 | 14 | 16
| Mymensingh Area Total |  |  |  |  | 232 | 224 | 151 | 166 | 168 | 166 | 49 | 0
60 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 80 | 29 | 29 | 29 | 29 |  | 30 | GT-2 (10/06/2016) |  | 2016-11-06
61 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 62 | 76 | 76 | 76
| Shahjibazar 330 MW |  | Gas |  |  |  |  | 0 | 0 | 0 | 0 |  |  | on test
62 | Fenchugonj (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 15 | 50 | 48 | 50
63 | Fenchuganj (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 43 | 43 | 44
64 | Hobiganj (Confidence-EP) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 11
65 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 53 | 40 | 68 | 66 | 66
66 | Shahjibazar (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 50 | 84 | 84 | 84
67 | Shahjibazar (Energyprima) |  | Gas | RPP | 27*2.0 | 50 | 50 | 42 | 44 | 44 | 44 |  |  | Engine problem
68 | Sylhet 150 MW GT |  | Gas | PDB | 1*142 | 142 | 142 | 100 | 42 | 107 | 120 |  |  | Gas shortage
69 | Sylhet 20 MW GT |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 20 | Engine problem
70 | Sylhet (Energyprima) |  | Gas | RPP | 27*2 | 50 | 50 | 40 | 42 | 12 | 43
71 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 25 | 24 | 24
72 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 351 | 300 | 239 | 341
73 | Sylhet (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1101 | 1066 | 836 | 795 | 794 | 952 | 66 | 50
74 | Bheramara GT: Unit- 1,2,3 |  | HSD | PDB | 3X20 | 60 | 46 | 0 | 31 | 0 | 46
75 | Bheramara (Quantum) |  | HSD | RPP | 12*8.5+2*6+2*13 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | contract date experid 31/12/2013
** | Bheramara Interconnector(HVDC ) |  |  | Imported Power |  | 500 | 500 | 450 | 440 | 444 | 449
76 | a) Khulna ST 110MW |  | HFO | PDB | 1*110 | 110 | 55 | 0 | 0 | 0 | 0 |  | 55 | 2014-04-11
| b) Khulna ST 60 MW |  | HFO | PDB | 1*60 |  |  | 0 | 0 | 0 | 0 |  |  | Plant retired in FY 2013-2014
77 | Khulna (KPCL-1) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 108 | 110 | 110
78 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 115 | 115 | 115 | 115
79 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 18 | 35 | 40 | 40
80 | Khulna 150MW GT |  | HSD | NWZPGCL | 1*150 | 158 | 158 | 182 | 182 | 163 | 220
81 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 68 | 80 | 80
82 | Noapara (Quantam) |  | HFO | RPP | 5*9.9+6*9.5+2*9.2 | 101 | 101 | 0 | 0 | 0 | 0 |  | 101 | Long term maint.
83 | Noapara (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 32 | 40 | 40
84 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 13 | 45 | 47
| Khulna Area Total |  |  |  |  | 1517 | 1448 | 807 | 1024 | 1037 | 1147 | 0 | 261
85 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 100 | 111 | 110 | 110
86 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 22 | 0 | 22
87 | Bhola (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 10 | 17 | 7 | 18 |  | 15 | Engine problem
88 | Bhola CCPP GT-1,2,ST |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 96 | 96 | 95 | 98 |  | Gas shortage
| Barisal Area Total |  |  |  |  | 377 | 367 | 197 | 246 | 213 | 245 | 0 | 15
89 | a) Baghabari GT |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 53 | 67 | 65
| b) Baghabari GT |  | Gas | PDB | 1*100 | 100 | 100 | 98 | 82 | 80 | 100
90 | Baghabari Peaking |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 47 | 0 | 47
91 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 50 | 0 | 57
92 | Amnura |  | HFO | QRPP | 7*7.79 | 50 | 50 | 42 | 50 | 50 | 50
93 | Katakhali (Northern) |  | HFO | QRPP | 6*8.92 | 50 | 50 | 25 | 50 | 45 | 50
94 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 45
95 | Sirajganj CCPP |  | Gas | NWPGCL | 1*150+1*75 | 210 | 210 | 218 | 180 | 222 | 222
96 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 43
97 | Bogra (GBB) |  | Gas | RPP | 6*4 | 20 | 22 | 21 | 22 | 22 | 22
98 | Bogra (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 20 | 11 | 14 | 14 | 15 |  | 6 | Engine problem
99 | Ullapara (Summit) |  | Gas | SIPP,REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
100 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
| Rajshahi Area Total |  |  |  |  | 807 | 809 | 484 | 683 | 563 | 779 | 0 | 6
101 | a) Barapukuria ST: Unit-1 |  | Coal | PDB | 1*125 | 125 | 100 | 89 | 89 | 89 | 88
| b) Barapukuria ST: Unit-2 |  | Coal | PDB | 1*125 | 125 | 100 | 88 | 85 | 86 | 85
102 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | under maint.
103 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 0 | 18
104 | Thakurgaon (RZ) |  | HSD | RPP | 20*1.5+21*1.1 | 47 | 40 | 0 | 20 | 20 | 20 |  | 20 | Engine problem
| Rangpur Area Total |  |  |  |  | 337 | 280 | 177 | 212 | 195 | 211 | 0 | 40
| Total |  |  |  |  | 12339 | 11744 | 7155 | 8588 | 8255 | 9435 | 723 | 1693
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6719.2682 | 8065 | 7752.2793 | 8169
A. |  | 2016-07-01 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 8795 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6744 | MW at | 17:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 8588 | MW
3 | Day peak Generation : |  |  | 7320 | MW at | 10:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 8065 | MW
4 | Evening peak Generation : |  |  | 8588 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  |  | 182.5605 | MKWHr |  |  | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 111.5417 | MKWHr |  | By Oil: | 52.294 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 3.8439 | MKWHr |  | By Hydro: | 2.1627 | MKWHr | Area | Demand | Supply | Loadshed | (Duration) |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Gas: | 723 | For Oil: | 0 | MW | Dhaka | 3057 | 3057 | 0
|  |  | For Water Shortage: |  |  | 0 | MW | Chittagong | 886 | 886 | 0 |  |  | 18:00 |  | 0
|  |  | For Plants S/D or M/C prob: |  |  | 1693 | MW | Khulna | 986 | 986 | 0 |  |  | 18:30 |  | 0
7 | Total Gas Supplied : |  | 1085.09 | MMCFD |  |  |  | Rajshahi | 920 | 920 | 0 |  |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 70221050.471 | ii) Oil : | Taka | 539536004.494 | Comilla | 747 | 747 | 0 |  |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 14960559.992 | Total | Taka | 624717614.957 | Mymensingh | 462 | 462 | 0 |  |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.8675 | MKWHr. | Sylhet | 361 | 361 | 0 |  |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -620 | MW at | 21:00 | hrs | Barisal | 178 | 178 | 0 |  |  | 22:00 |  | 0
| iii) Maximum : |  |  | -260 | MW at | 12:00 | hrs | Rangpur | 468 | 468 | 0 |  |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 8065 | 8065 | 0
B. |  | 2016-07-02 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 8700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 9435 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7700 | MW
4 | Reserve (Generation end) |  |  |  | 735 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 182 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6356 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.8567 | MKWHr. | ii) During Peak demand: |  | 440 | MW at | 21:00 | hrs. | iii)Maximum: | 451 | 3:00
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.8614 | MKWHr.
*Cost for HVDC & Tripura energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.74 |  |  |  | (b) Today: | 87.58 | (c) Rule Curve: |  | 84.16
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2016-07-02
Till now the maximum generation is : - |  |  | 9036 MW | 21:00 | Hrs on | 2016-06-30
The Summary of Yesterday's |  | 2016-07-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7155 | MW Hour : | 10:00 | Min. Gen. at | 7:00 | 6356 | MW
Evening Peak Generation : |  | 8588 | MW Hour : | 21:00 | Max Generation : |  | 9435 | MW
E.P. Demand (at gen end) : |  | 8588 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 8700 | MW
Maximum Generation : |  | 8795 | MW Hour : | 1:00 | Shortage(Generation end) : |  | 735 | MW
Total Gen. (MKWH) : |  | 182.5605 | System L/ Factor : | 86.49% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -260 | MW at | 12:00 | Energy | 7.8675 | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2016-07-02
Actual : | 87.58 | Ft.(MSL) , | Rule curve : | 84.16 | Ft.( MSL )
Gas Consumed : | Total | 1085.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 70221050.471
|  | Coal : | 14960559.992 | Oil : | 539536004.494 | Total : | 624717614.957
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | - | 0:00 | 3260 |  |  | - | -
Chittagong Area | - | 0:00 | 911 |  |  | - | -
Khulna Area | - | 0:00 | 925 |  |  | - | -
Rajshahi Area | - | 0:00 | 892 |  |  | - | -
Comilla Area | - | 0:00 | 670 |  |  | - | -
Mymensingh Area | - | 0:00 | 509 |  |  | - | -
Sylhet Area | - | 0:00 | 328 |  |  | - | -
Barisal Area | - | 0:00 | 178 |  |  | - | -
Rangpur Area | - | 0:00 | 496 |  |  | - | -
Total | 0 |  | 8169 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Ghorasal ST: Unit-6 (18/07/2010) |  | 9) Sikalbaha 60MW (23/11/15)
| Nil |  |  | 2) Ashuganj ST: Unit-1 (12/09/2015) |  | 10) Ashuganj ST: Unit-2 (12/6/16)
|  |  |  | 3) Ashuganj CCPP 225 MW |  | 11) Ashuganj GT: Unit-2 (29/6/16)
4) Khulna ST 110 MW (04/11/2014)
5) Kaptai Hydro: Unit-5,
6) Haripur GT-3
7 Bhola GT-2
8) Meghnaghat 450 MW(24/04/2016)
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
| Description |  |  | Comments on Power Interruption
a) Barisal (N) 230/132 kV T2 transformer was switched on at 10:21.
b) Sylhet 150 MW tripped at 14:15 due to gas booster problem and was synchronized at 16:48.
c) Barapukuria Unit-1 tripped at 16:10 due to tripping of coal mill and was synchronized at 19:57.
d) Haripur 230/132 kV T01 transformer tripped at 15:32 from 132 kV side showing oil temperature high
and was switched on at 16:55.
e) After maintenance Ashuganj 450 MW GT was synchronized at 17:56.
f) Hasnabad-Shyampur 132 kV Ckt was under shut down from 06:02 to 10:34 for tower painting work.
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2016-07-01 | [6 empty] | Page -2
[5 empty] | Present | Peak Hour | Energy
| Name of Power Station |  | Unit | Producer | Generation | Generation | Generated |  | Remarks
Capacity
[5 empty] | MW | MW | KWHr
1a | Ghorasal ST: Unit-1, 2 |  | 2*55 | PDB | 85 | 32 | 1632000
40
1b | Ghorasal ST: Unit-3 |  | 1*210 | PDB | 170 | 170 | 3310650
1c | Ghorasal ST: Unit-4 |  | 1*210 | PDB | 180 | 120 | 2767905
1d | Ghorasal ST: Unit-5 |  | 1*210 | PDB | 190 | 170 | 3953250
1e | Ghorasal ST: Unit-6 |  | 1*210 | PDB | 190 | 0 |  | Long term maint.
2 | Ghorashal 100MW(Agreko) |  | 128*0.85 | QRPP | 100 | 95 | 2325320
3 | Ghorashal 45MW(Agreko) |  | 58*0.85 | QRPP | 45 | 45 | 1035220
4 | Ghorashal 78.5 MW (MAX) |  | 4*21.5 | QRPP | 78 | 70 | 1321500 | Engine problem
5 | Ghorashal (Regent) |  | 34*3.35 | IPP | 108 | 86 | 2205909 | Engine problem
6 |  |  | 1*32 | PDB | 20 | 20 | 973900
| Haripur GT: Unit-1, 2, 3 |  | 1*32 | PDB | 20 | 20
|  |  | 1*32 | PDB | 20 | 0 |  | Under maint.
7 | Haripur EGCB 412 MW CCPP |  | 1*273+1*139 | EGCB | 412 | 417 | 10007868
8 | Haripur NEPC(HFO) |  | 8*15 | IPP | 110 | 110 | 2076000
9 | Haripur Power CCPP |  | 1*235+1*125 | IPP | 360 | 300 | 4460000 | Gas Shortage
10 | Meghnaghat CCPP |  | 2*150+1*150 | IPP | 450 | 0 | 0 | Under maint.
11 | Meghnaghat (IEL) |  | 12*8.9 | RPP | 100 | 99 | 2271360
12 | Meghnaghat CCPP(Summit) |  | 2*110+1*110 | IPP | 305 | 200 | 5358080 | Low demand
13 | Madanganj (Summit) |  | 6*17 | QRPP | 100 | 97 | 2096856
14 | Madanganj-55 MW |  | 5*17.08+1*11.3 | IPP | 55 | 55 | 1260000
15 | Keraniganj (Powerpac) |  | 8*13.45 | RPP | 100 | 100 | 2058948
16 | Narsingdi (Doreen) |  | 8 * 2.9 | SIPP, REB | 22 | 10 | 343908
17 | Siddhirgonj ST |  | 1*210 | PDB | 150 | 110 | 2652300 | Gas Shortage
18 | Siddhirgonj GT : Unit-1 & 2 |  | 2*105 | EGCB | 210 | 97 | 1532000 | Gas shortage
19 | Siddhirgonj (Desh) |  | 96*1.2 | QRPP | 98 | 10 | 770880 | Low demand
20 | Siddhirgonj (Dutch Bangla) |  | 12*8.9 | RPP | 100 | 97 | 1988960 | Engine problem
21 | Pagla (DPA) |  | 100*0.5 | QRPP | 50 | 10 | 517000 | Low demand
22 | Gagnagar (Orion) |  | 12*8.924 | IPP | 102 | 80 | 1933632 | Engine problem
23 | Katpotti 52 MW |  |  | RPP | 51 | 40 | 883200 | Engine problem
24 | Kodda Peaking |  | 9*17.06 | BPDB-RPCL | 149 | 150 | 3481920
| Southern Power |  |  | RPP |  | 36 | 542383 | On test
| CLCPC Keranigonj 108 MW |  |  |  |  | 0 | 0 | On test
25 | Summit Power,(Madhabdi+Ashulia) |  | 6*3.67+7*8.73 | SIPP, REB | 80 | 56 | 1203740 | Engine problem
26 | Summit Power, Maona |  | 4*8.73 | SIPP, REB | 33 | 33 | 758300
27 | Summit Power, Rupganj |  | 4*8.74 | SIPP, REB | 33 | 25 | 752400
28 | Gazipur (RPCL) |  | 6*8.9 | IPP | 52 | 42 | 990720 | Engine problem
29 | Tongi GT |  | 1*105 | PDB | 105 | 0 | 0 | Gas shortage
| Dhaka Area Total |  |  |  | 4433 | 3042 | 67466109
30 | a) Chitagong ST:Unit-1 |  | 1*210 | PDB | 180 | 100 | 2100000 | Gas shortage
| b) Chitagong ST:Unit-2 |  | 1*210 | PDB | 180 | 120 | 2600000 | Gas shortage
31 | Raozan 25 MW (RPCL) |  | 3*8.9 | IPP | 25 | 26 | 469440
32 | Patenga 50 MW(Barakatulla) |  | 8*6.89 | IPP | 50 | 51 | 1106400
33 | Chittagong ECPV 108 MW |  |  | IPP | 108 | 96 | 2184000 | Engine problem
34 |  |  | 1*40 | PDB | 40 | 40 | 1995000
|  |  | 1*40 | PDB | 40 | 40
| Karnafuli Hydro Power Station |  | 1*50 | PDB | 50 | 10
|  |  | 1*50 | PDB | 50 |  | 167700
|  |  | 1*50 | PDB | 50 | 30
35 | Shikalbaha ST |  | 1*60 | PDB | 40 | 0 | 0 | Under maint.
36 | Shikalbaha peaking GT |  | 1*150 | PDB | 150 | 120 | 2591509 | Gas shortage
37 | Hathazari peaking |  | 11*8.9 | PDB | 98 | 76 | 687288
38 | Dohazari-Kalaish peaking |  | 6*17 | PDB | 102 | 39 | 780526
39 | Juldah (Acorn) |  | 8*13.45 | QRPP | 100 | 101 | 2050920
40 | Shikalbaha (Energis) |  |  | RPP | 43 | 34 | 647520 | Engine problem
41 | Barabkunda (regent) |  | 8*2.90 | SIPP, PDB | 22 | 21 | 479850
* | Malancha, Ctg EPZ(United) |  |  |  |  | 32 | 785760
| Chittagong Area Total |  |  |  | 1328 | 936 | 18645913
42 | a) Ashuganj ST: Unit- 1 & 2 |  | 1*64 | APSCL | 97 | 0 | 0 | Under maint.
|  |  | 1*64 | APSCL |  | 0
| b) Ashuganj ST: Unit- 3 |  | 1*150 | APSCL | 135 | 132 | 3143748
| c) Ashuganj ST: Unit- 4 |  | 1*150 | APSCL | 129 | 150 | 3532515
| d) Ashuganj ST: Unit- 5 |  | 1*150 | APSCL | 134 | 135 | 3225796
| Ashuganj : GT-2 |  | 1*56 | APSCL | 40 | 0 | 0
43 | a) Ashuganj CCPP 225 MW |  | 1*142+1*75 | APSCL | 217 | 0 | 5432000 | Under maint.
| b) Ashuganj CCPP 450 MW |  |  | APSCL | 0 | 200 | 0 | On test
44 | Ashuganj-Engines |  | 14*3.968 | APSCL | 45 | 18 | 421272 | Engine problem
45 | Ashugonj (Precision) |  | 15*4 | RPP | 55 | 52 | 1156320
46 | Ashuganj (Aggrekko) |  | 82*1.1 | RPP | 95 | 97 | 1402190
47 | Ashuganj (United) |  | 14*4 | RPP | 53 | 53 | 720000
48 | Ashuganj Modular 200 MW |  | 20*9.7+1*16 | IPP | 195 | 175 | 3897454 | Gas Shortage
49 | Ashuganj (Midland) |  | 6*9.34 | IPP | 51 | 40 | 765070 | Engine problem
50 | Brahmanbaria (Aggreko) |  | 72*1.1 | QRPP | 85 | 85 | 1647000
51 | Titas (Daudkandi) Peaking |  | 6 * 8.92 | PDB | 52 | 48 | 402704
52 | Chandpur CCPP |  | 1*106+1*57 | PDB | 163 | 90 | 2098990 | ST under maint.
53 | Feni(Doreen) |  | 8 *2.94 | SIPP, PDB | 22 | 16 | 382716
54 | Feni Mohipal (Doreen) |  | 4*2.9 | SIPP, REB | 11 | 11 | 231120
** | Tripura |  |  |  | 100 | 98 | 1861440
55 | Jangalia (Summit) |  | 4*8.73 | SIPP, PDB | 33 | 30 | 736500
56 | Lakdamavi-52 MW |  |  | IPP | 52 | 34 | 548850
57 | Summit Power,Comilla |  | 3*3.67+2*6.9 | SIPP, REB | 25 | 20 | 527640 | Engine problem
| Comilla Area Total |  |  |  | 1789 | 1484 | 32133325
58 | RPCL CCPP |  | 4*35+1*70 | IPP | 202 | 153 | 3470000 | Gas Shortage
59 | Tangail (Doreen) |  | 8 *2.9 | SIPP,PDB | 22 | 13 | 275508 | Engine problem
| Mymensingh Area Total |  |  |  | 224 | 166 | 3745508
60 | Fenchugonj CCPP-1 |  | 2*32+1*33 | PDB | 80 | 29 | 652000
61 | Fenchugonj CCPP-2 |  | 2*35+1*35 | PDB | 90 | 76 | 1566760
| Shahjibazar CCPP 330 MW |  |  |  |  | 0 |  | On test
62 | Fenchugonj RPP (51 MW) |  | 2.9*19 | RPP | 51 | 50 | 873600
63 | Fenchuganj (Energyprima) |  | 12*3.3+5*2 | RPP | 44 | 43 | 789000
64 | Hobiganj (Confidence-EP) |  | 4*2.9 | SIPP, REB | 11 | 10 | 226272
65 | Shahjibazar GT: Unit-8,9 |  | 32*2.9 | PDB | 66 | 40 | 1102000
66 | Shahjibazar (Shahjibazar) |  | 32*2.9 | RPP | 86 | 84 | 1437680
67 | Shahjibazar (Energyprima) |  | 27*2.0 | RPP | 50 | 44 | 734400 | Engine problem
68 | Sylhet 150 MW GT |  | 1*142 | PDB | 142 | 42 | 1649070
69 | Sylhet 20 MW GT |  | 1*20 | PDB | 20 | 0 | 0 | Engine problem
70 | Sylhet (Energyprima) |  | 27 * 2.0 | RPP | 50 | 42 | 739420 | Engine problem
71 | Shahjahanulla 25MW |  | 3 * 9.34 | CIPP,REB | 25 | 25 | 563688
72 | Summit Bibiana-2 |  | 1*222+1*119 | IPP | 341 | 300 | 6939600
73 | Sylhet (Desh) |  | 6*1.95 | RPP | 10 | 10 | 237600
| Sylhet Area Total |  |  |  | 1066 | 795 | 17511090
|  |  | 1*20 | PDB | 16 | 0 | 800000
74 | Bheramara GT: Unit-1,2,3 |  | 1*20 | PDB | 14 | 15
|  |  | 1*20 | PDB | 16 | 16
75 | Bheramara (Quantum) |  | 12*8.5+2*6+2*13 | RPP | 105 | 0 | 0 | All Engine problem, Long term maint
** | Bheramara Interconnector(HVDC) |  |  | Imported Power | 500 | 440 | 10856727
76 | a) Khulna ST 110 MW |  | 1*110 | PDB | 55 | 0 | 0 | Under maint
| b) Khulna ST 60 MW |  | 1*60 | PDB |  | 0 | 0 | Plant Retired in FY 2013-2014
77 | Khulna (KPCL-1) |  | 19*6.5 | IPP | 110 | 108 | 1122240
78 | Khulna (KPCL-2) |  | 7*17 | QRPP | 115 | 115 | 2000640
79 | Faridpur Peaking |  | 8*6.89 | PDB | 54 | 35 | 589
80 | Khulna 150 MW GT |  | 1*150 | NWZPGCL | 158 | 182 | 4620480
81 | Gopalganj Peaking |  | 16*6.98 | PDB | 109 | 68 | 329000
82 | Noapara (Quantam) |  | 9.9*5+9.5*6+9.2*2 | RPP | 101 | 0 | 0 | All Engine problem, Long term maint
83 | Noapara (Khanjahan Ali) |  | 5*8.5 | QRPP | 40 | 32 | 565875
84 | Khulna (Aggreko) 55MW |  | 71*0.85 | QRPP | 55 | 13 | 222930 | Low demand
| Khulna Area Total |  |  |  | 1448 | 1024 | 20518481
85 | Summit Barisal 110MW |  | 7*17.076 | IPP | 110 | 111 | 2608320
86 | Barisal GT: Unit-1,2 |  | 1*20 | PDB | 16 | 12 | 245519
|  |  | 1*20 | PDB | 14 | 10
87 | Bhola (Venture) |  | 1*34.5 | RPP | 33 | 17 | 289195 | Engine problem
88 | Bhola CCPP GT-1,2,ST |  | 2*63+1*68 | PDB | 194 | 96 | 2177466 | Gas shortage
| Barisal Area Total |  |  |  | 367 | 246 | 5320500
89 | a) Baghabari GT |  | 1*71 | PDB | 71 | 53 | 1060000
| b) Baghabari GT |  | 1*100 | PDB | 100 | 82 | 2163000
90 | Baghabari Peaking |  | 6*8.9 | PDB | 52 | 47 | 374920
91 | Bera Peaking |  | 9*8.29 | PDB | 71 | 50 | 416402
92 | Amnura |  | 7*7.79 | QRPP | 50 | 50 | 919820
93 | Katakhali (Northern) |  | 6*8.92 | QRPP | 50 | 50 | 768168
94 | Katakhali Peaking |  | 6*8.7 | PDB | 50 | 44 | 430580
95 | Sirajganj CCPP |  | 1*50+1*75 | NWPGCL | 210 | 180 | 4998627 | Low demand
96 | Santahar Peaking |  | 6*8.7 | PDB | 50 | 28 | 326141
97 | Bogra (GBB) |  | 6*4 | RPP | 22 | 22 | 510290
98 | Bogra (Energyprima) |  | 5*3.3+5*2 | RPP | 20 | 14 | 330444 | Engine problem
99 | Ullapara (Summit) |  | 4 *2.90 | SIPP, REB | 11 | 11 | 249410
100 | Rajlanka 52 MW |  | 6*8.92 | IPP | 52 | 52 | 584160
| Rajshahi Area Total |  |  |  | 809 | 683 | 13131962
101 | a) Barapukuria ST: Unit-1 |  | 1*125 | PDB | 100 | 89 | 1746327
| b) Barapukuria ST: Unit-2 |  | 1*125 | PDB | 100 | 85 | 2097599
102 | Rangpur GT |  | 1*20 | PDB | 20 | 0 | 0 | Under maint.
103 | Saidpur GT |  | 1*20 | PDB | 20 | 18 | 145000
104 | Thakurgaon (RZ) |  | 20*1.5+21*1.1 | RPP | 40 | 20 | 98680 | Engine problem
| Rangpur Area Total |  |  |  | 280 | 212 | 4087606
| Total |  |  |  | 11744 | 8588 | 182560494
| Eastern Grid Total |  |  |  | 8488 | 6423 | 139501945
| Western Grid Total |  |  |  | 2600 | 2165 | 43058549
| National Grid Total |  |  |  | 11088 | 8588 | 182560494
*Data collected from respective power station over telephone.

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2016-07-01 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 5513 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2552 | MW
i) Dhaka area |  |  | 3057 | MW | i) Khulna area |  |  | 986 | MW
ii) Chittagong area |  |  | 886 | MW | ii) Rajshahi area |  |  | 920 | MW
iii) Comilla area |  |  | 747 | MW | iii) Barisal area |  |  | 178 | MW
iv) Mymensingh area |  |  | 462 | MW | iv) Rangpur area |  |  | 468 | MW
v) Sylhet area |  |  | 361 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 8065 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 100 | Kishorganj | 55 | 1000 | Noapara | 52 | 100
Munsiganj | 106 | 2100 | Netrokona | 50 | 1900 | Jessore | 120 | 2100
Megnaghat | 50 | 400 | Jamalpur | 71 | 700 | Jhenida | 70 | 100
Shyampur | 150 | 400 | Sherpur | 46 | 1500 | Bottail | 92 | 300
Bhulta | 138 | 100 | Srimongal | 31 | 1930 | G.K Project | 44 | 2100
Madanganj | 47 | 300 | Shahjibazar | 64 | 1930 | Faridpur | 114 | 2100
Shitalakhya | 90 | 100 | Fenchuganj | 39 | 2000 | Madaripur | 100 | 1930
Rahim steel | 8 | 700 | Khulawara | 37 | 1900 | Gopalganj | 52 | 2000
Matuail | 64 | 400 | Sylhet | 146 | 2100 | Bagerhat | 64 | 100
Ghorasal | 92 | 2100 | Chatak | 48 | 2100 | Mongla | 23 | 2000
Narsingdi | 82 | 300 | Comilla (S) | 96 | 2100 | Satkhira | 73 | 2000
Haripur (SBU) | 69 | 2100 | Comilla(N) | 140 | 2200 | Gallamari | 44 | 100
Ullon | 85 | 100 | Chandpur | 84 | 2000 | Magura | 35 | 2200
Hasnabad | 137 | 100 | Feni | 103 | 2000 | Chuadanga | 47 | 1930
Magbazar | 111 | 2200 | Chowmuhani | 168 | 1900 | Barisal | 96 | 2000
Maniknagar | 82 | 100 | Ashuganj | 58 | 2300 | Patuakhali | 51 | 1930
Bangabhaban | 20 | 1200 | Daudkandi | 70 | 1930 | Bhandaria | 34 | 2100
Narinda | 82 | 2200 | B.Baria | 87 | 2100 | Ishurdi | 46 | 2100
Dhanmondi | 120 | 1900 | Madanhat | 54 | 2200 | Natore | 86 | 2100
Lalbag | 62 | 1100 | Hathazari | 97 | 2100 | Bogra | 207 | 200
Madartek | 42 | 2200 | Khulshi | 176 | 100 | Noagaon | 95 | 2100
Mirpur | 90 | 1200 | Halishahar | 120 | 2000 | Rajshahi | 118 | 2000
Kalyanpur | 111 | 2300 | Baraulia | 109 | 600 | C.Nawabganj | 56 | 2100
Gulshan | 107 | 1930 | Sikalbaha | 32 | 300 | Amnura | 31 | 300
Uttara | 97 | 2200 | Dohazari | 76 | 100 | Pabna | 89 | 200
Kamrangirchar | 72 | 2300 | Cox'sbazar | 53 | 1900 | Shahjadpur | 69 | 2100
Savar | 102 | 2100 | Chandraghona | 26 | 1830 | Serajganj | 64 | 2100
Bhasantec | 108 | 2200 | Kaptai | 4 | 2000 | Niyamatpur | 42 | 2100
Agargaon | 49 | 1930 | A. Khaer Stl. | 12 | 200 | Joypurhat | 27 | 2100
Satmosjid | 66 | 100 | Bakulia | 100 | 100 | Rangpur | 93 | 300
Tongi | 97 | 2100 | Julda | 19 | 100 | Lalmonirhat | 68 | 1930
Kabirpur | 165 | 900 | TK chemical | 8 | 400 | Saidpur | 70 | 100
Basundhara | 107 | 2000 | Modern Steel | 17 | 200 | Purbasadipur | 68 | 500
Manikganj | 80 | 2100 | Shahmirpur | 24 | 300 | Thakurgaon | 60 | 2100
Joydevpur | 251 | 900 | Abul Khair 230 | 170 | 1400 | Palashbari | 71 | 300
New Tongi | 111 | 1200 | BSRM | 76 | 1100 | Barapukuria | 35 | 2000
Tangail | 129 | 2200 | Goalpara | 32 | 100 | Panchagar | 29 | 2000
Mymensing | 160 | 2100 | Central s/s | 84 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## L.curve
Date | 2016-07-01 | [8 empty] | QF-LDC-11
TIME | E-W INT. | EAST GRID | WEST GRID | TOTAL |  | Demand | Hour
0:00 | -510 | 6349 | 2187 | 8536 | -510 | 8536 | 0:00 | DAILY LOAD CURVE | 2016-07-01
0:30 | -485 | 6427 | 2238.5 | 8665.5 | -460 | 8665.5 | 1:00
1:00 | -460 | 6505 | 2290 | 8795 | -480 | 8795 | 2:00
1:30 | -470 | 6495.5 | 2264.5 | 8760 | -550 | 8760 | 3:00
2:00 | -480 | 6486 | 2239 | 8725 | -540 | 8725 | 4:00
2:30 | -515 | 6470 | 2217.5 | 8687.5 | -590 | 8687.5 | 5:00
3:00 | -550 | 6454 | 2196 | 8650 | -590 | 8650 | 6:00
3:30 | -545 | 6435.5 | 2163 | 8598.5 | -540 | 8598.5 | 7:00
4:00 | -540 | 6417 | 2130 | 8547 | -540 | 8547 | 8:00
4:30 | -565 | 6224 | 1949 | 8173 | -500 | 8173 | 9:00
5:00 | -590 | 6031 | 1768 | 7799 | -440 | 7799 | 10:00
5:30 | -590 | 5894.5 | 1687.5 | 7582 | -380 | 7582 | 11:00
6:00 | -590 | 5758 | 1607 | 7365 | -260 | 7365 | 12:00
6:30 | -565 | 5727 | 1525 | 7252 | -340 | 7252 | 13:00
7:00 | -540 | 5696 | 1443 | 7139 | -360 | 7139 | 14:00 |  |  |  | 8795 | 1:00
7:30 | -540 | 5621 | 1427.5 | 7048.5 | -320 | 7048.5 | 15:00 |  |  |  | 7320 | 10:00
8:00 | -540 | 5546 | 1412 | 6958 | -264 | 6958 | 16:00
8:30 | -520 | 5575.5 | 1396 | 6971.5 | -310 | 6971.5 | 17:00
9:00 | -500 | 5605 | 1380 | 6985 | -320 | 6985 | 18:00
9:30 | -470 | 5714.5 | 1438 | 7152.5 | -380 | 7152.5 | 18:30
10:00 | -440 | 5824 | 1496 | 7320 | -460 | 7320 | 19:00
10:30 | -410 | 5721 | 1531 | 7252 | -460 | 7252 | 19:30
11:00 | -380 | 5618 | 1566 | 7184 | -510 | 7184 | 20:00
11:30 | -320 | 5554 | 1615.5 | 7169.5 | -620 | 7169.5 | 21:00
12:00 | -260 | 5490 | 1665 | 7155 | -620 | 7155 | 22:00
12:30 | -300 | 5404 | 1606.5 | 7010.5 | -580 | 7010.5 | 23:00
13:00 | -340 | 5318 | 1548 | 6866 | -580 | 6866 | 24:00
13:30 | -350 | 5417.5 | 1528 | 6945.5 |  | 6945.5
14:00 | -360 | 5517 | 1508 | 7025 | 128.92 | 7025
14:30 | -340 | 5467 | 1577.5 | 7044.5 | 86.5 | 7044.5
15:00 | -320 | 5417 | 1647 | 7064 |  | 7064
15:30 | -292 | 5417 | 1617 | 7034 | 7867500 | 7034
16:00 | -264 | 5417 | 1587 | 7004 |  | 7004
16:30 | -287 | 5320 | 1554 | 6874 |  | 6874
17:00 | -310 | 5223 | 1521 | 6744 | 700 | 6744
17:30 | -310 | 5266.5 | 1555.5 | 6822 | 1800 | 6822
18:00 | -310 | 5310 | 1590 | 6900 | 100 | 6900
18:30 | -380 | 5412 | 1679 | 7091 | 1400 | 7091
19:00 | -460 | 5627 | 2032 | 7659 | 100 | 7659
19:30 | -460 | 6356 | 2133 | 8489 | 1800 | 8489
20:00 | -510 | 6409 | 2132 | 8541 | 1800 | 8541
20:30 | -565 | 6416 | 2148.5 | 8564.5 | 1800 | 8564.5
21:00 | -620 | 6423 | 2165 | 8588 | 2100 | 8588
21:30 | -620 | 6427.5 | 2172.5 | 8600 | 1900 | 8600
22:00 | -620 | 6432 | 2180 | 8612 | 1900 | 8612
22:30 | -600 | 6438 | 2184.5 | 8622.5 |  | 8622.5
23:00 | -580 | 6444 | 2189 | 8633 |  | 8633
23:30 | -580 | 6372 | 2143.5 | 8515.5 |  | 8515.5
24:00 | -580 | 6300 | 2098 | 8398 |  | 8398
*MAX.GEN.(E.P.) |  | 8795 |  | 1:00
*MAX.GEN.(D.P.) |  | 7320 |  | 10:00
|  |  |  | min | max
|  | 3063.9 | 3349 | 8:00 | 1:00
|  | 2664.1 | 3286.1 | 13:00 | 11:00
|  | 2910.2 | 3139.4 | 18:30 | 24:00
|  | 2664.1 | 3349 | 13:00 | 1:00
|  | 282 |  | 4:00
|  | 276 |  | 18:00
|  | 348 |  | 21:00
|  | 348 |  | 21:00
| Deputy Manager |  |  | Manager |  |  | Deputy General Manager
| Load Despatch Division |  |  | Load Despatch Division |  |  | Load Despatch Circle
NATIONAL LOAD DESPATCH CENTER
3595 MW (09:00 )
4008 MW(05:00 )
.4MW (19:30)
8588 MW (21:00)
7320 MW (10:00)

## En.Curve
QF-LDC-12
Date | 2016-07-01 |  | Energy | 182560494 | 0
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | Tripura |  | DAILY ENERGY CURVE |  | 2016-07-01
0:00 | 1461 | 451 | 3102 | 2032 | 173 | 103 | 554 | 0 | 90
0:30 | 1452 | 451 | 3171 | 2107.5 | 170.5 | 90.5 | 553.5 | 0 | 87
1:00 | 1443 | 451 | 3240 | 2183 | 168 | 78 | 553 | 0 | 84
1:30 | 1438 | 451 | 3214 | 2168 | 168.5 | 94 | 552.5 | 0 | 83 | [5 empty] | 182.5605
2:00 | 1433 | 451 | 3188 | 2153 | 169 | 110 | 552 | 0 | 82 | [5 empty] | 0
2:30 | 1437.5 | 451 | 3165.5 | 2155.5 | 172.5 | 100 | 537.5 | 0 | 81 | [5 empty] | 182.5605
3:00 | 1442 | 451 | 3143 | 2158 | 176 | 90 | 523 | 0 | 80
3:30 | 1432 | 451 | 3189.5 | 2165.5 | 176 | 90 | 421.5 | 0 | 74
4:00 | 1422 | 451 | 3236 | 2173 | 176 | 90 | 320 | 0 | 68
4:30 | 1396.5 | 451 | 3114.5 | 2029.5 | 175.5 | 91 | 229 | 0 | 69
5:00 | 1371 | 451 | 2993 | 1886 | 175 | 92 | 138 | 0 | 70
5:30 | 1361 | 451 | 2888.5 | 1781 | 175 | 102 | 122 | 0 | 68
6:00 | 1351 | 451 | 2784 | 1676 | 175 | 112 | 106 | 0 | 66
6:30 | 1355 | 450.5 | 2766.5 | 1656.5 | 174.5 | 98.5 | 72.5 | 0 | 63
7:00 | 1359 | 450 | 2749 | 1637 | 174 | 85 | 39 | 0 | 60
7:30 | 1335.5 | 450 | 2702 | 1642.5 | 175 | 77.5 | 39 | 0 | 61
8:00 | 1312 | 450 | 2655 | 1648 | 176 | 70 | 39 | 0 | 62
8:30 | 1307.5 | 450 | 2691.5 | 1647 | 169.5 | 70 | 36.5 | 0 | 62
9:00 | 1303 | 450 | 2728 | 1646 | 163 | 70 | 34 | 0 | 62
9:30 | 1319 | 450 | 2790 | 1698.5 | 170.5 | 80 | 34 | 0 | 67
10:00 | 1335 | 450 | 2852 | 1751 | 178 | 90 | 34 | 0 | 72
10:30 | 1304 | 450 | 2787.5 | 1767.5 | 179.5 | 89 | 34 | 0 | 73
11:00 | 1273 | 450 | 2723 | 1784 | 181 | 88 | 34 | 0 | 74
11:30 | 1338.5 | 450 | 2861 | 1753 | 179 | 86.5 | 34 | 0 | 74
12:00 | 1404 | 450 | 2999 | 1722 | 177 | 85 | 34 | 0 | 74
12:30 | 1378.5 | 450 | 2964 | 1643 | 178.5 | 84 | 34 | 0 | 75
13:00 | 1353 | 450 | 2929 | 1564 | 180 | 83 | 34 | 0 | 76
13:30 | 1350.5 | 450.5 | 2912 | 1498.5 | 179 | 84 | 34 | 0 | 77
14:00 | 1348 | 451 | 2895 | 1433 | 178 | 85 | 34 | 0 | 78
14:30 | 1324 | 451 | 3026.5 | 1533.5 | 176 | 85 | 30.5 | 0 | 77
15:00 | 1300 | 451 | 3158 | 1634 | 174 | 85 | 27 | 0 | 76
15:30 | 1275.5 | 450.5 | 3098 | 1634.5 | 173 | 85.5 | 34 | 0 | 77
16:00 | 1251 | 450 | 3038 | 1635 | 172 | 86 | 41 | 0 | 78 | Max Temp. in Dhaka |  | MW at
16:30 | 1271.5 | 450 | 2994 | 1565 | 128.5 | 83 | 46.5 | 0 | 75
17:00 | 1292 | 450 | 2950 | 1495 | 85 | 80 | 52 | 0 | 72
17:30 | 1315 | 450 | 2910 | 1502.5 | 84.5 | 80 | 115.5 | 0 | 73
18:00 | 1338 | 450 | 2870 | 1510 | 84 | 80 | 179 | 0 | 74
18:30 | 1361 | 450 | 2815 | 1432 | 84 | 70 | 371 | 0 | 92
19:00 | 1417 | 442 | 2907 | 1698 | 83 | 128 | 502 | 0 | 90
19:30 | 1431 | 440 | 3310 | 2031 | 84 | 130 | 550 | 0 | 92
20:00 | 1352 | 440 | 3318 | 2131 | 102 | 130 | 563 | 0 | 92
20:30 | 1398.5 | 440 | 3324 | 2110.5 | 138 | 125 | 535.5 | 0 | 92
21:00 | 1445 | 440 | 3330 | 2090 | 174 | 120 | 508 | 0 | 92
21:30 | 1449.5 | 440.5 | 3344 | 2079 | 176.5 | 119 | 514 | 0 | 91
22:00 | 1454 | 441 | 3358 | 2068 | 179 | 118 | 520 | 0 | 90
22:30 | 1473 | 445.5 | 3363 | 2087.5 | 174.5 | 117 | 464 | 0 | 87
23:00 | 1492 | 450 | 3368 | 2107 | 170 | 116 | 408 | 0 | 84
23:30 | 1466.5 | 450 | 3351.5 | 2065 | 170.5 | 107.5 | 397.5 | 0 | 81
24:00 | 1441 | 450 | 3335 | 2023 | 171 | 99 | 387 | 0 | 78
|  | 1490 |  |  |  |  | 2380 | 0
|  | Deputy / Asstt. Manager |  |  | Manager
|  | Load Despatch Division |  |  | Load Despatch Division
NATIONAL LOAD DESPATCH CENTER
Tripura

## volt
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2016-07-01
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 222 | 11:00 | 220 | 1:00 | Tongi | 213 | 13:00 | 204 | 1:00
Ishurdi | 235 | 18:30 | 225 | 20:00 | Comilla (N) | 222 | 7:00 | 219 | 1:00
Ashuganj | 233 | 18:30 | 229 | 12:00 | Hathazari | 220 | 19:00 | 214 | 4:00
Serajganj | 224 | 18:00 | 216 | 3:00 | Megnaghat | 217 | 18:00 | 209 | 1:00
Baghabari | 223 | 13:00 | 218 | 6:00 | Fenchuganj | 233 | 16:00 | 226 | 1:00
Barapukuria | 225 | 13:00 | 215 | 19:30 | Siddhirganj | 227 | 8:00 | 222 | 12:00
Bogra | 222 | 11:00 | 210 | 19:30 | Maniknagar | 226 | 8:00 | 220 | 1:00
Khulna South | 239 | 15:00 | 230 | 5:00 | Old Airport | 210 | 18:00 | 204 | 1:00
Rampura | 213 | 14:00 | 209 | 1:00 | Barisal | 239 | 17:00 | 229 | 19:30
Haripur | 211 | 14:00 | 207 | 1:00 | AKSML | 219 | 15:00 | 212 | 19:30
Hasnabad | 211 | 13:00 | 205 | 1:00 | BSRM | 220 | 18:00 | 213 | 1:00
Aminbazar | 210 | 17:00 | 204 | 1:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 136 | 600 | 133 | 1200 | Madanhat | 138 | 1930 | 134 | 1100
Munsiganj | 136 | 700 | 134 | 1500 | Hathazari | 132 | 2000 | 128 | 400
Megnaghat | 133 | 1900 | 130 | 200 | Khulshi | 136 | 1800 | 132 | 1100
Shyampur | 131 | 300 | 127 | 700 | Halishahar | 134 | 1800 | 130 | 400
Bhulta | 131 | 1300 | 126 | 100 | Baraulia | 130 | 1800 | 126 | 900
Madanganj | 134 | 1000 | 132 | 100 | Sikalbaha | 133 | 1800 | 129 | 500
Shitalakhya | 134 | 1300 | 129 | 100 | Dohazari | 133 | 1800 | 128 | 100
Rahim steal | 134 | 300 | 132 | 1200 | Cox'sbazar | 132 | 1600 | 126 | 100
Matuail | 133 | 400 | 131 | 1200 | Chandraghona | 134 | 1800 | 130 | 1400
Ghorasal | 135 | 1800 | 130 | 100 | Kaptai | 133 | 1500 | 130 | 100
Narsinghdi | 135 | 1300 | 129 | 100 | A. Khaer Stl. | 130 | 1300 | 127 | 1000
Haripur (SBU) | 134 | 800 | 132 | 100 | Bakulia | 131 | 1700 | 127 | 1000
Ullon | 132 | 600 | 129 | 1300 | Julda | 132 | 1800 | 129 | 400
Hasnabad | 132 | 800 | 130 | 1500 | TK Chemical | 135 | 1800 | 131 | 700
Magbazar | 131 | 1800 | 129 | 600 | Modern Steel | 131 | 1600 | 129 | 700
Maniknagar | 132 | 600 | 130 | 1200 | Shahmirpur | 132 | 1500 | 129 | 400
Bangabhaban | 132 | 600 | 130 | 1200 | Goalpara | 139 | 1500 | 133 | 2100
Narinda | 132 | 600 | 130 | 1200 | Central s/s | 138 | 1200 | 133 | 600
Dhanmondi | 131 | 1800 | 129 | 600 | Noapara | 135 | 1200 | 127 | 2100
Lalbag | 129 | 600 | 127 | 1200 | Jessore | 130 | 1500 | 120 | 1930
Madartek | 130 | 600 | 128 | 1200 | Jhenida | 132 | 1600 | 116 | 2200
Mirpur | 129 | 500 | 124 | 100 | Bottail | 133 | 1800 | 125 | 1930
Kalyanpur | 133 | 1800 | 128 | 100 | G.K.Project | 137 | 1800 | 127 | 300
Gulshan | 131 | 600 | 127 | 100 | Faridpur | 131 | 1400 | 123 | 2100
Uttara | 128 | 1800 | 123 | 100 | Madaripur | 135 | 1800 | 125 | 1930
Kamrangirchar | 131 | 700 | 126 | 100 | Gopalganj | 139 | 1830 | 129 | 1930
Savar | 130 | 700 | 126 | 100 | Bagerhat | 137 | 1500 | 130 | 2300
Bhasantec | 133 | 1800 | 128 | 100 | Mongla | 135 | 1500 | 128 | 400
Agargaon | 134 | 1800 | 129 | 100 | Satkhira | 135 | 1600 | 127 | 2100
Satmosjid | 133 | 1800 | 129 | 100 | Gallamari | 138 | 1200 | 133 | 600
Tongi | 135 | 1300 | 127 | 2100 | Magura | 130 | 1200 | 114 | 2200
Kabirpur | 134 | 1800 | 126 | 100 | Chuadanga | 128 | 1830 | 116 | 200
Basundhara | 127 | 1800 | 122 | 100 | Barisal | 140 | 1600 | 131 | 2300
Manikganj | 133 | 1400 | 124 | 2100 | Patuakhali | 136 | 1600 | 127 | 100
Joydevpur | 133 | 1300 | 126 | 100 | Bhandaria | 137 | 1600 | 130 | 2100
New Tongi | 132 | 1300 | 122 | 100 | Ishurdi | 135 | 1600 | 129 | 500
Tangail | 130 | 1400 | 115 | 100 | Natore | 132 | 1300 | 127 | 2100
Mymensing | 118 | 1600 | 110 | 500 | Bogra | 131 | 1100 | 122 | 2000
Kishorganj | 124 | 1600 | 120 | 300 | Noagaon | 129 | 1700 | 120 | 300
Netrokona | 122 | 1500 | 111 | 600 | Rajshahi | 132 | 1800 | 125 | 600
Jamalpur | 115 | 1500 | 105 | 700 | C.Nawabganj | 131 | 1300 | 124 | 300
Sherpur | 116 | 1500 | 104 | 200 | Amnura | 135 | 1300 | 129 | 300
Srimongal | 137 | 300 | 135 | 1930 | Pabna | 130 | 1300 | 124 | 2000
Shahjibazar | 138 | 1500 | 134 | 2300 | Shahjadpur | 136 | 1100 | 133 | 100
Fenchuganj | 137 | 200 | 135 | 1900 | Serajganj | 130 | 900 | 125 | 2000
Khulawara | 136 | 300 | 134 | 1900 | Niyamatpur | 128 | 1800 | 115 | 2100
Sylhet | 135 | 1000 | 130 | 2400 | Joypurhat | 130 | 1700 | 119 | 2100
Chatak | 135 | 700 | 131 | 500 | Rangpur | 123 | 1100 | 111 | 1930
Comilla(s) | 132 | 700 | 127 | 1930 | Lalmonirhat | 120 | 900 | 105 | 1930
Comilla(n) | 132 | 700 | 130 | 1500 | Saidpur | 120 | 800 | 110 | 1930
Chandpur | 126 | 1200 | 125 | 1900 | Purbasadipur | 123 | 800 | 111 | 1930
Feni | 120 | 900 | 117 | 400 | Thakurgaon | 120 | 700 | 110 | 1930
Chowmuhani | 124 | 1600 | 121 | 1930 | Palashbari | 125 | 800 | 115 | 1930
Ashuganj | 134 | 1900 | 132 | 500 | Barapukuria | 125 | 1300 | 115 | 1930
Daudkandi | 132 | 1830 | 130 | 700 | Panchagar | 115 | 700 | 100 | 1930
B.Baria | 133 | 1300 | 129 | 2300
Page 7 of 7