## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:August 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-08-01 |  | 2022-07-01 |  | 2021-08-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13985 | 2022-08-25 | 13765 | 2022-07-17 | 13271 | 2021-08-22 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 9620 | 2022-08-12 | 7802 | 2022-07-10 | 8249 | 2021-08-01 | - | -
|  |  | 6:00 |  | 6:00 |  | 22:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13985 | 2022-08-25 | 13765 | 2022-07-17 | 13271 | 2021-08-22 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11848 | 2022-08-25 | 12258 | 2022-07-18 | 11410 | 2021-08-31 | 12895 | 2022-04-26
|  |  | 12:00 |  | 10:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14745 | 2022-08-31 | 15001 | 2022-07-19 | 13271 | 2021-08-22 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 13078.4194 |  | 12574.9032 |  | 12483.5806 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 10988.2258 |  | 10718.3548 |  | 10126.9918 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 922 | 2022-08-08 | 926 | 2022-07-17 | 907 | 2021-07-01 | 956 | 27/3/2019
|  |  | 3:00 |  | 1:30 |  | 0:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 182 | 2022-08-07 | 182 | 2022-07-19 | 172 | 2021-07-10 | 194 | 12/06/19
|  |  | 15:00 |  | 23:00 |  | 23:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1537 | 2022-08-06 | 2385 | 2022-07-19 | 0 | - | 1459 | 04/05/2010
|  |  | 21:00 |  | 21:00 |  | - |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 12132 | 2022-08-06 | 11739 | 2022-07-19 | - | - | 2385 | 2022-07-19
|  | - | 21:00 | - | 21:00 | - | - |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 54 | 2022-08-15 | 0 | - | 0 | -
21:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 13051 | 2022-08-15 | - | - | - | -
21:00
14 | Maximum Load Shed (MW) at Day Peak | 1638 | 2022-08-12 | - | - | - | -
10:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 9923 | 2022-08-12 | - | - | - | -
10:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2022-08-15 | - | - | - | -
10:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 10622 | 2022-08-15 | - | - | - | -
10:00
18 | Nos. of Days Load Shed at Evening Peak | 31 |  | - |  | 0
19 | Nos. of Days Load Shed at Day Peak | 30 |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1900.8429 |  | 1773.1307 |  | 1762.3785 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 135.2896 |  | 135.2896 |  | 118.3845
22 | Net Generation of BPDB (MKWH) | 1765.5533 |  | 1637.8411 |  | 1643.994
23 | Net Generation of IPP (MKWH) | 5487.1901 |  | 5534.1867 |  | 5157.2882
24 | Net Generation of REB (MKWH) | 127.2082 |  | 130.5165 |  | 144.3267
24 | Net Generation of Rental Power Plant (MKWH) | 411.3038 |  | 382.0653 |  | 511.1298
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7791.2554 |  | 7684.6096 |  | 7456.7388 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4273.9758 |  | 4256.9757 |  | 4736.6321 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 623.3092 |  | 240.1426 |  | 442.1105 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1993.2091 |  | 2402.1611 |  | 1803.3426 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 95.7122 |  | 88.9738 |  | 86.881 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 37.0888 |  | 38.5148 |  | 30.5606 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 903.25 |  | 793.1312 |  | 475.5964 |  | 903.25 | August'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 776.6715 |  | 681.8974 |  | 593.113 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 92.6177 |  | 91.9201 |  | 82.7278 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:July 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | ` |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13985 | 2022-08-25 | 21:00
Generation Period
| Dhaka | MW | 4749
| Chattogram | MW | 1338
| Cumilla | MW | 1340
| Mymensingh | MW | 992
| Sylhet | MW | 554
a) | Total supply in East zone | MW | 8973
| Khulna | MW | 1688.6
| Barisal | MW | 397.89
| Rajshahi | MW | 1467.1
| Rangpur | MW | 893
b) | Total supply in West zone | MW | 4446.59
c) | Total supply in both zone ( a+b) | MW | 13419.59
Ref: | 27.21.0000.603.16.087.20.547 | Date: 18/09/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 120 | 2022-08-16 | 19:00
| b) Ishurdi end | MW | 562 | 2022-08-07 | 9:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1480 | 2022-08-30 | 14:00
| b) Ishurdi end | MW | 14 | 2022-08-16 | 19:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.006892
| b) Ishurdi end | MKWH | 245.38
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 50 | 2022-08-16 | 20:00
| b)Serajganj end | MW | 700 | 2022-08-29 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 640 | 2022-08-07 | 9:00
| b)Sirajganj end | MW | 60 | 2022-08-16 | 19:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.03 | 2022-08-01
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 151.418
| b)Sirajganj end | MKWH | 155.6
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 147.44
| b)Sirajganj end | MKWH | 147.35
30 | Transmission loss of EWI /NO-2 | % | 3.999%
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
2nd East-West Interconnector Loss:
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062
| Difference (-) : | 3516000
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: August2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV transformer T-3 | 2022-08-01 22:38 | 2022-08-01 23:46 | 1:08 | T | Due to 33 kV feeder fault | 20 | 22.6667 | Power interruption
Mymensingh | 132/33 kV transformers T-1 & T-2 | 2022-08-03 10:25 | 2022-08-03 10:31 | 0:06 | T | Due to 33 kV feeder fault | 120 | 12 | Power interruption
Dhamrai | 132/33 kV transformers T-1 | 2022-08-03 17:09 | 2022-08-03 17:20 | 0:11 | T | Due to 33 kV feeder fault
| 132/33 kV transformers T-2 | 2022-08-03 17:09 | 2022-08-03 17:23 | 0:14 | T |  | 70 | 16.3333 | Power interruption
Mymensingh | 132/33 kV transformers T-1 & T-2 | 2022-08-05 07:22 | 2022-08-05 07:30 | 0:08 | T | Tripped showing O/C . relay | 134 | 17.8667 | Power interruption
Kabirpur | 132/33 kV transformer T-2 with 33 kV Bus | 2022-08-10 15:15 | 2022-08-10 17:07 | 1:52 | T | Due to red-hot maint by PBS work | 100 | 186.6667 | Power interruption
Mirpur | 132/33 kV transformer T-1 | 2022-08-18 15:21 | 2022-08-18 15:21 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-2 | 2022-08-19 10:10 | 2022-08-19 10:13 | 0:03 | T | Due to 33 kV feeder fault | 30 | 1.5 | Power interruption
Dhamrai | 132/33 kV transformers T-1 & T-2 | 2022-08-20 05:38 | 2022-08-20 05:51 | 0:13 | T | Tripped showing O/C . relay at 33 kV side | 76 | 16.4667 | Power interruption
Manikganj | 132/33 kV transformer GT-4 | 2022-08-22 10:25 | 2022-08-22 11:49 | 1:24 | T | Due to red-hot maint | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformers T-1 & T-2 | 2022-08-23 04:16 | 2022-08-23 04:22 | 0:06 | T | Due to 33 kV feeder fault | 82 | 8.2 | Power interruption
Manikganj | 132/33 kV transformer T-2 | 2022-08-23 07:46 | 2022-08-23 08:22 | 0:36 | T | Tripped showing O/C . relay at 33 kV side | 40 | 24 | Power interruption
Savar | 33 kV Bus-A | 2022-08-24 08:54 | 2022-08-24 11:02 | 2:08 | T | Due to red-hot maint at P/P bus DS | 0 | 0 | No interruption
Rajenrapur | 132/33 kV transformer T-1 | 2022-08-29 15:47 | 2022-08-29 15:55 | 0:08 | T | Due to 33 kV feeder fault | 35 | 4.6667 | Power interruption
|  |  | Total : | 8:17 |  | Unserved Energy: |  | 310.3667
Dhaka (South) Grid Circle :
Siddhirganj | 230/132 kV transformer T-2 | 2022-08-10 02:26 | 2022-08-10 02:26 | 0:00 | T | Tripped showing PRD . relay | 0 | 0 | No interruption
Ullon | 132 kV full Bus | 2022-08-12 15:13 | 2022-08-12 16:05 | 0:52 | E/O | Due to bursting of Y-phase CT | 140 | 121.3333 | Power interruption
Munshiganj | 132/33 kV transformer T-2 | 2022-08-15 11:40 | 2022-08-15 13:40 | 2:00 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Bhulta | 132/33 kV transformers T-1 | 2022-08-18 05:54 | 2022-08-18 06:24 | 0:30 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
| 132/33 kV transformers T-2 | 2022-08-18 05:54 | 2022-08-18 06:32 | 0:38 | T | Tripped showing O/C . relay | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T-2 | 2022-08-22 19:48 | 2022-08-22 20:01 | 0:13 | T | Due to 33 kV feeder fault | 34 | 7.3667 | Power interruption
Sreenagar | 132/33 kV transformer T-2 | 2022-08-23 20:27 | 2022-08-23 21:23 | 0:56 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-08-23 21:36 | 2022-08-23 22:57 | 1:21 | E/O |  | 40 | 54 | Power interruption
Hasnabad | 33 kV reserve Bus | 2022-08-24 08:45 | 2022-08-24 19:03 | 10:18 | E/O | Due to red-hot maint.at DS clamp | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-08-25 07:11 | 2022-08-25 07:21 | 0:10 | T | Due to Zinzira feeder fault | 20 | 3.3333 | Power interruption
Siddhirganj | 132/33 kV transformer T1 | 2022-08-26 06:14 | 2022-08-26 06:14 | 0:00 | E/O | Due to red-hot maint.
Haripur | Haripur 230 kV -Haripur 230 kV CB-808 | 2022-08-31 09:48 | 2022-08-31 10:53 | 1:05 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
|  |  | Total : | 18:03 |  | Unserved Energy: |  | 186.0333
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV transformer T3 | 2022-08-01 18:48 | 2022-08-01 18:59 | 0:11 | T | Tripped showing O/C. relay | 65 | 11.9167 | Power interruption
| 132/33 kV transformer T3 | 2022-08-04 05:22 | 2022-08-04 06:46 | 1:24 | E/O | Due to red-hot maint.33 kV side | 30 | 42 | Power interruption
| 132/33 kV transformer T2 | 2022-08-04 07:07 | 2022-08-04 07:36 | 0:29 | T |  | 0 | 0 | No interruption
Hathazari | 132/33 kV transformer T1 | 2022-08-07 02:55 | 2022-08-07 10:14 | 7:19 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformers T-1 & T-2 | 2022-08-08 19:03 | 2022-08-08 20:00 | 0:57 | T | Tripped showing O/C. relay at 33 kV side | 70 | 66.5 | Power interruption
Cox'sbazar | 132/33 kV transformers T-1 & T-2 | 2022-08-13 11:12 | 2022-08-13 12:30 | 1:18 | T | Due to 33 kV feeder fault | 40 | 52 | Power interruption
Baoierhat | 132/33 kV transformer T2 with 33 kV Bus | 2022-08-14 07:37 | 2022-08-14 09:18 | 1:41 | E/O | Due to red-hot maint.33 kV side | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV transformers T-1 & T-2 | 2022-08-19 08:00 | 2022-08-19 08:14 | 0:14 | T | Due to 33 kV feeder fault | 12 | 2.8 | Power interruption
GK | 132/33 kV transformer T3 | 2022-08-19 09:30 | 2022-08-19 12:25 | 2:55 | E/O | Due to red-hot maint.33 kV side | 18 | 52.5 | Power interruption
|  |  | Total : | 16:28 |  | Unserved Energy: |  | 227.7167
Cumilla Grid Circle :
Ramganj | 132/33 kV transformer T2 | 2022-08-10 08:42 | 2022-08-10 10:01 | 1:19 | T | Due to red-hot maint. | 25 | 32.9167 | Power interruption
Sylhet | 132/33 kV transformer T4 | 2022-08-12 22:42 | 2022-08-13 00:21 | 1:39 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T1 & T2 | 2022-08-13 12:27 | 2022-08-13 12:40 | 0:13 | T | Tripped showing E/F. relay at 33 kV side | 110 | 23.8333 | Power interruption
Cumilla(N) | 132/33 kV transformers T3 | 2022-08-16 04:28 | 2022-08-16 04:44 | 0:16 | T | Tripped showing O/C. relay at 33 kV side | 55 | 14.6667 | Power interruption
| 132/33 kV transformers T4 | 2022-08-16 04:28 | 2022-08-16 04:42 | 0:14 | T
| 132/33 kV transformers T4 | 2022-08-17 18:46 | 2022-08-17 23:01 | 4:15 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Chandpur | 132/33 kV transformers T5 | 2022-08-18 06:04 | 2022-08-18 07:32 | 1:28 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
| 132/33 kV transformers T-1 & T2 | 2022-08-18 07:41 | 2022-08-18 09:09 | 1:28 | E/O | Due to red-hot maint.of 33 kV feeder | 22 | 32.2667 | Power interruption
Cumilla(S) | 132/33 kV transformers T3 | 2022-08-18 18:28 | 2022-08-18 19:07 | 0:39 | T | Tripped showing 33 kV feeder fault
| 132/33 kV transformers T4 | 2022-08-18 18:28 | 2022-08-18 19:01 | 0:33 | T |  | 52 | 28.6 | Power interruption
Cumilla(N) | 132/33 kV transformers T05 | 2022-08-23 17:25 | 2022-08-23 18:28 | 1:03 | E/O | Due to bursting of 33 kV PT | 27 | 28.35 | Power interruption
Ramganj | 132/33 kV transformer T2 | 2022-08-30 08:23 | 2022-08-30 09:29 | 1:06 | T | Due to red-hot maint. | 30 | 33 | Power interruption
|  |  | Total : | 14:13 |  |  |  | 193.6333
Khulna Grid Circle :
Barishal(N) | 132/33 kV transformer T4 | 2022-08-02 08:56 | 2022-08-02 17:41 | 8:45 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Gallamari | 132/33 kV transformers T1 & T2 | 2022-08-02 17:08 | 2022-08-02 17:55 | 0:47 | T | Due to 33 kV feeder fault | 40 | 31.3333 | Power interruption
Bhandaria | 132/33 kV transformers T1 & T2 | 2022-08-09 14:40 | 2022-08-09 14:46 | 0:06 | T | Tripped showing 33 kV feeder fault | 12 | 1.2 | Power interruption
Shariatpur | 132/33 kV transformers T1 & T2 | 2022-08-09 18:45 | 2022-08-09 19:04 | 0:19 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Norail | 132/33 kV transformer T1 | 2022-08-11 09:56 | 2022-08-11 11:55 | 1:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| 132/33 kV transformers T1 | 2022-08-12 07:08 | 2022-08-12 07:08 | 0:00 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
| 132/33 kV transformers T2 | 2022-08-12 07:13 | 2022-08-12 07:13 | 0:00 | E/O |  | 0 | 0 | No interruption
Bhandaria | 132/33 kV transformer T2 | 2022-08-13 08:21 | 2022-08-13 09:14 | 0:53 | E/O | Due to red-hot maint at 33 kV side | 15 | 13.25 | Power interruption
Gopalganj | 132/33 kV transformers T1 & T2 | 2022-08-13 16:31 | 2022-08-13 16:41 | 0:10 | T | Due to 33 kV feeder fault | 47 | 7.8333 | Power interruption
Gallamari | 132/33 kV transformer TR2 | 2022-08-15 05:16 | 2022-08-15 05:16 | 0:00 | T | Tripped showing diff. relay | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T3 | 2022-08-17 09:54 | 2022-08-17 10:03 | 0:09 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Gallamari | 132/33 kV transformers T1 & T2 | 2022-08-17 18:10 | 2022-08-17 18:30 | 0:20 | E/O | Due to bursting of CT at 33 kV side | 50 | 16.6667 | Power interruption
Madaripur | 132/33 kV transformer T2 | 2022-08-18 15:47 | 2022-08-18 16:49 | 1:02 | E/O | Due to red-hot maint at 33 kV side | 21 | 21.7 | Power interruption
Khulna(C) | 132/33 kV transformer T3 | 2022-08-18 17:40 | 2022-08-18 18:11 | 0:31 | T | Tripped showing O/C relay at 33 kV | 30 | 15.5 | Power interruption
| 132/33 kV transformer T3 | 2022-08-21 22:05 | 2022-08-21 23:10 | 1:05 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformer T3 | 2022-08-23 15:41 | 2022-08-23 18:05 | 2:24 | E/O | Due to red-hot maint at 33 kV side | 95 | 228 | Power interruption
Fridpur | 132/33 kV transformer T1 & 33 kV Bus | 2022-08-24 12:31 | 2022-08-24 14:50 | 2:19 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Barishal(N) | 132/33 kV transformer T4 with 33 kV Bus | 2022-08-25 09:43 | 2022-08-25 12:20 | 2:37 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 23:26 |  | Unserved Energy: |  | 335.4833
HVDC Grid Circle :
Bheramara GK | 132/33 kV transformer T3 | 2022-08-02 07:27 | 2022-08-02 10:28 | 3:01 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T2 with 33 kV Bus | 2022-08-02 17:52 | 2022-08-02 19:59 | 2:07 | E/O | Due to red-hot maint at 33 kV Bus | 22 | 57.5667 | Power interruption 17:22 to 19:59
Shahjadpur | 132/33 kV transformer T3 | 2022-08-06 23:55 | 2022-08-07 00:15 | 0:20 | E/O | Due to red-hot maint at 33 kV Bus | 10 | 3.3333 | Power interruption
Jashore | 132/33 kV transformer T1 | 2022-08-09 16:14 | 2022-08-09 16:33 | 0:19 | T | Tripped showing 33 kV feeder fault | 30 | 9.5 | Power interruption
|  |  | Total : | 5:47 |  |  |  | 70.4
Bogura Grid Circle:
Bogura (O) | 132/33 kV transformer T1 | 2022-08-03 12:42 | 2022-08-03 12:42 | 0:00 | E/O | Due to Oil leakage at 33kV B-phase bushing | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T1 | 2022-08-05 17:25 | 2022-08-05 18:48 | 1:23 | E/O | Due to red-hot maint | 24 | 33.2 | Power interruption
C.nawabganj | 132/33 kV transformer T1 | 2022-08-07 22:05 | 2022-08-08 00:59 | 2:54 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Bogura | 132/33 kV transformers T1 & T2 | 2022-08-08 09:21 | 2022-08-08 09:57 | 0:36 | T | Due to 33 kV feeder fault | 55 | 33 | Power interruption
Rangpur | 132/33 kV transformer T1 | 2022-08-09 07:55 | 2022-08-09 10:10 | 2:15 | E/O | Due to red-hot maint | 30 | 67.5 | Power interruption
Natore | 132/33 kV transformer T3 | 2022-08-09 08:15 | 2022-08-09 10:26 | 2:11 | E/O | Due to red-hot maint | 15 | 32.75 | Power interruption
Rangpur | 132/33 kV transformer T2 | 2022-08-09 08:38 | 2022-08-09 10:01 | 1:23 | E/O | Due to red-hot maint at 33 kV side | 40 | 55.3333 | Power interruption
Mithapukur | 132 kV Bus-1 | 2022-08-10 11:45 | 2022-08-10 14:16 | 2:31 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformers T1 & T2 | 2022-08-12 00:05 | 2022-08-12 00:28 | 0:23 | T | Due to 33 kV feeder fault | 79 | 30.2833 | Power interruption
Sherpur(Bogura) | 132/33 kV transformers T1 & T2 | 2022-08-14 15:02 | 2022-08-14 15:22 | 0:20 | T | Due to 33 kV feeder fault | 25 | 8.3333 | Power interruption
Bogura(O) | 132/33 kV transformer T2 | 2022-08-14 14:30 | 2022-08-14 15:23 | 0:53 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer Tr1 | 2022-08-18 10:35 | 2022-08-18 10:35 | 0:00 | E/O | Due to Oil cenrifuge | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T2 | 2022-08-18 20:20 | 2022-08-18 20:34 | 0:14 | T | Due to low Voltage | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T1 with 33 kV Bus-3 | 2022-08-21 07:07 | 2022-08-21 08:56 | 1:49 | E/O | Due to red-hot maint | 35 | 63.5833 | Power interruption
Rajshahi(N) | 132/33 kV transformer T2 with 33 kV Bus | 2022-08-21 19:54 | 2022-08-21 20:55 | 1:01 | E/O | Due to red-hot maint at 33 kV side | 8 | 8.1333 | Power interruption
Kuriagram | 132/33 kV transformers T1 & T2 with 33 kV Bus | 2022-08-21 14:35 | 2022-08-21 14:55 | 0:20 | T | Tripped showing O/C. relay | 42 | 14 | Power interruption
Bogura(O) | 132/33 kV transformer T1 | 2022-08-26 07:45 | 2022-08-26 09:24 | 1:39 | E/O | Due to red-hot maint | 5 | 8.25 | Power interruption
|  |  | Total : | 19:52 |  |  |  | 354.3667
Others :
Ashuganj | 230/132 kV transformer OAT12 | 2022-08-02 12:02 | 2022-08-02 12:23 | 0:21 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-08-08 09:21 | 2022-08-08 15:21 | 6:00 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-10 13:17 | 2022-08-10 13:31 | 0:14 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-14 13:17 | 2022-08-14 15:04 | 1:47 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 132/33 kV transformer OAT12 | 2022-08-18 06:04 | 2022-08-18 10:33 | 4:29 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-21 11:15 | 2022-08-21 11:28 | 0:13 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-23 08:27 | 2022-08-23 08:36 | 0:09 | T | Tripped showing O/C. relay at 33 kV side | 0 | 0 | No interruption
| 230/132 kV transformer OAT12 | 2022-08-23 23:07 | 2022-08-23 23:23 | 0:16 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
|  |  | Total : | 13:29 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 119:35 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:August2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | Jamalpur-Jamalpur 95 P/P 230 Ckt | 2022-08-03 12:42 | 2022-08-03 17:54 | 5:12 | E/O | Due to heavy flashing at 132 kV DS of P/P | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-08-05 07:21 | 2022-08-05 07:28 | 0:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-08-05 09:01 | 2022-08-05 10:55 | 1:54 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Mymensingh-Netrakona 132 kV Ckt-1 | 2022-08-06 05:51 | 2022-08-06 06:49 | 0:58 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2022-08-18 12:05 | 2022-08-18 12:11 | 0:06 | T | Tripped showing O/C. relay | 120 | 12 | Power interruption
| Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-18 12:05 | 2022-08-19 13:06 | 25:01 | T | Tripped showing Dist. relay
| Kabirpur-Kaliakoir132 kV Ckt-2 | 2022-08-18 12:05 | 2022-08-19 18:01 | 29:56 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Mymensingh 132 kV Ckt-1 | 2022-08-23 13:13 | 2022-08-23 13:32 | 0:19 | T | Tripped showing E/F. relay | 85 | 26.9167 | Power interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-08-24 11:05 | 2022-08-24 21:21 | 10:16 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-26 11:10 | 2022-08-26 11:26 | 0:16 | T | Tripped showing Dist. relay | 235 | 62.6667 | Power interruption
| Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-26 14:15 | 2022-08-26 14:33 | 0:18 | T | Tripped showing Dist. relay | 208 | 62.4 | Power interruption 14:15 to 14:33
|  |  | Total : | 74:23 |  | Unserved Energy: |  | 163.9833
Dhaka (South) Grid Circle :
Ghorshal | Ghorshal-Ishurdi 230 kV Ckt-1 | 2022-08-07 14:02 | 2022-08-07 14:23 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ghorshal-Ashuganj 132 kV Ckt-1 | 2022-08-19 13:20 | 2022-08-19 13:39 | 0:19 |  |  |  |  | No interruption
Rampura | Rampura-Ullon 132 kV Ckt-2 | 2022-08-20 10:40 | 2022-08-20 10:40 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ghorashal | Ghorashal(GIS)-Ishurdi 230 kV Ckt-2 | 2022-08-23 12:05 | 2022-08-23 12:52 | 0:47 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ghorashal(GIS)-Ishurdi 230 kV Ckt-1 | 2022-08-24 12:05 | 2022-08-24 12:26 | 0:21 | T | Tripped showing O/C . relay. | 0 | 0 | No interruption
Keraniganj | Keraniganj-Kamrangirchar 132 kV Ckt | 2022-08-24 10:15 | 2022-08-24 10:26 | 0:11 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2022-08-25 09:59 | 2022-08-25 10:34 | 0:35 | T | Tripped showing O/C. relay | 60 | 35 | Power interruption
Haripur | Haripur-Narshingdi 132 kV Ckt | 2022-08-25 13:00 | 2022-08-25 13:34 | 0:34 | T | Tripped showing Dist. relay | 93 | 52.7 | Power interruption
| Haripur-Ullon 132 kV Ckt | 2022-08-29 10:41 | 2022-08-29 10:53 | 0:12 | T | Tripped showing Dist. relay | 100 | 20 | Power interruption
|  |  | Total : | 3:20 |  | Unserved Energy: |  | 107.7
Chattogram Grid Circle :
Halishahar | Halishahar -Khulshi132 kV Ckt-3 | 2022-08-05 08:29 | 2022-08-05 08:55 | 0:26 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2022-08-05 19:24 | 2022-08-05 19:51 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-1 & 2 | 2022-08-16 01:04 | 2022-08-16 01:35 | 0:31 | T | Tripped showing O/C & E/F. relay. | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 & 2 | 2022-08-18 06:04 | 2022-08-18 07:00 | 0:56 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV Ckt-2 | 2022-08-21 20:48 | 2022-08-21 22:58 | 2:10 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt 1 | 2022-08-22 19:03 | 2022-08-22 19:29 | 0:26 | T | Tripped showing Dist. relay | 22 | 9.5333 | Power interruption
| Chandraghona-Rangamati 132 kV Ckt 2 | 2022-08-22 19:03 | 2022-08-22 20:26 | 1:23 | T
Hathazari | Hathazari-Kaptai 132 kV Ckt-1 & 2 | 2022-08-22 18:59 | 2022-08-22 19:24 | 0:25 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt- 1 | 2022-08-22 14:37 | 2022-08-22 14:48 | 0:11 | T | Tripped showing Dist. relay | 95 | 17.4167 | Power interruption
| Dohazari-Cox'sbazar 132 kV Ckt- 2 | 2022-08-22 14:37 | 2022-08-22 14:49 | 0:12 | T
|  |  | Total : | 7:07 |  | Unserved Energy: |  | 26.95
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj P.S 132 kV Ckt | 2022-07-04 03:10 | 2022-07-04 03:16 | 0:06 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chattak 132 kV Ckt | 2022-07-31 06:30 | 2022-07-31 07:00 | 0:30 | T | Tripped showing 67N PT fuse fail | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2022-08-04 06:13 | 2022-08-04 10:23 | 4:10 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 132 kV Ckt | 2022-08-04 14:28 | 2022-08-04 14:44 | 0:16 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-1 | 2022-08-06 04:28 | 2022-08-06 04:33 | 0:05 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandpur desh | Chandpur desh-Ramganj 132 kV Ckt | 2022-08-12 07:13 | 2022-08-12 07:13 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Chowddagram 132 kV Ckt-1 & 2 | 2022-08-16 01:04 | 2022-08-16 01:16 | 0:12 | T | Tripped showing O/C & E/F. relay. | 516 | 103.2 | Power interruption
Kachua | Kachua-Chandpur 132 kV Ckt-1 & 2 | 2022-08-16 01:04 | 2022-08-16 01:30 | 0:26 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
Chandpur desh | Chandpur desh-Ramganj 132 kV Ckt-1 & 2 | 2022-08-16 01:04 | 2022-08-16 01:38 | 0:34 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Chandpur desh-Chandpur S/S 132 kV Ckt-1 & 2 | 2022-08-16 01:04 | 2022-08-16 01:30 | 0:26 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| Chandpur desh-Ramganj 132 kV Ckt-1 & 2 | 2022-08-18 06:04 | 2022-08-18 06:25 | 0:21 | T | Tripped showing backup prot.relay | 0 | 0 | No interruption
Chandpur S/S | Chandpur -Kachua 132 kV Ckt-1 & 2 | 2022-08-18 06:04 | 2022-08-18 06:18 | 0:14 | T | Tripped showing O/C. relay | 50 | 11.6667 | Power interruption
Cumilla(S) | Cumilla(S)-Chaddogram 132 kV Ckt-1 & 2 | 2022-08-18 06:04 | 2022-08-18 06:12 | 0:08 | T |  | 0 | 0 | No interruption
Sylhet | Sylhet-Chattak 132 kV Ckt-1 | 2022-08-23 01:06 | 2022-08-23 01:20 | 0:14 | T | Tripped showing Dist. relay. | 20 | 4.6667 | Power interruption
| Sylhet-Sylhet 50 MW P/P 132 kV Ckt | 2022-08-31 15:36 | 2022-08-31 15:59 | 0:23 | E/O | Due to SF6 gas filling by P/P | 0 | 0 | No interruption
|  |  | Total : | 8:05 |  | Unserved Energy: |  | 119.5333
Khulna Grid Circle :
Faridpur | Faridpur -Rajbari132 kV Ckt-2 | 2022-08-01 16:38 | 2022-08-01 17:35 | 0:57 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV Ckt | 2022-08-02 16:34 | 2022-08-02 16:48 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-2 | 2022-08-02 16:00 | 2022-08-02 16:13 | 0:13 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Rampal 400 V Ckt | 2022-08-08 09:36 | 2022-08-08 09:36 | 0:00 | T | Tripped showing O/V. relay. | 0 | 0 | No interruption
| Gopalganj(N)-Payra 400 kV Ckt | 2022-08-08 09:36 | 2022-08-08 09:36 | 0:00 | T |  | 0 | 0 | No interruption
Payra S/S | Payra S/S-Payra P/P 400 kV Ckt-1 & 2 | 2022-08-08 09:36 | 2022-08-08 10:40 | 1:04 | T |  | 0 | 0 | No interruption
Barisal | Barisal-Patuakhali 132 kV Ckt | 2022-08-09 15:20 | 2022-08-09 15:25 | 0:05 | T | Tripped showing Dist. relay | 75 | 6.25 | Power interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-2 | 2022-08-12 14:38 | 2022-08-13 12:28 | 21:50 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bhola | Bhola-Barisal(N) 230 kV Ckt-1 | 2022-08-18 15:55 | 2022-08-18 16:39 | 0:44 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bhandaria | Bhandaria-Baisal 132 kV Ckt | 2022-08-18 16:40 | 2022-08-18 16:45 | 0:05 | T | Tripped showing Dist. relay | 21 | 1.75 | Power interruption
| Bhandaria-Baisal 132 kV Ckt | 2022-08-18 16:46 | 2022-08-18 20:49 | 4:03 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barisal | Barisal-Bhandaia 132 kV Ckt-1 | 2022-08-19 08:43 | 2022-08-19 11:00 | 2:17 | T | Tripped showing Dist. relay | 4 | 9.1333 | Power interruption
Barisal(S) | Barisal-Patuakhali 132 kV Ckt | 2022-08-20 11:37 | 2022-08-20 11:51 | 0:14 | T | Tripped showing Dist. relay | 90 | 21 | Power interruption
|  |  | Total : | 31:46 |  | Unserved Energy: |  | 38.1333
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-2 | 2022-08-01 11:45 | 2022-08-01 12:34 | 0:49 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV Ckt-2 | 2022-08-02 12:02 | 2022-08-02 12:19 | 0:17 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV Ckt-1 | 2022-08-02 12:03 | 2022-08-02 12:15 | 0:12 | T | Tripped showing O/C & E/F. relay. | 0 | 0 | No interruption
Shahjiadpur | Shahjiadpur-Bahabari 132 kV Ckt-1 & 2 | 2022-08-10 06:36 | 2022-08-10 07:29 | 0:53 | E/O | Due to bursting of PT | 0 | 0 | No interruption
Baghabari | Baghabari-Ishurdi 132 kV Ckt | 2022-08-10 06:36 | 2022-08-10 06:36 | 0:00 | E/O | Due to bursting of PT | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt-1 | 2022-08-12 12:51 | 2022-08-12 13:24 | 0:33 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Jashore-Jhenaidah 132 kV Ckt-2 | 2022-08-12 12:51 | 2022-08-12 13:25 | 0:34 | T |  | 0 | 0 | No interruption
| Jashore-Noapara 132 kV Ckt-1 & 2 | 2022-08-12 12:55 | 2022-08-12 13:36 | 0:41 | T | Tripped showing Dist. relay. | 99 | 67.65 | Power interruption
| Jashore-Noapara 132 kV Ckt-1 | 2022-08-12 14:11 | 2022-08-12 17:39 | 3:28 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 7:27 |  | Unserved Energy: |  | 67.65
Bogura Grid Circle:
Chapai | Chapai-Rohonpur 132 kV Ckt | 2022-08-03 13:55 | 2022-08-03 14:48 | 0:53 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Mithapukur | Mithapukur-Conf.132 kV Ckt-1 | 2022-08-10 11:14 | 2022-08-10 14:16 | 3:02 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Amnura | Amnura-Amnura P/S 132 kV Ckt | 2022-08-14 20:47 | 2022-08-14 20:47 | 0:00 | T | Tripped showing O/C . relay. | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura(Sherpur) 132 kV Ckt-1 | 2022-08-16 08:38 | 2022-08-16 09:36 | 0:58 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi(O) 132 kV Ckt | 2022-08-16 13:20 | 2022-08-16 14:35 | 1:15 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rohanpur 132 kV Ckt | 2022-08-18 23:54 | 2022-08-19 00:50 | 0:56 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Sherpur 132 kV Ckt-1 | 2022-08-19 15:01 | 2022-08-19 15:20 | 0:19 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Rohanpur | Rohanpur-Adani 400 kV Ckt-2 | 2022-08-20 06:10 | 2022-08-21 13:58 | 31:48 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV Ckt-2 | 2022-08-27 13:38 | 2022-08-27 14:52 | 1:14 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 40:25 |  | Unserved Energy: |  | 0
Others :
Ullon | Ullon-Dhanmondi 132 kV Ckt-3 | 2022-08-28 10:41 | 2022-08-28 11:04 | 0:23 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 0:23 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 172:56 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: August 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kabirpur | 132/33 kV transformer T-1 | 2022-08-03 05:33 | 2022-08-03 06:44 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-3 | 2022-08-04 10:15 | 2022-08-04 11:33 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-1 | 2022-08-04 15:58 | 2022-08-04 15:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Amimbazar | 230/132 kV transformer T-02 | 2022-08-06 12:25 | 2022-08-06 17:54 | 5:29 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV main Bus | 2022-08-06 17:34 | 2022-08-06 19:44 | 2:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-01 | 2022-08-07 09:59 | 2022-08-07 21:56 | 11:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T-03 | 2022-08-08 10:32 | 2022-08-08 16:37 | 6:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | 132/33 kV transformer T-2 | 2022-08-08 11:10 | 2022-08-08 16:38 | 5:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T-3 | 2022-08-08 16:12 | 2022-08-08 16:44 | 0:32 | S/O | Due to TRTUD work | 0 | 0 | No interruption
Netrakona | 132/33 kV transformer T-1 | 2022-08-09 09:28 | 2022-08-09 10:37 | 1:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-08-10 11:36 | 2022-08-10 12:46 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 A & B | 2022-08-10 08:33 | 2022-08-10 21:25 | 12:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-08-10 09:19 | 2022-08-10 17:10 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2022-08-10 09:22 | 2022-08-10 14:31 | 5:09 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2022-08-10 14:50 | 2022-08-10 16:27 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2022-08-12 09:17 | 2022-08-12 12:10 | 2:53 | S/O | Due to high temperature | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-3 | 2022-08-13 11:01 | 2022-08-13 17:26 | 6:25 | S/O | Due to abnormal sound | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2022-08-14 10:48 | 2022-08-14 15:46 | 4:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2022-08-14 14:15 | 2022-08-14 15:25 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132 kV Bus-2 | 2022-08-16 12:38 | 2022-08-16 17:05 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV transformer T-2 | 2022-08-18 06:20 | 2022-08-18 06:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | 230/132 kV transformer T-02 | 2022-08-19 06:28 | 2022-08-19 06:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2022-08-19 06:45 | 2022-08-19 06:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132 kV Bus-B | 2022-08-20 10:30 | 2022-08-20 14:52 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-2 | 2022-08-23 10:06 | 2022-08-23 11:35 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 33 kV reserve Bus | 2022-08-24 11:01 | 2022-08-24 21:22 | 10:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Amimbazar | 400/230 kV transformer T-01 | 2022-08-25 10:51 | 2022-08-25 10:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 230/132 kV transformer T-01 | 2022-08-26 06:02 | 2022-08-26 06:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV transformer T2 | 2022-08-27 09:21 | 2022-08-27 17:01 | 7:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-08-28 09:28 | 2022-08-28 15:47 | 6:19 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-08-29 06:02 | 2022-08-29 06:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T3 | 2022-08-29 06:36 | 2022-08-29 08:15 | 1:39 | S/O | Due to C/M work | 20 | 33 | Power interruption
Kodda | 132/33 kV transformer T3 | 2022-08-29 13:13 | 2022-08-29 14:05 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 116:33 |  | Unserved Energy: |  | 33
Dhaka (South) Grid Circle :
Rampura | 132 kV Bus-1 | 2022-08-04 12:25 | 2022-08-04 15:29 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 230/132 kV transformer T-01 | 2022-08-04 18:16 | 2022-08-04 18:16 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T1 | 2022-08-05 10:35 | 2022-08-05 12:30 | 1:55 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-08-05 12:32 | 2022-08-05 13:14 | 0:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | 230 kV GIS Bus coupler | 2022-08-11 11:54 | 2022-08-11 15:49 | 3:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhulta | 400/230 kV transformer ART-1 | 2022-08-12 07:32 | 2022-08-12 10:07 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 400/230 kV transformer ART-2 | 2022-08-12 10:17 | 2022-08-12 12:01 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Munshiganj | 132/33 kV transformer T1 | 2022-08-14 11:27 | 2022-08-14 14:05 | 2:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-08-14 14:11 | 2022-08-14 15:52 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Ullon | 132/33 kV transformer T2 | 2022-08-17 10:32 | 2022-08-17 14:47 | 4:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | 132/33 kV transformer T2 | 2022-08-25 11:28 | 2022-08-25 12:10 | 0:42 | S/O | Due to C/M work by PBS | 0 | 0 | No interruption
Shyampur(O) | 132/33 kV transformer T3 | 2022-08-26 00:20 | 2022-08-26 00:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformer T-03 | 2022-08-28 09:12 | 2022-08-28 12:16 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV transformer T1 | 2022-08-29 20:38 | 2022-08-29 23:48 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T1 | 2022-08-31 07:02 | 2022-08-31 07:44 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Mushiganj | 132/33 kV transformer T1 | 2022-08-31 10:48 | 2022-08-31 13:34 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 32:53 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Sikalbaha | 132/33 kV transformer T3 | 2022-08-01 14:20 | 2022-08-01 16:12 | 1:52 | S/O | Due to C/M work | 15 | 28 | Power interruption
Dohazari | 132/33 kV transformer T1 with 33 kV Bus | 2022-08-03 07:38 | 2022-08-03 07:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-08-03 10:40 | 2022-08-03 12:45 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T3 | 2022-08-06 09:22 | 2022-08-06 12:30 | 3:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T2 |  | 2022-08-08 15:27 |  | S/O | After maint.work | 0 | 0 | No interruption
Madunaghat | 132/33 kV transformer T2 | 2022-08-09 15:53 | 2022-08-09 18:48 | 2:55 | S/O | Due to 33 kV feeder maint. | 0 | 0 | No interruption
Rampur | 132/33 kV transformer ATR-2 | 2022-08-17 10:26 | 2022-08-17 11:17 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirsharai | 230/132 kV transformer T2 | 2022-08-20 10:59 | 2022-08-20 14:26 | 3:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230/132 kV transformer T01 | 2022-08-22 11:40 | 2022-08-22 14:52 | 3:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-08-22 15:42 | 2022-08-22 17:45 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 33 kV Bus | 2022-08-23 07:01 | 2022-08-23 09:55 | 2:54 | S/O | Due to C/M work by PBD | 60 | 174 | Power interruption
Hathazari | 230/132 kV transformer T03 | 2022-08-23 09:47 | 2022-08-23 12:54 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Sholoshahrar | 132/33 kV transformer T-1 | 2022-08-24 11:42 | 2022-08-24 17:58 | 6:16 | S/O | Due to D/W work by PDB | 0 | 0 | No interruption
BSRM | 230/132 kV transformer T01 | 2022-08-27 09:54 | 2022-08-27 16:36 | 6:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132/33 kV transformer T3 | 2022-08-27 09:57 | 2022-08-27 16:44 | 6:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV transformer T2 | 2022-08-28 07:09 | 2022-08-28 07:09 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-08-28 09:48 | 2022-08-28 11:28 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Matarbari | 132/33 kV transformer T-2 | 2022-08-28 13:53 | 2022-08-28 14:35 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 47:41 |  | Unserved Energy : |  | 202
Cumilla Grid Circle :
Chandpur | 132/33 kV transformer T5 | 2022-08-02 07:12 | 2022-08-02 10:45 | 3:33 | S/O | Due to maint.work | 0 | 0 | No interruption
Beanibazar | 132/33 kV transformer T2 | 2022-08-03 10:55 | 2022-08-03 18:05 | 7:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T4 | 2022-08-04 11:46 | 2022-08-04 12:46 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shajibazar | 132/33 kV transformer T2 | 2022-08-05 07:00 | 2022-08-05 08:13 | 1:13 | S/O | Due to C/M work | 87 | 105.85 | Power interruption
| 132/33 kV transformer T4 | 2022-08-06 06:36 | 2022-08-06 07:10 | 0:34 | S/O | Due to C/M work | 40 | 22.6667 | Power interruption
Chaddagram | 132/33 kV transformer T1 with 33 kV Bus | 2022-08-06 12:45 | 2022-08-06 14:44 | 1:59 | S/O | Due to C/M work | 22 | 43.6333 | Power interruption
Ashuganj | 132 kV Bus | 2022-08-10 06:59 | 2022-08-10 06:59 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T1 | 2022-08-12 07:15 | 2022-08-12 09:46 | 2:31 | S/O | Due to C/M work | 10 | 25.1667 | Power interruption
Cumilla(S) | 132/33 kV transformer T2 with 33 kV Bus-2 | 2022-08-12 08:42 | 2022-08-12 11:24 | 2:42 | S/O | Due to C/M work | 22 | 59.4 | Power interruption
Kachua | 132/33 kV transformer T1 | 2022-08-13 09:06 | 2022-08-13 14:48 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformers T1 | 2022-08-16 12:35 | 2022-08-16 12:51 | 0:16 | S/O | Due to maint.of 33 kV feeder | 80 | 21.3333 | Power interruption
| 132/33 kV transformers T2 | 2022-08-16 12:35 | 2022-08-16 14:52 | 2:17 | S/O |  | 0 | 0 | No interruption
Kulaura | 132/33 kV transformers T-1 | 2022-08-17 01:20 | 2022-08-17 02:02 | 0:42 | S/O | Due to jumper broke down at auxiliary transformer at 33 kV | 36 | 25.2 | Power interruption
| 132/33 kV transformers T-2 | 2022-08-17 01:20 | 2022-08-17 02:37 | 1:17 | S/O
Chandpur | 132/33 kV transformer T5 |  | 2022-08-17 13:40 |  | S/O | After maint.work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T-2 | 2022-08-28 09:24 | 2022-08-29 03:10 | 17:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T-1 | 2022-08-29 06:34 | 2022-08-29 08:18 | 1:44 | S/O | Due to C/M work | 5 | 8.6667 | Power interruption
| 132/33 kV transformer T-1 | 2022-08-31 15:28 | 2022-08-31 15:49 | 0:21 | S/O | Due to C/M work at 33 kV side | 34 | 11.9 | Power interruption
|  |  | Total : | 50:47 |  | Unserved Energy : |  | 323.8167
Khulna Grid Circle :
Barisal | 132/33 kV transformer T1 | 2022-08-03 06:33 | 2022-08-03 06:33 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-08-03 08:44 | 2022-08-03 09:58 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T-2 | 2022-08-10 09:48 | 2022-08-10 11:46 | 1:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Norail | 132/33 kV transformer T-2 | 2022-08-10 14:14 | 2022-08-10 15:07 | 0:53 | S/O | Due to C/M work | 10 | 8.8333 | Power interruption
Gopalganj | 132/33 kV transformer T-5 &-T6 | 2022-08-13 20:58 | 2022-08-13 17:15 |  | S/O | Due to D/W work | 0 | 0 | No interruption
Rampal | 400/230 kV Transformer |  | 2022-08-15 16:04 |  |  | new connection | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-1 | 2022-08-16 07:20 | 2022-08-16 07:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV transformers T4 & T5 | 2022-08-16 10:43 | 2022-08-16 12:43 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T1 | 2022-08-17 12:14 | 2022-08-17 12:14 | 0:00 | S/O | Due to C/M work at 33 kV side | 0 | 0 | No interruption
Shariatpur | 132/33 kV transformer T-1 with 33 kV Bus-1 | 2022-08-18 08:37 | 2022-08-18 09:56 | 1:19 | S/O | Due to C/M work | 10 | 13.1667 | Power interruption
Bagerhat | 132/33 kV transformer T2 | 2022-08-19 21:11 | 2022-08-19 21:50 | 0:39 | S/O | Due to C/M work | 10 | 6.5 | Power interruption
Gallamari | 132/33 kV transformer T2 | 2022-08-20 07:04 | 2022-08-20 07:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformers T1 & T2 with 33 kV Bus | 2022-08-20 08:15 | 2022-08-20 16:54 | 8:39 | S/O | Due to C/M work | 35 | 302.75 | Power interruption
Barisal(N) | 132/33 kV transformer T5 | 2022-08-20 10:57 | 2022-08-20 12:17 | 1:20 | S/O | Due to C/M work | 27 | 36 | Power interruption
Payra | 132 kV Bus | 2022-08-20 13:25 | 2022-08-20 15:24 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T2 | 2022-08-21 08:12 | 2022-08-21 09:10 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T03 | 2022-08-22 14:48 | 2022-08-22 16:36 | 1:48 | S/O | Due to maint.of 33 kV feeder | 36 | 64.8 | Power interruption
Faridpur | 132/33 kV transformer T2 with 33 kV Bus | 2022-08-24 09:21 | 2022-08-24 12:14 | 2:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(N) | 400/132 kV transformer T01 |  | 2022-08-24 16:43 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132 kV Bus | 2022-08-24 17:50 | 2022-08-24 17:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 33/415V 500MVA auxiliary |  | 2022-08-24 17:06 |  |  | new connection | 0 | 0 | No interruption
Khulna(S) | 230 kV Bus-1 | 2022-08-26 07:09 | 2022-08-26 09:40 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2022-08-27 07:07 | 2022-08-27 07:07 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(N) | 132/33 kV transformer T5 | 2022-08-27 09:25 | 2022-08-27 13:34 | 4:09 | S/O | Due to C/M work | 10 | 41.5 | Power interruption
Gopalganj(O) | 132/33 kV transformer T2 | 2022-08-29 10:16 | 2022-08-29 18:41 | 8:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T2 | 2022-08-29 10:39 | 2022-08-29 14:41 | 4:02 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-08-29 16:17 | 2022-08-29 18:51 | 2:34 | S/O | Due to C/M work | 20 | 51.3333 | Power interruption
Khulna(C) | 132/33 kV transformer T1 | 2022-08-29 16:35 | 2022-08-29 17:10 | 0:35 | S/O | Due to C/M work by WZPDCO | 15 | 8.75 | Power interruption
Payra | 132/33 kV transformer T1 | 2022-08-31 10:20 | 2022-08-31 10:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-A | 2022-08-31 10:30 | 2022-08-31 10:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 47:56 |  | Unserved Energy : |  | 533.6333
HVDC Grid Circle
Shahjadpur | 132/33 kV transformer T3 | 2022-08-01 17:46 | 2022-08-01 18:37 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-08-01 08:36 | 2022-08-01 22:34 | 13:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bharamara GK | 132/33 kV transformer T2 with 33 kV Bus-2 | 2022-08-10 10:31 | 2022-08-10 11:35 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
G.K | 132/33 kV transformer T2 | 2022-08-14 14:16 | 2022-08-14 16:32 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Ishurdi | 132/33 kV transformer T2 | 2022-08-22 06:49 | 2022-08-22 08:49 | 2:00 | S/O | Due to 33 kV feeder maint.work | 20 | 40 | Power interruption
Bottail | 132/33 kV transformer T1 | 2022-08-24 06:28 | 2022-08-24 06:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | 20DF12 filter | 2022-08-24 13:11 | 2022-08-24 13:55 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV transformer T3 |  | 2022-08-24 00:08 |  | S/O | After maint.work | 0 | 0 | No interruption
G.K | 132/33 kV transformer T1 |  | 2022-08-25 15:34 |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-08-25 16:58 | 2022-08-25 17:23 | 0:25 | S/O | Due to 33 kV Bus problem | 0 | 0 | No interruption
|  |  | Total : | 21:18 |  | Unserved Energy : |  | 40
Bogura Grid Circle:
Bogura | 230/132 kV transformer T3 | 2022-08-03 09:02 | 2022-08-03 10:28 | 1:26 | S/O | Due to C/M work | 55 | 78.8333 | Power interruption
Jaldhaka | 132 kV capacitor bank | 2022-08-03 10:37 | 2022-08-03 10:37 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T4 | 2022-08-06 05:20 | 2022-08-06 05:20 | 0:00 | S/O | Due to maint.by NESCO | 0 | 0 | No interruption
Mohastanghor | 132/33 kV transformer T1 | 2022-08-07 11:25 | 2022-08-07 12:17 | 0:52 | S/O | Due to C/M work | 30 | 26 | Power interruption
Niamatpur | 132/33 kV transformers T1 & T2 with 33 kV Bus | 2022-08-07 09:45 | 2022-08-07 10:54 | 1:09 | S/O | Due to Y-phase 33 kV Bus problem | 25 | 28.75 | Power interruption
Mithapukur | 132/33 kV transformer T2 | 2022-08-08 10:37 | 2022-08-08 12:32 | 1:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T2 | 2022-08-09 06:04 | 2022-08-09 06:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 with 33 kV Bus | 2022-08-10 15:14 | 2022-08-10 16:28 | 1:14 | S/O | Due to C/M work | 12 | 14.8 | Power interruption
Palashbari | 132/33 kV transformer T3 | 2022-08-10 16:29 | 2022-08-10 18:25 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Joypurhat | 132/33 kV transformer T2 | 2022-08-12 10:33 | 2022-08-12 11:52 | 1:19 | S/O | Due to maint.of 33 kV feeder | 14 | 18.4333 | Power interruption
| 132/33 kV transformer T3 | 2022-08-12 10:45 | 2022-08-12 11:53 | 1:08 | S/O
Bogura(O) | 132/33 kV transformer T4 | 2022-08-17 07:09 | 2022-08-17 07:09 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-08-17 08:56 | 2022-08-17 10:48 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV transformer T2 | 2022-08-17 12:10 | 2022-08-17 14:22 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 230/132 kV transformer T-2 |  | 2022-08-18 09:12 |  | S/O | After.maint.work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T2 |  | 2022-08-18 08:08 |  | S/O |  | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T3 | 2022-08-19 06:25 | 2022-08-21 22:51 | 64:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Niamatpur | 132/33 kV transformer T1 | 2022-08-19 23:12 | 2022-08-20 00:27 | 1:15 | S/O | Due to C/M work | 36 | 45 | Power interruption
Natore | 132/33 kV transformer T3 | 2022-08-20 07:52 | 2022-08-20 10:55 | 3:03 | S/O |  | 13 | 39.65 | Power interruption
Purbasadipur | 132/33 kV transformers T1 & T2 | 2022-08-22 05:58 | 2022-08-22 11:45 | 5:47 | S/O | Due to installation work | 40 | 81.3333 | Power interruption 05:58 to 8:30
| 132/33 kV transformer T2 | 2022-08-22 09:39 | 2022-08-22 11:45 | 2:06 | S/O | Due to C/M work | 40 | 84 | Power interruption
Bogura(O) | 132/33 kV transformer T2 | 2022-08-23 09:10 | 2022-08-23 12:35 | 3:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV transformer T1 | 2022-08-23 12:13 | 2022-08-23 14:21 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T4 with 33 kV Bus | 2022-08-24 11:30 | 2022-08-24 14:12 | 2:42 | S/O | Due to C/M work | 18 | 48.6 | Power interruption
Niamatpur | 132/33 kV transformer T1 | 2022-08-29 20:52 | 2022-08-29 22:05 | 1:13 | S/O | Due to C/M work | 20 | 24.3333 | Power interruption
Rajshahi(N) | 230/132 kV transformer ATR-01 | 2022-08-31 09:41 | 2022-08-31 10:26 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer ATR-02 | 2022-08-31 10:33 | 2022-08-31 11:14 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 102:34 |  | Unserved Energy : |  | 489.7333
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 419:42 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: August2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi -Kodda P/S 230 kV Ckt | 2022-08-01 12:43 | 2022-08-01 17:18 | 4:35 | S/O | Due to DFDR work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 V Ckt-2 | 2022-08-02 10:25 | 2022-08-02 19:38 | 9:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi -Kodda P/S 230 kV Ckt | 2022-08-02 10:44 | 2022-08-02 17:15 | 6:31 | S/O | Due to DFDR work | 0 | 0 | No interruption
| Tongi -Kaliakoir 230 kV Ckt | 2022-08-02 16:13 | 2022-08-02 16:56 | 0:43 | S/O | Due to protection test | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-2 | 2022-08-03 09:11 | 2022-08-03 13:38 | 4:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi -Gazipur Summit P/P 230 kV Ckt | 2022-08-03 12:50 | 2022-08-03 17:54 | 5:04 | S/O | Due to DFDR work | 0 | 0 | No interruption
| Tongi -Gazipur Summit P/P 230 kV Ckt | 2022-08-04 14:45 | 2022-08-04 19:17 | 4:32 | S/O | Due to DFDR work | 0 | 0 | No interruption
| Tongi -Kaliakoir 230 kV Ckt | 2022-08-04 14:50 | 2022-08-04 19:09 | 4:19 | S/O | Due to DFDR work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2022-08-05 06:58 | 2022-08-05 06:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kodda 132 kV Ckt-1 | 2022-08-06 08:52 | 2022-08-06 19:16 | 10:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-08-06 11:04 | 2022-08-06 18:19 | 7:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi S/S | Tongi S/S-Tongi P/S 230 kV Ckt | 2022-08-07 12:55 | 2022-08-07 17:29 | 4:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2022-08-08 09:30 | 2022-08-08 12:14 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 V Ckt-2 | 2022-08-08 16:50 | 2022-08-08 21:09 | 4:19 | S/O | Due to relay work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2022-08-09 06:52 | 2022-08-09 06:52 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-09 14:50 | 2022-08-09 14:50 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 kV Ckt-2 | 2022-08-10 06:10 | 2022-08-10 06:10 | 4:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-1 | 2022-08-10 09:18 | 2022-08-10 16:52 | 7:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-10 06:25 | 2022-08-10 06:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid 132 kV Ckt-1 | 2022-08-11 12:35 | 2022-08-11 22:38 | 10:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-12 06:40 | 2022-08-12 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-2 | 2022-08-12 06:44 | 2022-08-12 06:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-13 06:31 | 2022-08-13 06:31 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-08-13 10:15 | 2022-08-13 17:15 | 7:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-14 05:58 | 2022-08-14 05:58 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milgate 132 kV Ckt-1 | 2022-08-14 11:21 | 2022-08-14 15:48 | 4:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-16 05:49 | 2022-08-16 05:49 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV Ckt-2 | 2022-08-16 09:52 | 2022-08-16 17:23 | 7:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Tongi milgate 132 kV Ckt-1 | 2022-08-16 12:30 | 2022-08-16 17:11 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2022-08-17 06:19 | 2022-08-17 06:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kalikoir 230 kV Ckt | 2022-08-17 10:42 | 2022-08-18 04:48 | 18:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-1 | 2022-08-20 09:11 | 2022-08-20 13:55 | 4:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 kV Ckt-2 | 2022-08-22 06:36 | 2022-08-22 06:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kodda-Kabirpur 132 kV Ckt-2 | 2022-08-23 06:12 | 2022-08-23 06:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV Ckt-1 | 2022-08-25 07:25 | 2022-08-25 07:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2022-08-26 06:02 | 2022-08-26 06:02 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV Ckt-1 | 2022-08-29 06:05 | 2022-08-29 08:40 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2022-08-29 09:58 | 2022-08-29 11:25 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi S/S | Tongi 230 S/S-Tongi P/S 132 kV Ckt | 2022-08-31 09:25 | 2022-08-31 13:40 | 4:15 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 145:22 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Sonargaon | Sonargaon-Haripur 132 kV Ckt-1 | 2022-08-02 09:52 | 2022-08-02 12:40 | 2:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sonargaon-Haripur 132 kV Ckt-2 | 2022-08-02 12:41 | 2022-08-02 13:47 | 1:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV Ckt-2 | 2022-08-02 15:18 | 2022-08-02 16:22 | 1:04 | S/O | Due to SCADA work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV Ckt-2 | 2022-08-03 15:29 | 2022-08-03 17:18 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Aftabnagar 132 kV Ckt-1 | 2022-08-04 11:36 | 2022-08-04 15:36 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 | 2022-08-04 18:16 | 2022-08-06 21:16 | 51:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-1 | 2022-08-05 06:58 | 2022-08-05 06:58 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Sonargaon Orion P/P 132 kV Ckt | 2022-08-05 14:04 | 2022-08-05 14:44 | 0:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt-2 | 2022-08-07 10:25 | 2022-08-07 15:04 | 4:39 | S/O | Due to C/M work | 0 | 0 | No interruption
| Haripur-Sonargaon 132 kV Ckt-1 | 2022-08-07 15:15 | 2022-08-07 17:07 | 1:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Munshiganj | Munshiganj-Madanganj 132 kV Ckt-2 | 2022-08-08 09:51 | 2022-08-08 17:19 | 7:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Aftabnagar 132 kV Ckt-2 | 2022-08-08 10:47 | 2022-08-08 16:48 | 6:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt | 2022-08-10 08:58 | 2022-08-10 13:06 | 4:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-1 | 2022-08-10 13:54 | 2022-08-10 16:44 | 2:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV Ckt-2 | 2022-08-10 16:48 | 2022-08-10 18:03 | 1:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-1 | 2022-08-11 12:05 | 2022-08-11 13:26 | 1:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | Agargaon-Satmosjid 132 kV Ckt-2 | 2022-08-14 09:33 | 2022-08-14 11:50 | 2:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-1 | 2022-08-17 07:55 | 2022-08-17 14:11 | 6:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal GIS | Ghorashal GIS-Ghorashal #04 230 kV Ckt | 2022-08-17 11:49 | 2022-08-17 16:53 | 5:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakyha 132 kV Ckt | 2022-08-19 06:05 | 2022-08-19 08:42 | 2:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Sitalakyha 132 kV Ckt | 2022-08-19 08:44 | 2022-08-19 08:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kamrangirchar 132 kV Ckt |  | 2022-08-19 10:09 |  | S/O | After maint.work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV Ckt-2 | 2022-08-21 08:12 | 2022-08-21 13:15 | 5:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Rahim Steel 132 kV Ckt | 2022-08-21 13:09 | 2022-08-21 14:54 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur(N) 132 kV Ckt-2 | 2022-08-22 06:48 | 2022-08-22 06:48 | 0:00 | S/O | Due to maint.by DPDC | 0 | 0 | No interruption
Haripur | Haripur-Meghnaghat 230 kV Ckt-2 mid CB | 2022-08-24 09:36 | 2022-08-24 13:16 | 3:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Kazla 132 kV Ckt-2 | 2022-08-29 10:13 | 2022-08-29 17:25 | 7:12 | S/O | Due to replacement work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-2 | 2022-08-31 12:04 | 2022-08-31 13:01 | 0:57 | S/O |  | 0 | 0 | No interruption
|  |  | total | 126:52 |  |  |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Raozan 230 kV Ckt-2 | 2022-08-02 08:25 | 2022-08-02 17:31 | 9:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Juldah 132 kV Ckt | 2022-08-16 08:28 | 2022-08-16 16:25 | 7:57 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sikalbaha-Juldah 132 kV Ckt | 2022-08-17 08:24 | 2022-08-17 16:52 | 8:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-08-23 08:20 | 2022-08-23 13:16 | 4:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-08-23 10:28 | 2022-08-23 10:28 | 0:00 | S/O | Due to protection test | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazri 132 kV Ckt-1 | 2022-08-24 06:14 | 2022-08-24 06:14 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 30:27 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2022-08-02 06:38 | 2022-08-02 06:38 | 0:00 | S/O | Due to right of way | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-08-03 09:11 | 2022-08-03 13:38 | 4:27 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV Ckt-1 | 2022-08-03 14:51 | 2022-08-03 15:12 | 0:21 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV Ckt-1 | 2022-08-10 09:01 | 2022-08-10 23:49 | 14:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 kV Ckt | 2022-08-13 09:05 | 2022-08-13 09:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Kachua 132 kV Ckt | 2022-08-13 09:00 | 2022-08-13 09:00 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Cumilla(S)-Kachua 132 kV Ckt | 2022-08-13 09:50 | 2022-08-13 15:10 | 5:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| Cumilla(S)-Kachua 132 kV Ckt | 2022-08-13 09:56 | 2022-08-13 15:21 | 5:25 | S/O | Due to D/W work | 0 | 0 | No interruption
BSRM | BSRM-GPH 230 kV Ckt | 2022-08-18 17:24 | 2022-08-18 18:38 | 1:14 | S/O | Due to tree trimming | 0 | 0 | No interruption
Ashuganj(N) | Ashuganj(N)-Bhulta 400 kV Ckt-1 | 2022-08-21 09:13 | 2022-08-21 20:43 | 11:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur Desh P/P 132 kV Ckt-1 | 2022-08-24 06:24 | 2022-08-24 06:29 | 0:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 k Ckt-1 |  | 2022-08-25 11:50 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Kachua | Kachua-Comilla(N) 132 kV Ckt | 2022-08-26 06:52 | 2022-08-26 06:52 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kachua-Comilla(S) 132 kV Ckt | 2022-08-26 06:52 | 2022-08-26 06:52 | 0:00 | S/O
Chandpur desh | Chandpur Desh -RamganjP/P 132 kV Ckt-1 | 2022-08-27 09:28 | 2022-08-27 11:29 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| Chandpur Desh -RamganjP/P 132 kV Ckt-2 | 2022-08-27 11:36 | 2022-08-27 12:49 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | Chattak-Sylhet 132 kV Ckt-1 | 2022-08-28 12:12 | 2022-08-28 13:26 | 1:14 | S/O | Due to removing bird nest | 0 | 0 | No interruption
|  |  | Total : | 47:38 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Faridpur | Faridpur -Rajbari132 kV Ckt-2 | 2022-08-01 16:38 | 2022-08-01 17:35 | 0:57 | S/O | Due to emergency tree trimming | 0 | 0 | No interruption
Gopalganj | Gopalganj-Rampal 400 kV Ckt-1 | 2022-08-13 09:28 | 2022-08-13 09:28 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Barisal 132 kV Ckt-2 | 2022-08-14 21:11 | 2022-08-14 22:25 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Rampal 230 kV Ckt-1 | 2022-08-16 07:20 | 2022-08-16 07:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna(S)-Rampal 230 kV Ckt-2 | 2022-08-16 12:14 | 2022-08-16 17:44 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | Rampal-Gopalganj 400 kV Ckt-1 |  | 2022-08-17 18:02 |  | S/O | after maint.work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-1 |  | 2022-08-17 17:24 |  | S/O |  | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna 330 MW 230 kV Ckt |  | 2022-08-22 11:07 |  | S/O | after maint.work | 0 | 0 | No interruption
Noapara | Noapara-Khulna© 132 kV Ckt-1 |  | 2022-08-24 11:37 |  | S/O |  | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Madaripur 132 kV Ckt-2 | 2022-08-25 08:56 | 2022-08-25 12:20 | 3:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Rampal 230 kV Ckt-2 | 2022-08-26 06:59 | 2022-08-26 10:13 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna(S)-Rampal 230 kV Ckt-1 | 2022-08-26 10:15 | 2022-08-26 16:35 | 6:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna(S)-Rampal 230 kV Ckt-2 | 2022-08-26 10:32 | 2022-08-26 16:08 | 5:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV Ckt-1 | 2022-08-27 07:43 | 2022-08-27 07:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt |  | 2022-08-27 08:25 |  | S/O | after maint.work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj P/S 132 kV Ckt | 2022-08-27 10:41 | 2022-08-27 15:57 | 5:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Gopalganj 132 kV Ckt-2 | 2022-08-27 12:12 | 2022-08-27 14:44 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampal | Rampal-Khulna(S) 230 kV Ckt-1 | 2022-08-30 10:06 | 2022-08-30 10:42 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 34:39 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-1 & 2 | 2022-08-02 17:08 | 2022-08-02 17:55 | 0:47 | S/O | Due to protection test | 0 | 0 | No interruption
Jashore | Jashore-Noapara 132 kV Ckt-2 | 2022-08-13 10:38 | 2022-08-13 18:48 | 8:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Chuadanga 132 kV Ckt | 2022-08-20 11:49 | 2022-08-20 14:22 | 2:33 | S/O | Due to C/M work | 40 | 102 | Power interruption
Pabna | Pabna-ishurdi 132 kV Ckt | 2022-08-22 10:03 | 2022-08-22 18:55 | 8:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Bhrampur 400 kV Ckt-1 | 2022-08-22 09:25 | 2022-08-22 12:56 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 23:53 |  | Unserved Energy: |  | 102
Bogura Grid Circle :
Bogura | Bogura-Sherpur 132 kV Ckt-1 | 2022-08-07 08:20 | 2022-08-07 09:46 | 1:26 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rohanpur 132 kV Ckt | 2022-08-11 09:31 | 2022-08-11 09:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rohanpur | Rohanpur-Adani Power 400 kV Ckt-2 |  | 2022-08-15 17:50 |  | S/O | new connection | 0 | 0 | No interruption
Adani Power | Adani Power-Rohanpur 400 kV Ckt-2 |  | 2022-08-15 18:33 |  | S/O |  | 0 | 0 | No interruption
Amnura | Amnura S/S -Amnura P/S 132 kV Ckt |  | 2022-08-15 16:21 |  | S/O |  | 0 | 0 | No interruption
Mohasthangar | Mohasthangar-Bogura 132 kV Ckt-2 | 2022-08-16 10:24 | 2022-08-16 13:50 | 3:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Mohasthangar 132 kV Ckt-1 | 2022-08-17 09:26 | 2022-08-17 11:52 | 2:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpr confi.P/S 132 kV Ckt | 2022-08-19 08:47 | 2022-08-19 18:23 | 9:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur-Rangpr confi.P/S 132 kV Ckt | 2022-08-19 08:48 | 2022-08-19 18:24 | 9:36 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur-Rangpr confi.P/S 132 kV Ckt-1 | 2022-08-20 08:13 | 2022-08-20 19:07 | 10:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Rangpr confi.P/S 132 kV Ckt-2 | 2022-08-20 08:16 | 2022-08-20 19:08 | 10:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Thaurgaon P/S | Thaurgaon P/S-Thakugaon S/S 132 kV Ckt-1 | 2022-08-20 11:24 | 2022-08-20 11:38 | 0:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Thaurgaon P/S-Thakugaon S/S 132 kV Ckt-2 | 2022-08-20 11:41 | 2022-08-20 11:54 | 0:13 | S/O | Due to C/M work | 0 | 0 | No interruption
| Thaurgaon P/S-Purbasadipur 132 kV Ckt-1 | 2022-08-20 10:24 | 2022-08-20 10:58 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
| Thaurgaon P/S-Purbasadipur 132 kV Ckt-2 | 2022-08-20 11:00 | 2022-08-20 11:20 | 0:20 | S/O | Due to C/M work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rohanpur 132 kV Ckt-1 | 2022-08-20 12:59 | 2022-08-20 15:00 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Bogura confi.132 kV Ckt-1 | 2022-08-26 06:05 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-HVDC 230 kV Ckt-1 | 2022-08-31 11:28 | 2022-08-31 12:01 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 52:11 |  | Unserved Energy: |  | 0
Others :
Ullon | Ullon-Dhanmondi 132 kV Ckt-2 |  | 2022-08-13 09:43 |  | S/O | After maint.work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Narinda 132 kV Ckt-1 | 2022-08-20 07:06 | 2022-08-20 07:06 |  | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 461:02 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
g) Thakurgaon P/S-Thakurgaon S/S 132 kV Ckt-1 was under shut down from 11:24 to 11:38 for C/M.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August 2022
| Area | Previous Month (July' 2022) |  |  |  | Current Month (August '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 18 | 7 | 30 | 55 | 22 | 3 | 72 | 97
2 | Dhaka (South) Grid Circle. | 19 | 8 | 25 | 52 | 12 | 8 | 44 | 64
3 | Chattogram Grid Circle. | 12 | 6 | 22 | 40 | 15 | 4 | 24 | 43
4 | Cumilla Grid Circle. | 12 | 6 | 24 | 42 | 23 | 4 | 35 | 62
5 | Khulna Grid Circle. | 11 | 13 | 30 | 54 | 20 | 11 | 46 | 77
6 | HVDC Grid Circle | 6 | 2 | 13 | 21 | 9 | 4 | 15 | 28
7 | Bogura Grid Circle. | 8 | 12 | 33 | 53 | 14 | 12 | 45 | 71
8 | Others | 0 | 0 | 0 | 0 | 9 | 0 | 2 | 11
9 | Total | 86 | 54 | 177 | 317 | 124 | 46 | 283 | 453
`
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August 2022
| Area | Previous Month (July' 2022) |  |  |  | Current Month (August '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 422.02 |  | 290 | 712.02 | 287.68 | 186.67 | 33 | 507.35
2 | Dhaka (South) Grid Circle. | 161 |  | 15.25 | 176.25 | 118.4 | 175.33 |  | 293.73
3 | Chattogram Grid Circle. | 32 |  | 70.25 | 102.25 | 160.17 | 94.5 | 202 | 456.67
4 | Cumilla Grid Circle. | 119.27 | 944.93 | 231.08 | 1295.28 | 252.55 | 60.62 | 323.82 | 636.99
5 | Khulna Grid Circle. | 216.75 | 236.95 | 189.05 | 642.75 | 93.99 | 279.62 | 533.63 | 907.24
6 | HVDC Grid Circle | 24.28 | 78.5 | 55.25 | 158.03 | 77.15 | 60.9 | 142 | 280.05
7 | Bogura Grid Circle. | 27.96 | 185.67 | 1572.86 | 1786.49 | 85.61 | 268.75 | 489.73 | 844.09
8 | Others |  |  |  | 0 |  |  |  | 0
9 | Total | 1003.28 | 1446.05 | 2423.74 | 4873.07 | 1075.55 | 1126.39 | 1724.18 | 3926.12
`
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 1 | 11 | 7 | 1 | 3 | 343.37
2 | Dhaka (South) | 5031.6 | 4 |  | 4 | 2 | 1 | 1 | 186.0333
3 | Chattogram | 2042 | 6 | 2 | 8 | 2 | 1 | 5 | 429.72
4 | Khulna | 2434 | 8 | 9 | 17 | 3 | 5 | 9 | 869.11
5 | HVDC | 5954.3 | 3 | 1 | 4 | 1 | 2 | 1 | 110.4
6 | Bogura | 3145.6 | 12 | 11 | 23 | 4 | 2 | 17 | 844.1
7 | Cumilla | 2981 | 7 | 9 | 16 | 4 | 3 | 9 | 517.45
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3300.1833
`
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.9%
4 | Khulna | 99.87%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.89% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 |  | 4 | 4 |  |  |  | 163.9833
2 | Dhaka (South) | 990.29 |  | 3 |  | 3 | 1 | 2 |  |  | 107.7
3 | Chattogram | 917 | - | 2 | - | 2 | 2 | - | - | - | 26.95
4 | Khulna | 1238.4 | - | 4 |  | 4 | 3 | 1 | - | - | 38.13
5 | HVDC | 1325 | - | 1 | 1 | 2 | - | 1 | - | 1 | 169.65
6 | Bogura | 1803.3 | - | - | - | - | - | - | - | - | -
7 | Cumilla | 1648.16 | - | 3 |  | 3 | 3 |  |  |  | 119.5333
8 | ` | - |  |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 625.9467
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.94%
2 | Dhaka (South) | 99.95%
3 | Chattogram | 99.97%
4 | Khulna | 99.91%
5 | Bheramara (HVDC) | 99.96% | [7 empty] | Executive Engineer
6 | Bogura | 99.88% | [7 empty] | Information Management Division
7 | Cumilla | 99.92% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-08-01 | 13 | - | 6 | 8hr30 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
`
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Jamalpur | 1 | 1:08 | 20 | 22.6667 | Due to tripping of 33 kV feeder fault
Mymensingh | 1 | 0:06 | 120 | 12
Dhamrai | 1 | 0:14 | 70 | 16.3333 | Due to tripping of 132/33 kV transformersT 1 & T2
Mymensingh |  | 0:08 | 134 | 17.8667
Kabirpur |  | 1:52 | 100 | 186.6667 | Due to red-hot maint 132/33 kV Transformer T1 with 33 kV Bus
Joydevpur | 1 | 0:03 | 30 | 1.5 | Due to tripping of 33 kV feeder fault
Dhamrai | 1 | 0:13 | 76 | 16.4667 | Due to tripping of 132/33 kV transformersT 1 & T2
Dhamrai | 1 | 0:06 | 82 | 8.2 | Due to tripping of 33 kV feeder fault
Manikganj | 2 | 0:36 | 40 | 24 | Due to tripping of 132/33 kV transformerT2
Rajenrapur |  | 0:08 | 35 | 4.6667 | Due to tripping of 33 kV feeder fault
Kabirpur | 1 | 0:06 | 120 | 12 | Due to tripping of Kobirpur-Kodda 132 kV Ckt-1 & 2
Kishoreganj | ` | 0:19 | 85 | 26.9167 | Due to tripping of Kishoreganj-Mymensingh 132 kV Ckt-1
Kabirpur | 3 | 0:16 | 235 | 62.6667 | Due to tripping of Kabirpur-Kodda 132 kV Ckt-2
|  | 0:18 | 208 | 62.4
|  | 1:39 | 20 | 33 | Due to S/D of 132/33 kV transformer T3
Ullon | 1 | 0:52 | 140 | 121.3333 | Due to Bursting of Y-phase CT at 132 kV full Bus
Sonargaon | 1 | 0:13 | 34 | 7.3667 | Due to tripping of 33 kV feeder fault
Sreenagar | 1 | 1:21 | 40 | 54 | Due to red-hot maint 132/33 kV Transformer T1
Hasnabad |  | 0:10 | 20 | 3.3333 | Due to tripping of Zinzira feeder fault
Siddhirganj |  | 0:35 | 60 | 35 | Due to tripping of Siddhirganj-Matuail 132 kV Ckt
Haripur | 2 | 0:34 | 93 | 52.7 | Due to tripping of Haripur-Narshingdi 132 kV Ckt
|  | 0:12 | 100 | 20 | Due to tripping of Haripur-Ullon 132 kV Ckt
Cox'sbazar | 2 | 0:11 | 65 | 11.9167 | Due to tripping of 132/33 kV transformerT3
|  | 1:24 | 30 | 42 | Due to red-hot maint 132/33 kV Transformer T3
Madunaghat | 1 | 0:57 | 70 | 66.5 | Due to tripping 132/33 kV transformer T1 & T2
Cox'sbazar | 1 | 1:18 | 40 | 52
Cox'sbazar | 1 | 0:14 | 12 | 2.8 | Due to 33 kV feeder fault
GK |  | 2:55 | 18 | 52.5 | Due to red-hot maint 132/33 kV Transformer T3
Chandraghona | 1 | 0:26 | 22 | 9.5333 | Due to tripping of Chandraghona-Rangamati 132 kV Ckt 1
Dohazari | 1 | 0:11 | 95 | 17.4167 | Due to tripping of Dohazari-Cox'sbazar 132 kV Ckt- 1
Sikalbaha | 1 | 1:52 | 15 | 28 | Due to S/D of 132/33 kV transformer T-3
Halishahar | 1 | 2:54 | 60 | 174 | Due to S/D of 33 kV Bus
Ramganj |  | 1:19 | 25 | 32.9167 | Due to red-hot maint 132/33 kV Transformer T2
B.Baria |  | 0:13 | 110 | 23.8333 | Due to tripping 132/33 kV transformers T2 & T2
Cumilla(N) | 1 | 0:16 | 55 | 14.6667 | Due to tripping 132/33 kV transformer T3
Chandpur |  | 1:28 | 22 | 32.2667 | Due to red-hot maint 132/33 kV Transformer T3
Cumilla(S) |  | 0:33 | 52 | 28.6 | Due to tripping 132/33 kV transformer T4
Cumilla(N) |  | 1:03 | 27 | 28.35 | Due to bursting of 33 kV PT
Ramganj |  | 1:06 | 30 | 33 | Due to red-hot maint 132/33 kV Transformer T2
Cumilla(S) | 2 | 0:12 | 516 | 103.2 | Due to tripping of Cumilla(S)-Chowddagram 132 kV Ckt-1 & 2
Chandpur S/S |  | 0:14 | 50 | 11.6667 | Due to tripping of Chandpur -Kachua 132 kV Ckt-1 & 2
Sylhet |  | 0:14 | 20 | 4.6667 | Due to tripping of Sylhet-Chattak 132 kV Ckt-1
Shajibazar | 2 | 1:13 | 87 | 105.85 | Due to S/D of 132/33 kV transformer T2
|  | 0:34 | 40 | 22.6667 | Due to S/D of 132/33 kV transformer T4
Chaddagram | 1 | 1:59 | 22 | 43.6333 | Due to S/D of 132/33 kV transformer T1
Chandpur |  | 2:31 | 10 | 25.1667 | Due to S/D of 132/33 kV transformer T1
Cumilla(S) | 2 | 2:42 | 22 | 59.4 | Due to S/D of 132/33 kV transformer T2
|  | 0:16 | 80 | 21.3333 | Due to S/D of 132/33 kV transformer T-1
Kulaura |  | 0:42 | 36 | 25.2
Feni | 2 | 1:44 | 5 | 8.6667 | Due to S/D of 132/33 kV transformer T-1
|  | 0:21 | 34 | 11.9
Gallamari | 2 | 0:47 | 40 | 31.3333 | Due to 33 kV feeder fault
Bhandaria |  | 0:06 | 12 | 1.2
| 1 | 0:53 | 15 | 13.25 | Due to red-hot maint of 132/33 kV Transformer T2
Gopalganj | 1 | 0:10 | 47 | 7.8333 | Due to 33 kV feeder fault
Gallamari | 1 | 0:20 | 50 | 16.6667 | Due to bursting of CT at 33 kV side
Madaripur |  | 1:02 | 21 | 21.7 | Due to red-hot maint of 132/33 kV Transformer T2
Khulna(C) | 1 | 0:31 | 30 | 15.5 | Due to tripping 132/33 kV transformer T3
Patuakhali | 1 | 2:24 | 95 | 228 | Due to red-hot maint of 132/33 kV Transformer T3 | 4068.5833
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:August 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Barisal | 1 | 0:05 | 75 | 6.25 | Due to tripping of Barisal-Patuakhali 132 kV Ckt
Bhandaria | 1 | 0:05 | 21 | 1.75 | Due to tripping of Bhandaria-Baisal 132 kV Ckt
Barisal | 1 | 2:17 | 4 | 9.1333 | Due to tripping of Barisal-Bhandaia 132 kV Ckt-1
Barisal(S) | 1 | 0:14 | 90 | 21 | Due to tripping of Barisal-Patuakhali 132 kV Ckt
Norail | 1 | 0:53 | 10 | 8.8333 | Due to S/D of 132/33 kV transformer T-2
Shariatpur | 1 | 1:19 | 10 | 13.1667 | Due to S/D of 132/33 kV transformer T-1
Bagerhat | 2 | 0:39 | 10 | 6.5 | Due to S/D of 132/33 kV transformer T-2
Bagerhat |  | 8:39 | 35 | 302.75 | Due to S/D of 132/33 kV transformers T-1 & T2
Barisal(N) | 1 | 1:20 | 27 | 36 | Due to S/D of 132/33 kV transformer T-5
Bagerhat | 1 | 1:48 | 36 | 64.8 | Due to S/D of 132/33 kV transformer T-3
Barisal(N) | 1 | 4:09 | 10 | 41.5 | Due to S/D of 132/33 kV transformer T-5
Bagerhat | 1 | 2:34 | 20 | 51.3333 | Due to S/D of 132/33 kV transformer T-1
Khulna(C) | 1 | 0:35 | 15 | 8.75
Jhenaidah | 1 | 2:07 | 22 | 57.5667 | Due to red-hot maint of 132/33 kV Transformer T2
Shahjadpur | 1 | 0:20 | 10 | 3.3333 | Due to red-hot maint of 132/33 kV Transformer T3
Jashore | 2 | 0:19 | 30 | 9.5 | Due to tripping 132/33 kV transformer T1
|  | 0:41 | 99 | 67.65 | Due to tripping of Jashore-Noapara 132 kV Ckt-1 & 2
Ishurdi | 1 | 2:00 | 20 | 40 | Due to S/D of 132/33 kV transformer T-2
Jhenaidah | 1 | 2:33 | 40 | 102 | Due to S/D ofJhenaidah-Chuadanga 132 kV Ckt
Niyamatpur | 1 | 1:23 | 24 | 33.2 | Due to red-hot maint of 132/33 kV Transformer T1
Bogura | 1 | 0:36 | 55 | 33 | Due to 33 kV feeder fault
Rangpur | 1 | 2:15 | 30 | 67.5 | Due to red-hot maint of 132/33 kV Transformer T1
Natore | 1 | 2:11 | 15 | 32.75 | Due to red-hot maint of 132/33 kV Transformer T3
Rangpur | 1 | 1:23 | 40 | 55.3333 | Due to red-hot maint of 132/33 kV Transformer T2
Purbasadipur | 1 | 0:23 | 79 | 30.2833 | Due to 33 kV feeder fault
Sherpur(Bogura) | 1 | 0:20 | 25 | 8.3333
Naogaon | 1 | 1:49 | 35 | 63.5833 | Due to red-hot maint of 132/33 kV Transformer T1
Rajshahi(N) | 1 | 1:01 | 8 | 8.1333 | Due to red-hot maint of 132/33 kV Transformer T2
Kuriagram | 1 | 0:20 | 42 | 14 | Due to tripping 132/33 kV transformers T1 & T2
Bogura(O) | 2 | 1:39 | 5 | 8.25 | Due to red-hot maint of 132/33 kV Transformer T1
|  | 1:26 | 55 | 78.8333 | Due to S/D of 230/132 kV transformer T3
Mohastanghor | 1 | 0:52 | 30 | 26 | Due to S/D of 230/132 kV transformer T1
Niamatpur | 1 | 1:09 | 25 | 28.75 | Due to S/D of 132/33 kV transformers T1 & T2
Naogaon | 1 | 1:14 | 12 | 14.8 | Due to S/D of 132/33 kV transformer T2
Joypurhat | 1 | 1:19 | 14 | 18.4333
Niamatpur | 1 | 1:15 | 36 | 45 | Due to S/D of 132/33 kV transformer T1
Natore | 1 | 3:03 | 13 | 39.65 | Due to S/D of 132/33 kV transformer T3
Purbasadipur | 2 | 5:47 | 40 | 81.3333 | Due to S/D of 132/33 kV transformers T1 & T2
|  | 2:06 | 40 | 84 | Due to S/D of 132/33 kV transformer T2
Barapukuria | 1 | 2:42 | 18 | 48.6 | Due to S/D of 132/33 kV transformer T4
Niamatpur | 1 | 1:13 | 20 | 24.3333 | Due to S/D of 132/33 kV transformer T1
| Total Unserved energy : |  |  | 3926.1333 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August '2022
Sl. No | Name of the Sub-station | Date and Time | MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2022-08-18 16:00 | 36
2 | Agargaon 230/132kV Grid Sub-Station | 2022-08-03 09:00 | 106
3 | Agrabad 132/33kV Grid Sub-Station | 2022-08-03 17:00 | 82
4 | AKS 132/33kV Grid Sub-Station | 2022-08-11 08:00 | 21
5 | AKSML 230/33kV Grid Sub-Station | 2022-08-28 05:00 | 159
6 | Amnura 132/33kV Grid Sub-Station | 2022-08-12 21:00 | 67
7 | Ashuganj 230/132/33kV Sub-Station | 2022-08-25 01:00 | 79
8 | Bagerhat 132/33kV Grid Sub-Station | 2022-08-23 20:00 | 104
9 | Bakulia 132/33kV Grid Sub-Station | 2022-08-02 18:00 | 138
10 | Banani 132/33kV Grid Sub-Station | 2022-08-28 11:00 | 79
11 | Bangabhaban 132/33kV Grid Sub-Station | 2022-08-21 11:00 | 24
12 | Barapukuria 230/132/33kV Grid Sub-Station | 2022-08-18 22:00 | 60
13 | Barguna 132/33kV Grid Sub-Station | 2022-08-01 23:00 | 22
14 | Barishal 132/33kV Grid Sub-Station | 2022-08-17 23:00 | 120
15 | Barishal 230/132kV Grid Sub-Station | 2022-08-09 | 90
16 | Baroaulia 132/33kV Grid Sub-Station | 2022-08-03 04:00 | 83
17 | Baroirhat 132/33kV Grid Sub-Station | 2022-08-07 21:00 | 68
18 | Bashundhara 132/33kV Grid Sub-Station | 2022-08-22 18:30 | 178
19 | BashundharaCement 132/33kV Sub-Station | 2022-08-08 04:00 | 13
20 | Beanibazar 132/33kV Grid Sub-Station | 2022-08-08 22:00 | 76
21 | Benapole 132/33kV Grid Sub-Station | 2022-08-26 22:00 | 58
22 | Bhaluka 132/33kV Grid Sub-Station | 2022-08-19 20:00 | 140
23 | Bhandaria 132/33kV Grid Sub-Station | 2022-08-01 23:00 | 53.3
24 | Bhangura 132/33kV Grid Sub-Station | 2022-08-27 19:30 | 38
25 | Bheramara(GK) 132/33kV Grid Sub-Station | 2022-08-13 21:00 | 79
26 | Bhulta 132/33kV Grid Sub-Station | 2022-08-01 09:00 | 263
27 | Bog-Sherpur 132/33kV Grid Sub-Station | 2022-08-18 21:00 | 72
28 | Bogura 132/33kV Grid Sub-Station | 2022-08-26 23:00 | 179
29 | Borhanuddin 230/33kV Grid Sub-Station | 2022-08-19 01:00 | 238
30 | Brahmanbaria 132/33kV Grid Sub-Station | 2022-08-29 21:00 | 192
31 | BSRM 230/33kV Grid Sub-Station | 2022-08-28 17:00 | 169
32 | Cantonment 132/33kV GIS Grid Sub-Station | 2022-08-18 19:00 | 170
33 | Chandpur 132/33kV Grid Sub-Station | 2022-08-26 23:00 | 72
34 | Chandraghona 132/33kV Grid Sub-Station | 2022-08-04 19:00 | 38
35 | Chapai 132/33kV Grid Sub-Station | 2022-08-13 21:00 | 77
36 | Charsaidpur 132/33kV Sub-Station | 2022-08-28 21:00 | 51
37 | Chauddagram 132/33kV Grid Sub-Station | 2022-08-21 22:00 | 65
38 | Chhatak 132/33kV Grid Sub-Station | 2022-08-20 19:30 | 37
39 | Chowmuhani 132/33kV Grid Sub-Station | 2022-08-26 23:00 | 214
40 | Chuadanga 132/33kV Grid Sub-Station | 2022-08-27 20:00 | 113
41 | Coxsbazar 132/33kV Grid Sub-Station | 2022-08-06 20:00 | 124
42 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2022-08-26 16:00 | 255
43 | Cumilla(S) 132/33kV Grid Sub-Station | 2022-08-07 15:00 | 182
44 | Daudkandi 132/33kV Grid Sub-Station | 2022-08-07 19:00 | 159
45 | Dhaka University 132/33kV Grid Sub-Station | 2022-08-31 12:00 | 50
46 | Dhamrai 132/33kV Grid Sub-Station | 2022-08-28 19:00 | 130
47 | Dhanmondi 132/33kV Grid Sub-Station | 2022-08-07 16:00 | 160.1
48 | Dohazari 132/33kV Grid Sub-Station | 2022-08-08 20:00 | 104
49 | Faridpur 132/33kV Grid Sub-Station | 2022-08-25 23:00 | 165
50 | Fatullah 132/33kV Grid Sub-Station | 2022-08-21 10:00 | 77
51 | Fenchuganj 230/132/33kV Grid Sub-Station | 2022-08-20 22:00 | 55
52 | Feni 132/33kV Grid Sub-Station | 2022-08-20 19:00 | 124
53 | Ghorashal 132/33kV Sub-Station | 2022-08-29 02:00 | 153
Page: 2/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August '2022
Sl. No | Name of the Sub-station | Date and Time | MW
54 | Goalpara 132/33kV Grid Sub-Station | 2022-08-18 21:00 | 36
56 | Gollamari 132/33kV Grid Sub-Station | 2022-08-15 13:00 | 62
57 | Gopalganj 132/33kV Grid Sub-Station | 2022-08-30 19:00 | 113.6
58 | GPH 230/33kV Grid Sub-Station | 2022-08-31 12:00 | 102
59 | Gulshan 132/33kV Grid Sub-Station | 2022-08-16 17:00 | 138
60 | Halishahar 132/33kV Grid Sub-Station | 2022-08-31 11:00 | 99
61 | HaripurSBU 132/33kV Sub-Station | 2022-08-27 23:00 | 165
62 | Hasnabad 132/33kV Grid Substation | 2022-08-18 21:00 | 112
63 | Hathazari 230/132/33kV Grid Sub-Station | 2022-08-02 19:00 | 108
64 | Ishurdi 132/33kV Grid Sub-Station | 2022-08-29 19:00 | 84
65 | Jaldhaka 132/33kV Grid Sub-Station | 2022-08-20 23:00 | 74
66 | Jamalpur 132/33kV Grid Sub-Station | 2022-08-15 20:00 | 157
67 | Jashore 132/33kV Grid Sub-Station | 2022-08-26 22:00 | 139
68 | Jhenaidah 132/33kV Grid Sub-Station | 2022-08-27 21:00 | 133
69 | Joydebpur 132/33kV Grid Sub-Station | 2022-08-28 19:30 | 218
70 | Joypurhat 132/33kV Grid Sub-Station | 2022-08-18 21:00 | 70
71 | Juldah 132/33kV Grid Sub-Station | 2022-08-04 13:00 | 33
72 | Kabirpur 132/33kV Grid Sub-Station | 2022-08-22 19:00 | 285
73 | Kachua 132/33kV Grid Sub-Station | 2022-08-21 21:00 | 82
74 | Kallyanpur 132/33kV Grid Sub-Station | 2022-08-29 16:00 | 135
75 | Kalurghat 132/33kV Grid Sub-Station | 2022-08-22 10:00 | 36
76 | Kamrangirchar 132/33kV Grid Sub-Station | 2022-08-25 13:00 | 64
77 | Kaptai 132/33kV Sub-Station | 2022-08-03 19:00 | 5
78 | Kazla 132/33kV Grid Sub-Station | 2022-08-31 17:00 | 99
79 | Keranigonj 230/132/33kV Grid Sub-Station | 2022-08-25 19:00 | 124
80 | Khagrachori 132/33kV Grid Sub-Station | 2022-08-02 19:00 | 30
81 | Khulna (C) 132/33kV Grid Sub-Station | 2022-08-27 20:00 | 101
82 | Khulshi 132/33kV Grid Sub-Station | 2022-08-22 18:00 | 193
83 | Kishoreganj 132/33kV Grid Sub-Station | 2022-08-19 19:30 | 154
84 | Kodda 132/33kV Grid Sub-Station | 2022-08-18 20:00 | 333
85 | KSRM 132/33kV Grid Sub-Station | 2022-08-22 11:00 | 40
86 | Kulaura 132/33kV Grid Sub-Station | 2022-08-12 23:00 | 56
87 | Kurigram 132/33kV Grid Sub-Station | 2022-08-17 19:00 | 78
88 | Kushtia 132/33kV Grid Sub-Station | 2022-08-18 19:00 | 162
89 | Lalbag 132/33kV Grid Sub-Station | 2022-08-28 11:00 | 105
90 | Lalmonirhat 132/33kV Grid Sub-Station | 2022-08-07 21:00 | 54
91 | Madanganj 132/33kV Grid Sub-Station | 2022-08-26 23:00 | 98
92 | Madaripur 132/33kV Grid Sub-Station | 2022-08-31 22:00 | 116
93 | Madartek 132/33kV Grid Sub-Station | 2022-08-30 23:00 | 100
94 | Madunaghat 132/33kV Grid Sub-Station | 2022-08-07 | 73
95 | Magura 132/33kV Grid Sub-Station | 2022-08-12 21:00 | 64
96 | Mahasthangarh 132/33kV Grid Sub-Station | 2022-08-19 | 78
97 | Manikganj 132/33kV Grid Sub-Station | 2022-08-07 21:00 | 102
98 | Maniknagar 132/33kV Grid Sub-Station | 2022-08-29 13:00 | 86
99 | Matarbari 132/33kV Sub-Station | 2022-08-01 19:00 | 46
100 | Matuail 132/33kV Grid Sub-Station | 2022-08-30 10:00 | 71
101 | Millgate Tongi 132/33kV Grid Sub-Station | 2022-08-25 10:00 | 78
101 | Mirpur 132/33kV Grid Sub-Station | 2022-08-27 19:00 | 150
102 | Mirsorai 230/33kV Grid Sub-Station | 2022-08-01 19:00 | 2.4
Page: 3/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August '2022
Sl. No | Name of the Sub-station | Date and Time | MW
103 | Mithapukur 132/33kV Grid Sub-Station | 2022-08-31 20:00 | 44
104 | Modern Steel 132/11kV Grid Sub-Station | 2022-08-01 | 0
105 | Mogbazar 132/33kV Grid Sub-Station | 2022-08-31 17:00 | 142
106 | Mongla 132/33kV Grid Sub-Station | 2022-08-07 11:00 | 36
107 | Motijheel 132/33kV Grid Sub-Station | 2022-08-31 15:00 | 41
108 | Munshiganj 132/33kV Grid Sub-Station | 2022-08-30 21:00 | 116
109 | Mymensingh 132/33kV Grid Sub-Station | 2022-08-13 19:30 | 250
110 | Naogaon 132/33kV Grid Sub-Station | 2022-08-12 22:00 | 136
111 | Narail 132/33kV Grid Sub-Station | 2022-08-05 22:00 | 48
112 | Narinda 132/33kV Grid Sub-Station | 2022-08-31 17:00 | 80
113 | Narshingdi 132/33kV Grid Sub-Station | 2022-08-07 23:00 | 208
114 | Natore 132/33kV Grid Sub-Station | 2022-08-18 20:00 | 160
115 | Nawabganj 132/33kV Grid Sub-Station | 2022-08-22 22:00 | 61.5
116 | Netrakona 132/33kV Grid Sub-Station | 2022-08-15 20:00 | 136
117 | New Tongi 132/33kV Grid Sub-Station | 2022-08-29 16:00 | 88.8
118 | Niamatpur 132/33kV Grid Sub-Station | 2022-08-18 08:00 | 92
119 | Noapara 132/33kV Grid Sub-Station | 2022-08-08 19:30 | 56
120 | Pabna 132/33kV Grid Sub-Station | 2022-08-25 21:00 | 119
121 | Palashbari 132/33kV Grid Sub-Station | 2022-08-26 23:00 | 142
122 | Panchagarh 132/33kV Grid Sub-Station | 2022-08-26 22:00 | 69
123 | Patuakhali 132/33kV Grid Sub-Station | 2022-08-07 23:00 | 136
124 | Payra 400/132/33kV Grid Sub-Station | 2022-08-02 10:00 | 1.14
125 | PHP 132/33kV Sub-Station | 2022-08-07 10:00 | 10
126 | Postogola 132/33kV Grid Sub-Station | 2022-08-06 19:00 | 48
127 | Purbachal 132/33kV Grid Sub-Station | 2022-08-18 19:00 | 19
128 | Purbasadipur 132/33kV Grid Sub-Station | 2022-08-07 22:00 | 130
129 | Rahanpur_I 400/132kV Grid Sub-Station | 2022-08-31 19:30 | 4.7
130 | Rahim Steel 132/33kV Sub-Station | 2022-08-16 16:00 | 38
131 | Rajbari 132/33kV Grid Sub-Station | 2022-08-27 22:00 | 74
132 | Rajendrapur 132/33kV Grid Sub-Station | 2022-08-07 22:00 | 114
133 | Rajshahi 132/33kV Grid Sub-Station | 2022-08-27 21:00 | 165
134 | Rajshahi 230/132/33kV Grid Sub-Station | 2022-08-21 23:00 | 45
135 | Ramganj 132/33kV Grid Sub-Station | 2022-08-26 21:00 | 132
136 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2022-08-05 23:00 | 35
137 | Rangamati 132/33kV Grid Sub-Station | 2022-08-17 19:00 | 16
138 | Rangpur 132/33kV Grid Sub-Station | 2022-08-18 20:00 | 173
139 | Ruppur 132/11kV Grid Sub-Station | 2022-08-30 08:00 | 5.2
140 | Saidpur 132/33kV Grid Sub-Station | 2022-08-07 20:00 | 114
141 | Satkhira 132/33kV Grid Sub-Station | 2022-08-30 22:00 | 132
142 | Satmasjid 132/33kV Grid Sub-Station | 2022-08-17 23:00 | 113
143 | Savar 132/33kV Grid Sub-Station | 2022-08-07 21:00 | 201
144 | Shahjadpur 132/33kV Grid Sub-Station | 2022-08-29 19:30 | 111
145 | Shahjibazar 132/33kV Grid Sub-Station | 2022-08-22 21:00 | 148
146 | Shahmirpur 132/33kV Grid Sub-Station | 2022-08-01 | 54.5
147 | Shariatpur 132/33kV Grid Sub-Station | 2022-08-29 22:00 | 84
148 | Sherpur 132/33kV Grid Sub-Station | 2022-08-15 21:00 | 156
149 | Shikalbaha 132/33kV Sub-Station | 2022-08-01 19:00 | 33
150 | Shitalakhya 132/33kV Grid Sub-Station | 2022-08-22 19:00 | 133
151 | Shyampur 132/33kV Grid Sub-Station | 2022-08-26 11:00 | 184
152 | Siddhirganj 132/33kV Grid Sub-Station | 2022-08-20 10:00 | 130
153 | Sirajganj 132/33kV Grid Sub-Station | 2022-08-23 20:00 | 126
154 | Sonargaon 132/33kV Grid Sub-Station | 2022-08-07 22:00 | 112
155 | Sreemongol 132/33kV Grid Sub-Station | 2022-08-11 21:00 | 63
156 | Srinagar 132/33kV Grid Sub-Station | 2022-08-22 21:00 | 52.23
157 | SSM 132/33kV Grid Sub-Station | 2022-08-17 | 20
158 | Sunamganj 132/33kV Grid Sub-Station | 2022-08-26 21:00 | 62
159 | Sylhet 132/33kV Grid Sub-Station | 2022-08-11 20:00 | 179
160 | Tangail 132/33kV Grid Sub-Station | 2022-08-05 21:00 | 228
161 | Thakurgaon 132/33kV Grid Sub-Station | 2022-08-07 21:00 | 90
162 | TK chemical 132kV Grid Sub-Station | 2022-08-02 22:00 | 33.7
163 | Tongi 230/132/33kV Grid Sub-Station | 2022-08-28 17:00 | 132
164 | Ullon 132/33kV Grid Sub-Station | 2022-08-07 | 57
165 | Uttara 132/33kV Grid Sub-Station | 2022-08-30 16:00 | 102
166 | UttaraNew 132/33kV Grid Sub-Station | 2022-08-17 15:00 | 40
167 | Zigatola 132/33kV Grid Sub-Station | 2022-08-31 23:00 | 71
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:August 2022
Area | MW | Date | Hour | Remarks
Dhaka | 4986.9 | 16/08/2022 | 20:00
Chattogram | 1491.3 | 21/08/2022 | 19:00
Cumilla | 1385 | 26/08/2022 | 22:00
Mymensingh | 1128 | 15/08/2022 | 20:00
Sylhet | 633 | 22/08/2022 | 22:00
Khulna | 1694.4 | 27/08/2022 | 22:00
Barishal | 551.72 | 19/08/2022 | 01:00
Rajshahi | 1496.3 | 27/08/2022 | 22:00
Rangpur | 932 | 19/08/2022 | 20:00
`
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2022
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Bhulta 400/230kV Grid Sub-Station | 400 | 396 | 2022-08-12 08:00 | 360 | 2022-08-23 12:00
2 | Bibiana 400/230kV Sub-Station | 400 | 410 | 2022-08-02 21:00 | 367 | 2022-08-09 11:00
3 | BIPTC | 400 | 407 | 2022-08-14 11:00 | 391 | 2022-08-17 19:30
4 | Gopalganj_I 400/132kV Grid Sub-Station | 400 | 418 | 2022-08-11 17:00 | 387 | 2022-08-20 23:00
5 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 394 | 2022-08-09 19:00 | 361 | 2022-08-19 20:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 226 | 2022-08-14 20:00 | 205 | 2022-08-25 09:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 237 | 2022-08-02 20:00 | 205 | 2022-08-30 09:00
3 | Aminbazar 230/132kV Grid Sub-Station | 230 | 228 | 2022-08-14 20:00 | 207 | 2022-08-27 12:00
4 | Baghabari 230/132kV Grid Sub-Station | 230 | 236 | 2022-08-11 18:30 | 224 | 2022-08-25 22:00
5 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 240 | 2022-08-01 04:00 | 207 | 2022-08-11 21:00
6 | Barishal 230/132kV Grid Sub-Station | 230 | 248 | 2022-08-14 12:00 | 219 | 2022-08-12 04:00
7 | Bheramara 230/132kV Grid Sub-Station | 230 | 252 | 2022-08-21 16:00 | 220 | 2022-08-07 09:00
8 | Bogura 230/132kV Grid Sub-Station | 230 | 231 | 2022-08-01 18:00 | 213 | 2022-08-26 01:00
9 | BSRM 230/33kV Grid Sub-Station | 230 | 234 | 2022-08-05 19:30 | 209 | 2022-08-31 13:00
10 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 229 | 2022-08-04 20:00 | 212 | 2022-08-30 09:00
11 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 243 | 2022-08-07 19:00 | 229 | 2022-08-29 16:00
12 | GPH 230/33kV Grid Sub-Station | 230 | 239 | 2022-08-03 19:00 | 209 | 2022-08-17 09:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 226 | 2022-08-12 19:00 | 209 | 2022-08-23 17:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 228 | 2022-08-14 20:00 | 204 | 2022-08-04 15:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 237 | 2022-08-07 19:00 | 210 | 2022-08-18 13:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 238 | 2022-08-11 17:00 | 224 | 2022-08-18 05:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 239 | 2022-08-10 21:00 | 215 | 2022-08-05 23:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 226 | 2022-08-14 20:00 | 205 | 2022-08-25 09:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 243 | 2022-08-11 17:00 | 219 | 2022-08-05 23:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 231 | 2022-08-02 11:00 | 210 | 2022-08-23 14:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 254 | 2022-08-07 03:00 | 213 | 2022-08-24 16:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 233 | 2022-08-01 19:30 | 218 | 2022-08-01 17:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 237 | 2022-08-31 19:30 | 219 | 2022-08-13 22:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 231 | 2022-08-27 10:00 | 210 | 2022-08-04 15:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 237 | 2022-08-02 19:30 | 209 | 2022-08-18 13:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 230 | 2022-08-12 15:00 | 207 | 2022-08-29 11:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 229 | 2022-08-12 19:00 | 211 | 2022-08-23 12:00
28 | Sirajgonj 230 kV Switching Station | 230 | 257 | 2022-08-19 21:00 | 220 | 2022-08-25 06:00
29 | Tongi 230/132/33kV Grid Sub-Station | 230 | 255 | 2022-08-12 08:00 | 206 | 2022-08-24 08:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-11 20:00 | 124 | 2022-08-28 15:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 20:00 | 121 | 2022-08-18 12:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-03 18:30 | 120 | 2022-08-17 09:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-18 23:00 | 123 | 2022-08-13 22:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 143 | 2022-08-10 12:00 | 131 | 2022-08-30 11:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-11 14:00 | 119 | 2022-08-05 23:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-06 19:00 | 120 | 2022-08-23 12:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-15 19:30 | 118 | 2022-08-29 16:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-12 19:00 | 120 | 2022-08-11 16:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-14 19:00 | 125 | 2022-08-01 22:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 142 | 2022-08-08 20:00 | 122 | 2022-08-01 22:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2022-08-02 19:00 | 120 | 2022-08-17 09:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-03 19:30 | 117 | 2022-08-25 01:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-15 19:30 | 118 | 2022-08-29 16:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 138 | 2022-08-03 02:00 | 122 | 2022-08-11 12:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-01 10:00 | 123 | 2022-08-12 20:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-11 17:00 | 123 | 2022-08-05 23:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-01 06:00 | 113 | 2022-08-13 08:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 144 | 2022-08-14 09:00 | 123 | 2022-08-22 22:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-01 11:00 | 130 | 2022-08-18 07:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-02 18:00 | 132 | 2022-08-05 22:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 126 | 2022-08-05 20:00 | 114 | 2022-08-20 11:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-01 08:00 | 121 | 2022-08-13 04:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-01 06:00 | 124 | 2022-08-18 07:00
| Page: 2/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2022
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-03 19:30 | 126 | 2022-08-23 21:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 138 | 2022-08-14 20:00 | 123 | 2022-08-26 11:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-03 23:00 | 115 | 2022-08-25 21:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 20:00 | 123 | 2022-08-31 23:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-18 23:00 | 122 | 2022-08-13 03:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 135 | 2022-08-01 19:30 | 123 | 2022-08-07 09:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-03 19:00 | 118 | 2022-08-31 06:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-01 04:00 | 122 | 2022-08-12 23:00
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-03 19:00 | 115 | 2022-08-25 01:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-11 14:00 | 121 | 2022-08-26 23:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 132 | 2022-08-03 19:00 | 113 | 2022-08-01 17:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-04 20:00 | 121 | 2022-08-29 16:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-09 19:00 | 122 | 2022-08-11 12:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-12 19:00 | 120 | 2022-08-31 14:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-10 18:30 | 116 | 2022-08-26 11:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 132.2 | 2022-08-01 20:00 | 121.5 | 2022-08-25 09:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-06 19:00 | 118 | 2022-08-17 09:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-14 18:00 | 126 | 2022-08-25 23:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-07 21:00 | 124 | 2022-08-25 09:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-03 03:00 | 120 | 2022-08-25 14:00
45 | Ghorashal 132/33kV Sub-Station | 132 | 140 | 2022-08-11 20:00 | 124 | 2022-08-04 15:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-08 15:00 | 124 | 2022-08-05 23:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-06 20:00 | 124 | 2022-08-05 23:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-13 19:00 | 130 | 2022-08-25 23:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-14 20:00 | 124 | 2022-08-04 13:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 19:00 | 120 | 2022-08-23 12:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 138 | 2022-08-06 15:00 | 120 | 2022-08-31 08:00
52 | Hasnabad 132/33kV Grid Substation | 132 | 142 | 2022-08-09 21:00 | 128 | 2022-08-04 14:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-01 18:00 | 130 | 2022-08-18 05:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-01 03:00 | 113 | 2022-08-07 21:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-09 18:00 | 114 | 2022-08-19 06:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-28 19:00 | 124 | 2022-08-05 22:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 142 | 2022-08-11 14:00 | 130 | 2022-08-05 22:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 144 | 2022-08-11 19:00 | 125 | 2022-08-24 08:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-01 08:00 | 114 | 2022-08-18 07:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 19:00 | 121 | 2022-08-30 10:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-09 19:00 | 113 | 2022-08-29 16:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-12 16:00 | 116 | 2022-08-31 04:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-13 19:30 | 122 | 2022-08-20 10:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 19:00 | 120 | 2022-08-25 10:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-13 19:00 | 126 | 2022-08-01 12:00
66 | Kaptai 132/33kV Sub-Station | 132 | 139 | 2022-08-02 18:30 | 125 | 2022-08-08 13:00
67 | Kazla 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-11 19:30 | 123 | 2022-08-01 17:00
68 | Khagrachori 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-07 19:30 | 123 | 2022-08-25 12:00
69 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-31 19:00 | 124 | 2022-08-05 23:00
70 | Khulshi 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-07 19:00 | 119 | 2022-08-18 12:00
71 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-12 23:00 | 113 | 2022-08-24 03:00
72 | Kodda 132/33kV Grid Sub-Station | 132 | 144 | 2022-08-25 19:00 | 119 | 2022-08-20 09:00
73 | KSRM 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 19:00 | 122 | 2022-08-25 14:00
74 | Kulaura 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-01 06:00 | 129 | 2022-08-12 23:00
75 | Kurigram 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-18 23:00 | 113 | 2022-08-16
76 | Kushtia 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-07 16:00 | 129 | 2022-08-26 22:00
77 | Lalbag 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-14 20:00 | 123 | 2022-08-28 13:00
78 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-01 05:00 | 113 | 2022-08-07 20:00
79 | Madanganj 132/33kV Grid Sub-Station | 132 | 133 | 2022-08-01 19:30 | 122 | 2022-08-11 12:00
80 | Madaripur 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-12 18:30 | 127 | 2022-08-22 22:00
81 | Madartek 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-14 20:00 | 124 | 2022-08-23 17:00
82 | Madunaghat 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-02 19:00 | 122 | 2022-08-30 14:00
83 | Magura 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-14 18:00 | 126 | 2022-08-05 23:00
84 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-01 17:00 | 120 | 2022-08-18 07:00
85 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-01 13:00 | 117 | 2022-08-22 14:00
86 | Maniknagar 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-14 20:00 | 123 | 2022-08-23 17:00
87 | Matarbari 132/33kV Sub-Station | 132 | 135 | 2022-08-02 15:00 | 113 | 2022-08-02 18:00
88 | Matuail 132/33kV Grid Sub-Station | 132 | 133 | 2022-08-22 02:00 | 122 | 2022-08-25 09:00
| Page:3/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: August '2022
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 132 KV Substation | kV | kV |  | kV
89 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-15 19:00 | 119 | 2022-08-29 16:00
90 | Mirpur 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-13 19:00 | 121 | 2022-08-20 11:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-20 18:00 | 116 | 2022-08-20 01:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 140 | 2022-08-06 19:00 | 120 | 2022-08-23 01:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-02 21:00 | 125 | 2022-08-04 15:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-07 15:00 | 119 | 2022-08-06 06:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-12 19:00 | 120 | 2022-08-11 14:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-02 21:00 | 123 | 2022-08-25 08:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-31 11:00 | 113 | 2022-08-19 20:00
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-01 06:00 | 115 | 2022-08-18 07:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-06 20:00 | 125 | 2022-08-05 22:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-01 04:00 | 115 | 2022-08-16 10:00
101 | Natore 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-01 18:30 | 125 | 2022-08-18 05:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-12 22:00 | 126 | 2022-08-01 09:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-05 09:00 | 113 | 2022-08-13 07:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-15 19:30 | 120 | 2022-08-29 11:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-02 18:30 | 113 | 2022-08-19 22:00
106 | Noapara 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-07 18:00 | 123 | 2022-08-05 23:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-01 18:00 | 126 | 2022-08-22 13:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-01 18:30 | 114 | 2022-08-18 06:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-02 20:00 | 113 | 2022-08-10 02:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-11 16:00 | 127 | 2022-08-01 22:00
111 | PHP 132/33kV Sub-Station | 132 | 136 | 2022-08-03 23:00 | 116 | 2022-08-31 06:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 144 | 2022-08-14 20:00 | 127 | 2022-08-01 17:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-15 19:30 | 118 | 2022-08-29 16:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-18 23:00 | 113 | 2022-08-15
115 | Rahim Steel 132/33kV Sub-Station | 132 | 133 | 2022-08-02 21:00 | 123 | 2022-08-23 17:00
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-14 18:30 | 120 | 2022-08-06 07:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-11 19:30 | 117 | 2022-08-20 09:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-18 23:00 | 123 | 2022-08-26 17:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-02 17:00 | 113 | 2022-08-31 05:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-02 19:00 | 123 | 2022-08-30 14:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-01 08:00 | 113 | 2022-08-18 07:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 139 | 2022-08-18 23:00 | 130 | 2022-08-21 14:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-01 18:30 | 114 | 2022-08-21 07:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-20 15:00 | 117 | 2022-08-05 22:00
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-14 20:00 | 124 | 2022-08-26 11:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-14 20:00 | 120 | 2022-08-20 11:00
127 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 143 | 2022-08-03 17:00 | 132 | 2022-08-10 07:00
128 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-02 19:30 | 127 | 2022-08-25 12:00
129 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-07 19:00 | 121 | 2022-08-18 12:00
130 | Shariatpur 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-13 09:00 | 126 | 2022-08-22 22:00
131 | Sherpur 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-18 23:00 | 113 | 2022-08-09 08:00
132 | Shikalbaha 132/33kV Sub-Station | 132 | 141 | 2022-08-02 19:00 | 120 | 2022-08-25 03:00
133 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 143 | 2022-08-14 20:00 | 125 | 2022-08-01 17:00
134 | Shyampur 132/33kV Grid Sub-Station | 132 | 136 | 2022-08-12 19:00 | 123 | 2022-08-07 09:00
135 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-23 08:00 | 123 | 2022-08-23 17:00
136 | Sirajganj 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-01 11:00 | 125 | 2022-08-24 21:00
137 | Sonargaon 132/33kV Grid Sub-Station | 132 | 134 | 2022-08-02 21:00 | 122 | 2022-08-23 17:00
138 | Sreemongol 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-02 12:00 | 130 | 2022-08-14 11:00
139 | Srinagar 132/33kV Grid Sub-Station | 132 | 141 | 2022-08-14 20:00 | 126 | 2022-08-02 10:00
140 | SSM 132/33kV Grid Sub-Station | 132 | 142 | 2022-08-02 19:00 | 122 | 2022-08-18 12:00
141 | Sunamganj 132/33kV Grid Sub-Station | 132 | 132 | 2022-08-01 06:00 | 118 | 2022-08-22 22:00
142 | Sylhet 132/33kV Grid Sub-Station | 132 | 135 | 2022-08-01 10:00 | 127 | 2022-08-12 21:00
143 | Tangail 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-09 18:00 | 121 | 2022-08-26 15:00
144 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-31 14:00 | 113 | 2022-08-05 08:00
145 | TK chemical 132kV Grid Sub-Station | 132 | 141 | 2022-08-07 19:00 | 122 | 2022-08-18 15:00
146 | Ullon 132/33kV Grid Sub-Station | 132 | 139 | 2022-08-14 20:00 | 124 | 2022-08-04 13:00
147 | Uttara 132/33kV Grid Sub-Station | 132 | 137 | 2022-08-21 01:00 | 121 | 2022-08-01 10:00
148 | UttaraNew 132/33kV Grid Sub-Station | 132 | 138 | 2022-08-13 19:00 | 120 | 2022-08-23 11:00
149 | Zigatola 132/33kV Grid Sub-Station | 132 | 140 | 2022-08-19 19:00 | 125 | 2022-08-01 17:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: August 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 79 | 244
Hasnabad | TR2 | 225 | 79 | 244 | 27.08.2022 | 16:00
| TR3 | 225 | 79 | 244
| TR1 | 225 | 180 | 540
Tongi | TR2 | 225 | 180 | 540 | 25.08.2022 | 16:00
| TR3 | 225 | 180 | 540
Haripur | TR1 | 225 | 125 | 370
| TR2 | 225 | 125 | 370 | 10.08.2022 | 06:00
| TR3 | 225 | 125 | 370
| TR1 | 225 | 200 | 575
Rampura | TR2 | 225 | 200 | 575 | 29.08.2022 | 16:00
| TR3 | 225 | 200 | 575
Keraniganj | ATR1 | 300 | 117 | 350
| ` | 300 | 117 | 350 | 03.08.2022 | 19:00
| ATR3 | 300 | 117 | 350
| TR1 | 225 | 170 | 526
Aminbazar | TR2 | 225 | 170 | 526 | 27.08.2022 | 11:00
| TR3 | 225 | 178 | 547
Agargaon | TR1 | 300 | 173 | 514
| TR2 | 300 | 173 | 514 | 23.08.2022 | 13:00
Maniknagar | TR1 | 300 | 155 | 490 | 19.08.2022 | 13:00
| TR2 | 300 | 155 | 490
Cumilla (N) | TR1 | 225 | 172 | 490 | 26.08.22 | 2:00
| TR2 | 225 | 170 | 488
Fenchuganj | AT2 | 300 | 212 | 578 | 22.08.22 | 22:00
| MT1 | 150 | 91 | 255
Hathazari | MT2 | 150 | 91 | 255
| MT3 | 150 | 91 | 255 | 23.08.22 | 20:00
| MT4 | 150 | 91 | 255
| TR1 | 225 | 89 | 225
Ishurdi | TR2 | 225 | 89 | 225 | 17.08.22 | 19:15
| TR3 | 225 | 89 | 225
Khulna(S) | TR1 | 225 | 100 | 262
| TR2 | 225 | 100 | 262 | 12.08.22 | 17:00
| TR3 | 300 | 130 | 340
Bogura | TR1 | 225 | 132 | 415
| TR2 | 225 | 132 | 415 | 26.08.22 | 21:00
| TR3 | 225 | 178 | 545
Baghabari | TR1 | 300 | 175 | 490 | 27.08.22 | 22:00
| TR2 | 225 | 130 | 360
Rajshahi | ATR-01 | 300 | 134 | 356
| ATR-02 | 300 | 134 | 356 | 27.08.22 | 4:00
Barapukuria | TR1 | 225 | 182 | 880 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 184 | 900 | 19.08.22 | 13:00 | 132 kV current is being provided
| TR6 | 300 | 239 | 1142
Bheramara | Transformer-1 | 225 | 78 | 217
| Transformer-2 | 225 | 78 | 217 | 17.08.2022 | 19:30
Shyampur | ATR-01 | 300 | 88 | 297
| ATR-02 | 300 | 88 | 297 | 21.08.2022 | 7:00
Kaliakoir | TR1 | 300 | 134.1 | 319 | 28.08.2022 | 18:45
Sikalbaha | ATR-1 | 300 | 178 | 533
| ATR-2 | 300 | 178 | 533 | 22.08.2022 | 18:00
Jhenaidah | T1(230/132 kV) | 300 | 172 | 366 | 26.08.2022 | 22:00
| T2(230/132 kV) | 300 | 172 | 366
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:August 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 191.5 | 331 | 23.08.2022 | 12:15
| TR2(400/230 kV) | 520 | 193.5 | 333
| TR1(400/132 kV) | 325 | 320.5 | 546 | 28.08.2022 | 22:15
| TR2(400/132 kV) | 325 | 322.5 | 549
Bibiyana | ICT1(400/230 kV) | 520 | 206 | 315 | 22.08.2022 | 21:00
| ICT2(400/230kV) | 520 | 200 | 315
Bhulta | ATR1(400/230 kV) | 520 | 355 | 601 | 01.08.2022 | 5:00
| ATR2(400/230kV) | 520 | 355 | 601
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 371 | 617.43 | 02.08.2022 | 12:01
Gopalganj | ATR1(400/138 kV) | 325 | 322 | 479 | 16.08.2022 | 21:00
| ATR2(400/138kV) | 325 | 322 | 479
Payra | GSUT1 | 270 | 660 | 888 | 16.08.2022 | 1:05
| GSUT2 | 270 | 650 | 892 | 23.08.2022 | 10:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
423

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:August 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:August 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-08-01 | 12755 | 13800 | 410 | 21:00 | 120 | 0 | 180 | 0 | 110 | 0 | 0 | 0 | 0 | - | 2022-08-01 | 10429 | 10429 | 770 | 10:00 | 180 | 93 | 150 | 85 | 110 | 78 | 34 | 0 | 40 | -
2022-08-02 | 12392 | 13800 | 1298 | 21:00 | 390 | 90 | 170 | 150 | 160 | 170 | 60 | 0 | 108 | - | 2022-08-02 | 10830 | 10830 | 525 | 10:00 | 160 | 64 | 63 | 79 | 50 | 57 | 12 | 0 | 40 | -
2022-08-03 | 12496 | 13800 | 1202 | 21:00 | 245 | 117 | 176 | 177 | 146 | 181 | 58 | 0 | 102 |  | 2022-08-03 | 10779 | 10779 | 388 | 10:00 | 143 | 34 | 49 | 63 | 33 | 27 | 7 | 0 | 32 | -
2022-08-04 | 12499 | 13800 | 1199 | 21:00 | 245 | 104 | 150 | 155 | 170 | 200 | 75 | 0 | 100 | - | 2022-08-04 | 10681 | 10681 | 663 | 10:00 | 150 | 80 | 98 | 80 | 70 | 100 | 35 | 0 | 50 | -
2022-08-05 | 12885 | 13450 | 421 | 21:00 | 40 | 0 | 66 | 65 | 75 | 110 | 0 | 0 | 65 | - | 2022-08-05 | 10438 | 10438 | 380 | 10:00 | 98 | 48 | 48 | 62 | 39 | 45 | 8 | 0 | 32 | -
2022-08-06 | 12132 | 13800 | 1537 | 21:00 | 380 | 180 | 200 | 190 | 170 | 210 | 87 | 0 | 120 | - | 2022-08-06 | 10629 | 10629 | 618 | 10:00 | 100 | 90 | 80 | 70 | 90 | 100 | 28 | 0 | 60 | -
2022-08-07 | 13227 | 14200 | 897 | 21:00 | 170 | 50 | 160 | 120 | 100 | 180 | 80 | 0 | 37 | - | 2022-08-07 | 10149 | 10149 | 1614 | 10:00 | 400 | 180 | 208 | 200 | 200 | 220 | 80 | 0 | 130 | -
2022-08-08 | 12970 | 14200 | 856.6371 | 21:00 | 223 | 0 | 128 | 147 | 100 | 141 | 0 | 0 | 117 | - | 2022-08-08 | 10946 | 10946 | 1063 | 10:00 | 393 | 122 | 121 | 140 | 94 | 99 | 24 | 0 | 70 | -
2022-08-09 | 12815 | 13400 | 539 | 21:00 | 109 | 0 | 70 | 75 | 90 | 140 | 0 | 0 | 55 | - | 2022-08-09 | 10618 | 11100 | 444 | 10:00 | 40 | 100 | 0 | 0 | 94 | 160 | 50 | 0 | 0 | -
2022-08-10 | 12397 | 13700 | 1201 | 21:00 | 231 | 0 | 160 | 202 | 230 | 290 | 22 | 0 | 66 | - | 2022-08-10 | 10291 | 11350 | 976 | 10:00 | 378 | 113 | 110 | 130 | 40 | 120 | 20 | 0 | 65 | -
2022-08-11 | 12452 | 13450 | 920 | 21:00 | 190 | 0 | 175 | 150 | 175 | 190 | 40 | 0 | 0 | - | 2022-08-11 | 10459 | 11350 | 821 | 10:00 | 250 | 140 | 80 | 30 | 100 | 140 | 30 | 0 | 51 | -
2022-08-12 | 12739 | 13250 | 471 | 21:00 | 30 | 0 | 0 | 31 | 100 | 210 | 0 | 0 | 100 | - | 2022-08-12 | 9923 | 11700 | 1638 | 10:00 | 640 | 184 | 183 | 205 | 140 | 145 | 38 | 0 | 103 | -
2022-08-13 | 12811 | 13200 | 358 | 21:00 | 0 | 0 | 0 | 0 | 0 | 255 | 45 | 0 | 58 | - | 2022-08-13 | 10554 | 12200 | 1517 | 10:00 | 589 | 171 | 170 | 191 | 130 | 135 | 35 | 0 | 96 | -
2022-08-14 | ` | 12750 | 247 | 21:00 | 60 | 0 | 0 | 0 | 0 | 187 | 0 | 0 | 0 | - | 2022-08-14 | 10279 | 10700 | 388 | 10:00 | 40 | 0 | 0 | 35 | 53 | 200 | 30 | 0 | 30 | -
2022-08-15 | 13051 | 13110 | 54 | 21:00 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | - | 2022-08-15 | 10622 | 10622 | 0 | 10:00 | - | - | - | - | - | - | - | - | - | -
2022-08-16 | 13526 | 14100 | 529 | 21:00 | 0 | 0 | 170 | 79 | 50 | 180 | 0 | 0 | 50 | - | 2022-08-16 | 11231 | 11800 | 217 | 10:00 | 20 | 67 | 0 | 0 | 0 | 130 | 0 | 0 | 0 | -
2022-08-17 | 13413 | 14200 | 725 | 21:00 | 0 | 0 | 165 | 155 | 105 | 170 | 55 | 0 | 75 | - | 2022-08-17 | 11231 | 11900 | 617 | 10:00 | 200 | 74 | 73 | 89 | 58 | 64 | 14 | 0 | 45 | -
2022-08-18 | 12946 | 13450 | 464 | 21:00 | 118 | 0 | 36 | 82 | 60 | 89 | 36 | 0 | 42 | - | 2022-08-18 | 11356 | 11900 | 501 | 10:00 | 76 | 66 | 64 | 97 | 51 | 87 | 14 | 0 | 46 | -
2022-08-19 | 12644 | 12759 | 106 | 21:00 | 0 | 0 | 0 | 0 | 0 | 106 | 0 | 0 | 0 | - | 2022-08-19 | 10658 | 11000 | 315 | 10:00 | 98 | 0 | 0 | 0 | 28 | 177 | 12 | 0 | 0 | -
2022-08-20 | 13432 | 13950 | 431 | 21:00 | 60 | 0 | 0 | 0 | 71 | 300 | 0 | 0 | 0 | - | 2022-08-20 | 10924 | 11500 | 531 | 10:00 | 50 | 180 | 0 | 0 | 61 | 200 | 40 | 0 | 0 | -
2022-08-21 | 13387 | 13950 | 657 | 21:00 | 70 | 0 | 137 | 70 | 70 | 220 | 40 | 0 | 50 | - | 2022-08-21 | 11224 | 12100 | 807 | 10:00 | 100 | 100 | 100 | 50 | 90 | 250 | 37 | 0 | 80 | -
2022-08-22 | 13371 | 14450 | 994 | 21:00 | 130 | 0 | 174 | 170 | 180 | 250 | 0 | 0 | 90 | - | 2022-08-22 | 11163 | 12300 | 1048 | 10:00 | 385 | 120 | 119 | 138 | 92 | 100 | 24 | 0 | 70 | -
2022-08-23 | 13646 | 14200 | 511 | 21:00 | 85 | 0 | 0 | 0 | 60 | 366 | 0 | 0 | 0 | - | 2022-08-23 | 11433 | 11433 | 707 | 10:00 | 80 | 44 | 0 | 60 | 40 | 403 | 30 | 0 | 50 | -
2022-08-24 | 13472 | 14100 | 579 | 21:00 | 150 | 0 | 0 | 0 | 30 | 320 | 79 | 0 | 0 | - | 2022-08-24 | 11418 | 11418 | 721 | 10:00 | 250 | 170 | 0 | 0 | 61 | 170 | 70 | 0 | 0 | -
2022-08-25 | 13985 | 14561 | 531 | 21:00 | 131 | 0 | 0 | 0 | 60 | 232 | 73 | 0 | 35 | - | 2022-08-25 | 11848 | 12200 | 324 | 10:00 | 100 | 81 | 0 | 0 | 20 | 123 | 0 | 0 | 0 | -
2022-08-26 | 13777 | 14112 | 309 | 21:00 | 46 | 0 | 0 | 0 | 20 | 222 | 0 | 0 | 21 | - | 2022-08-26 | 11430 | 11700 | 249 | 10:00 | 105 | 0 | 0 | 0 | 0 | 133 | 11 | 0 | 0 | -
2022-08-27 | 13461 | 13915 | 418 | 20:00 | 146 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | - | 2022-08-27 | 11759 | 11869 | 101 | 12:00 | 71 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | -
2022-08-28 | 13537 | 14150 | 565 | 21:00 | 98 | 0 | 109 | 108 | 70 | 162 | 0 | 0 | 18 | - | 2022-08-28 | 11639 | 11965 | 300 | 12:00 | 177 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | -
2022-08-29 | 13423 | 14300 | 808 | 21:00 | 177 | 0 | 120 | 90 | 130 | 175 | 50 | 0 | 66 |  | 2022-08-29 | 11841 | 12300 | 423 | 12:00 | 117 | 53 | 49 | 9 | 42 | 52 | 0 | 67 | 34
2022-08-30 | 13338 | 14300 | 1255 | 21:00 | 397 | 43 | 120 | 110 | 180 | 225 | 90 | 0 | 90 |  | 2022-08-30 | 11717 | 12300 | 785 | 10:00 | 388 | 200 | 0 | 0 | 27 | 170 | 0 | 0 | 0
2022-08-31 | 13581 | 14745 | 1073 | 21:00 | 327 | 0 | 296 | 0 | 186 | 206 | 58 | 0 | 0 | - | 2022-08-31 | 11822 | 12260 | 218 | 9:00 | 218 | 36 | 0 | 0 | 21 | 129 | 0 | 0 | 0
21565.6371
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -
|  |  | - | -
[15 empty] | -511 | 1777 | 12
[15 empty] | -389 | 1646 | 13
[15 empty] | -268 | 421 | 14
[15 empty] | -59 | 0 | 15
[15 empty] | -574 | 569 | 16
[15 empty] | -787 | 669 | 17
[15 empty] | -504 | 544 | 18
[15 empty] | -115 | 342 | 19
[15 empty] | -518 | 576 | 20
[15 empty] | -563 | 876 | 21
[15 empty] | -1079 | 1137 | 22
[15 empty] | -554 | 0 | 23
[15 empty] | -628 | 0 | 24
[15 empty] | -576 | 352 | 25
[15 empty] | -335 | 270 | 26
[15 empty] | -454 | 110 | 27
[15 empty] | -613 | 326 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:August 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13985 | 2022-08-25 | 21:00
2 | Maximum Day Peak Genaration | MW | 11848 | 2022-08-25 | 12:00
3 | Maximum Evening Peak Demand | MW | 14745 | 2022-08-31 | 21:00
4 | Minimum Generation | MW | 9620 | 2022-08-12 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13078.4194 | - | -
6 | Average of the daily day peak Genaration | MW | 10988.2258 | - | -
7 | Maximum load shed | MW | 1537 | 2022-08-06 | 21:00
8 | Minimum load shed | MW | 54 | 2022-08-15 | 21:00
9 | Total nos. of load shed days | Day | 31 | - | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 695.6657 | - | -
11 | Total Generation | MkWh | 8703.2165 | - | -
12 | Total Generation by BPDB | MkWh | 1900.8429 | % of total Gen. | 21.84%
13 | Total Generation by IPP | MkWh | 2701.324 | '' | 31.04%
14 | A) Total Generation by Generation Companies | MkWh | 2785.8661 | '' | 32.01%
| ` | MkWh | 127.2082 | " | 1.462%
| C) Total Generation by RENTAL | MkWh | 411.3038 | " | 4.726%
| D) Total Imported from India (BIPTC) | MkWh | 672.5796 | " | 7.728%
| E) Total Imported from Tripura, India (A.C) | MkWh | 104.0918 | " | 1.196%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4273.9758 | % of total Gen. | 49.11%
| B) Oil | MkWh | 2616.5183 | '' | 30.06%
| C) Hydro | MkWh | 95.7122 | '' | 1.1%
| D) Solar | MkWh | 37.0888 | '' | 0.4262%
| E) Coal | MkWh | 903.25 | '' | 10.38%
| F) BIPTC (Import from India) | MkWh | 672.5796 | '' | 7.728%
| G) A.C (Import from Tripura, India) | MkWh | 104.0918 | '' | 1.196%
16 | Maximun of the daily total Generation . | MkWh | 313.338 | 2022-08-27
17 | Monthly Load factor | % | 92.6177 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 49050.3894 | - | -
| A) Gas | M.Taka | 4870.6454 | - | -
| B) Liquid fuel | M.Taka | 34660.9077 | - | -
| C) Coal | M.Taka | 6491.412 | - | -
| D) BIPTC (Import from India) | M.Taka | 2280.0449 | - | -
| E) Tripura(Import from India) | M.Taka | 747.3794 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1862.5572 | 2022-08-20
| A) Gas | M.Taka | 176.4206 | 2022-08-19
| B) Liquid fuel | M.Taka | 1510.3659 | 2022-08-01
| C) Coal | M.Taka | 306.7786 | 2022-08-15
| D) BIPTC (Import from India) | M.Taka | 74.9104 | 2022-08-01
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.8911
| B) Excluding Hydro & Solar | Taka/kWhR | 6.9971
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.67 | 31/08/2022 | 06:00
b) | Actual | FT (MSL) | 96.43 | 31/08/2022 | 06:00
22 | Peak Genaration of August2021 | MW | 13271 | 2021-08-22 | 21:00
23 | Peak Demand of August 2021 | MW | 13271 | 2021-08-22 | 21:00
24 | Maximum peak Generation recorded upto 31/08/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 31/08/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 31/08/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | bar: FGMO Status 1 to FGMO Status 31
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Meghnaghat CCPP(Summit) | IPP | 335
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360
8 | Ashuganj 225 MW CCPP | APSCL | 221
9 | Bheramara 410 MW CCPP | NWPGCL | 410
10 | Haripur 412 MW CCPP | EGCB | 412
11 | Fenchugonj CCPP Phase-1 | BPDB | 97
12 | Chandpur 150 MW CCPP | BPDB | 163
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210
14 | Shikalbaha 225 MW CCPP | BPDB | 225
15 | Shikalbaha Peaking GT | BPDB | 150
16 | Shahjibazar 330 MW CCPP | BPDB | 330
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360
18 | Fenchugonj CCPP Phase-2 | BPDB | 104
19 | Bhola 225 MW CCPP | BPDB | 194
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
22 | Siddhirganj 335 MW CCPP | EGCB | 335
23 | Bibiyana-III 400 MW CCPP | BPDB | 400
24 | Sylhet 225 MW CCPP | BPDB | 231
25 | RPCL 210 MW CCPP | IPP | 210
26 | Khulna 225 MW CCPP | NWPGCL | 230
27 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
30 | Bibiyana South 400 MW CCPP | BPDB | 383
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
32 | Shajibazar 100 MW PP | BPDB | 100
33 | Payra 1320 MW Unit-1 | BCPCL | 622
34 | Kushiara 163 MW CCPP (KP) | IPP | 163
35 | Haripur 360MW CCPP(HPL) | IPP | 360
36 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage