## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-01-17 | Tuesday
|  | Date (day): | 2023-01-17 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 8427.6 | MW |  |  | (b) At Evening Peak Hour : |  | 9565 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-01-16 | 2023-01-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 200 | 200 | 200 | 200 |  | 165 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 76 | 77 | 74 | 77 | 31 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 269 | 349 | 300 | 350 | 62 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 230 | 196 | 240 | 250 | 110 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 8 | 8 | 8 | 92 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 155 | 138 | 140 | 140 | 195 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 34 | 34 | 20 | 34 | 68 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 30 | 25 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 19
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 9 | 9 | 8 | 9 | 91 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 8 | 8 | 8 | 8 | 94 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 0 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 48 | 32 | 80 | 69 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 0 | 34 | 21 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 17 | 34 | 21 |  | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 49 | 49 | 49 |  | 31 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 25 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 30 | 33 | 33
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 8 | 8 | 16 | 36 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 33 | 65 | 33 | 65 | 234 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 35 | 35 | 35 | 35 | 114 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 88 | 70 | 88 |  | 17 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 0 | 17 | 87 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 17 | 17 | 145 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1343 | 1586 | 1398 | 1697 | 2629 | 1533
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 19 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 34 | 34 | 25 | 34 | 25 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 154 | 156 | 160 | 160 |  | 65 | ST Under S/D
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 68 | 34 | 68 | 37 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 32 | 32 | 32 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 9 | 5 | 10
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 51 | 284 | 51 | 284 |  | 16 | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 71 | 52 | 50 | 70 | 40 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 68 | 34 | 107 | 9 |  | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 562 | 890 | 594 | 952 | 1183 | 231
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 196 | 171 | 180 | 180 | 41 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 280 | 290 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 25 | 300 | 300 | 60 |  | Gas shortage
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 290 | 148 | 0 | 0 | 400 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 3 | 0 | 0 | 0 | 45 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 | 55 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 0 | 0 | 0 | 195 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 8 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 35 | 34 | 31 | 34 |  | 18 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 0 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 10 | 10
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 114 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 14 | 21 | 19 | 21
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 0 | 0 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 19 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 0 | 0 | 114 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 117 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 52 | 94 | 54 | 94 |  | 21 | Engine problem
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1189 | 1147 | 1159 | 1346 | 1615 | 243
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 47 | 101 | 50 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 21 | 22
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 46 | 48 | 48 | 48 | 152 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 28 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 32 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 7 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 183 | 224 | 204.6 | 223 | 102 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 0 | 0 | 0 |  | 90 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under S/D
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 14 | 11 | 11 | 40 |  | Gas shortage
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 10 | 10 | 10 | 10 | 40 |  | Gas shortage
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 | 11 |  | Gas shortage
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 33 | 33 | 33 |  | 33 | GT-8 Under maint.
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 30 | 81 | 50 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 199 | 200 | 200 | 200 |  | 31 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 19 | 19 | 0 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 |  | 25 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 392 | 365 | 400 | 400
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 389 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1454 | 1441 | 1444 | 1497 | 91 | 812
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 910 | 792 | 932 | 932
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 66 | 16 | 99 |  | 16 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 33 | 0 | 33 |  | 21 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 62 | 0 | 62 |  | 47 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 90 | 90 | 90 | 10
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 18 | 87 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Fuel shortage
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 994 | 1068 | 1138 | 1242 | 890 | 84
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 110 | 48 | 110 |  |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 25 | 19 | 25 |  | 15 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 126 | 134 | 135 | 135 |  | 59 | ST Under S/D
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 470 | 622 | 622 | 622 |  | 622 | Unit-2 U/M
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 220 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 54 | 100 | 150 | 150 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 954 | 1211 | 1194 | 1262 | 0 | 696
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 26 | 0 | 26 |  | 45 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 34 | 34 | 34 |  | 16 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32 |  | 18 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 147 | 150 | 150 | 40 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 0 | 0 | 0 | 0 |  | 220 | Under maint
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 366 | 333 | 350 | 350 | 64
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 37 | 0 | 37 |  | 13 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 21 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 8 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 92 | 0 | 92 |  | 12 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 0 | 35 | 35 | 35 | 78 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 35 | 35 | 35 | 78 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 688 | 887 | 647 | 863 | 885 | 342
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 83 | 81 | 83
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 |  | 24 | Machine problem
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 35 | 35 | 35 | 35 | 78 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 115 | 115 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 5 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 119 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 606 | 483 | 649 | 483 | 118 | 109
| Total |  |  |  |  | 23482 | 22700 | 7973 | 8937 | 8427.6 | 9565 | 7513 | 4050
A. |  | 2023-01-16 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 9017 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 6445 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9970 | MW
3 | Day peak Generation : |  |  | 7973 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9393.46 | MW
4 | Evening peak Generation : |  |  | 8937 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 952 | MW
5 | Total Energy Generation : |  | 190.6505 | MKWHr | By Solar | 1.5739 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 111.3526 | MKWHr |  | By Oil: | 32.6615 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 22.7321 | MKWHr |  | By Hydro: | 0.70338 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7513 | MW | Dhaka | 3322.46 | 3008.46 |  | 314 |  | 18:00 |  | 722
|  |  | For Plants S/D or M/C prob = |  |  | 4050 | MW | Chittagong | 897.7 | 887.7 |  | 10 |  | 19:00 |  | 1094.8311
|  |  | Total = |  |  | 11563 | MW | Khulna | 1156.5 | 919.5 |  | 237 |  | 19:30 |  | 1032.164
7 | Total Gas Supplied : |  |  | 842.61 | MMCFD |  |  | Rajshahi | 999.2 | 861.2 |  | 138 |  | 20:00 |  | 951.987
8 | Fuel Cost : | i) Gas : | Taka | 114229797.376 | ii) Oil : | Taka | 432881239.59 | Comilla | 806 | 806 |  | 0 |  | 21:00 |  | 854.3
|  | iii) Coal : |  | 175943861.87 | Total | Taka | 723054898.836 | Mymensingh | 878 | 816 |  | 62 |  | 22:00 |  | 238.6879
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.0165 | MKWHr. | Sylhet | 362 | 304 |  | 58 |  | 23:00 |  | 39.6277
| ii) During Peak Demand : |  |  | 484 | MW (E to W) at | 20:00 | hrs | Barisal | 268.6 | 268.6 |  | 0 |  | 24:00 |  | 39.6277
| iii) Maximum : |  |  | 140 | MW at | 7:00 | hrs | Rangpur | 703 | 570 |  | 133
10 | Maximum Temperature in Dhaka was |  |  |  | 24° C |  |  | Total | 9393.46 | 8441.46 |  | 952
B. |  | 2023-01-17 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 24.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 585 | MW
2 | Maximum Generation (Generation end) |  |  |  | 9565 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 215.6632 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6615 | MW at | 5:00 | 125 | 60 | 120 | 110 | 40 | 60 | 20 | 0 | 50
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.2145 | MKWHr. | ii) HVDC Flow at Peak Time |  | 792 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4125 | MKWHr. | iii) Maximum HVDC Flow : |  | 911 | MW at | 14:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 85.2 |  | (b) Today: | 85.08 |  | (c) Rule Curve: |  | 99.96
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-01-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 190 | 77 | 0 | 289 | 250 |  | 0 | 0 | 150 | 8 | 25 | 15 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 26 | 25 | 32 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 25 | 0 | 21 | 0 | 0 | 0 | 280 | 0 | 226 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 21 | 90 | 110 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 86 | 0 | 195 | 19 | 0 | 10 | 260 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 376 | 28 | 0 | 34 | 0 | 51 | 0 | 70 | 0 | 55 | 25 | 370 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 50 | 17 | 297 | 0 | 0 |  | 727 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 20 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 222 | 0 | 17 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4558 | 2865 | 7423 | 3113 | 727 | 1569 | 0 | 941 | 953 | 30 | 0 | 0 | 90 | 0 | 0 | 85.21
2:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 289 | 254 |  | 0 | 0 | 152 | 9 | 2 | 15 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 26 | 25 | 32 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 300 | 0 | 225 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 21 | 80 | 110 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 30 | 86 | 0 | 195 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 6 | 376 | 8 | 0 | 34 | 0 | 51 | 0 | 70 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 34 | 0 | 0 | 0 | 25 | 0 | 297 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 0 | 389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4313 | 2531 | 6844 | 3170 | 633 | 1609 | 0 | 369 | 953 | 30 | 0 | 0 | 80 | 0 | 0 | 85.21
3:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 293 | 256 |  | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 26 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 227 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 19 | 80 | 110 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 50 | 0 | 195 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 6 | 376 | 8 | 0 | 34 | 0 | 51 | 0 | 51 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 |  | 634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 580 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4196 | 2511 | 6707 | 3190 | 634 | 1613 | 0 | 249 | 911 | 30 | 0 | 0 | 80 | 0 | 0 | 85.21
4:00 | 0 | 0 | 0 | 0 | 200 | 35 | 0 | 293 | 251 |  | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 23 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 280 | 0 | 226 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 19 | 80 | 110 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 20 | 0 | 195 | 19 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 6 | 375 | 8 | 0 | 34 | 0 | 51 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 0 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4070 | 2397 | 6467 | 3192 | 633 | 1484 | 0 | 215 | 833 | 30 | 0 | 0 | 80 | 0 | 0 | 85.2
5:00 | 0 | 0 | 0 | 0 | 200 | 35 | 0 | 293 | 245 |  | 0 | 0 | 152 | 9 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 24 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 280 | 0 | 227 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 21 | 10 | 33 | 19 | 76 | 110 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 20 | 0 | 193 | 19 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 5 | 370 | 8 | 0 | 34 | 0 | 51 | 0 | 17 | 0 | 0 | 0 | 400 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4055 | 2390 | 6445 | 3188 | 633 | 1472 | 0 | 215 | 831 | 30 | 0 | 0 | 76 | 0 | 0 | 85.2
6:00 | 0 | 0 | 0 | 0 | 200 | 35 | 0 | 294 | 257 |  | 0 | 0 | 152 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 24 | 25 | 33 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 161 | 0 | 0 | 0 |  | 3 | 0 | 0 | 22 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 325 | 0 | 226 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 33 | 19 | 80 | 109 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 20 | 0 | 194 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 6 | 0 | 10 | 4 | 6 | 375 | 8 | 0 | 34 | 0 | 51 | 0 | 29 | 0 | 0 | 10 | 400 | 0 | 0 | 17 | 23 | 0 | 0 | 0 | 25 | 3 | 320 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 169 | 0 | 0 | 0 | 0 | 0 | 358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 220 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4237 | 2447 | 6684 | 3236 | 633 | 1505 | 0 | 369 | 831 | 30 | 0 | 0 | 80 | 0 | 0 | 85.2
7:00 | 0 | 0 | 0 | 0 | 200 | 35 | 0 | 294 | 242 |  | 0 | 0 | 155 | 9 | 2 | 12 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 6 | 25 | 33 | 2 | 0 | 30 | 0 | 0 | 0 | 2 | 161 | 0 | 0 | 0 |  | 12 | 0 | 0 | 22 | 0 | 1 | 0 | 42 | 0 | 0 | 0 | 350 | 0 | 224 | 8 | 0 | 3 | 2 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 24 | 19 | 84 | 54 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 32 | 50 | 0 | 194 | 19 | 0 | 10 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 32 | 1 | 25 | 13 | 8 | 375 | 28 | 8 | 34 | 0 | 51 | 0 | 70 | 0 | 0 | 20 | 400 | 0 | 1 | 17 | 34 | 0 | 0 | 1 | 53 | 10 | 320 | 0 | 0 |  | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 220 | 0 | 0 | 0 | 1 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4490 | 2637 | 7127 | 3181 | 633 | 1636 | 0 | 681 | 860 | 30 | 0 | 16 | 84 | 6 | 205.5112 | 85.19
8:00 | 0 | 0 | 0 | 0 | 200 | 74 | 0 | 288 | 245 |  | 0 | 0 | 152 | 8 | 20 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 27 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 161 | 0 | 0 | 0 |  | 12 | 32 | 0 | 22 | 0 | 25 | 0 | 16 | 0 | 0 | 0 | 280 | 0 | 229 | 8 | 0 | 3 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 19 | 19 | 94 | 55 | 0 | 21 | 0 | 0 | 43 | 11 | 10 | 0 | 0 | 33 | 50 | 0 | 194 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 33 | 0 | 0 | 47 | 0 | 35 | 5 | 25 | 1 | 8 | 376 | 28 | 34 | 34 | 1 | 51 | 0 | 70 | 0 | 7 | 25 | 400 | 10 | 6 | 17 | 34 | 0 | 0 | 4 | 52 | 17 | 294 | 0 | 0 |  | 863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 19 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 0 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 222 | 0 | 29 | 0 | 13 | 115 | 0 | 0 | 0 | 1 | 0 | 0 | 9 |  | 4604 | 3068 | 7672 | 3110 | 863 | 1625 | 0 | 922 | 941 | 30 | 0 | 48 | 94 | 39 | 609.1611 | 85.19
9:00 | 0 | 0 | 0 | 0 | 200 | 74 | 0 | 287 | 240 |  | 0 | 0 | 150 | 9 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 27 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 |  | 12 | 32 | 0 | 22 | 0 | 32 | 0 | 7 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 20 | 0 | 19 | 10 | 15 | 17 | 102 | 55 | 0 | 22 | 1 | 0 | 43 | 11 | 10 | 0 | 0 | 32 | 10 | 0 | 203 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 33 | 0 | 0 | 47 | 0 | 35 | 11 | 25 | 17 | 6 | 376 | 28 | 39 | 34 | 2 | 52 | 0 | 70 | 0 | 9 | 25 | 365 | 17 | 17 | 0 | 34 | 0 | 3 | 12 | 52 | 17 | 294 | 0 | 0 |  | 815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 622 | 220 | 0 | 150 | 1 | 31 | 115 | 0 | 0 | 0 | 2 | 0 | 0 | 41 |  | 4529 | 3198 | 7727 | 3030 | 815 | 1497 | 0 | 1114 | 952 | 30 | 0 | 68 | 102 | 119 | 944.6144 | 85.18
10:00 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 273 | 235 |  | 0 | 0 | 150 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 27 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 |  | 12 | 32 | 0 | 22 | 0 | 33 | 0 | 3 | 0 | 0 | 0 | 295 | 0 | 193 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 21 | 0 | 19 | 10 | 14 | 17 | 104 | 54 | 0 | 22 | 1 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 10 | 0 | 203 | 19 | 0 | 10 | 285 | 0 | 0 | 0 | 33 | 0 | 0 | 47 | 0 | 35 | 15 | 25 | 17 | 6 | 325 | 28 | 70 | 34 | 3 | 52 | 2 | 70 | 0 | 9 | 25 | 400 | 17 | 27 | 0 | 34 | 0 | 17 | 17 | 53 | 17 | 305 | 0 | 0 |  | 815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 18 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 388 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 20 | 570 | 160 | 0 | 150 | 2 | 47 | 115 | 0 | 0 | 0 | 6 | 0 | 0 | 55 |  | 4570 | 3154 | 7724 | 3000 | 815 | 1428 | 0 | 1205 | 899 | 30 | 0 | 69 | 104 | 174 | 793.4761 | 85.18
11:00 | 0 | 0 | 0 | 0 | 200 | 71 | 0 | 272 | 235 |  | 0 | 0 | 148 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 27 | 33 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 156 | 0 | 0 | 0 |  | 12 | 32 | 0 | 22 | 0 | 28 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 182 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 23 | 3 | 19 | 10 | 14 | 21 | 110 | 47 | 0 | 22 | 1 | 0 | 43 | 11 | 10 | 0 | 0 | 31 | 10 | 0 | 199 | 19 | 0 | 10 | 305 | 0 | 0 | 0 | 33 | 0 | 0 | 47 | 0 | 35 | 18 | 25 | 17 | 6 | 360 | 28 | 70 | 34 | 3 | 51 | 17 | 70 | 0 | 9 | 25 | 400 | 17 | 30 | 0 | 34 | 0 | 17 | 18 | 53 | 17 | 305 | 0 | 0 |  | 815 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 18 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 52 | 0 | 18 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 35 | 450 | 160 | 0 | 100 | 2 | 60 | 115 | 0 | 0 | 0 | 7 | 0 | 0 | 116 |  | 4617 | 3080 | 7697 | 2986 | 815 | 1437 | 0 | 1211 | 780 | 30 | 0 | 71 | 110 | 257 | 919.7318 | 85.17
12:00 | 0 | 0 | 0 | 0 | 200 | 76 | 0 | 269 | 230 |  | 0 | 0 | 155 | 9 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 27 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 7 | 32 | 0 | 22 | 0 | 34 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 196 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 35 | 8 | 19 | 10 | 14 | 21 | 110 | 47 | 0 | 22 | 1 | 0 | 43 | 11 | 10 | 0 | 0 | 30 | 30 | 0 | 199 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 33 | 0 | 0 | 46 | 0 | 35 | 19 | 25 | 0 | 6 | 392 | 28 | 70 | 34 | 4 | 51 | 17 | 71 | 0 | 9 | 25 | 400 | 0 | 32 | 0 | 34 | 0 | 17 | 20 | 52 | 17 | 290 | 0 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 20 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 52 | 0 | 18 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 35 | 470 | 220 | 0 | 54 | 3 | 68 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 119 |  | 4731 | 3242 | 7973 | 3089 | 910 | 1517 | 0 | 1145 | 801 | 30 | 0 | 99 | 110 | 272 | 939.0849 | 85.17
13:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 267 | 230 |  | 0 | 0 | 150 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 24 | 33 | 17 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 34 | 0 | 2 | 0 | 0 | 0 | 305 | 0 | 219 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 37 | 8 | 19 | 10 | 14 | 21 | 106 | 47 | 0 | 22 | 1 | 0 | 0 | 11 | 10 | 0 | 0 | 31 | 50 | 0 | 197 | 19 | 0 | 10 | 320 | 0 | 0 | 0 | 33 | 0 | 0 | 48 | 0 | 35 | 18 | 25 | 0 | 6 | 385 | 28 | 34 | 34 | 4 | 51 | 17 | 75 | 0 | 9 | 25 | 400 | 0 | 26 | 0 | 34 | 0 | 17 | 21 | 53 | 17 | 238 | 0 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 21 | 64 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 42 | 0 | 52 | 0 | 18 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 351 | 0 | 0 | 20 | 0 | 34 | 0 | 1 | 35 | 580 | 220 | 0 | 54 | 3 | 62 | 115 | 0 | 0 | 0 | 7 | 0 | 0 | 92 |  | 4579 | 3354 | 7933 | 2952 | 910 | 1521 | 0 | 1133 | 913 | 30 | 0 | 133 | 106 | 235 | 1020.1835 | 85.16
14:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 261 | 228 |  | 0 | 0 | 151 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 22 | 27 | 33 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 6 | 23 | 0 | 22 | 0 | 34 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 186 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 37 | 8 | 19 | 10 | 14 | 21 | 116 | 45 | 0 | 22 | 1 | 0 | 0 | 22 | 15 | 0 | 0 | 30 | 50 | 0 | 197 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 15 | 25 | 0 | 5 | 385 | 28 | 34 | 34 | 3 | 51 | 17 | 73 | 0 | 9 | 25 | 400 | 0 | 25 | 0 | 34 | 0 | 17 | 15 | 52 | 17 | 267 | 0 | 0 |  | 911 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 19 | 73 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 8 | 0 | 0 | 17 | 0 | 8 | 86 | 0 | 250 | 0 | 0 | 0 | 0 | 158 | 0 | 0 | 0 | 0 | 0 | 341 | 0 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 622 | 220 | 0 | 72 | 2 | 54 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 70 |  | 4549 | 3359 | 7908 | 2919 | 911 | 1513 | 0 | 1135 | 958 | 30 | 0 | 135 | 116 | 191 | 978.7127 | 85.17
15:00 | 0 | 0 | 0 | 0 | 200 | 76 | 0 | 258 | 220 |  | 0 | 0 | 148 | 9 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 3 | 0 | 22 | 26 | 33 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 156 | 0 | 0 | 0 |  | 6 | 23 | 51 | 22 | 0 | 34 | 0 | 2 | 0 | 0 | 0 | 280 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 28 | 8 | 19 | 10 | 14 | 20 | 109 | 45 | 0 | 22 | 1 | 0 | 0 | 24 | 20 | 0 | 0 | 31 | 50 | 0 | 195 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 11 | 25 | 0 | 6 | 366 | 28 | 34 | 34 | 2 | 51 | 17 | 67 | 0 | 10 | 25 | 400 | 0 | 16 | 0 | 60 | 0 | 17 | 14 | 53 | 17 | 278 | 0 | 0 |  | 911 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 17 | 80 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 8 | 0 | 25 | 17 | 0 | 8 | 85 | 0 | 250 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 0 | 0 | 0 | 329 | 0 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 560 | 160 | 0 | 54 | 2 | 37 | 115 | 0 | 0 | 0 | 9 | 0 | 0 | 79 |  | 4557 | 3197 | 7754 | 2869 | 911 | 1414 | 0 | 1152 | 895 | 30 | 0 | 202 | 109 | 172 | 991.6147 | 85.15
16:00 | 0 | 0 | 0 | 0 | 200 | 72 | 0 | 289 | 196 |  | 0 | 0 | 138 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 22 | 26 | 33 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 157 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 3 | 34 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 184 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 28 | 8 | 19 | 10 | 14 | 18 | 100 | 47 | 0 | 22 | 1 | 0 | 0 | 22 | 20 | 0 | 0 | 31 | 50 | 0 | 195 | 19 | 0 | 10 | 275 | 0 | 0 | 0 | 35 | 0 | 0 | 57 | 0 | 35 | 6 | 25 | 0 | 6 | 365 | 28 | 40 | 56 | 1 | 51 | 17 | 56 | 0 | 86 | 25 | 400 | 0 | 9 | 0 | 107 | 0 | 17 | 7 | 52 | 17 | 288 | 0 | 0 |  | 909 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 80 | 16 | 64 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 8 | 0 | 38 | 17 | 0 | 8 | 84 | 0 | 250 | 0 | 0 | 0 | 0 | 148 | 0 | 0 | 0 | 0 | 0 | 320 | 0 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 450 | 160 | 0 | 17 | 0 | 19 | 115 | 0 | 0 | 0 | 7 | 0 | 0 | 38 |  | 4715 | 2951 | 7666 | 2910 | 909 | 1349 | 0 | 1283 | 784 | 30 | 0 | 212 | 100 | 89 | 690.2597 | 85.15
17:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 339 | 180 |  | 0 | 0 | 130 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 12 | 34 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 183 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 33 | 0 | 19 | 10 | 15 | 18 | 104 | 54 | 0 | 22 | 0 | 20 | 0 | 17 | 10 | 0 | 0 | 31 | 50 | 0 | 194 | 19 | 0 | 10 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 35 | 1 | 25 | 9 | 5 | 365 | 28 | 85 | 68 | 0 | 118 | 13 | 53 | 0 | 113 | 25 | 400 | 0 | 2 | 0 | 116 | 0 | 17 | 1 | 73 | 17 | 318 | 0 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 36 | 35 | 0 | 132 | 15 | 64 | 0 | 0 | 0 | 8 | 4 | 35 | 0 | 42 | 8 | 0 | 37 | 17 | 0 | 8 | 86 | 0 | 250 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 0 | 0 | 0 | 317 | 0 | 0 | 35 | 0 | 35 | 0 | 1 | 35 | 470 | 160 | 0 | 17 | 0 | 4 | 115 | 0 | 0 | 0 | 1 | 0 | 0 | 8 |  | 5035 | 3047 | 8082 | 3070 | 910 | 1336 | 0 | 1481 | 806 | 30 | 0 | 327 | 104 | 18 | 569.5333 | 85.14
18:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 339 | 180 |  | 0 | 0 | 125 | 8 | 34 | 21 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 17 | 19 | 22 | 19 | 33 | 29 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 12 | 34 | 0 | 2 | 0 | 0 | 0 | 345 | 18 | 200 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 0 | 19 | 10 | 15 | 21 | 130 | 55 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 30 | 81 | 0 | 195 | 19 | 0 | 10 | 300 | 0 | 0 | 0 | 67 | 0 | 0 | 57 | 0 | 35 | 0 | 25 | 17 | 6 | 431 | 47 | 88 | 68 | 0 | 271 | 17 | 52 | 0 | 116 | 25 | 400 | 9 | 0 | 17 | 78 | 0 | 17 | 0 | 94 | 17 | 228 | 0 | 0 |  | 840 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 43 | 73 | 8 | 130 | 23 | 80 | 0 | 0 | 0 | 25 | 5 | 91 | 0 | 34 | 8 | 52 | 37 | 18 | 0 | 8 | 87 | 0 | 250 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 90 | 0 | 0 | 325 | 0 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 570 | 220 | 0 | 17 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5421 | 3446 | 8867 | 3139 | 840 | 1436 | 90 | 1848 | 907 | 30 | 0 | 447 | 130 | 0 | 722 | 85.14
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 346 | 185 |  | 0 | 0 | 130 | 8 | 34 | 23 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 44 | 55 | 17 | 19 | 22 | 27 | 33 | 15 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 12 | 34 | 0 | 2 | 0 | 0 | 0 | 280 | 22 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 0 | 19 | 10 | 16 | 21 | 124 | 99 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 32 | 81 | 0 | 201 | 19 | 0 | 10 | 320 | 0 | 0 | 0 | 80 | 0 | 0 | 57 | 0 | 35 | 0 | 25 | 17 | 6 | 364 | 47 | 88 | 68 | 0 | 282 | 17 | 52 | 0 | 117 | 25 | 400 | 17 | 0 | 17 | 72 | 0 | 17 | 0 | 94 | 17 | 160 | 0 | 0 |  | 808 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 33 | 68 | 8 | 130 | 24 | 96 | 0 | 0 | 0 | 34 | 11 | 92 | 0 | 34 | 32 | 52 | 37 | 22 | 0 | 8 | 87 | 0 | 250 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 90 | 0 | 0 | 327 | 4 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 620 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5330 | 3572 | 8902 | 2968 | 808 | 1473 | 90 | 1980 | 957 | 30 | 0 | 472 | 124 | 0 | 1094.8311 | 85.12
19:30 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 347 | 185 |  | 0 | 0 | 130 | 9 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 22 | 27 | 0 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 155 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 2 | 34 | 0 | 3 | 0 | 0 | 0 | 280 | 7 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 0 | 19 | 10 | 16 | 21 | 126 | 99 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 31 | 81 | 0 | 200 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 404 | 47 | 88 | 68 | 0 | 284 | 17 | 52 | 0 | 117 | 25 | 400 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 150 | 0 | 0 |  | 792 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 33 | 62 | 8 | 132 | 25 | 96 | 0 | 0 | 0 | 34 | 18 | 92 | 0 | 34 | 32 | 52 | 37 | 22 | 0 | 8 | 84 | 0 | 250 | 0 | 0 | 0 | 0 | 146 | 0 | 0 | 90 | 0 | 0 | 329 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 54 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5285 | 3575 | 8860 | 2965 | 792 | 1467 | 90 | 1961 | 956 | 30 | 0 | 473 | 126 | 0 | 1032.164 | 0
20:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 349 | 196 |  | 0 | 0 | 138 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 22 | 27 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 0 | 34 | 0 | 9 | 0 | 0 | 0 | 280 | 25 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 0 | 19 | 10 | 21 | 21 | 114 | 101 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 33 | 81 | 0 | 200 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 8 | 365 | 47 | 88 | 68 | 0 | 284 | 17 | 52 | 0 | 117 | 25 | 389 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 148 | 0 | 0 |  | 792 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 33 | 62 | 8 | 134 | 25 | 110 | 0 | 0 | 0 | 34 | 26 | 92 | 0 | 34 | 32 | 52 | 37 | 22 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 90 | 0 | 0 | 333 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 100 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5288 | 3649 | 8937 | 2979 | 792 | 1476 | 90 | 2020 | 955 | 30 | 0 | 481 | 114 | 0 | 951.987 | 85.13
21:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 375 | 208 |  | 0 | 0 | 148 | 9 | 34 | 16 | 0 | 0 | 0 | 9 | 16 | 82 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 22 | 27 | 33 | 32 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 158 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 0 | 33 | 0 | 12 | 0 | 0 | 0 | 280 | 62 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 0 | 19 | 10 | 21 | 21 | 112 | 106 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 32 | 81 | 0 | 200 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 77 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 5 | 365 | 47 | 88 | 68 | 0 | 52 | 17 | 52 | 0 | 117 | 25 | 400 | 0 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 151 | 0 | 0 |  | 815 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 33 | 62 | 8 | 130 | 19 | 110 | 0 | 0 | 0 | 34 | 29 | 92 | 0 | 0 | 32 | 8 | 37 | 22 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 152 | 0 | 0 | 90 | 0 | 0 | 340 | 17 | 0 | 40 | 0 | 35 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5188 | 3700 | 8888 | 3065 | 815 | 1522 | 90 | 1781 | 955 | 30 | 0 | 518 | 112 | 0 | 854.3 | 85.12
22:00 | 0 | 0 | 0 | 0 | 180 | 77 | 0 | 383 | 227 |  | 0 | 0 | 152 | 8 | 34 | 30 | 0 | 0 | 0 | 9 | 16 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 32 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 158 | 0 | 0 | 0 |  | 6 | 32 | 51 | 22 | 0 | 33 | 0 | 18 | 0 | 0 | 0 | 280 | 92 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 25 | 21 | 108 | 112 | 0 | 21 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 33 | 81 | 0 | 198 | 19 | 0 | 10 | 260 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 0 | 6 | 366 | 47 | 88 | 68 | 0 | 52 | 17 | 67 | 0 | 118 | 25 | 400 | 0 | 0 | 17 | 87 | 0 | 17 | 0 | 94 | 17 | 148 | 0 | 0 |  | 911 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 33 | 62 | 0 | 132 | 26 | 110 | 0 | 0 | 0 | 34 | 25 | 92 | 0 | 25 | 24 | 8 | 37 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 157 | 0 | 0 | 89 | 0 | 0 | 350 | 17 | 0 | 50 | 0 | 35 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5190 | 3827 | 9017 | 3096 | 911 | 1518 | 89 | 1804 | 954 | 30 | 0 | 507 | 108 | 0 | 238.6879 | 85.12
23:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 387 | 238 |  | 0 | 0 | 150 | 8 | 30 | 20 | 0 | 0 | 0 | 9 | 16 | 82 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 25 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 162 | 0 | 0 | 0 |  | 4 | 32 | 7 | 22 | 0 | 33 | 0 | 21 | 0 | 0 | 0 | 280 | 85 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 35 | 0 | 19 | 10 | 25 | 21 | 110 | 114 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 33 | 81 | 0 | 198 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 36 | 0 | 25 | 6 | 6 | 343 | 47 | 35 | 68 | 0 | 52 | 17 | 60 | 0 | 84 | 25 | 400 | 0 | 0 | 17 | 90 | 0 | 17 | 0 | 65 | 17 | 150 | 0 | 0 |  | 910 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 33 | 52 | 0 | 136 | 24 | 110 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 25 | 0 | 8 | 37 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 362 | 17 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 622 | 220 | 0 | 150 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4995 | 3565 | 8560 | 3098 | 910 | 1550 | 0 | 1579 | 954 | 30 | 0 | 329 | 110 | 0 | 39.6277 | 85.11
24:00 | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 391 | 228 |  | 0 | 0 | 148 | 9 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 158 | 0 | 0 | 0 |  | 5 | 32 | 0 | 22 | 0 | 33 | 0 | 29 | 0 | 0 | 0 | 280 | 85 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 0 | 0 | 19 | 10 | 25 | 21 | 98 | 114 | 0 | 21 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 33 | 81 | 0 | 198 | 19 | 0 | 10 | 270 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 36 | 0 | 25 | 17 | 5 | 343 | 28 | 35 | 68 | 0 | 52 | 17 | 52 | 0 | 36 | 16 | 400 | 0 | 0 | 17 | 95 | 0 | 17 | 0 | 53 | 17 | 150 | 0 | 0 |  | 910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 22 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 0 | 362 | 0 | 0 | 50 | 0 | 34 | 0 | 0 | 55 | 622 | 220 | 0 | 100 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4815 | 3266 | 8081 | 3098 | 910 | 1544 | 0 | 1367 | 954 | 30 | 0 | 80 | 98 | 0 | 39.6277 | 85.11
KWH | 0 | 0 | 0 | 0 | 4677900 | 1680045 | 0 | 7563260 | 5472000 |  | 0 | 0 | 3538822 | 192960 | 539880 | 360608 | 0 | 0 | 0 | 192000 | 214704 | 712800 | 0 | 0 | 0 | 0 | 266040 | 316761 | 327934 | 405576 | 528000 | 580680 | 667080 | 760500 | 166560 | 0 | 703380 | 0 | 0 | 0 | 225088 | 3678799 | 0 | 0 | 0 |  | 167760 | 511873 | 426343 | 447600 | 42240 | 585120 | 0 | 360960 | 0 | 0 | 0 | 7460000 | 366000 | 4864000 | 117090 | 0 | 38304 | 17280 | 0 | 1254472 | 0 | 465952 | 49718 | 448668 | 245700 | 536000 | 469110 | 2412480 | 1852800 | 0 | 497736 | 7850 | 215000 | 540360 | 324000 | 334584 | 0 | 0 | 764448 | 1302720 | 0 | 5029940 | 439000 | 0 | 253800 | 7196000 | 0 | 0 | 0 | 853091 | 0 | 0 | 1096800 | 0 | 714096 | 119340 | 514560 | 239040 | 157236 | 9044000 | 678000 | 1101204 | 1155018 | 23160 | 1957091 | 261459 | 1429339 | 0 | 1095360 | 503040 | 9554200 | 97920 | 184360 | 267840 | 1288418 | 0 | 285480 | 123874 | 1333440 | 354600 | 6276400 | 0 | 0 |  | 19214545 | 0 | 0 | 0 | 469440 | 0 | 0 | 0 | 231840 | 396160 | 34875 | 3016000 | 462392 | 1531296 | 0 | 0 | 0 | 182483 | 97072 | 680544 | 0 | 599470 | 132208 | 325536 | 305714 | 466560 | 0 | 193698 | 1967127 | 0 | 6069300 | 0 | 0 | 0 | 0 | 4032555 | 0 | 0 | 452160 | 0 | 0 | 8723272 | 97440 | 0 | 575232 | 0 | 594192 | 0 | 8227 | 675552 | 14695700 | 5102864 | 0 | 1527600 | 17760 | 398880 | 2157696 | 0 | 0 | 0 | 52216 | 0 | 0 | 638250 |  | 114524651 | 76125856 | 190650507 | 74745714 | 19214545 | 36606861 | 452160 | 28066334 | 22732127 | 703380 | 0 | 4142989 | 2412480 | 1573917 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 5239248 | 2234459.85 | 0 | 7941423 | 5909760 |  | 0 | 0 | 3928092.42 | 2157292.8 | 7153410 | 4778056 | 0 | 0 | 0 | 2807040 | 3020885.28 | 11554488 | 0 | 0 | 0 | 0 | 3384028.8 | 4276273.5 | 4397594.94 | 304182 | 396000 | 0 | 0 | 0 | 2833185.6 | 0 | 189912.6 | 0 | 0 | 0 | 3680188.8 | 3825950.96 | 0 | 0 | 0 |  | 2189268 | 8538041.64 | 7256357.86 | 6047076 | 535603.2 | 6769838.4 | 0 | 1201996.8 | 0 | 0 | 0 | 8280600 | 398940 | 5642240 | 151046.1 | 0 | 43283.52 | 25747.2 | 0 | 2094968.24 | 0 | 8046991.04 | 668707.1 | 614675.16 | 184275 | 938000 | 351832.5 | 17321606.4 | 2019552 | 0 | 676920.96 | 125129 | 294550 | 713275.2 | 563760 | 578830.32 | 0 | 0 | 1483029.12 | 2970201.6 | 0 | 5080239.4 | 943850 | 0 | 502524 | 7196000 | 0 | 0 | 0 | 11644692.15 | 0 | 0 | 14784864 | 0 | 9890229.6 | 1395084.6 | 5310259.2 | 3265286.4 | 2086521.72 | 8320480 | 8244480 | 15923409.84 | 14610977.7 | 0 | 22976248.34 | 2847288.51 | 15193873.57 | 0 | 14119190.4 | 5925811.2 | 8789864 | 1268064 | 2664002 | 3398889.6 | 14662196.84 | 0 | 3728368.8 | 1480294.3 | 19961596.8 | 4670082 | 0 | 0 | 0 |  | 57643635 | 0 | 0 | 0 | 4886870.4 | 0 | 0 | 0 | 4175438.4 | 7130880 | 501153.75 | 3377920 | 897040.48 | 16691126.4 | 0 | 0 | 0 | 3060239.91 | 1697789.28 | 10643708.16 | 0 | 9927223.2 | 2235637.28 | 4437055.68 | 5157395.18 | 965779.2 | 0 | 146629.386 | 11429007.87 | 0 | 32106597 | 0 | 0 | 0 | 0 | 5161670.4 | 0 | 0 | 9486316.8 | 0 | 0 | 8636039.28 | 1309593.6 | 0 | 6804994.56 | 0 | 7546238.4 | 0 | 90908.35 | 8201201.28 | 132408257 | 5204921.28 | 0 | 11304240 | 200865.6 | 4678862.4 | 33077479.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 397622483.88 | 411222715.206 | 808845199.086 | 71168630.606 | 57643635 | 43061166.77 | 9486316.8 | 353897956.04 | 175943861.87 | 189912.6 | 0 | 69496966.75 | 17321606.4 | 10635146.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 200 | 76 | 0 | 269 | 230 |  | 0 | 0 | 155 | 9 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 22 | 27 | 33 | 25 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 7 | 32 | 0 | 22 | 0 | 34 | 0 | 2 | 0 | 0 | 0 | 340 | 0 | 196 | 8 | 0 | 3 | 0 | 0 | 51 | 0 | 35 | 8 | 19 | 10 | 14 | 21 | 110 | 47 | 0 | 22 | 1 | 0 | 43 | 11 | 10 | 0 | 0 | 30 | 30 | 0 | 199 | 19 | 0 | 10 | 310 | 0 | 0 | 0 | 33 | 0 | 0 | 46 | 0 | 35 | 19 | 25 | 0 | 6 | 392 | 28 | 70 | 34 | 4 | 51 | 17 | 71 | 0 | 9 | 25 | 400 | 0 | 32 | 0 | 34 | 0 | 17 | 20 | 52 | 17 | 290 | 0 | 0 |  | 910 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 20 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 52 | 0 | 18 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 366 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 35 | 470 | 220 | 0 | 54 | 3 | 68 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 119 |  | 7973 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 349 | 196 | 0 | 0 | 0 | 138 | 8 | 34 | 15 | 0 | 0 | 0 | 9 | 8 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 22 | 27 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 17 | 156 | 0 | 0 | 0 | 0 | 6 | 32 | 51 | 22 | 0 | 34 | 0 | 9 | 0 | 0 | 0 | 280 | 25 | 171 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 0 | 19 | 10 | 21 | 21 | 114 | 101 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 33 | 81 | 0 | 200 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 8 | 365 | 47 | 88 | 68 | 0 | 284 | 17 | 52 | 0 | 117 | 25 | 389 | 17 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 148 | 0 | 0 |  | 792 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 33 | 62 | 8 | 134 | 25 | 110 | 0 | 0 | 0 | 34 | 26 | 92 | 0 | 34 | 32 | 52 | 37 | 22 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 | 0 | 147 | 0 | 0 | 90 | 0 | 0 | 333 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 | 0 | 100 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 8937 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 200 | 77 | 0 | 350 | 250 | 0 | 0 | 0 | 140 | 8 | 34 | 30 | 0 | 0 | 0 | 9 | 8 | 80 | 0 | 0 | 0 | 0 | 54 | 34 | 34 | 19 | 22 | 27 | 33 | 33 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 160 | 0 | 0 | 0 | 0 | 6 | 32 | 51 | 22 | 0 | 34 | 0 | 10 | 0 | 0 | 0 | 300 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 34 | 8 | 21 | 10 | 21 | 21 | 153 | 100 | 0 | 22 | 0 | 30 | 0 | 11 | 10 | 0 | 0 | 33 | 84 | 0 | 200 | 19 | 0 | 10 | 300 | 0 | 0 | 0 | 65 | 0 | 0 | 48 | 0 | 35 | 0 | 25 | 17 | 6 | 400 | 47 | 88 | 68 | 0 | 284 | 17 | 70 | 0 | 113 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 |  | 94 | 17 | 0 |  |  |  | 932 | 0 | 0 |  | 99 | 0 | 0 | 0 | 33 | 62 | 8 | 135 | 25 | 110 | 0 | 0 | 0 | 34 | 26 | 92 | 0 | 34 | 32 | 8 | 37 | 22 | 0 | 8 | 83 | 0 | 250 | 0 | 0 | 0 |  | 150 | 0 | 0 | 90 | 0 | 0 | 350 | 18 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 622 | 220 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 0
Forecast for Day | 0 | 0 | 0 | 0 | 200 | 74 | 0 | 300 | 240 | 0 | 0 | 0 | 140 | 8 | 20 | 15 | 0 | 0 | 0 | 8 | 8 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 27 | 25 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 6 | 32 | 51 | 22 | 0 | 25 | 0 | 5 | 0 | 0 | 0 | 290 | 300 | 180 | 0 | 0 | 0 | 0 | 0 | 51 | 0 | 31 | 0 | 21 | 10 | 19 | 19 | 135 | 50 | 0 | 21 | 1.6 | 30 | 0 | 11 | 10 | 0 | 0 | 33 | 50 | 0 | 200 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 33 | 0 | 0 | 48 | 0 | 35 | 20 | 25 | 17 | 6 | 400 | 28 | 70 | 34 | 5 | 51 | 17 | 50 | 0 | 9 | 25 | 400 | 0 | 50 | 17 | 34 | 0 | 17 | 30 | 54 | 17 | 0 |  |  |  | 932 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 19 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 0 | 350 | 0 | 0 | 35 | 0 | 35 | 0 | 8 | 35 | 622 | 220 |  | 150 | 6 | 100 | 115 | 0 |  | 0 | 30 | 0 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 200 | 75 | 0 | 389 | 241 | 0 | 0 | 0 | 148 | 9 | 34 | 12 | 0 | 0 | 0 | 9 | 8 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 16 | 22 | 28 | 25 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 160 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 22 | 0 | 3 | 0 | 19 | 0 | 0 | 0 | 280 | 80 | 188 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 19 | 10 | 25 | 21 | 98 | 54 | 0 | 22 | 0 | 30 | 0 | 14 | 10 | 0 | 0 | 31 | 40 | 0 | 195 | 0 | 0 | 10 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 33 | 6 | 25 | 17 | 6 | 386 | 28 | 34 | 34 | 1 | 51 | 0 | 49 | 0 | 9 | 25 | 400 | 9 | 9 | 17 | 107 | 0 | 0 | 5 | 52 | 17 | 150 | 0 | 0 | 0 | 911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 19 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 8 | 0 | 22 | 0 | 8 | 85 | 0 | 250 | 0 | 0 | 0 | 0 | 177 | 0 | 0 | 0 | 0 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 622 | 222 | 0 | 8 | 0 | 14 | 115 | 0 | 0 | 0 | 4 | 0 | 0 | 9 | 0 |  |  |  | 111.3526 | 19.2145 | 32.6615 | 22.7321 | 0.70338 | 2.4125 | 1.5739
190.6505
| Minimum Generation |  | 6445 | 5:00
| Highest Generation |  | 9017 | 22:00
| Day Peak Generation |  | 7973 | 12:00
| Evening Peak Generation |  | 8937 | 20:00
| HVDC Max Flow |  | 911 | 14:00
| HVDC EvPeak Flow |  | 792 | 20:00
| Load factor L.F |  | 88.1% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-01-17
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-01-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 7973 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 6615
Evening Peak Generation : |  |  | 8937 | MW Hour : | 20:00 | Available Max Generation : |  | 9565
E.P. Demand (at gen end) : |  |  | 9970 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10200
Maximum Generation : |  |  | 9017 | MW Hour : | 22:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 190.6505 | System Load Factor : | 88.1% | Load Shed : |  | 585
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 140 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-01-17
Actual : |  | 85.08 | Ft.(MSL) , | Rule curve : | 99.96 | Ft.( MSL )
Gas Consumed : |  | Total = | 842.61 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 114229797.376
: |  |  | Coal : | 175943861.87 | Oil : | 432881239.59 | Total : | 723054898.836
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 314 | 7536:00 | 3233.9672 |  |  | 125 | 3.865%
Chittagong Area |  | 10 | 240:00 | 916.1267 |  |  | 60 | 6.549%
Khulna Area |  | 237 | 5688:00 | 1209.2111 |  |  | 120 | 9.924%
Rajshahi Area |  | 138 | 3312:00 | 1072.8714 |  |  | 110 | 10.25%
Cumilla Area |  | 0 | 0:00 | 913.3054 |  |  | 40 | 4.38%
Mymensingh Area |  | 62 | 1488:00 | 754.5267 |  |  | 60 | 7.952%
Sylhet Area |  | 58 | 1392:00 | 337.2406 |  |  | 20 | 5.93%
Barisal Area |  | 0 | 0:00 | 274.9102 |  |  | 0 | 0%
Rangpur Area |  | 133 | 3192:00 | 595.7481 |  |  | 50 | 8.393%
Total |  | 952 |  | 9307.9075 |  |  | 585
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3, 4
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1,3
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:00 | 17:39 | Dhamrai 132/33kV S/S Transformer-2 HT Scheduled S/D Due to Annual maintenance.
08:18 | 12:13 | APR-Hasnabad 230kV Ckt-2 Scheduled S/D from Hasnabad 230/132kV end Due to Due to annual Maintenance
08:22 | 17:18 | Chowmuhani-Feni 132 kV Ckt-1 Scheduled S/D from Chowmuhani 132/33kV end Due to Yeary maintenance work.
08:34 |  | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end Due to S/D taken by the
Rampura substation with concern of NLDC.
08:36 | 14:47 | Kishoreganj 132/33kV S/S T3(A+B) (424TA & 424TB) HT Scheduled S/D Due to Relay testing work by SPMD
08:38 | 15:01 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Halishahar 132/33kV end Due to Yearly dead line
checking of Julda grid s/s
08:45 | 16:39 | Bhulta-Rampura 230 kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Annual maintenance.
08:51 | 14:45 | Rajbari 132/33kV S/S Bheramara-1 Scheduled S/D Due to Annual maintenance
08:51 | 17:06 | Baghabari-Sirajganj 230 kV Ckt-2 Scheduled S/D from Baghabari 230/132kV end Due to Annual Maintenance
and from Sirajgonj 230 end Due to Annual Maintenance Work
08:52 | 14:46 | Bheramara P/S-Faridpur 132 kV Ckt-1 Scheduled S/D from Bheramara 230/132kV end Due to Annual maintenance
09:06 | 10:00 | Ashuganj-Kishoreganj 132kV Ckt-2 Scheduled S/D from Kishoreganj 132/33kV end Due to
Relay testing work by SPMD
09:19 | 16:24 | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to Due 132KV
B-Bus DS(212S) of Jamal ckt-2 Annual Maintenance work purposes.
09:19 | 11:30 | Bhulta-Haripur 230 kV Ckt-2 Scheduled S/D from Bhulta 400/230kV end. and from Haripur 230/132kV end
Due to Work on other side
09:25 |  | Brahmanbaria-Narsinghdi 132 kV Ckt-1 Scheduled S/D from Brahmanbaria 132/33kV end Due to Annual maintenance
09:25 | 16:43 | Brahmanbaria-Narsinghdi 132 kV Ckt-2 Scheduled S/D from Brahmanbaria 132/33kV end Due to Annual maintenance
09:26 | 13:25 | Jhenaidah 230/132kV S/S 230 kV Bus Scheduled S/D Due to Annual maintenance
09:30 | 14:58 | Halishahar-Julda 132kV Ckt-1 Scheduled S/D from Juldah
132/33kV end Due to Breaker open 8:39am Isolator open
8:42am Grounding close 9.22am
09:31 |  | Jamalpur-Mymensingh 132kV Ckt-2 Scheduled S/D from Jamalpur 132/33kV end Due to Annual Maintenance
work MYM S/S End
09:40 |  | Moghbazar-Rampura 132kV Ckt-2 Scheduled S/D from Rampura 230/132kV end Due to Shutdown.
09:45 | 16:44 | Fenchuganj -Sylhet 132kV Ckt-1 Scheduled S/D from Sylhet 132/33kV end Due to 202B Gas Leakage Inspection.
09:54 |  | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to Oil leak repairing work.
09:54 |  | Gopalganj 132/33kV S/S T2 HT Scheduled S/D Due to Oil leak repairing work.
09:54 |  | Gopalganj 132/33kV S/S T2 LT Scheduled S/D Due to Oil leak repairing work.
09:56 | 14:10 | Kodda 132/33kV S/S Tr-4 (436T) LT Scheduled S/D
09:56 | 14:08 | Kodda 132/33kV S/S Tr-4 (436T) HT Scheduled S/D
10:06 | 17:32 | Savar 132/33kV S/S 132kV Manikganj PS-Savar Ckt-2 Scheduled S/D Due to annual maintenance
10:12 | 16:48 | Fenchuganj 230/132/33kV S/S TR-02 HT Scheduled S/D Due to Annual Maintenance.
10:16 | 16:30 | Fenchuganj 230/132/33kV S/S 132 KV Bus-2 Scheduled S/D Due to Annual Maintenance.
10:19 | 15:55 | Kishoreganj-Mymensingh 132kV Ckt-2 Scheduled S/D from Mymensingh 132/33kV end Due to Due
132KV B-Bus DS(202S) of Kish ckt-2 Annual Maintenance work purposes. and from
Kishoreganj 132/33kV end Due to Relay testing work by SPMD
10:31 | 13:11 | Fenchuganj-Kulaura 132 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Annual Maintenance.
10:48 | 14:40 | Lalmonirhat 132/33kV S/S Transformer T-2 415T LT Scheduled S/D Due to Incoming CT test T-1 Transformer Bay.
10:48 | 17:54 | Aminbazar 400/230/132kV S/S ATR-03 LT Scheduled S/D Due to DS , Automation Work
10:48 | 12:55 | Lalmonirhat 132/33kV S/S Transformer T-1 425T HT Scheduled S/D Due to Incoming CT test T-1Transformer Bay.
10:50 | 17:52 | Aminbazar 400/230/132kV S/S ATR-03 HT Scheduled S/D Due to DS, Automation Work
10:51 |  | Madanganj 132/33kV S/S Madanganj -Shitalakhya 132 kv Ckt Forced S/D
11:03 | 18:15 | Aminbazar 400/230/132kV S/S Gopalganj-1 Scheduled S/D Due to DS Automation Work
11:04 | 18:48 | Aminbazar 400/230/132kV S/S Gopalganj-2 Scheduled S/D Due to DS automation work
11:05 | 17:58 | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to DS Automation Work
11:05 | 17:58 | Aminbazar 400/230/132kV S/S ATR-02 LT Scheduled S/D Due to DS Automation Work
11:07 | 16:55 | Ishurdi 230/132kV S/S 230/132 kV T-01 HT Scheduled S/D Due to 230 kv T01 PT oil leakage work
11:08 | 17:58 | Aminbazar 400/230/132kV S/S ATR-02 HT Scheduled S/D Due to DS Automatio Work
11:11 | 12:16 | Siddhirganj 132/33kV S/S 120MW EGCB GT1 Forced S/D Due to Unit Transformer Inspection By EGCB authority
11:24 | 17:47 | Aminbazar 400/230/132kV S/S 230 kv Bus 02 Scheduled S/D Due to DS Automation Work
12:00 |  | Day peak gen: 7974 MW.
12:18 | 19:59 | Shyampur 230/132kV S/S 230 kV APR (D04) Scheduled S/D Due to Annual Maintenance at Apr end
12:40 |  | Fenchuganj CCPP-2 tripped. |  |  |  |  | 43.0MW power interruption.
| 12:55 | Lalmonirhat 132/33kV S/S Transformer T-1 425T LT is restored.
13:05 | 14:40 | Lalmonirhat 132/33kV S/S Transformer T-2 415T HT Scheduled S/D Due to Incoming CT
test T-2 Transformer Bay.
13:05 | 14:40 | Lalmonirhat 132/33kV S/S Transformer T-2 415T LT Scheduled S/D Due to Incoming CT test T-12 Transformer Bay.
13:14 | 16:15 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Annual Maintenance.
14:00 |  | Shift duty received in normal condition. Load shade continue at Rajshahi and Rangpur zone.
| 14:15 | Khulna (C) S/S TR-1 425T HT is restored.
| 14:16 | Khulna (C) S/S TR-1 425T LT is restored.
14:29 | 14:56 | Chandpur 132/33kV S/S 422T LT Scheduled S/D Due to 33KV T-5 Bus section auxilary transformer -2 fuse repair |  |  |  |  | 18.0MW power interruption.
14:30 | 14:55 | Chandpur 132/33kV S/S 422T HT Scheduled S/D Due to 33KV T-5 Bus section auxilary transformer -2 fuse repair
| 14:47 | Khagrachori 132/33kV S/S TR-1 HT is restored.
15:03 |  | Re-allocation Rajshahi zone 730 MW .
15:15 |  | L/S free Rajshahi zone.
| 15:40 | Mymensingh 132/33kV S/S Bus A is restored.
15:48 |  | L/S free Rangpur zone.
| 15:55 | Kishoreganj-Mymensingh 132kV Ckt-2 is restored.
| 15:58 | Munshiganj 132/33kV S/S Sinha Peoples Energy Limited (SPEL) 52.5 MW IPP is restored.
16:02 |  | SS Power (Banshkhali) U-1 400/22 kv, 840 MVA Tr. (unit Transformer) was switched on for 24 hr observation
16:02 |  | SS Power (Banshkhali) U-1 400/22 kv, 840 MVA Tr. (unit Transformer) was switched on for 24 hr observation
16:35 |  | Allocation Rajshahi zone 710 MW & Rangpur zone 530 MW
16:53 |  | Fenchugonj gt-2 sync.
17:14 |  | Ashuganj South 360MW GT was sync.
| 17:26 | Haripur 230/132kV S/S Shyampur (Fatulla) is restored.
| 17:28 | Dhamrai-Kaliakoir 132 kV Ckt-2 is restored.
| 17:40 | Dhamrai 132/33kV S/S Transformer-2 LT is restored.
17:50 |  | Aminbazar - Gopalganj 400 KV Ckt 02 is restored.
17:52 |  | Aminbazar - Gopalganj 400 KV Ckt 01 is restored.
18:05 |  | Re-allocation Rajshahi zone 670 MW Rangpur zone 500 MW.
18:20 |  | L/S free Rajshahi(N), Rajshahi (o), Capai. & Amnura S/Ss.
18:46 |  | L/S free Nator S/S.
19:01 |  | Re-allocation Rajshahi zone 720 MW Rangpur zone 530 MW.
20:00 |  | Evening Peak Gen. 8937 MW
06:19 |  | Dohazari 132/33kV S/S Power Transformer -T-2 HT Project Work S/D Due to G2G Pilling work for transformer
upgradation.
06:20 |  | Dohazari 132/33kV S/S Power Transformer -T-2 LT Project Work S/D Due to G2G Pilling work for transformer
upgradation.
07:21 |  | Patuakhali 132/33kV S/S 425T (T-3) LT Project Work S/D Due to 33 Kv capacitor bank DS loop remove
07:22 |  | Patuakhali 132/33kV S/S 425T (T-3) HT Project Work S/D Due to 33 Kv capacitor bank ds loop remove
07:23 |  | Patuakhali-Payra 132kV Ckt-1 Scheduled S/D from Patuakhali 132/33kV end Due to Annual Maintenance
and from Payra 400/132/33kV end Due to Maintenance
07:29 |  | Cumilla(N) 230/132/33kV S/S 132KV T-05 HT Scheduled S/D Due to Maintenance work
07:29 |  | Cumilla(N) 230/132/33kV S/S 132KV T-05 LT Scheduled S/D Due to Maintenance work
07:44 |  | Meghnaghat-Shyampur 230kV Ckt-2 Scheduled S/D from Shyampur 230/132kV end Due to Due to deadline checking
07:57 |  | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Annual maintenance works.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-01-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 200 | 4677900 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 77 | 1680045 | Machine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 349 | 7563260 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 196 | 5472000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 8 | 192960 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 138 | 3538822 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 34 | 539880 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 360608 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 405576 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 9 | 192000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 8 | 214704 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 266040 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 712800 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 316761 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 327934 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1108680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 667080
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 760500
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 8 | 166560 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 65 | 853091 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 35 | 714096 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1101204 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 97920 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 267840 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 123874
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 354600 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1586 | 32676735
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 225088 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 119340
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 34 | 585120 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 703380 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 156 | 3678799 | ST under S/D
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 68 | 1155018 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 32 | 511873 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 426343 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 447600 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 514560 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 360960
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 42240 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 23160
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 284 | 1957091 | High Voltage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 261459 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 52 | 1429339 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 503040 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1288418 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 890 | 14232828
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 171 | 4864000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7460000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 25 | 366000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 148 | 6276400 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 38304 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 0 | 17280 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 117090 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1254472
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 8 | 157236 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 34 | 465952 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 239040 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448668
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 245700 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2412480
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 21 | 536000 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 49718 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 469110 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 117 | 1095360
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 285480 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1333440 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1147 | 28131730
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 101 | 1852800 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 497736
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 7850
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 48 | 1096800 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 678000 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 184360
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 167760 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 224 | 4485306
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 215000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 540360 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 14 | 324000 | Gas shortage
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 10 | 334584 | Gas shortage
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 764448
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1302720
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 200 | 5029940 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 439000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7196000 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 365 | 9044000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 253800
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 389 | 9554200
| Sylhet Area Total |  |  |  | 2427 | 1441 | 34998052
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 792 | 19214545 | Generation shortage in INDIA
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 66 | 469440 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 33 | 231840 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 62 | 396160 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 34875 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 90 | 452160
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 97440 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 398880
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3001 | 1068 | 21295340
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1531296 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 25 | 462392 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 134 | 3016000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14695700 | Unit-2 Under maint.
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5102864
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1527600
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | On test.
| Barisal Area Total |  |  |  | 2265 | 1211 | 26335852
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 182483
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 26 | 97072
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 599470 | High Voltage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 132208 | High Voltage
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 147 | 4032555
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 0 | 0 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 333 | 8723272 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 37 | 305714 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 466560
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 193698 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 325536 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 680544 | High Voltage
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 35 | 575232 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 675552 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17760
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 887 | 17007656
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 83 | 1967127 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6069300
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 35 | 594192 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 8227
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 115 | 2157696
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 52216
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 638250
| Rangpur Area Total |  |  |  | 750 | 483 | 11487008
| Total |  |  |  | 22700 | 8937 | 190650507
| Eastern Grid Total |  |  |  | 14555 | 5288 | 114524651
| Western Grid Total |  |  |  | 8145 | 3649 | 76125856
| National Grid Total |  |  |  | 22700 | 8937 | 190650507
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-01-16
| (a) ENTIRE EASTERN GRID : |  | 5822.16 | MW | (b) ENTIRE WESTERN GRID : |  | 2619.3 | MW
| i) Dhaka area |  | 3008.46 | MW | i) Khulna area |  | 919.5 | MW
| ii) Chittagong area |  | 887.7 | MW | ii) Rajshahi area |  | 861.2 | MW
| iii) Comilla area |  | 806 | MW | iii) Barisal area |  | 268.6 | MW
| iv) Mymensingh area |  | 816 | MW | iv) Rangpur area |  | 570 | MW
| v) Sylhet area |  | 304 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 8441.46 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 16 | 18:00 | Kamrangirchar | 63 | 18:00 | Natore | 100 | 19:00 | Shitalakhya | 100 | 12:00
2 | AKSML | 92 | 06:00 | Chowmuhani | 139 | 18:30 | Kaptai | 3.5 | 18:00 | Nawabganj | 27.9 | 20:00 | Sholosohor | 23 | 12:00
3 | Aftabnagar | 22 | 18:00 | Chuadanga | 63 | 13:00 | Kazla | 86 | 18:30 | Netrakona | 112 | 23:00 | Shyampur | 120 | 00:00
4 | Agargaon | 51 | 13:00 | Coxsbazar | 87 | 21:00 | Keranigonj | 42 | 13:00 | New | 55 | 12:00 | Siddhirganj | 86 | 12:00
5 | Agrabad | 44 | 20:00 | Cumilla(N) | 100 | 19:30 | Khagrachori | 24 | 18:00 | Niamatpur | 67 | 22:00 | Sirajganj | 63 | 18:30
6 | Amnura | 43 | 18:30 | Cumilla(S) | 129 | 18:00 | Khulna | 66 | 13:00 | Noapara | 28 | 22:00 | Sonargaon | 79 | 00:00
7 | Ashuganj | 42 | 18:00 | Daudkandi | 80 | 21:00 | Khulshi | 136 | 21:00 | PHP | 11 | 14:00 | Sreemongol | 35 | 22:00
8 | BIPTC | N/A | N/A | Dhaka | 24 | 12:00 | Kishoreganj | 108 | 21:00 | Pabna | 60 | 18:00 | Srinagar | 29.2 | 21:00
9 | BSRM | 111 | 15:00 | Dhamrai | 74 | 18:00 | Kodda | 185 | 22:00 | Palashbari | 84 | 08:00 | Sunamganj | 29 | 22:00
10 | Bagerhat | 71 | 18:00 | Dhanmondi | 74 | 13:00 | Kulaura | 24 | 18:00 | Panchagarh | 40 | 22:00 | Sylhet | 84 | 21:00
11 | Bakulia | 64 | 19:30 | Dohazari | 74 | 19:30 | Kurigram | 50 | 23:00 | Patuakhali | 70 | 22:00 | TK | 14.5 | 17:00
12 | Banani | 23 | 15:00 | Faridpur | 95 | 22:00 | Kushtia | 82 | 12:00 | Payra | 10.6 | 20:00 | Tangail | 146 | 20:00
13 | Bangabhaban | 9 | 11:00 | Fatullah | 48 | 18:00 | Lalbag | 73 | 18:00 | Postogola | 30 | 18:00 | Thakurgaon | 59 | 20:00
14 | Barapukuria | 56 | 15:00 | Fenchuganj | 24 | 19:00 | Lalmonirhat | 19 | 21:00 | Purbachal | 12 | 12:00 | Tongi | 90 | 11:00
15 | Barguna | 12 | 18:00 | Feni | 81 | 21:00 | Madanganj | 30 | 20:00 | Purbasadipur | 93 | 22:00 | Ullon | 34 | 21:00
16 | Barishal | 71 | 18:30 | GPH | 90 | 15:00 | Madaripur | 65 | 22:00 | Rahanpur_I | 3.4 | 15:00 | Uttara | 52 | 14:00
17 | Barishal-230 | 48 | 19:30 | Ghorashal | 46 | 22:00 | Madartek | 46 | 18:00 | Rahim | 37 | 09:00 | UttaraNew | 12 | 15:00
18 | Baroaulia | 58 | 15:00 | Goalpara | 20 | 13:00 | Madunaghat | 39 | 18:00 | Rajbari | 46 | 22:00 | Zigatola | 32 | 15:00
19 | Baroirhat | 37 | 19:30 | Gollamari | 38 | 12:00 | Magura | 34 | 18:00 | Rajendrapur | 72 | 07:00
20 | Bashundhara | 104 | 18:00 | Gopalganj | 66 | 18:00 | Mahasthangarh | 36 | 08:00 | Rajshahi | 102 | 20:00
21 | BashundharaCement | 12 | 16:00 | Gulshan | 62 | 18:30 | Manikganj | 71 | 22:00 | Rajshahi-230 | 24 | 19:00
22 | Beanibazar | 38 | 18:00 | Halishahar | 79 | 15:00 | Maniknagar | 36 | 13:00 | Ramganj | 74 | 20:00
23 | Benapole | 46 | 12:00 | HaripurSBU | 134 | 00:00 | Matarbari | 32 | 19:30 | Rampur | 18 | 18:00
24 | Bhaluka | 102 | 23:00 | Hasnabad | 64 | 12:00 | Matuail | 52.2 | 12:00 | Rangamati | 10 | 18:00
25 | Bhandaria | 36 | 18:00 | Hathazari | 43 | 19:30 | Millgate | 50 | 16:00 | Rangpur | 89 | 18:00
26 | Bhangura | 20 | 18:00 | Ishurdi | 45 | 18:00 | Mirpur | 85 | 18:30 | Ruppur | 3.4 | 09:00
27 | Bheramara(GK) | 33 | 22:00 | Jaldhaka | 38 | 22:00 | Mirsorai | 3 | 19:00 | SSM | 2 | 01:00
28 | Bhulta | 203 | 00:00 | Jamalpur | 114 | 19:30 | Mithapukur | 22 | 18:00 | Saidpur | 78 | 17:00
29 | Bog-Sherpur | 48 | 07:00 | Jashore | 109 | 13:00 | Modern | 0 | 00:00 | Satkhira | 70 | 13:00
30 | Bogura | 92 | 22:00 | Jhenaidah | 74 | 13:00 | Mogbazar | 81 | 18:00 | Satmasjid | 59 | 18:30
31 | Borhanuddin | 32 | 21:00 | Joydebpur | 122 | 10:00 | Mongla | 16 | 00:00 | Savar | 118 | 18:30
32 | Brahmanbaria | 104 | 20:00 | Joypurhat | 36 | 19:00 | Motijheel | 22 | 18:00 | Shahjadpur | 63 | 19:30
33 | Cantonment | 88 | 18:00 | Juldah | 27 | 10:00 | Munshiganj | 63 | 21:00 | Shahjibazar | 88 | 22:00
34 | Chandpur | 45 | 19:00 | KSRM | 31.5 | 02:00 | Mymensingh | 180 | 20:00 | Shahmirpur | 33.7 | 00:00
35 | Chandraghona | 22 | 18:00 | Kabirpur | 192 | 08:00 | Naogaon | 81 | 00:00 | Shariatpur | 48 | 22:00
36 | Chapai | 48 | 18:30 | Kachua | 44 | 18:30 | Narail | 31 | 18:00 | Sherpur | 114 | 21:00
37 | Charsaidpur | 43 | 17:00 | Kallyanpur | 57 | 13:00 | Narinda | 43 | 12:00 | Shikalbaha | 21 | 10:00
38 | Chauddagram | 29 | 18:00 | Kalurghat | 24 | 11:00 | Narshingdi | 115 | 22:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-01-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 416 | 21:00 | 380 | 20:00 | Gopalganj_I | N/A | N/A | N/A | N/A
| Bhulta | 399 | 21:00 | 383 | 12:00 | Kaliakoir | 403 | 01:00 | 388 | 14:00
| Bibiana | 409 | 00:00 | 397 | 12:00 | Payra | 425 | 11:00 | 411 | 13:00
| BIPTC | 407 | 03:00 | 391 | 13:00 | Rahanpur_I | 417 | 18:00 | 390 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 242 | 01:00 | 225 | 12:00 | Hasnabad | 242 | 21:00 | 226 | 13:00
| AKSML | 244 | 18:00 | 224 | 10:00 | Hathazari | 244 | 19:00 | 233 | 12:00
| Aminbazar | 243 | 03:00 | 227 | 11:00 | Ishurdi | 246 | 20:00 | 227 | 12:00
| Ashuganj | 245 | 01:00 | 235 | 12:00 | Jhenaidah | 244 | 20:00 | 225 | 13:00
| Baghabari | 240 | 01:00 | 227 | 12:00 | Kaliakoir | 241 | 01:00 | 228 | 14:00
| Barapukuria | 232 | 00:00 | 227 | 12:00 | Keranigonj | 241 | 01:00 | 240 | 04:00
| Barishal | 248 | 19:00 | 241 | 13:00 | Khulna(S) | 246 | 21:00 | 226 | 13:00
| Bheramara | 244 | 20:00 | 225 | 14:00 | Maniknagar | 239 | 01:00 | 225 | 12:00
| Bhulta | 242 | 05:00 | 228 | 12:00 | Meghnaghat | 245 | 02:00 | 235 | 12:00
| Bibiana | 241 | 09:00 | 234 | 12:00 | Mirsorai | 241 | 00:00 | 228 | 12:00
| BIPTC | 246 | 20:00 | 227 | 12:00 | Rajshahi | 251 | 20:00 | 231 | 12:00
| Bogura | 237 | 18:30 | 229 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 250 | 15:00 | 248 | 00:00 | Rampura | 239 | 01:00 | 226 | 12:00
| BSRM | 244 | 19:00 | 232 | 10:00 | Shikalbaha | 244 | 19:00 | 233 | 10:00
| Cumilla(N) | 242 | 20:00 | 230 | 12:00 | Shyampur | 241 | 20:00 | 225 | 12:00
| Fenchuganj | 243 | 00:00 | 235 | 16:00 | Siddhirganj | 240 | 00:00 | 231 | 13:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 237 | 20:00 | 228 | 12:00
| GPH | 243 | 19:00 | 229 | 10:00 | Tongi | 239 | 01:00 | 224 | 11:00
| Haripur | 237 | 20:00 | 226 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 139 | 00:00 | 130 | 12:00 | Kushtia | 141 | 20:00 | 129 | 12:00
| Agargaon | 141 | 01:00 | 131 | 12:00 | Lalbag | 136 | 05:00 | 125 | 12:00
| Agrabad | 141 | 15:00 | 132 | 10:00 | Lalmonirhat | 134 | 19:00 | 130 | 17:00
| AKS | 140 | 17:00 | 133 | 07:00 | Madanganj | 141 | 20:00 | 133 | 10:00
| Aminbazar | 140 | 01:00 | 129 | 11:00 | Madaripur | 139 | 02:00 | 131 | 12:00
| Amnura | 138 | 18:00 | 127 | 12:00 | Madartek | 139 | 01:00 | 130 | 12:00
| Ashuganj | 140 | 21:00 | 136 | 11:00 | Madunaghat | 142 | 20:00 | 134 | 10:00
| Bagerhat | 140 | 18:30 | 126 | 13:00 | Magura | 140 | 00:00 | 128 | 12:00
| Bakulia | 143 | 18:00 | 134 | 10:00 | Mahasthangarh | 139 | 19:00 | 132 | 12:00
| Banani | 139 | 01:00 | 128 | 12:00 | Manikganj | 135 | 00:00 | 128 | 11:00
| Bangabhaban | 139 | 00:00 | 129 | 12:00 | Maniknagar | 139 | 03:00 | 130 | 12:00
| Barapukuria | 137 | 00:00 | 134 | 04:00 | Matarbari | 137 | 18:00 | 127 | 03:00
| Barguna | 142 | 09:00 | 137 | 13:00 | Matuail | 140 | 20:00 | 132 | 12:00
| Barishal | 140 | 00:00 | 135 | 13:00 | Millgate | 138 | 00:00 | 128 | 12:00
| Barishal-230 | 141 | 05:00 | 136 | 13:00 | Mirpur | 139 | 04:00 | 127 | 12:00
| Baroaulia | 143 | 18:00 | 136 | 10:00 | Mithapukur | 137 | 00:00 | 131 | 12:00
| Baroirhat | 143 | 22:00 | 134 | 12:00 | Modern | 140 | 21:00 | 133 | 10:00
| Bashundhara | 139 | 00:00 | 128 | 12:00 | Mogbazar | 140 | 00:00 | 131 | 12:00
| BashundharaCement | 141 | 20:00 | 133 | 10:00 | Mongla | 139 | 01:00 | 126 | 13:00
| Beanibazar | 135 | 01:00 | 132 | 12:00 | Motijheel | 139 | 00:00 | 129 | 12:00
| Benapole | 139 | 18:30 | 124 | 13:00 | Munshiganj | 141 | 21:00 | 133 | 12:00
| Bhaluka | 130 | 16:00 | 119 | 23:00 | Mymensingh | 133 | 00:00 | 118 | 06:00
| Bhandaria | 140 | 00:00 | 135 | 13:00 | Naogaon | 138 | 18:30 | 129 | 12:00
| Bhangura | 144 | 01:00 | 135 | 12:00 | Narail | 140 | 01:00 | 126 | 12:00
| Bheramara | 141 | 20:00 | 130 | 12:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 141 | 19:00 | 134 | 11:00 | Narshingdi | 138 | 20:00 | 131 | 12:00
| Bhulta | 135 | 20:00 | 128 | 12:00 | Natore | 138 | 00:00 | 131 | 12:00
| Bog-Sherpur | 140 | 00:00 | 132 | 12:00 | Nawabganj | 137 | 01:00 | 125 | 12:00
| Bogura | 141 | 21:00 | 133 | 12:00 | Netrakona | 130 | 10:00 | 118 | 23:00
| Bogura-230 | 140 | 00:00 | 134 | 12:00 | New | 139 | 03:00 | 128 | 12:00
| Brahmanbaria | 135 | 00:00 | 131 | 12:00 | Niamatpur | 136 | 00:00 | 127 | 12:00
| Cantonment | 141 | 01:00 | 141 | 21:00 | Noapara | 142 | 21:00 | 127 | 12:00
| Chandpur | 142 | 00:00 | 134 | 12:00 | Pabna | 142 | 19:00 | 132 | 12:00
| Chandraghona | 143 | 18:30 | 135 | 10:00 | Palashbari | 136 | 00:00 | 130 | 07:00
| Chapai | 137 | 21:00 | 127 | 12:00 | Panchagarh | 140 | 09:00 | 126 | 02:00
| Charsaidpur | 142 | 21:00 | 133 | 12:00 | Patuakhali | 142 | 10:00 | 134 | 08:00
| Chauddagram | 141 | 00:00 | 135 | 12:00 | Payra | 141 | 11:00 | 134 | 22:00
| Chhatak | 135 | 02:00 | 132 | 10:00 | PHP | 141 | 00:00 | 134 | 12:00
| Chowmuhani | 143 | 18:00 | 130 | 12:00 | Postogola | 139 | 01:00 | 127 | 12:00
| Chuadanga | 139 | 19:00 | 124 | 13:00 | Purbachal | 140 | 00:00 | 128 | 12:00
| Coxsbazar | 135 | 12:00 | 126 | 06:00 | Purbasadipur | 138 | 00:00 | 131 | 05:00
| Cumilla(N) | 144 | 20:00 | 136 | 12:00 | Rahim | 141 | 20:00 | 134 | 12:00
| Cumilla(S) | 143 | 22:00 | 127 | 11:00 | Rajbari | 138 | 18:30 | 127 | 13:00
| Daudkandi | 141 | 19:00 | 134 | 12:00 | Rajendrapur | 141 | 01:00 | 126 | 12:00
| Dhaka | 140 | 21:00 | 130 | 12:00 | Rajshahi | 135 | 00:00 | 128 | 07:00
| Dhamrai | 141 | 01:00 | 129 | 12:00 | Rajshahi-230 | 136 | 20:00 | 125 | 12:00
| Dhanmondi | 142 | 20:00 | 134 | 12:00 | Ramganj | 142 | 00:00 | 132 | 11:00
| Dohazari | 140 | 15:00 | 126 | 08:00 | Rampur | 140 | 18:00 | 132 | 12:00
| Faridpur | 138 | 21:00 | 128 | 12:00 | Rampura | 139 | 00:00 | 130 | 12:00
| Fatullah | 140 | 01:00 | 129 | 12:00 | Rangamati | 142 | 19:00 | 134 | 10:00
| Fenchuganj | 138 | 00:00 | 134 | 12:00 | Rangpur | 135 | 09:00 | 131 | 12:00
| Feni | 142 | 01:00 | 135 | 12:00 | Ruppur | 142 | 21:00 | 131 | 12:00
| Ghorashal | 143 | 21:00 | 139 | 13:00 | Saidpur | 136 | 09:00 | 130 | 06:00
| Goalpara | 142 | 18:30 | 129 | 12:00 | Satkhira | 140 | 04:00 | 126 | 13:00
| Gollamari | 141 | 18:30 | 128 | 12:00 | Satmasjid | 141 | 01:00 | 131 | 12:00
| Gopalganj | 139 | 04:00 | 129 | 12:00 | Savar | 139 | 01:00 | 125 | 12:00
| Gopalganj-400 | N/A | N/A | N/A | N/A | Shahjadpur | 147 | 00:00 | 142 | 10:00
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 137 | 00:00 | 134 | 10:00
| Gulshan | 138 | 00:00 | 130 | 12:00 | Shahmirpur | 141 | 18:00 | 133 | 10:00
| Halishahar | 141 | 15:00 | 132 | 10:00 | Shariatpur | 138 | 00:00 | 129 | 13:00
| Haripur | 141 | 20:00 | 134 | 12:00 | Sherpur | 133 | 15:00 | 117 | 07:00
| HaripurSBU | 140 | 19:30 | 134 | 11:00 | Shikalbaha | 143 | 15:00 | 134 | 10:00
| Hasnabad | 139 | 21:00 | 129 | 12:00 | Shikalbaha-230 | 141 | 18:30 | 135 | 04:00
| Hathazari | 143 | 19:00 | 137 | 10:00 | Shitalakhya | 138 | 00:00 | 125 | 12:00
| Ishurdi | 142 | 19:00 | 131 | 12:00 | Sholosohor | 141 | 19:00 | 133 | 10:00
| Jaldhaka | 135 | 00:00 | 122 | 18:30 | Shyampur | 138 | 21:00 | 128 | 12:00
| Jamalpur | 135 | 19:00 | 120 | 07:00 | Shyampur-230 | 139 | 04:00 | 129 | 12:00
| Jashore | 139 | 20:00 | 122 | 13:00 | Siddhirganj | 140 | 01:00 | 133 | 12:00
| Jhenaidah | 141 | 00:00 | 127 | 12:00 | Sirajganj | 143 | 00:00 | 132 | 12:00
| Jhenaidah-230 | 141 | 01:00 | 129 | 13:00 | Sonargaon | 138 | 19:00 | 133 | 09:00
| Joydebpur | 142 | 00:00 | 138 | 12:00 | Sreemongol | 139 | 04:00 | 136 | 11:00
| Joypurhat | 137 | 00:00 | 129 | 12:00 | Srinagar | 136 | 03:00 | 125 | 12:00
| Juldah | 139 | 21:00 | 134 | 09:00 | SSM | 145 | 18:30 | 138 | 10:00
| Kabirpur | 138 | 20:00 | 127 | 12:00 | Sunamganj | 134 | 03:00 | 130 | 11:00
| Kachua | 143 | 22:00 | 135 | 12:00 | Sylhet | 134 | 01:00 | 132 | 14:00
| Kaliakoir | 136 | 23:00 | 129 | 11:00 | Tangail | 135 | 00:00 | 127 | 19:30
| Kallyanpur | 140 | 21:00 | 128 | 12:00 | Thakurgaon | 141 | 09:00 | 126 | 02:00
| Kalurghat | 142 | 19:00 | 134 | 10:00 | TK | 141 | 20:00 | 135 | 09:00
| Kamrangirchar | 136 | 05:00 | 125 | 12:00 | Tongi | 140 | 01:00 | 130 | 11:00
| Kaptai | 142 | 00:00 | 134 | 01:00 | Ullon | 139 | 01:00 | 130 | 12:00
| Kazla | 138 | 01:00 | 130 | 13:00 | Uttara | 139 | 00:00 | 127 | 12:00
| Keranigonj | 137 | 01:00 | 125 | 12:00 | UttaraNew | 139 | 01:00 | 127 | 12:00
| Khagrachori | 142 | 22:00 | 134 | 10:00 | Zigatola | 136 | 04:00 | 125 | 12:00
| Khulna | 141 | 03:00 | 127 | 13:00
| Khulna(S) | 141 | 01:00 | 130 | 12:00
| Khulshi | 140 | 07:00 | 133 | 10:00
| Kishoreganj | 133 | 07:00 | 126 | 23:00
| Kodda | 142 | 21:00 | 128 | 11:00
| KSRM | 142 | 20:00 | 133 | 10:00
| Kulaura | 137 | 00:00 | 134 | 12:00
| Kurigram | 134 | 09:00 | 127 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-01-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 480 | 4815 | 3266 | 8081 |  |  |  | QF-LDC-11
0:30 | 425 | 4686.5 | 3065.5 | 7752 | Date: | 2023-01-16
1:00 | 370 | 4558 | 2865 | 7423
1:30 | 340 | 4435.5 | 2698 | 7133.5
2:00 | 310 | 4313 | 2531 | 6844
2:30 | 305 | 4254.5 | 2521 | 6775.5 | [5 empty] | Gen. at Eve. Peak | 8937 | 9664 MW (19:00 )
3:00 | 300 | 4196 | 2511 | 6707 | [6 empty] | 20:00
3:30 | 310 | 4133 | 2454 | 6587 | [5 empty] | Gen. at Day Peak | 7973 | 8717 MW (12:00 )
4:00 | 320 | 4070 | 2397 | 6467 | [6 empty] | 12:00
4:30 | 310 | 4062.5 | 2393.5 | 6456 | [5 empty] | Highest Generation | 9017
5:00 | 300 | 4055 | 2390 | 6445 | [6 empty] | 22:00
5:30 | 265 | 4146 | 2418.5 | 6564.5
6:00 | 230 | 4237 | 2447 | 6684
6:30 | 185 | 4363.5 | 2542 | 6905.5
7:00 | 140 | 4490 | 2637 | 7127
7:30 | 232 | 4547 | 2852.5 | 7399.5
8:00 | 324 | 4604 | 3068 | 7672
8:30 | 447 | 4566.5 | 3133 | 7699.5
9:00 | 570 | 4529 | 3198 | 7727
9:30 | 717 | 4549.5 | 3176 | 7725.5
10:00 | 864 | 4570 | 3154 | 7724
10:30 | 1037 | 4593.5 | 3117 | 7710.5
11:00 | 1210 | 4617 | 3080 | 7697
11:30 | 1240 | 4674 | 3161 | 7835
12:00 | 1270 | 4731 | 3242 | 7973
12:30 | 1255 | 4655 | 3298 | 7953
13:00 | 1240 | 4579 | 3354 | 7933
13:30 | 1290 | 4564 | 3356.5 | 7920.5
14:00 | 1340 | 4549 | 3359 | 7908
14:30 | 1345 | 4553 | 3278 | 7831
15:00 | 1350 | 4557 | 3197 | 7754
15:30 | 1220 | 4636 | 3074 | 7710
16:00 | 1090 | 4715 | 2951 | 7666
16:30 | 1075 | 4875 | 2999 | 7874
17:00 | 1060 | 5035 | 3047 | 8082
17:30 | 775 | 5228 | 3246.5 | 8474.5
18:00 | 490 | 5421 | 3446 | 8867
18:30 | 500 | 5375.5 | 3509 | 8884.5
19:00 | 510 | 5330 | 3572 | 8902
19:30 | 470 | 5285 | 3575 | 8860
20:00 | 484 | 5288 | 3649 | 8937 |  |  |  | Executive Engineer
20:30 | 497 | 5238 | 3674.5 | 8912.5 |  |  |  | Network Operation Division
21:00 | 510 | 5188 | 3700 | 8888
21:30 | 555 | 5189 | 3763.5 | 8952.5
22:00 | 600 | 5190 | 3827 | 9017 |  |  |  |  | Page 6 of 7
22:30 | 550 | 5092.5 | 3696 | 8788.5
23:00 | 500 | 4995 | 3565 | 8560
23:30 | 490 | 4905 | 3415.5 | 8320.5
24:00 | 480 | 4815 | 3266 | 8081
9664 MW (19:00 )
8717 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-01-16 |  | Energy |  | 190650507
[13 empty] | 2023-01-16 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3098 | 910 | 1544 | 0 | 1367 | 954 | 30 | 0 | 80 | 98 | 0 | 0
0:30 | 3105.5 | 818.5 | 1556.5 | 0 | 1154 | 953.5 | 30 | 0 | 40 | 94 | 0 | 0 | Date: | 2023-01-16
1:00 | 3113 | 727 | 1569 | 0 | 941 | 953 | 30 | 0 | 0 | 90 | 0 | 0
1:30 | 3141.5 | 680 | 1589 | 0 | 655 | 953 | 30 | 0 | 0 | 85 | 0 | 0 | [7 empty] | Total Energy | 190.6505 | Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
2:00 | 3170 | 633 | 1609 | 0 | 369 | 953 | 30 | 0 | 0 | 80 | 0 | 0 | [7 empty] | Energy not Served | 12.0495
2:30 | 3180 | 633.5 | 1611 | 0 | 309 | 932 | 30 | 0 | 0 | 80 | 0 | 0 | [7 empty] | Energy Requirement | 202.7
3:00 | 3190 | 634 | 1613 | 0 | 249 | 911 | 30 | 0 | 0 | 80 | 0 | 0
3:30 | 3191 | 633.5 | 1548.5 | 0 | 232 | 872 | 30 | 0 | 0 | 80 | 0 | 0 | [5 empty] | Shortage
4:00 | 3192 | 633 | 1484 | 0 | 215 | 833 | 30 | 0 | 0 | 80 | 0 | 0
4:30 | 3190 | 633 | 1478 | 0 | 215 | 832 | 30 | 0 | 0 | 78 | 0 | 0
5:00 | 3188 | 633 | 1472 | 0 | 215 | 831 | 30 | 0 | 0 | 76 | 0 | 0
5:30 | 3212 | 633 | 1488.5 | 0 | 292 | 831 | 30 | 0 | 0 | 78 | 0 | 0
6:00 | 3236 | 633 | 1505 | 0 | 369 | 831 | 30 | 0 | 0 | 80 | 0 | 0
6:30 | 3208.5 | 633 | 1570.5 | 0 | 525 | 845.5 | 30 | 0 | 8 | 82 | 3 | 102.7556 |  |  |  | Coal
7:00 | 3181 | 633 | 1636 | 0 | 681 | 860 | 30 | 0 | 16 | 84 | 6 | 205.5112
7:30 | 3145.5 | 748 | 1630.5 | 0 | 801.5 | 900.5 | 30 | 0 | 32 | 89 | 22.5 | 407.3362 |  |  | Oil |  |  |  | ,
8:00 | 3110 | 863 | 1625 | 0 | 922 | 941 | 30 | 0 | 48 | 94 | 39 | 609.1611
8:30 | 3070 | 839 | 1561 | 0 | 1018 | 946.5 | 30 | 0 | 58 | 98 | 79 | 776.8877
9:00 | 3030 | 815 | 1497 | 0 | 1114 | 952 | 30 | 0 | 68 | 102 | 119 | 944.6144
9:30 | 3015 | 815 | 1462.5 | 0 | 1159.5 | 925.5 | 30 | 0 | 68.5 | 103 | 146.5 | 869.0452
10:00 | 3000 | 815 | 1428 | 0 | 1205 | 899 | 30 | 0 | 69 | 104 | 174 | 793.4761
10:30 | 2993 | 815 | 1432.5 | 0 | 1208 | 839.5 | 30 | 0 | 70 | 107 | 215.5 | 856.604
11:00 | 2986 | 815 | 1437 | 0 | 1211 | 780 | 30 | 0 | 71 | 110 | 257 | 919.7318
11:30 | 3037.5 | 862.5 | 1477 | 0 | 1178 | 790.5 | 30 | 0 | 85 | 110 | 264.5 | 929.4084
12:00 | 3089 | 910 | 1517 | 0 | 1145 | 801 | 30 | 0 | 99 | 110 | 272 | 939.0849
12:30 | 3020.5 | 910 | 1519 | 0 | 1139 | 857 | 30 | 0 | 116 | 108 | 253.5 | 958.8988
13:00 | 2952 | 910 | 1521 | 0 | 1133 | 913 | 30 | 0 | 133 | 106 | 235 | 978.7127
13:30 | 2952 | 910 | 1521 | 0 | 1133 | 913 | 30 | 0 | 133 | 106 | 235 | 978.7127
14:00 | 2952 | 910 | 1521 | 0 | 1133 | 913 | 30 | 0 | 133 | 106 | 235 | 978.7127
14:30 | 2910.5 | 910.5 | 1467.5 | 0 | 1142.5 | 904 | 30 | 0 | 167.5 | 107.5 | 203.5 | 985.1637
15:00 | 2869 | 911 | 1414 | 0 | 1152 | 895 | 30 | 0 | 202 | 109 | 172 | 991.6147
15:30 | 2889.5 | 910 | 1381.5 | 0 | 1217.5 | 839.5 | 30 | 0 | 207 | 104.5 | 130.5 | 840.9372
16:00 | 2910 | 909 | 1349 | 0 | 1283 | 784 | 30 | 0 | 212 | 100 | 89 | 690.2597
16:30 | 2990 | 909.5 | 1342.5 | 0 | 1382 | 795 | 30 | 0 | 269.5 | 102 | 53.5 | 629.8965
17:00 | 3070 | 910 | 1336 | 0 | 1481 | 806 | 30 | 0 | 327 | 104 | 18 | 569.5333
17:30 | 3104.5 | 875 | 1386 | 45 | 1664.5 | 856.5 | 30 | 0 | 387 | 117 | 9 | 645.7667
18:00 | 3139 | 840 | 1436 | 90 | 1848 | 907 | 30 | 0 | 447 | 130 | 0 | 722
18:30 | 3053.5 | 824 | 1454.5 | 90 | 1914 | 932 | 30 | 0 | 459.5 | 127 | 0 | 908.4155
19:00 | 2968 | 808 | 1473 | 90 | 1980 | 957 | 30 | 0 | 472 | 124 | 0 | 1094.8311
19:30 | 2965 | 792 | 1467 | 90 | 1961 | 956 | 30 | 0 | 473 | 126 | 0 | 1023.409
20:00 | 2979 | 792 | 1476 | 90 | 2020 | 955 | 30 | 0 | 481 | 114 | 0 | 951.987
20:30 | 3022 | 803.5 | 1499 | 90 | 1900.5 | 955 | 30 | 0 | 499.5 | 113 | 0 | 903.1435
21:00 | 3065 | 815 | 1522 | 90 | 1781 | 955 | 30 | 0 | 518 | 112 | 0 | 854.3
21:30 | 3080.5 | 863 | 1520 | 89.5 | 1792.5 | 954.5 | 30 | 0 | 512.5 | 110 | 0 | 546.494
22:00 | 3096 | 911 | 1518 | 89 | 1804 | 954 | 30 | 0 | 507 | 108 | 0 | 238.6879
22:30 | 3097 | 910.5 | 1534 | 44.5 | 1691.5 | 954 | 30 | 0 | 418 | 109 | 0 | 139.1578
23:00 | 3098 | 910 | 1550 | 0 | 1579 | 954 | 30 | 0 | 329 | 110 | 0 | 39.6277
23:30 | 3098 | 910 | 1547 | 0 | 1473 | 954 | 30 | 0 | 204.5 | 104 | 0 | 39.6277 | Max Temp. in Dhaka |  | 24° C
24:00 | 3098 | 910 | 1544 | 0 | 1367 | 954 | 30 | 0 | 80 | 98 | 0 | 39.6277
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-01-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 703380
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 225088
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 5 | 11 | 15 | 18 | 19 | 18 | 15 | 11 | 6 | 1 | 0 | [8 empty] | 119340
6 | Sikalbaha 225MW CCPP (Gas) | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 160 | 160 | 156 | 154 | 154 | 154 | 156 | 157 | 156 | 156 |  | 156 | 155 | 156 | 158 | 158 | 162 | 158 | 3678799
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [13 empty] | 0 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 7 |  | 426343
12 | Hathazari 100 MW peaking PP | [7 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 23 | 23 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 511873
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 56 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1155018
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [8 empty] | 20 | 21 | 23 | 35 | 37 | 37 | 28 | 28 | 33 | 34 |  | 34 | 34 | 34 | 34 | 35 | 35 | 0 | 465952
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 32 | 0 | [5 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 32 | 35 | 32 | 67 |  | 80 | 65 | 65 | 77 | 65 | 32 | 32 | 853091
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [12 empty] | 0 | 117090
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 190 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 200 | 200 | 200 | 180 | 200 | 200 | 4677900
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | [12 empty] | 0 | 38304
33 | Ashuganj 225 MW CCPP | 226 | 225 | 227 | 226 | 227 | 226 | 224 | 229 | 182 | 193 | 182 | 196 | 219 | 186 | 184 | 184 | 183 | 200 |  | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 4864000
34 | Ashuganj 450 MW CCPP(South) | [16 empty] | 0 | 18 |  | 22 | 7 | 25 | 62 | 92 | 85 | 85 | 366000
| Ashuganj 450 MW CCPP(North) | 280 | 300 | 280 | 280 | 280 | 325 | 350 | 280 | 280 | 295 | 280 | 340 | 305 | 280 | 280 | 285 | 290 | 345 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7460000
| Ashuganj 420 MW CCPP(East) | 297 | 297 | 320 | 320 | 320 | 320 | 320 | 294 | 294 | 305 | 305 | 290 | 238 | 267 | 278 | 288 | 318 | 228 |  | 160 | 150 | 148 | 151 | 148 | 150 | 150 | 6276400
35 | Ashuganj 55 MW PP (Precision) | [6 empty] | 2 | 10 | [17 empty] | 0 | 17280
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 289 | 289 | 293 | 293 | 293 | 294 | 294 | 288 | 287 | 273 | 272 | 269 | 267 | 261 | 258 | 289 | 339 | 339 |  | 346 | 347 | 349 | 375 | 383 | 387 | 391 | 7563260
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 250 | 254 | 256 | 251 | 245 | 257 | 242 | 245 | 240 | 235 | 235 | 230 | 230 | 228 | 220 | 196 | 180 | 180 |  | 185 | 185 | 196 | 208 | 227 | 238 | 228 | 5472000
42 | RPCL 210MW CCPP | 110 | 110 | 110 | 110 | 110 | 109 | 54 | 55 | 55 | 54 | 47 | 47 | 47 | 45 | 45 | 47 | 54 | 55 |  | 99 | 99 | 101 | 106 | 112 | 114 | 114 | 1852800
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 1 | 6 | 17 | 27 | 30 | 32 | 26 | 25 | 16 | 9 | 2 | 0 | [8 empty] | 184360
44 | Fenchugonj CCPP Phase-1 | [15 empty] | 0 | 20 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 215000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 0 | [13 empty] | 540360
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 31 | 30 | 31 | 31 | 31 | 31 | 32 | 33 | 32 | 31 | 31 | 30 | 31 | 30 | 31 | 31 | 31 | 30 |  | 32 | 31 | 33 | 32 | 33 | 33 | 33 | 764448
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 86 | 50 | 20 | 20 | 20 | 50 | 50 | 10 | 10 | 10 | 30 | 50 | 50 | 50 | 50 | 50 | 81 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1302720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 195 | 195 | 195 | 195 | 193 | 194 | 194 | 194 | 203 | 203 | 199 | 199 | 197 | 197 | 195 | 195 | 194 | 195 |  | 201 | 200 | 200 | 200 | 198 | 198 | 198 | 5029940
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 439000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253800
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 22 | 24 | 22 | 17 | 14 |  | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 324000
56 | Shahjahanulla 25 MW PP
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 270 | 290 | 280 | 280 | 290 | 341 | 310 | 290 | 285 | 305 | 310 | 320 | 310 | 290 | 275 | 300 | 300 |  | 320 | 310 | 290 | 310 | 260 | 270 | 270 | 7196000
| Bibiyana South 400 MW | 370 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 365 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 |  | 400 | 400 | 389 | 400 | 400 | 400 | 400 | 9554200
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  |  | 0 | 3 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 327934
59 | Tangail Palli Power Gen 22 MW | 12 | 0 |  |  | 0 | 3 | 12 | 12 | 12 | 12 | 12 | 7 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 4 | 5 | 167760
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 0 | 0 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 405576
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 21 | 22 | 21 | 497736
63 | Impoprt (Tripura) | 90 | 80 | 80 | 80 | 76 | 80 | 84 | 94 | 102 | 104 | 110 | 110 | 106 | 116 | 109 | 100 | 104 | 130 |  | 124 | 126 | 114 | 112 | 108 | 110 | 98 | 2412480
64 | Malancha, Ctg. EPZ (United) | 21 | 27 | 37 | 37 | 35 | 42 | 42 | 16 | 7 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 2 | 3 | 9 | 12 | 18 | 21 | 29 | 360960
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 448668
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 24 | 19 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 |  | 16 | 16 | 21 | 21 | 25 | 25 | 25 | 536000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 21 | 21 | 21 | 21 | 20 | 18 | 18 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 469110
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 26 | 26 | 26 | 23 | 24 | 24 | 6 | 27 | 27 | 27 | 27 | 27 | 24 | 27 | 26 | 26 | 27 | 19 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 580680
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 0 | 33 | 33 | 33 | 25 | 25 | 667080
72 | Rupganj 33 MW PP(Summit) | 32 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 25 | 17 | 31 | 31 | 31 | 30 | 29 |  | 15 | 30 | 30 | 32 | 32 | 32 | 33 | 760500
73 | Ghorashal 108MW PP (Regent) | 77 | 77 | 77 | 35 | 35 | 35 | 35 | 74 | 74 | 71 | 71 | 76 | 77 | 77 | 76 | 72 | 77 | 77 |  | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 1680045
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 55 | 0 | [5 empty] | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 86 | 113 | 116 |  | 117 | 117 | 117 | 117 | 118 | 84 | 36 | 1095360
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | [8 empty] | 0 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 267840
77 | Siddhirganj 100 PP(Dutch Bangla) | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 192000
78 | Gazipur 52 MW PP | [6 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 16 | 16 | 8 | 8 | 166560
79 | Kodda 150MW PP | [6 empty] | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 16 | 48 | 48 |  | 48 | 48 | 48 | 82 | 82 | 82 | 48 | 712800
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [10 empty] | 3 | 8 | 8 | 8 | 8 | 8 | 0 | [9 empty] | 49718
| Gazipur 100 MW PP | [6 empty] | 8 | 34 | 39 | 70 | 70 | 70 | 34 | 34 | 34 | 40 | 85 | 88 |  | 88 | 88 | 88 | 88 | 88 | 35 | 35 | 1101204
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 3 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 23160
| Jodiac Power | [9 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 13 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 261459
| Karnaphuli Power Ltd. | 70 | 70 | 51 | 17 | 17 | 29 | 70 | 70 | 70 | 70 | 70 | 71 | 75 | 73 | 67 | 56 | 53 | 52 |  | 52 | 52 | 52 | 52 | 67 | 60 | 52 | 1429339
82 | Madanganj 102 PP(Summit) | 25 | 2 | 0 |  |  |  | 2 | 20 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 30 | 34 | 539880
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 150 | 152 | 150 | 150 | 152 | 152 | 155 | 152 | 150 | 150 | 148 | 155 | 150 | 151 | 148 | 138 | 130 | 125 |  | 130 | 130 | 138 | 148 | 152 | 150 | 148 | 3538822
87 | Meghnaghat 100 MW(IEL) | 8 | 9 | 8 | 8 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 8 |  | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 192960
| Meghnaghat 104 MW PP (OPCL) | [7 empty] | 10 | 17 | 17 | 17 | [5 empty] | 0 | 9 |  | 17 | 17 | 17 | 0 |  |  | 0 | 97920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 | 0 |  |  | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 447600
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 20 | 20 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 334584
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1254472
94 | Gagnagar 102 MW PP (Digital Power) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 16 | 16 | 16 | 8 | 214704
95 | Patenga 50MW PP (Baraka) | 25 | 0 |  |  |  |  | 1 | 25 | 32 | 33 | 28 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 33 | 33 | 33 | 33 | 585120
96 | Chattogram 108 MW PP (ECPV) | [14 empty] | 0 | 3 | 12 | 12 |  | 12 | 2 | 0 |  |  |  | 0 | 42240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 0 |  |  |  | 12 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 21 |  | 23 | 15 | 15 | 16 | 30 | 20 | 15 | 360608
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 0 | 17 | 35 | 55 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 316761
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [9 empty] | 7850
103 | Kamalaghat 54 MW PP(Banco Energy) | [13 empty] | 17 | 17 | 17 | 17 | 17 |  | 44 | 54 | 54 | 35 | 17 | 17 | 17 | 266040
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 24 | 24 | 24 | 24 | 34 | 47 | 47 | 47 | 47 | 46 | 48 | 48 | 48 | 57 | 48 | 57 |  | 57 | 48 | 48 | 48 | 48 | 48 | 48 | 1096800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 35 | 0 |  |  | 0 | 6 | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 714096
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 0 |  |  | 0 | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 514560
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 0 |  | 0 | 4 | 13 | 1 | 17 | 17 | 17 |  |  |  |  | 0 | 9 | 17 |  | 17 | 17 | 17 | 17 |  | 6 | 17 | 239040
117 | Ashuganj 150MW PP (Midland) | 6 | 6 | 6 | 6 | 5 | 6 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 6 |  | 6 | 6 | 8 | 5 | 6 | 6 | 5 | 157236
118 | Bibiyana-III 400 MW CCPP | 376 | 376 | 376 | 375 | 370 | 375 | 375 | 376 | 376 | 325 | 360 | 392 | 385 | 385 | 366 | 365 | 365 | 431 |  | 364 | 404 | 365 | 365 | 366 | 343 | 343 | 9044000
| Jamalpur 115 MW PP (United) | 28 | 8 | 8 | 8 | 8 | 8 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 28 | 678000
| Anwara 300 MW PP (United) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 52 | 51 | 51 | 51 | 51 | 51 | 51 | 118 | 271 |  | 282 | 284 | 284 | 52 | 52 | 52 | 52 | 1957091
| Juldah unit-2 (Acorn) | 25 | 0 |  |  | 0 | 10 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 503040
| Anlima Energy Ltd. | 34 | 34 | 17 | 17 | 17 | 23 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 60 | 107 | 116 | 78 |  | 72 | 68 | 68 | 68 | 87 | 90 | 95 | 1288418
| Bhairob 54.5 MW | [8 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 285480
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 4 | 12 | 17 | 18 | 20 | 21 | 15 | 14 | 7 | 1 | 0 | [8 empty] | 123874
| Chandpur 115(Doreen) | 50 | 25 | 0 |  | 0 | 25 | 53 | 52 | 52 | 53 | 53 | 52 | 53 | 52 | 53 | 52 | 73 | 94 |  | 94 | 94 | 94 | 94 | 94 | 65 | 53 | 1333440
| Kanchan Purbachal Power Generation Ltd. | 17 | 0 |  |  | 0 | 3 | 10 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 354600
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4558 | 4313 | 4196 | 4070 | 4055 | 4237 | 4490 | 4604 | 4529 | 4570 | 4617 | 4731 | 4579 | 4549 | 4557 | 4715 | 5035 | 5421 |  | 5330 | 5285 | 5288 | 5188 | 5190 | 4995 | 4815 | 114524651
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 46 |  | 66 | 66 | 66 | 92 | 86 | 32 | 0 | 469440
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [14 empty] | 0 | 4 | 36 | 43 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 231840
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [17 empty] | 0 |  | 4 | 17 | 17 | 17 | 17 | 17 | 0 | 97440
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 13 | 31 | 47 | 60 | 68 | 62 | 54 | 37 | 19 | 4 | 0 | [8 empty] | 398880
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 17 | 0 | [5 empty] | 29 | 150 | 150 | 100 | 54 | 54 | 72 | 54 | 17 | 17 | 17 |  | 54 | 54 | 100 | 150 | 150 | 150 | 100 | 1527600
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 222 | 222 | 221 | 220 | 220 | 220 | 222 | 220 | 160 | 160 | 220 | 220 | 220 | 160 | 160 | 160 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5102864
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 72 | 0 | [5 empty] | 48 | 48 | 96 | 80 | 64 | 64 | 73 | 80 | 64 | 64 | 80 |  | 96 | 96 | 110 | 110 | 110 | 110 | 110 | 1531296
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 132 | 132 | 133 | 134 | 134 | 134 | 134 | 134 | 134 | 130 | 100 | 126 | 126 | 130 | 95 | 80 | 132 | 130 |  | 130 | 132 | 134 | 130 | 132 | 136 | 136 | 3016000
140 | Bhola 33 MW PP (Venture) | 20 | 20 | 19 | 18 | 17 | 19 | 19 | 19 | 18 | 18 | 18 | 20 | 21 | 19 | 17 | 16 | 15 | 23 |  | 24 | 25 | 25 | 19 | 26 | 24 | 22 | 462392
141 | Noapara 100 MW PP (Bangla Trac) | [9 empty] | 0 | [6 empty] | 0 | 90 |  | 90 | 90 | 90 | 90 | 89 |  | 0 | 452160
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 0 | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 34875
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 0 | 35 | 73 |  | 68 | 62 | 62 | 62 | 62 | 52 | 0 | 396160
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 727 | 633 | 634 | 633 | 633 | 633 | 633 | 863 | 815 | 815 | 815 | 910 | 910 | 911 | 911 | 909 | 910 | 840 |  | 808 | 792 | 792 | 815 | 911 | 910 | 910 | 19214545
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 622 | 622 | 580 | 500 | 500 | 500 | 530 | 610 | 622 | 570 | 450 | 470 | 580 | 622 | 560 | 450 | 470 | 570 |  | 620 | 622 | 622 | 622 | 622 | 622 | 622 | 14695700
149
150 | Barapukuria TPP Unit-1 | 81 | 81 | 81 | 83 | 81 | 81 | 80 | 81 | 80 | 79 | 80 | 81 | 83 | 86 | 85 | 84 | 86 | 87 |  | 87 | 84 | 83 | 83 | 82 | 82 | 82 | 1967127
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6069300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 0 | 8 | 25 |  | 34 | 34 | 34 | 34 | 34 |  |  | 182483
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 3 | 2 | 2 | 0 | 0 | [9 empty] | 17760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 153 | 152 | 162 | 168 | 169 | 169 | 172 | 179 | 180 | 150 | 163 | 164 | 158 | 158 | 157 | 148 | 146 | 146 |  | 146 | 146 | 147 | 152 | 157 | 160 | 160 | 4032555
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas)
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 371 | 389 | 400 | 360 | 356 | 358 | 418 | 416 | 380 | 388 | 380 | 366 | 351 | 341 | 329 | 320 | 317 | 325 |  | 327 | 329 | 333 | 340 | 350 | 362 | 362 | 8723272
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 0 | 4 | 5 |  | 11 | 18 | 26 | 29 | 25 |  |  | 97072
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 18 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 466560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193698
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 25 | 42 | 42 | 34 | 34 | 42 | 42 | 42 | 42 | 42 | 42 | 34 |  | 34 | 34 | 34 | 0 | 25 | 25 | 0 | 599470
167 | Katakhali 50 MW Peaking PP | [13 empty] | 8 | 8 | 8 | 8 | 8 |  | 32 | 32 | 32 | 32 | 24 |  |  | 132208
168 | Santahar 50 MW Peaking PP | [13 empty] | 0 | 25 | 38 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 |  | 305714
169 | Natore 52 MW PP (Rajlanka) | 8 | 0 |  |  |  |  | 8 | 8 | 8 | 8 | 52 | 52 | 52 | 0 |  |  | 0 | 52 |  | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 325536
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 32 | 35 | 35 | 35 | 35 | 91 |  | 92 | 92 | 92 | 92 | 92 | 51 | 0 | 680544
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 0 | [10 empty] | 20 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 40 | 50 | 50 | 50 | 575232
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 0 | [7 empty] | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 675552
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 35 | 0 | [6 empty] | 34 | 34 | 35 | 35 | 34 | 34 | 35 | 35 | 35 | 35 |  | 34 | 35 | 35 | 35 | 35 | 34 | 34 | 594192
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 8227
178 | Energypac Power Venture Thakurgaon Ltd. | 55 | 0 |  |  | 0 | 53 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2157696
| Intraco Solar 30 MW | [7 empty] | 1 | 2 | 6 | 7 | 5 | 7 | 5 | 9 | 7 | 1 | 0 | [8 empty] | 52216
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 2 | 9 | 41 | 55 | 116 | 119 | 92 | 70 | 79 | 38 | 8 | 0 | [8 empty] | 638250