## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-01-26 | Thursday
|  | Date (day): | 2023-01-26 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 9004.6 | MW |  |  | (b) At Evening Peak Hour : |  | 10300 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-01-25 | 2023-01-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 210 | 210 | 210 | 210
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 74 | 76 | 50 | 50 | 58 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 331 | 336 | 350 | 350 | 62 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 173 | 182 | 200 | 200 | 160 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 0 | 0 | 0 | 0 |  | 450 | Under maint
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 8 | 9 | 9 | 9 | 91 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 137 | 138 | 150 | 150 | 185 |  | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 0 | 11 | 17 | 17 | 85 |  | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  |  | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 0 | 8 | 0 | 8 | 92 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 48 | 24 | 48 | 54 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 35
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 48 | 16 | 48 | 101 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 35 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 17 | 35 |  |  | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 50 | 51 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 29 | 30 | 30 | 30 |  | 3 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 33 | 17 | 8 | 17 | 35 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 107 | 115 | 32 | 66 | 234 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 53 | 52 | 52 | 52 | 97 |  | Fuel shortage
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 70 | 52 | 34 | 52 | 17 |  | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 55 | 17 | 55 | 49 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 17 | 17 | 17 | 145 |  | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 17 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 17 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 1580 | 1663 | 1450 | 1639 | 3194 | 982
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 17 | 8 | 17
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 32 | 33 | 33 | 17 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 226 | 154 | 157 | 157 |  |  | ST Under S/D
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 34 | 85 | 32 | 85 | 20 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 31 | 31 | 32 | 32 | 66 |  | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 68 | 51 | 68 | 34 |  | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 22 | 22 | 22 | 22 | 78 |  | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 0 | 0 | 22 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 6 | 5 | 10
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 106 | 284 | 110 | 284 |  |  | Engine problem
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 17 | 17 | 37 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 92 | 52 | 92 | 18 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 25 | 25 | 25 | 25 | 75 |  | Fuel shortage
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 75 | 68 | 51 | 107 | 9 |  | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 764 | 956 | 675 | 1004 | 1119 | 150
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 194 | 222 | 200 | 200 | 21 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 285 | 290 | 290 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 316 | 327 | 300 | 300 | 100 |  | Gas shortage
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 10 | 10 | 10 | 10 | 40 |  | Gas shortage
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 20 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 6 | 6 | 6 | 144 |  | Fuel shortage
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 29 | 19 | 35 | 35 |  | 17 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 17 | 17 | 17 | 17 | 183 |  | Fuel shortage
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  |  | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 114 | 135 | 152
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 13 | 21 | 21 | 21 |  |  | Engine problem
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 20 | 20 | 20 |  | 5 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 10 | 0 | 100 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 25 | 17 | 17 | 17 | 114
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 9 | 107 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 53 | 94 | 54 | 94 | 21 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1259 | 1387 | 1232 | 1493 | 1238 | 582
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 35 | 104 | 50 | 60 | 142 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 18 | 18
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 48 | 57 | 48 | 48 | 152 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 28 | 47 | 28 | 47 | 68 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 0 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 136 | 232 | 201.6 | 179 | 142 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under S/D
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 51 | 11 | 11 |  |  | Gas shortage
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 47 | 49 | 10 | 10 |  |  | Gas shortage
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 0 | 0 | 0 |  | 3
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 62 | 62 | 62
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 0 | 10 | 84
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 140 | 140 | 140 |  | 91 | Machine problem
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 19 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 0 | 0 | 0 |  | 25 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 260 | 290 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 385 | 367 | 366 | 366
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1384 | 1431 | 1391 | 1475 | 0 | 799
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 904 | 859 | 922 | 922
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 49 | 49 |  | Fuel shortage
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 43 | 0 | 45 |  | 9 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 40 | 0 | 86 |  | 23 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 0 | 0 | 0 | 410 |  | Gas shortage.
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 0 | 8 | 0 | 8 | 32 |  | Fuel shortage
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 95 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 17 | 0 | 18 | 87 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 85 | 50 | 105
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 68 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 150 | 273 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1188 | 1341 | 1088 | 1233 | 919 | 32
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 16 | 16 | 16 |  | 94 | Engine problem
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 20 | 22 | 19 | 22 |  | 18 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 176 | 177 | 190 | 190
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1010 | 1244 | 1150 | 1190 |  | 54
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 217 | 110 | 110 | 110 |  |  | Line S/D
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 35 | 17 | 35 | 150
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 0 | 0 | 0 | 0 |  |  | Coal Shortage.
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1474 | 1586 | 1520 | 1678 | 0 | 166
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 34 | 0 | 34 |  | 18 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 4 | 10 | 0 | 17 |  | 54 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 50 | 34 | 50
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 40 | 15 | 41 |  | 9 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 193 | 182 | 196 | 200 |  | 20 | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 416 | 365 | 415 | 415
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 30 | 0 | 34 |  | 16 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 21 | 21
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  |  | Engine problem
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 50 | 50 | 10 | 95 |  | 12 | Engine problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 50 | 50 | 50 | 63 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 95 | 35 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 871 | 943 | 798 | 1068 | 926 | 129
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 77 | 81 | 81
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 |  | 24
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 38 | 70 | 35 | 85 | 28 |  | Fuel shortage
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 112 | 115 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 29 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 142 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 575 | 509 | 649 | 531 | 68 | 109
| Total |  |  |  |  | 23482 | 22700 | 9231 | 10048 | 9004.6 | 10300 | 7606 | 2949
A. |  | 2023-01-25 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10048 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
2 | Minimum Generation : |  |  | 6996 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10336 | MW
3 | Day peak Generation : |  |  | 9231 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9795.92 | MW
4 | Evening peak Generation : |  |  | 10048 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 265 | MW
5 | Total Energy Generation : |  | 208.2062 | MKWHr | By Solar | 1.7797 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 112.2407 | MKWHr |  | By Oil: | 35.7902 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 34.504 | MKWHr |  | By Hydro: | 0.73368 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 7606 | MW | Dhaka | 3552.02 | 3447.02 |  | 105 |  | 18:00 |  | 298
|  |  | For Plants S/D or M/C prob = |  |  | 2949 | MW | Chittagong | 947.5 | 947.5 |  | 0 |  | 19:00 |  | 368
|  |  | Total = |  |  | 10555 | MW | Khulna | 1123.6 | 1123.6 |  | 0 |  | 19:30 |  | 282
7 | Total Gas Supplied : |  |  | 845.63 | MMCFD |  |  | Rajshahi | 1022.8 | 1022.8 |  | 0 |  | 20:00 |  | 265
8 | Fuel Cost : | i) Gas : | Taka | 115519217.632 | ii) Oil : | Taka | 451683532.74 | Comilla | 830 | 830 |  | 0 |  | 21:00 |  | 345
|  | iii) Coal : |  | 282373040.58 | Total | Taka | 849575790.952 | Mymensingh | 937 | 828 |  | 109 |  | 22:00 |  | 186
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0 | MKWHr. | Sylhet | 375 | 324 |  | 51 |  | 23:00 |  | 157
| ii) During Peak Demand : |  |  | 880 | MW (E to W) at | 20:00 | hrs | Barisal | 283 | 283 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 850 | MW at | 7:00 | hrs | Rangpur | 725 | 725 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 28.5° C |  |  | Total | 9795.92 | 9530.92 |  | 265
B. |  | 2023-01-26 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 29.0° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 10300 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 213.4279 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7101 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.6378 | MKWHr. | ii) HVDC Flow at Peak Time |  | 859 | MW at | 20:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.52 | MKWHr. | iii) Maximum HVDC Flow : |  | 907 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.27 |  | (b) Today: | 84.15 |  | (c) Rule Curve: |  | 98.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-01-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 347 | 201 |  | 0 | 0 | 145 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 300 | 0 | 200 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 96 | 69 | 0 | 18 | 0 | 30 | 43 | 22 | 10 | 0 | 0 | 63 | 86 | 0 | 157 | 20 | 0 | 10 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 0 | 0 | 17 | 6 | 366 | 28 | 17 | 48 | 0 | 16 | 17 | 54 | 0 | 0 | 0 | 393 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 35 | 17 | 307 | 0 | 0 |  | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208 | 0 | 439 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1090 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4564 | 3329 | 7893 | 3379 | 767 | 1618 | 0 | 581 | 1422 | 30 | 0 | 0 | 96 | 0 | 0 | 84.29
2:00 | 0 | 0 | 190 | 0 | 0 | 76 | 0 | 345 | 186 |  | 0 | 0 | 145 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 233 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 300 | 0 | 203 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 90 | 85 | 0 | 18 | 0 | 30 | 43 | 14 | 10 | 0 | 0 | 63 | 50 | 0 | 157 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 0 | 0 | 0 | 6 | 366 | 28 | 0 | 34 | 0 | 16 | 0 | 34 | 0 | 0 | 0 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 | 307 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 380 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 1020 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4285 | 3191 | 7476 | 3381 | 766 | 1512 | 0 | 350 | 1347 | 30 | 0 | 0 | 90 | 0 | 0 | 84.29
3:00 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 345 | 196 |  | 0 | 0 | 145 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 232 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 300 | 0 | 211 | 8 | 0 | 10 | 20 | 0 | 20 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 80 | 85 | 0 | 18 | 0 | 30 | 43 | 14 | 10 | 0 | 0 | 62 | 30 | 0 | 156 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 17 | 0 | 0 | 0 | 5 | 366 | 28 | 0 | 34 | 0 | 16 | 0 | 34 | 0 | 0 | 0 | 402 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 | 320 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4180 | 3038 | 7218 | 3360 | 766 | 1418 | 0 | 315 | 1249 | 30 | 0 | 0 | 80 | 0 | 0 | 84.28
4:00 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 345 | 199 |  | 0 | 0 | 145 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 230 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 205 | 8 | 0 | 10 | 20 | 0 | 20 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 78 | 84 | 0 | 18 | 0 | 303 | 43 | 14 | 10 | 0 | 0 | 62 | 30 | 0 | 0 | 20 | 0 | 10 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 17 | 0 | 0 | 0 | 6 | 366 | 28 | 0 | 34 | 0 | 16 | 0 | 34 | 0 | 0 | 0 | 400 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 | 320 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4326 | 2939 | 7265 | 3460 | 766 | 1406 | 0 | 325 | 1200 | 30 | 0 | 0 | 78 | 0 | 0 | 84.28
5:00 | 0 | 0 | 150 | 0 | 0 | 32 | 0 | 346 | 196 |  | 0 | 0 | 145 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 234 | 0 | 0 | 0 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 320 | 0 | 201 | 8 | 0 | 10 | 20 | 0 | 20 | 0 | 0 | 0 | 21 | 8 | 33 | 15 | 78 | 83 | 0 | 18 | 0 | 30 | 43 | 14 | 10 | 0 | 0 | 63 | 30 | 0 | 0 | 20 | 0 | 10 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 17 | 0 | 0 | 0 | 6 | 393 | 28 | 0 | 34 | 0 | 16 | 0 | 35 | 0 | 0 | 0 | 402 | 17 | 0 | 17 | 34 | 0 | 17 | 0 | 0 | 17 | 307 | 0 | 0 |  | 766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4097 | 2899 | 6996 | 3203 | 766 | 1395 | 0 | 325 | 1199 | 30 | 0 | 0 | 78 | 0 | 0 | 84.27
6:00 | 0 | 0 | 150 | 0 | 0 | 74 | 0 | 348 | 193 |  | 0 | 0 | 145 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 2 | 235 | 0 | 0 | 0 |  | 6 | 0 | 0 | 22 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 335 | 0 | 194 | 8 | 0 | 10 | 20 | 0 | 20 | 0 | 0 | 1 | 21 | 8 | 33 | 15 | 92 | 83 | 0 | 18 | 0 | 30 | 43 | 14 | 10 | 0 | 0 | 62 | 30 | 0 | 0 | 20 | 0 | 10 | 320 | 0 | 0 | 0 | 5 | 0 | 0 | 48 | 0 | 17 | 0 | 25 | 9 | 6 | 423 | 28 | 4 | 34 | 0 | 16 | 2 | 36 | 0 | 8 | 18 | 400 | 17 | 0 | 17 | 37 | 0 | 17 | 0 | 24 | 17 | 298 | 0 | 0 |  | 767 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 22 | 0 | 8 | 79 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 335 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 870 | 181 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4330 | 2928 | 7258 | 3231 | 767 | 1442 | 0 | 489 | 1199 | 30 | 0 | 8 | 92 | 0 | 0 | 84.27
7:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 352 | 192 |  | 0 | 0 | 145 | 9 | 0 | 5 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 29 | 0 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 238 | 0 | 0 | 0 |  | 6 | 7 | 0 | 22 | 0 | 15 | 0 | 40 | 0 | 0 | 0 | 355 | 0 | 203 | 8 | 0 | 10 | 20 | 0 | 41 | 0 | 0 | 8 | 21 | 8 | 28 | 15 | 92 | 45 | 0 | 19 | 0 | 30 | 43 | 48 | 50 | 0 | 0 | 62 | 60 | 0 | 0 | 20 | 0 | 10 | 320 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 17 | 1 | 25 | 17 | 6 | 412 | 28 | 30 | 34 | 0 | 16 | 17 | 51 | 17 | 9 | 25 | 401 | 17 | 0 | 17 | 85 | 0 | 17 | 0 | 35 | 17 | 320 | 0 | 0 |  | 907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 20 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 8 | 78 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 442 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 940 | 182 | 0 | 0 | 0 | 1 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2 |  | 4721 | 3432 | 8153 | 3280 | 907 | 1674 | 0 | 875 | 1268 | 30 | 0 | 23 | 92 | 4 | 109.6674 | 84.26
8:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 347 | 193 |  | 0 | 0 | 142 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 29 | 25 | 31 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 232 | 0 | 0 | 0 |  | 6 | 24 | 0 | 22 | 0 | 25 | 0 | 10 | 0 | 0 | 0 | 360 | 0 | 181 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 16 | 15 | 96 | 45 | 0 | 19 | 0 | 30 | 43 | 48 | 50 | 0 | 0 | 62 | 60 | 0 | 0 | 19 | 0 | 9 | 330 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 6 | 25 | 17 | 6 | 433 | 28 | 34 | 34 | 1 | 16 | 17 | 51 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 3 | 35 | 17 | 287 | 0 | 0 |  | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 22 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 442 | 0 | 0 | 0 | 50 | 28 | 0 | 1 | 0 | 1060 | 214 | 0 | 17 | 0 | 13 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 28 |  | 4764 | 3615 | 8379 | 3249 | 838 | 1692 | 0 | 997 | 1380 | 30 | 0 | 40 | 96 | 57 | 399.9636 | 84.24
9:00 | 0 | 0 | 205 | 0 | 0 | 74 | 0 | 344 | 176 |  | 0 | 0 | 138 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 29 | 25 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 234 | 0 | 0 | 0 |  | 6 | 32 | 0 | 22 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 193 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 9 | 8 | 21 | 8 | 16 | 15 | 114 | 45 | 0 | 19 | 1 | 30 | 43 | 48 | 50 | 0 | 0 | 63 | 81 | 0 | 0 | 19 | 0 | 9 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 58 | 0 | 17 | 13 | 25 | 17 | 5 | 367 | 28 | 34 | 34 | 2 | 100 | 17 | 54 | 17 | 9 | 25 | 390 | 17 | 0 | 17 | 75 | 0 | 17 | 8 | 35 | 17 | 277 | 0 | 0 |  | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 21 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 418 | 0 | 0 | 0 | 50 | 40 | 0 | 2 | 0 | 1130 | 217 | 0 | 17 | 1 | 32 | 115 | 0 | 0 | 0 | 10 | 0 | 0 | 65 |  | 4672 | 3718 | 8390 | 3080 | 838 | 1621 | 0 | 1066 | 1450 | 30 | 0 | 57 | 114 | 134 | 669.985 | 84.25
10:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 334 | 175 |  | 0 | 0 | 137 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 22 | 29 | 33 | 29 | 33 | 0 | 30 | 0 | 0 | 0 | 8 | 234 | 0 | 0 | 0 |  | 6 | 25 | 0 | 22 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 204 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 20 | 8 | 21 | 8 | 16 | 15 | 116 | 45 | 0 | 19 | 1 | 30 | 43 | 48 | 50 | 0 | 0 | 40 | 81 | 0 | 0 | 18 | 0 | 9 | 270 | 0 | 0 | 0 | 43 | 0 | 0 | 48 | 0 | 17 | 17 | 25 | 17 | 6 | 366 | 28 | 70 | 36 | 3 | 100 | 17 | 55 | 17 | 9 | 25 | 400 | 51 | 0 | 17 | 68 | 0 | 17 | 12 | 34 | 17 | 305 | 0 | 0 |  | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 18 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 324 | 0 | 0 | 0 | 50 | 38 | 0 | 3 | 35 | 1110 | 220 | 0 | 17 | 2 | 51 | 35 | 0 | 0 | 0 | 21 | 0 | 0 | 105 |  | 4831 | 3640 | 8471 | 3116 | 838 | 1504 | 0 | 1127 | 1432 | 30 | 0 | 93 | 116 | 215 | 610.0827 | 84.25
11:00 | 0 | 0 | 210 | 0 | 0 | 69 | 0 | 331 | 173 |  | 0 | 0 | 135 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 28 | 33 | 29 | 33 | 0 | 30 | 0 | 0 | 0 | 8 | 233 | 0 | 0 | 0 |  | 6 | 31 | 0 | 22 | 0 | 30 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 199 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 29 | 8 | 21 | 8 | 13 | 15 | 110 | 44 | 0 | 17 | 2 | 30 | 43 | 48 | 47 | 0 | 0 | 40 | 84 | 0 | 0 | 18 | 0 | 9 | 290 | 0 | 0 | 0 | 98 | 0 | 0 | 48 | 0 | 40 | 20 | 25 | 17 | 6 | 366 | 28 | 70 | 34 | 4 | 105 | 17 | 55 | 17 | 9 | 25 | 400 | 51 | 0 | 17 | 68 | 0 | 17 | 15 | 48 | 17 | 316 | 0 | 0 |  | 838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 14 | 16 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 34 | 16 | 0 | 25 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 417 | 0 | 0 | 18 | 50 | 34 | 0 | 4 | 35 | 1080 | 220 | 0 | 17 | 3 | 64 | 35 | 0 | 0 | 0 | 27 | 0 | 0 | 130 |  | 4983 | 3857 | 8840 | 3113 | 838 | 1605 | 0 | 1267 | 1405 | 30 | 0 | 203 | 110 | 269 | 335.4533 | 84.24
12:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 331 | 173 |  | 0 | 0 | 137 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 29 | 33 | 29 | 33 | 0 | 30 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 31 | 51 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 194 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 29 | 8 | 21 | 8 | 13 | 15 | 124 | 35 | 0 | 17 | 2 | 30 | 43 | 48 | 47 | 0 | 0 | 40 | 84 | 0 | 0 | 18 | 0 | 9 | 280 | 0 | 0 | 0 | 107 | 0 | 0 | 48 | 0 | 53 | 20 | 25 | 17 | 6 | 385 | 28 | 70 | 34 | 4 | 106 | 17 | 55 | 25 | 9 | 25 | 400 | 53 | 0 | 17 | 75 | 0 | 17 | 17 | 53 | 17 | 316 | 0 | 0 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 20 | 16 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 34 | 30 | 0 | 30 | 18 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 416 | 0 | 0 | 50 | 50 | 38 | 0 | 5 | 35 | 1010 | 217 | 0 | 35 | 3 | 68 | 35 | 150 | 0 | 0 | 29 | 0 | 0 | 142 |  | 5123 | 4108 | 9231 | 3136 | 904 | 1604 | 0 | 1384 | 1336 | 30 | 150 | 273 | 124 | 290 | 309.6492 | 84.24
13:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 340 | 197 |  | 0 | 0 | 141 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 29 | 33 | 0 | 30 | 0 | 0 | 0 | 8 | 217 | 0 | 0 | 0 |  | 6 | 31 | 51 | 22 | 0 | 27 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 190 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 28 | 8 | 21 | 8 | 8 | 15 | 118 | 32 | 0 | 16 | 2 | 30 | 43 | 51 | 46 | 0 | 0 | 48 | 84 | 0 | 0 | 18 | 0 | 10 | 320 | 0 | 0 | 0 | 114 | 0 | 0 | 58 | 0 | 53 | 20 | 25 | 17 | 6 | 370 | 28 | 50 | 38 | 4 | 104 | 17 | 38 | 17 | 9 | 18 | 400 | 54 | 0 | 17 | 105 | 0 | 17 | 17 | 53 | 17 | 287 | 13 | 0 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 21 | 16 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 34 | 32 | 0 | 30 | 18 | 0 | 8 | 75 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 414 | 0 | 0 | 50 | 50 | 34 | 0 | 5 | 35 | 880 | 217 | 0 | 35 | 3 | 66 | 35 | 245 | 0 | 0 | 28 | 0 | 0 | 139 |  | 5104 | 4059 | 9163 | 3066 | 904 | 1659 | 0 | 1364 | 1205 | 30 | 258 | 275 | 118 | 284 | 264.492 | 84.23
14:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 345 | 196 |  | 0 | 0 | 138 | 9 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 25 | 33 | 29 | 33 | 0 | 30 | 0 | 0 | 0 | 8 | 150 | 0 | 0 | 0 |  | 6 | 31 | 67 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 330 | 0 | 211 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 26 | 8 | 20 | 8 | 8 | 15 | 128 | 35 | 0 | 17 | 2 | 30 | 43 | 51 | 46 | 0 | 0 | 60 | 84 | 0 | 0 | 18 | 0 | 10 | 290 | 0 | 0 | 0 | 114 | 0 | 0 | 50 | 0 | 54 | 17 | 25 | 17 | 6 | 413 | 28 | 34 | 48 | 3 | 104 | 17 | 42 | 17 | 8 | 25 | 395 | 55 | 0 | 17 | 116 | 0 | 17 | 14 | 53 | 17 | 297 | 0 | 0 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 18 | 16 | 0 | 0 | 0 | 0 | 5 | 50 | 0 | 34 | 32 | 0 | 30 | 18 | 0 | 8 | 74 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 392 | 0 | 0 | 50 | 50 | 34 | 0 | 5 | 35 | 880 | 212 | 0 | 17 | 3 | 55 | 35 | 240 | 0 | 0 | 24 | 0 | 0 | 117 |  | 5148 | 3962 | 9110 | 3125 | 904 | 1595 | 0 | 1355 | 1204 | 30 | 240 | 289 | 128 | 240 | 129.0205 | 84.24
15:00 | 0 | 0 | 120 | 0 | 0 | 68 | 0 | 346 | 183 |  | 0 | 0 | 138 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 29 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 149 | 0 | 0 | 0 |  | 6 | 31 | 67 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 216 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 18 | 8 | 20 | 8 | 8 | 15 | 118 | 35 | 0 | 16 | 1 | 30 | 43 | 48 | 46 | 0 | 0 | 60 | 84 | 0 | 50 | 18 | 0 | 10 | 315 | 0 | 0 | 0 | 114 | 0 | 0 | 58 | 0 | 27 | 13 | 25 | 17 | 6 | 367 | 28 | 34 | 51 | 2 | 104 | 17 | 61 | 17 | 28 | 25 | 400 | 55 | 0 | 17 | 114 | 0 | 17 | 11 | 53 | 17 | 287 | 0 | 0 |  | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 17 | 16 | 0 | 0 | 0 | 25 | 6 | 50 | 0 | 8 | 40 | 0 | 30 | 18 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 372 | 0 | 0 | 50 | 15 | 34 | 0 | 4 | 35 | 880 | 180 | 0 | 17 | 2 | 39 | 35 | 245 | 0 | 0 | 16 | 0 | 0 | 83 |  | 4994 | 3798 | 8792 | 2973 | 904 | 1545 | 0 | 1289 | 1202 | 30 | 245 | 315 | 118 | 171 | 283.8451 | 84.22
16:00 | 0 | 0 | 120 | 0 | 0 | 70 | 0 | 345 | 190 |  | 0 | 0 | 140 | 8 | 0 | 15 | 0 | 0 | 0 | 2 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 26 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 10 | 150 | 0 | 0 | 0 |  | 6 | 31 | 67 | 22 | 0 | 26 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 220 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 18 | 8 | 21 | 5 | 14 | 15 | 118 | 35 | 0 | 16 | 1 | 30 | 43 | 11 | 10 | 0 | 0 | 61 | 84 | 0 | 130 | 18 | 0 | 10 | 275 | 0 | 0 | 0 | 112 | 0 | 0 | 48 | 0 | 17 | 7 | 25 | 17 | 6 | 355 | 38 | 52 | 51 | 1 | 105 | 17 | 90 | 17 | 61 | 25 | 360 | 55 | 0 | 17 | 116 | 0 | 17 | 5 | 52 | 17 | 298 | 13 | 0 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 17 | 16 | 0 | 0 | 0 | 25 | 7 | 50 | 0 | 8 | 40 | 0 | 34 | 18 | 0 | 8 | 72 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 305 | 0 | 0 | 35 | 15 | 34 | 0 | 2 | 35 | 780 | 180 | 0 | 17 | 1 | 18 | 17 | 246 | 0 | 0 | 9 | 0 | 0 | 43 |  | 5014 | 3544 | 8558 | 3016 | 904 | 1376 | 0 | 1346 | 1102 | 30 | 259 | 320 | 118 | 87 | 315.1787 | 84.22
17:00 | 0 | 0 | 120 | 0 | 0 | 70 | 0 | 344 | 186 |  | 0 | 0 | 138 | 20 | 0 | 28 | 0 | 0 | 0 | 8 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 149 | 0 | 0 | 0 |  | 6 | 31 | 67 | 22 | 7 | 26 | 0 | 2 | 0 | 0 | 0 | 290 | 0 | 182 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 24 | 8 | 21 | 5 | 14 | 15 | 120 | 35 | 0 | 16 | 0 | 30 | 43 | 14 | 10 | 0 | 0 | 61 | 84 | 0 | 140 | 18 | 0 | 10 | 290 | 0 | 0 | 0 | 112 | 0 | 0 | 48 | 0 | 18 | 1 | 25 | 17 | 10 | 365 | 38 | 52 | 66 | 0 | 105 | 17 | 91 | 17 | 105 | 25 | 400 | 54 | 0 | 17 | 75 | 0 | 0 | 1 | 54 | 17 | 298 | 7 | 0 |  | 905 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 0 | 8 | 180 | 17 | 16 | 0 | 0 | 0 | 25 | 10 | 80 | 0 | 34 | 40 | 0 | 34 | 18 | 0 | 8 | 70 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 304 | 0 | 0 | 38 | 20 | 50 | 0 | 0 | 55 | 840 | 110 | 0 | 17 | 0 | 5 | 20 | 248 | 0 | 0 | 2 | 0 | 0 | 9 |  | 5098 | 3615 | 8713 | 3035 | 905 | 1317 | 0 | 1504 | 1160 | 30 | 255 | 369 | 120 | 18 | 246.0605 | 84.21
18:00 | 0 | 0 | 155 | 0 | 0 | 70 | 0 | 341 | 193 |  | 0 | 0 | 138 | 11 | 0 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 19 | 22 | 17 | 33 | 30 | 16 | 0 | 30 | 0 | 0 | 0 | 17 | 149 | 0 | 0 | 0 |  | 6 | 31 | 67 | 22 | 12 | 31 | 0 | 2 | 0 | 0 | 0 | 335 | 0 | 219 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 18 | 8 | 21 | 8 | 13 | 20 | 124 | 35 | 0 | 16 | 0 | 30 | 43 | 19 | 15 | 0 | 0 | 60 | 0 | 0 | 140 | 18 | 0 | 10 | 280 | 0 | 0 | 20 | 112 | 0 | 0 | 48 | 0 | 52 | 0 | 25 | 17 | 5 | 404 | 38 | 52 | 85 | 0 | 270 | 17 | 91 | 17 | 106 | 25 | 400 | 55 | 0 | 17 | 68 | 0 | 0 | 0 | 94 | 17 | 327 | 0 | 0 |  | 904 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 49 | 42 | 8 | 179 | 22 | 16 | 0 | 0 | 0 | 34 | 6 | 50 | 0 | 50 | 40 | 8 | 34 | 20 | 0 | 8 | 84 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 370 | 0 | 0 | 50 | 85 | 65 | 0 | 0 | 95 | 940 | 110 | 0 | 17 | 0 | 0 | 95 | 260 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5486 | 4091 | 9577 | 3220 | 904 | 1313 | 20 | 2013 | 1274 | 30 | 260 | 419 | 124 | 0 | 298 | 84.21
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 337 | 192 |  | 0 | 0 | 140 | 9 | 0 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 149 | 0 | 0 | 0 |  | 6 | 31 | 68 | 22 | 12 | 32 | 0 | 3 | 0 | 0 | 0 | 290 | 0 | 222 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 20 | 8 | 21 | 8 | 16 | 20 | 122 | 55 | 0 | 17 | 0 | 30 | 43 | 51 | 47 | 0 | 0 | 60 | 0 | 0 | 140 | 19 | 0 | 10 | 310 | 0 | 0 | 10 | 115 | 0 | 0 | 48 | 0 | 52 | 0 | 25 | 17 | 6 | 366 | 47 | 52 | 85 | 0 | 283 | 17 | 92 | 17 | 106 | 25 | 395 | 55 | 0 | 17 | 68 | 0 | 7 | 0 | 94 | 17 | 327 | 0 | 0 |  | 860 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 43 | 86 | 8 | 177 | 25 | 16 | 0 | 0 | 0 | 34 | 7 | 50 | 0 | 50 | 40 | 8 | 34 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 365 | 0 | 0 | 50 | 85 | 70 | 0 | 0 | 95 | 1160 | 110 | 0 | 17 | 0 | 0 | 113 | 274 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5651 | 4350 | 10001 | 3234 | 860 | 1412 | 10 | 2108 | 1490 | 30 | 274 | 461 | 122 | 0 | 368 | 84.19
19:30 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 336 | 191 |  | 0 | 0 | 138 | 9 | 8 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 28 | 25 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 154 | 0 | 0 | 0 |  | 6 | 31 | 68 | 22 | 12 | 32 | 0 | 5 | 0 | 0 | 0 | 295 | 0 | 222 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 19 | 8 | 21 | 8 | 16 | 20 | 120 | 76 | 0 | 17 | 0 | 30 | 43 | 51 | 48 | 0 | 0 | 62 | 0 | 0 | 140 | 19 | 0 | 10 | 275 | 0 | 0 | 10 | 115 | 0 | 0 | 54 | 0 | 52 | 0 | 25 | 17 | 6 | 367 | 47 | 52 | 85 | 0 | 282 | 17 | 92 | 17 | 108 | 25 | 400 | 55 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 327 | 0 | 0 |  | 859 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 40 | 8 | 177 | 25 | 16 | 0 | 0 | 0 | 34 | 7 | 50 | 0 | 50 | 40 | 8 | 34 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 364 | 5 | 0 | 50 | 85 | 70 | 0 | 0 | 95 | 1244 | 110 | 0 | 17 | 0 | 0 | 112 | 274 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5670 | 4374 | 10044 | 3264 | 859 | 1378 | 10 | 2121 | 1574 | 30 | 274 | 414 | 120 | 0 | 282 | 0
20:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 336 | 182 |  | 0 | 0 | 138 | 9 | 11 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 154 | 0 | 0 | 0 |  | 6 | 31 | 68 | 22 | 0 | 32 | 0 | 6 | 0 | 0 | 0 | 285 | 0 | 222 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 19 | 8 | 21 | 8 | 21 | 20 | 114 | 104 | 0 | 18 | 0 | 30 | 43 | 51 | 49 | 0 | 0 | 62 | 0 | 0 | 140 | 19 | 0 | 10 | 260 | 0 | 0 | 10 | 115 | 0 | 0 | 57 | 0 | 52 | 0 | 25 | 17 | 6 | 367 | 47 | 52 | 85 | 0 | 284 | 17 | 92 | 17 | 107 | 25 | 400 | 55 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 327 | 0 | 0 |  | 859 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 40 | 8 | 177 | 22 | 16 | 0 | 0 | 0 | 34 | 10 | 50 | 0 | 50 | 40 | 8 | 30 | 21 | 0 | 8 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 365 | 17 | 0 | 50 | 85 | 70 | 0 | 0 | 95 | 1244 | 110 | 0 | 17 | 0 | 0 | 112 | 273 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5669 | 4379 | 10048 | 3296 | 859 | 1354 | 10 | 2128 | 1571 | 30 | 273 | 413 | 114 | 0 | 265 | 84.2
21:00 | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 336 | 182 |  | 0 | 0 | 140 | 8 | 17 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 153 | 0 | 0 | 0 |  | 6 | 31 | 68 | 22 | 0 | 32 | 0 | 3 | 0 | 0 | 0 | 290 | 0 | 221 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 19 | 8 | 21 | 8 | 21 | 20 | 116 | 105 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 84 | 0 | 145 | 19 | 0 | 10 | 285 | 0 | 0 | 100 | 115 | 0 | 0 | 48 | 0 | 52 | 0 | 25 | 17 | 6 | 366 | 47 | 52 | 85 | 0 | 66 | 17 | 92 | 17 | 110 | 25 | 400 | 55 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 317 | 0 | 0 |  | 906 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 40 | 8 | 180 | 25 | 16 | 0 | 0 | 0 | 34 | 12 | 50 | 0 | 50 | 40 | 8 | 30 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 371 | 17 | 0 | 50 | 85 | 70 | 0 | 0 | 95 | 1244 | 110 | 0 | 108 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5513 | 4263 | 9776 | 3298 | 906 | 1392 | 100 | 1945 | 1574 | 30 | 0 | 415 | 116 | 0 | 345 | 84.19
22:00 | 0 | 0 | 210 | 0 | 0 | 75 | 0 | 338 | 182 |  | 0 | 0 | 140 | 8 | 17 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 27 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 152 | 0 | 0 | 0 |  | 6 | 23 | 68 | 22 | 0 | 32 | 0 | 7 | 0 | 0 | 0 | 290 | 0 | 218 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 19 | 8 | 21 | 8 | 25 | 15 | 108 | 106 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 84 | 0 | 145 | 19 | 0 | 10 | 270 | 0 | 0 | 10 | 115 | 0 | 0 | 48 | 0 | 52 | 0 | 25 | 17 | 6 | 366 | 47 | 52 | 85 | 0 | 16 | 17 | 92 | 17 | 110 | 25 | 388 | 55 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 317 | 0 | 0 |  | 907 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 25 | 16 | 0 | 0 | 0 | 34 | 0 | 50 | 0 | 0 | 0 | 8 | 6 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 376 | 17 | 0 | 50 | 105 | 71 | 0 | 0 | 95 | 1244 | 110 | 0 | 108 | 0 | 0 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5331 | 4081 | 9412 | 3293 | 907 | 1385 | 10 | 1857 | 1574 | 30 | 0 | 248 | 108 | 0 | 186 | 84.19
23:00 | 0 | 0 | 210 | 0 | 0 | 75 | 0 | 350 | 193 |  | 0 | 0 | 140 | 9 | 17 | 15 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 22 | 21 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 153 | 0 | 0 | 0 |  | 6 | 23 | 68 | 22 | 0 | 33 | 0 | 13 | 0 | 0 | 0 | 290 | 0 | 182 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 20 | 8 | 21 | 8 | 30 | 18 | 104 | 106 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 84 | 0 | 145 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 65 | 0 | 0 | 57 | 0 | 52 | 0 | 25 | 17 | 5 | 366 | 47 | 52 | 85 | 0 | 16 | 17 | 92 | 17 | 64 | 25 | 401 | 55 | 0 | 17 | 68 | 0 | 17 | 0 | 65 | 17 | 340 | 0 | 0 |  | 906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 386 | 0 | 0 | 50 | 67 | 34 | 0 | 0 | 35 | 1244 | 110 | 0 | 25 | 0 | 0 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5169 | 3751 | 8920 | 3308 | 906 | 1431 | 0 | 1408 | 1574 | 30 | 0 | 159 | 104 | 0 | 157 | 84.18
24:00 | 0 | 0 | 210 | 0 | 0 | 75 | 0 | 353 | 196 |  | 0 | 0 | 140 | 8 | 17 | 15 | 0 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 22 | 21 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 8 | 154 | 0 | 0 | 0 |  | 6 | 23 | 0 | 22 | 0 | 33 | 0 | 13 | 0 | 0 | 0 | 290 | 0 | 182 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 7 | 8 | 21 | 8 | 33 | 20 | 98 | 106 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 84 | 0 | 145 | 20 | 0 | 10 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 23 | 0 | 25 | 17 | 6 | 366 | 28 | 34 | 85 | 0 | 16 | 17 | 92 | 17 | 15 | 25 | 400 | 24 | 0 | 17 | 68 | 0 | 17 | 0 | 35 | 17 | 340 | 0 | 0 |  | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 386 | 0 | 0 | 50 | 60 | 34 | 0 | 0 | 35 | 1244 | 111 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 4868 | 3621 | 8489 | 3316 | 895 | 1433 | 0 | 1065 | 1574 | 30 | 0 | 78 | 98 | 0 | 0 | 84.18
KWH | 0 | 0 | 4521000 | 0 | 0 | 1587000 | 0 | 8359940 | 4538000 |  | 0 | 0 | 3396975 | 209280 | 59703 | 291499 | 0 | 0 | 0 | 48000 | 604224 | 776160 | 0 | 0 | 0 | 0 | 265320 | 448680 | 388662 | 445932 | 528000 | 618120 | 744480 | 713200 | 305280 | 0 | 733680 | 0 | 0 | 0 | 214376 | 4705917 | 0 | 0 | 0 |  | 148320 | 490944 | 784428 | 435480 | 36480 | 522240 | 0 | 296160 | 0 | 0 | 0 | 7688300 | 0 | 4913000 | 217454 | 0 | 278208 | 336000 | 0 | 1172893 | 0 | 331840 | 151354 | 499212 | 177660 | 515200 | 377400 | 2520000 | 1430400 | 0 | 420624 | 10800 | 715000 | 986520 | 736200 | 707544 | 0 | 0 | 1405 | 1453440 | 0 | 1602500 | 440000 | 0 | 243180 | 7141500 | 0 | 0 | 214656 | 1595782 | 0 | 0 | 1226400 | 0 | 796464 | 136350 | 485760 | 353760 | 157236 | 9090000 | 801600 | 889524 | 1305563 | 25078 | 1972145 | 367029 | 1564830 | 331740 | 909720 | 459840 | 9554900 | 904320 | 0 | 434880 | 1811564 | 0 | 410040 | 101605 | 1156800 | 432720 | 7399900 | 35127 | 0 |  | 20637818 | 0 | 0 | 0 | 164160 | 0 | 0 | 0 | 172320 | 181376 | 39000 | 4420133 | 480200 | 282240 | 0 | 0 | 0 | 245632 | 82024 | 592280 | 0 | 528183 | 337911 | 76896 | 355971 | 471120 | 0 | 199206 | 1826618 | 0 | 6092200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4782964 | 0 | 9138109 | 47040 | 0 | 727968 | 1124352 | 853632 | 0 | 34309 | 820416 | 26585200 | 4195827 | 0 | 519600 | 20820 | 418320 | 1383168 | 2126287 | 0 | 0 | 171970 | 0 | 0 | 860470 |  | 117210447 | 90995740 | 208206187 | 76129121 | 20637818 | 36111602 | 214656 | 29063270 | 34504018 | 733680 | 2161414 | 4350886 | 2520000 | 1779722 | 0
Fuel Cost | 0 | 0 | 6600660 | 0 | 0 | 2110710 | 0 | 8777937 | 4901040 |  | 0 | 0 | 3770642.25 | 2339750.4 | 791064.75 | 3862361.75 | 0 | 0 | 0 | 701760 | 8501431.68 | 12581553.6 | 0 | 0 | 0 | 0 | 3374870.4 | 6057180 | 5211957.42 | 334449 | 396000 | 0 | 0 | 0 | 5192812.8 | 0 | 198093.6 | 0 | 0 | 0 | 3505047.6 | 4894153.68 | 0 | 0 | 0 |  | 1935576 | 8188945.92 | 13350964.56 | 5883334.8 | 462566.4 | 6042316.8 | 0 | 986212.8 | 0 | 0 | 0 | 8534013 | 0 | 5699080 | 280515.66 | 0 | 314375.04 | 500640 | 0 | 1958731.31 | 0 | 5730876.8 | 2035711.3 | 683920.44 | 133245 | 901600 | 283050 | 18093600 | 1559136 | 0 | 572048.64 | 172152 | 979550 | 1302206.4 | 1280988 | 1224051.12 | 0 | 0 | 2725.7 | 3313843.2 | 0 | 1618525 | 946000 | 0 | 481496.4 | 7141500 | 0 | 0 | 4499189.76 | 21782424.3 | 0 | 0 | 16531872 | 0 | 11031026.4 | 1593931.5 | 5013043.2 | 4832361.6 | 2086521.72 | 8362800 | 9747456 | 12862517.04 | 16515371.95 | 0 | 23152982.3 | 3996945.81 | 16634142.9 | 4501711.8 | 11726290.8 | 5416915.2 | 8790508 | 11710944 | 0 | 5518627.2 | 20615598.32 | 0 | 5355122.4 | 1214179.75 | 17317296 | 5698922.4 | 0 | 0 | 0 |  | 61913454 | 0 | 0 | 0 | 1708905.6 | 0 | 0 | 0 | 3103483.2 | 3264768 | 560430 | 4950548.96 | 931588 | 3076416 | 0 | 0 | 0 | 4119248.64 | 1434599.76 | 9263259.2 | 0 | 8746710.48 | 5714075.01 | 1048092.48 | 6005230.77 | 975218.4 | 0 | 150798.942 | 10612650.58 | 0 | 32227738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5548238.24 | 0 | 9046727.91 | 632217.6 | 0 | 8611861.44 | 16246886.4 | 10841126.4 | 0 | 379114.45 | 9959850.24 | 239532652 | 4279743.54 | 0 | 3845040 | 235474.2 | 4906893.6 | 21203965.44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 443205676.57 | 495077007.482 | 938282684.052 | 72335569.042 | 61913454 | 43183648.59 | 4499189.76 | 374427337.52 | 282373040.58 | 198093.6 | 0 | 72757005.46 | 18093600 | 8501745.5 | 0
Yesterday Day Peak | 0 | 0 | 210 | 0 | 0 | 74 | 0 | 331 | 173 |  | 0 | 0 | 137 | 8 | 0 | 15 | 0 | 0 | 0 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 29 | 33 | 29 | 33 | 0 | 30 | 0 | 0 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 31 | 51 | 22 | 0 | 33 | 0 | 2 | 0 | 0 | 0 | 315 | 0 | 194 | 8 | 0 | 10 | 20 | 0 | 51 | 0 | 29 | 8 | 21 | 8 | 13 | 15 | 124 | 35 | 0 | 17 | 2 | 30 | 43 | 48 | 47 | 0 | 0 | 40 | 84 | 0 | 0 | 18 | 0 | 9 | 280 | 0 | 0 | 0 | 107 | 0 | 0 | 48 | 0 | 53 | 20 | 25 | 17 | 6 | 385 | 28 | 70 | 34 | 4 | 106 | 17 | 55 | 25 | 9 | 25 | 400 | 53 | 0 | 17 | 75 | 0 | 17 | 17 | 53 | 17 | 316 | 0 | 0 |  | 904 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 20 | 16 | 0 | 0 | 0 | 0 | 4 | 50 | 0 | 34 | 30 | 0 | 30 | 18 | 0 | 8 | 76 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 416 | 0 | 0 | 50 | 50 | 38 | 0 | 5 | 35 | 1010 | 217 | 0 | 35 | 3 | 68 | 35 | 150 | 0 | 0 | 29 | 0 | 0 | 142 |  | 9231 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 0 | 0 | 76 | 0 | 336 | 182 | 0 | 0 | 0 | 138 | 9 | 11 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 28 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 154 | 0 | 0 | 0 | 0 | 6 | 31 | 68 | 22 | 0 | 32 | 0 | 6 | 0 | 0 | 0 | 285 | 0 | 222 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 19 | 8 | 21 | 8 | 21 | 20 | 114 | 104 | 0 | 18 | 0 | 30 | 43 | 51 | 49 | 0 | 0 | 62 | 0 | 0 | 140 | 19 | 0 | 10 | 260 | 0 | 0 | 10 | 115 | 0 | 0 | 57 | 0 | 52 | 0 | 25 | 17 | 6 | 367 | 47 | 52 | 85 | 0 | 284 | 17 | 92 | 17 | 107 | 25 | 400 | 55 | 0 | 17 | 68 | 0 | 17 | 0 | 94 | 17 | 327 | 0 | 0 |  | 859 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 43 | 40 | 8 | 177 | 22 | 16 | 0 | 0 | 0 | 34 | 10 | 50 | 0 | 50 | 40 | 8 | 30 | 21 | 0 | 8 | 77 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 365 | 17 | 0 | 50 | 85 | 70 | 0 | 0 | 95 | 1244 | 110 | 0 | 17 | 0 | 0 | 112 | 273 | 0 | 0 | 0 | 0 | 0 | 0 |  | 10048 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 0 | 0 | 50 | 0 | 350 | 200 | 0 | 0 | 0 | 150 | 9 | 17 | 15 | 0 | 0 | 0 | 8 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 22 | 29 | 33 | 30 | 17 | 0 | 30 | 0 | 0 | 0 | 17 | 157 | 0 | 0 | 0 | 0 | 6 | 32 | 68 | 22 | 0 | 33 | 0 | 10 | 0 | 0 | 0 | 290 | 0 | 200 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 35 | 8 | 21 | 8 | 21 | 20 | 152 | 60 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 84 | 0 | 140 | 19 | 0 | 10 | 300 | 0 | 0 | 100 | 66 | 0 | 0 | 48 | 0 | 52 | 0 | 25 | 17 | 6 | 366 | 47 | 52 | 85 | 0 | 284 | 17 | 92 | 17 | 113 | 25 | 400 | 55 | 0 | 17 | 107 | 0 | 17 |  | 94 | 17 | 300 |  |  |  | 922 | 0 | 0 |  | 49 | 0 | 0 | 0 | 45 | 86 | 8 | 190 | 22 | 16 | 0 | 0 | 0 | 34 | 17 | 95 | 0 | 50 | 41 | 8 | 34 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 200 | 0 | 415 | 18 | 0 | 50 | 105 | 85 | 0 | 0 | 95 | 1190 | 110 |  | 150 |  |  | 115 | 0 |  | 0 |  | 0 | 0
Forecast for Day | 0 | 0 | 210 | 0 | 0 | 50 | 0 | 350 | 200 | 0 | 0 | 0 | 150 | 9 | 17 | 15 | 0 | 0 | 0 |  | 24 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 22 | 29 | 33 | 30 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 157 | 0 | 0 | 0 | 0 | 6 | 32 | 51 | 22 | 0 | 33 | 0 | 5 | 0 | 0 | 0 | 290 | 0 | 200 | 8 | 0 | 10 | 5 | 0 | 51 | 0 | 35 | 8 | 21 | 8 | 21 | 20 | 135 | 50 | 0 | 18 | 1.6 | 30 | 43 | 11 | 10 | 0 | 0 | 62 | 10 | 0 | 140 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 52 | 20 | 25 | 17 | 6 | 366 | 28 | 34 | 32 | 5 | 110 | 17 | 52 | 17 | 9 | 25 | 400 | 17 | 50 | 17 | 51 | 0 | 17 | 30 | 54 | 17 | 300 |  |  |  | 922 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 34 | 15 | 8 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 415 | 0 | 0 | 50 | 50 | 35 | 0 | 8 | 35 | 1150 | 110 |  | 35 | 6 | 100 | 115 | 0 |  | 0 | 30 | 0 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 210 | 0 | 0 | 47 | 0 | 354 | 212 | 0 | 0 | 0 | 145 | 9 | 17 | 15 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 29 | 33 | 32 | 8 | 0 | 30 | 0 | 0 | 0 | 8 | 157 | 0 | 0 | 0 | 0 | 6 | 23 | 0 | 22 | 0 | 32 | 0 | 2 | 0 | 0 | 0 | 285 | 0 | 216 | 0 | 0 | 20 | 0 | 0 | 51 | 0 | 4 | 0 | 21 | 8 | 14 | 20 | 88 | 52 | 0 | 18 | 0 | 30 | 43 | 11 | 10 | 0 | 0 | 63 | 10 | 0 | 145 | 19 | 0 | 10 | 290 | 0 | 0 | 0 | 32 | 0 | 0 | 48 | 0 | 18 | 7 | 25 | 17 | 6 | 366 | 28 | 34 | 32 | 1 | 16 | 17 | 52 | 17 | 9 | 25 | 400 | 17 | 0 | 17 | 51 | 0 | 0 | 2 | 36 | 17 | 310 | 0 | 0 | 0 | 905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 8 | 0 | 21 | 0 | 8 | 81 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 424 | 0 | 0 | 0 | 72 | 0 | 0 | 1 | 0 | 1140 | 111 | 0 | 17 | 0 | 10 | 115 | 0 | 0 | 0 | 5 | 0 | 0 | 22 | 0 |  |  |  | 112.2407 | 20.6378 | 35.7902 | 34.504 | 0.73368 | 2.52 | 1.7797
208.2062
| Minimum Generation |  | 6996 | 5:00
| Highest Generation |  | 10048 | 20:00
| Day Peak Generation |  | 9231 | 12:00
| Evening Peak Generation |  | 10048 | 20:00
| HVDC Max Flow |  | 907 | 7:00
| HVDC EvPeak Flow |  | 859 | 20:00
| Load factor L.F |  | 86.34% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-01-26
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-01-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 9231 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 7101
Evening Peak Generation : |  |  | 10048 | MW Hour : | 20:00 | Available Max Generation : |  | 10300
E.P. Demand (at gen end) : |  |  | 10336 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 10300
Maximum Generation : |  |  | 10048 | MW Hour : | 20:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 208.2062 | System Load Factor : | 86.34% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 850 | MW at | 7:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-01-26
Actual : |  | 84.15 | Ft.(MSL) , | Rule curve : | 98.6 | Ft.( MSL )
Gas Consumed : |  | Total = | 845.63 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 115519217.632
: |  |  | Coal : | 282373040.58 | Oil : | 451683532.74 | Total : | 849575790.952
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 105 | 2520:00 | 3265.9867 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 925.1972 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1221.1835 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1083.4939 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 922.348 |  |  | 0 | 0%
Mymensingh Area |  | 109 | 2616:00 | 761.9973 |  |  | 0 | 0%
Sylhet Area |  | 51 | 1224:00 | 340.5797 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 277.6321 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 601.6466 |  |  | 0 | 0%
Total |  | 265 |  | 9400.065 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 2
2) Ghorasal-3
3) Ashuganj-5
4) Baghabari-70,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1,2
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
08:12 | 17:51 | Madaripur-Shariatpur 132kV Ckt-2 Scheduled S/D from Madaripur 132/33kV end Due to Annual Maintenance
08:12 | 17:01 | Ishurdi 132/33kV S/S 132/33 kV T-2 HT Scheduled S/D Due to Annual Maintenance
08:12 | 17:10 | Ishurdi 132/33kV S/S 132/33 kV T-2 LT Scheduled S/D Due to Annual Maintenance
08:17 | 15:45 | Shahmirpur-Sikalbaha 132kV Ckt-1 Scheduled S/D from Shikalbaha 230/132kV end.
08:18 | 17:42 | Khagrachori 132/33kV S/S TR-1 HT Scheduled S/D Due to Annual Maintenance
08:19 | 16:23 | Kaliakoir 400/230/132kV S/S Bibiyana1 Scheduled S/D Due to Due to Dead Line Checking.
08:22 | 16:32 | Patuakhali 132/33kV S/S Barishal-Pautakhali 132kV Line Scheduled S/D Due to Annual Maintenance-2023
08:23 | 16:32 | Barishal-Patuakhali(Barguna T at Bakergonj) 132 kV Ckt Scheduled S/D from Barguna 132/33kV end Due to Annual
maintenance.
08:27 |  | Allocated load Rajshahi zone-610 MW & Rangpur zone-470 MW.
08:27 | 16:05 | Hathazari-Kaptai 132kV Ckt-2 Scheduled S/D from Hathazari 230/132/33kV end Due to Kaptai requirement & Nldc
instruction.
08:28 | 16:25 | Bibiyana-Kaliakoir 400 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
08:30 | 17:51 | Madaripur-Shariatpur 132kV Ckt-2 Scheduled S/D from Shariatpur 132/33kV end Due to Annual Maintenance .
08:37 | 16:18 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Fenchuganj 230/132/33kV end Due to Dead line checking
08:47 | 16:20 | Bibiyana-Fenchuganj 230 kV Ckt-1 Scheduled S/D from Bibiana 400/230kV end Due to AM
08:52 |  | Allocated load-650 MW & Rangpur zone-500 MW.
08:54 | 12:19 | Daudkandi 132/33kV S/S Transformer-3 LT Scheduled S/D Due to Maintenance work
08:54 | 12:17 | Daudkandi 132/33kV S/S Transformer-3 HT Scheduled S/D Due to Maintenance work
08:59 |  | Allocated load Rajshahi zone-700 MW & Rangpur zone-530 MW.
09:06 | 16:01 | Kodda(300MW)-Tongi 230kV Ckt-1 Scheduled S/D from Tongi 230/132/33kV end Due to Annual Maintenance Dead Line
Checking.
09:08 | 16:32 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 LT Scheduled S/D Due to Earth blade adjustment.
09:09 | 16:30 | Beanibazar 132/33kV S/S 132 KV Transformer TR-01 HT Scheduled S/D Due to Earth blade adjustment
09:09 |  | Basundhara 132/33kv gt-3 sd .
09:10 | 13:05 | Chapai 132/33kV S/S T-4 (435T) LT Scheduled S/D
09:10 | 13:05 | Chapai 132/33kV S/S T-4 (435T) LT Scheduled S/D
09:12 | 13:03 | Chapai 132/33kV S/S T-4 (435T) HT Scheduled S/D
09:14 |  | PDB Machines Demand=Full.
09:15 | 16:18 | Sirajgonj 230 S/S Bus-1 Scheduled S/D Due to Annual maintenance work.
09:18 | 17:30 | Savar 132/33kV S/S T-1 HT Scheduled S/D Due to Annual maintenance work.
09:18 | 17:30 | Savar 132/33kV S/S T-1 LT Scheduled S/D Due to Annual maintenance work.
09:18 | 17:33 | Fenchuganj-Sreemangal 132kV Ckt-1 Scheduled S/D from Sreemongol 132/33kV end. and from Fenchuganj 230/132/33kV
end Due to Shutdown taken by Srimongal SS.
09:21 | 17:34 | Haripur 230/132kV S/S Auto TR-1 LT Scheduled S/D Due to Annual Maintenance
09:21 | 17:33 | Haripur 230/132kV S/S Auto TR-1 HT Scheduled S/D Due to Annual Maintenance
09:44 | 18:00 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Srinagar 132/33kV end Due to Dead Line
Checking.
09:49 |  | Allocated load Rajshahi zone-750 MW & Rangpur zone-580 MW
09:57 | 17:16 | Mirpur-Uttara 132kV Ckt-1 Scheduled S/D from Mirpur 132/33kV end Due to AM & Relay testing
09:58 |  | L/S free Rajshahi zone & Rangpur zone.
10:01 | 15:36 | Sunamganj 132/33kV S/S Tr-1 LT Scheduled S/D
10:03 | 15:34 | Sunamganj 132/33kV S/S Tr-1 HT Scheduled S/D Due to None
10:15 | 17:59 | Keraniganj-Sreenagar (T at Powerpac 100MW) 132kV Ckt-2 Scheduled S/D from Keranigonj 230/132/33kV end Due to Dead
line check at srinagar end.
10:21 | 13:34 | Tangail 132/33kV S/S Tr-3 LT Scheduled S/D Due to Relay testing for annual maintenance.
10:21 | 13:34 | Tangail 132/33kV S/S Tr-3 HT Scheduled S/D Due to Relay testing for annual maintenance.
testing for annual maintenance.
10:21 | 13:34 | Tangail 132/33kV S/S Tr-3 LT Scheduled S/D Due to Relay testing for annual maintenance.
10:22 | 17:02 | Ashuganj-Bhulta 400 kV Ckt-1 Scheduled S/D from Bhulta 400/230kV end Due to Due to Annual Maintenance works.
10:31 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 LT Project Work S/D Due to Project work
10:35 |  | Payra 400/132/33kV S/S 400/132/33 kV Auto Transformer-02 HT Project Work S/D Due to Project work
11:10 |  | Khulna 330 MW CCPP GT was synch.
12:00 |  | Day Peak Gen. 9232 MW
| 12:25 | Chhatak 132/33kV S/S T-3 HT is restored.
| 12:25 | Chhatak 132/33kV S/S T-3 LT is restored.
12:47 |  | Basundhara 132/33 kv gt-3 was swiched on
13:34 |  | Sikalbaha 225MW ST was FSD | [5 empty] | 75MW generation interrup.
13:36 | 17:08 | Tangail 132/33kV S/S Tr-4 HT Scheduled S/D Due to Relay and tan delta test for annual maintenance
13:36 | 17:09 | Tangail 132/33kV S/S Tr-4 LT Scheduled S/D Due to Relay and tan delta test for annual maintenance
14:37 |  | Sylhet CCPP 225 MW GT was sync.
| 15:26 | Nawabganj 132/33kV S/S TR-2 HT is restored.
| 15:28 | Nawabganj 132/33kV S/S TR-2 LT is restored.
| 15:31 | Bagerhat-Mongla 132 kV Ckt-2 is restored.
| 15:45 | Shahmirpur-Sikalbaha 132kV Ckt-1 is restored.
16:02 |  | Bhola Natun Biddut BD LTD (GAS) GT11 was forced shutdown.
16:48 | 17:54 | Ashugonj 132/33 kV T3 along with 33 kV bus was S/D due to emergency maintenance work by Bhairab PDB | [5 empty] | 17MW generation interrup.
and 10MW Load interrup.
| 16:54 | Fenchuganj 230/132/33kV S/S TR-02 HT is restored.
| 16:55 | Fenchuganj 230/132/33kV S/S TR-02 LT is restored.
| 16:57 | Cumilla(S)-Kachua 132 kV Ckt-1 is restored.
| 16:58 | Cumilla(N)-Kachua 132 kV Ckt-2 is restored.
17:32 | 17:34 | Shahjibazar 132/33kV S/S SPCL 86 MW Tripped showing relay relays Due to None
17:35 | 20:20 | Shahjibazar 132/33kV S/S SPCL 86 MW Scheduled S/D Due to 86 MW Plant side Maintenance.
| 17:40 | Aminbazar-Kallyanpur 132kV Ckt-1 is restored.
20:00 |  | Evening Peak Generation = 10,049MW
23:20 | 23:52 | Madanganj 132/33kV S/S Madanganj -Bashundhara 132 kv Ckt Tripped showing Differential relay relays.
05:00 |  | Minimum Gen: 7102 MW.
07:12 |  | Bhandaria 132/33kV S/S Transformer-2 LT Project Work S/D Due to PGNS Project work.
07:13 |  | Bhandaria 132/33kV S/S Transformer-2 HT Project Work S/D Due to PGNS Project work.
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  | Load Despatch Circle

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-01-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 4521000
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 76 | 1587000 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 336 | 8359940 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 182 | 4538000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 0 | 0 | Under maint.
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 9 | 209280 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 138 | 3396975 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 11 | 59703 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 291499 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 445932
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 8 | 48000 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 48 | 604224 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 265320 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 776160 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 448680
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 388662 | Fuel shortage
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1146120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 744480
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 30 | 713200
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 17 | 305280 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 115 | 1595782 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 52 | 796464 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 52 | 889524 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 55 | 904320 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 434880 | Fuel shortage
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 101605
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 432720 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 1663 | 34004750
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Machine problem
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 17 | 214376 | Fuel shortage
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 136350
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 32 | 522240 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 733680 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 154 | 4705917
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 85 | 1305563 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 31 | 490944 | Fuel shortage
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 784428 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 22 | 435480 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 25 | 485760 | Fuel shortage
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 6 | 296160
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 36480 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25078
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 284 | 1972145 | Engine problem
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 367029 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 92 | 1564830 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 25 | 459840 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1811564 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 35127 | On test.
| Chattogram area Total |  |  |  | 2382 | 956 | 16382991
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 222 | 4913000 | 0
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7688300
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 327 | 7399900 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 278208 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 336000 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1172893
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 6 | 157236 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 19 | 331840 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 17 | 353760 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 499212
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 177660 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2520000
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 21 | 515200 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 151354 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 20 | 377400 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 10 | 214656 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 331740 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 107 | 909720 | Engine problem
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 410040 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 94 | 1156800 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1387 | 30112373
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 104 | 1430400 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 420624 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10800
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 57 | 1226400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 47 | 801600 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 0
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 148320 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 232 | 4038144
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 986520 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Gas shortage
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 51 | 736200
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 49 | 707544
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 0 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1405
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 0 | 1453440
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 1602500 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 19 | 440000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 0 | 0 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 260 | 7141500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 9090000
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 243180
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9554900
| Sylhet Area Total |  |  |  | 2427 | 1431 | 32672189
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 859 | 20637818
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 164160 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 43 | 172320 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 40 | 181376 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 0 | 0 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 39000 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 47040 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 85 | 1124352 | Fuel shortage
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 418320
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 273 | 2126287 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage
| Khulna Area Total |  |  |  | 3001 | 1341 | 24910673
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 282240 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 22 | 480200 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 177 | 4420133 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 26585200
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 110 | 4195827 | GT-1 Under maint.
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 519600 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 0 | 0 | Coal shortage
| Barisal Area Total |  |  |  | 2265 | 1586 | 36483200
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 34 | 245632 | Fuel shortage
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 82024 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 528183
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 337911 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4782964 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 365 | 9138109 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 355971 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 471120
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 199206 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 76896 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 592280 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 50 | 727968 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 820416 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 20820
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 943 | 18379500
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 77 | 1826618
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 6092200 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 70 | 853632 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34309
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 112 | 1383168
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 171970
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 860470
| Rangpur Area Total |  |  |  | 750 | 509 | 11222367
| Total |  |  |  | 22700 | 10048 | 208206187
| Eastern Grid Total |  |  |  | 14555 | 5669 | 117210447
| Western Grid Total |  |  |  | 8145 | 4379 | 90995740
| National Grid Total |  |  |  | 22700 | 10048 | 208206187
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-01-25
| (a) ENTIRE EASTERN GRID : |  | 6376.52 | MW | (b) ENTIRE WESTERN GRID : |  | 3154.4 | MW
| i) Dhaka area |  | 3447.02 | MW | i) Khulna area |  | 1123.6 | MW
| ii) Chittagong area |  | 947.5 | MW | ii) Rajshahi area |  | 1022.8 | MW
| iii) Comilla area |  | 830 | MW | iii) Barisal area |  | 283 | MW
| iv) Mymensingh area |  | 828 | MW | iv) Rangpur area |  | 725 | MW
| v) Sylhet area |  | 324 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 9530.92 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 0 | 00:00 | Chhatak | 18 | 19:00 | Kamrangirchar | 68 | 13:00 | Natore | 97 | 18:30 | Shitalakhya | 111 | 12:00
2 | AKSML | 98 | 01:00 | Chowmuhani | 132 | 18:30 | Kaptai | 4 | 18:00 | Nawabganj | 25.7 | 14:00 | Sholosohor | 22 | 09:00
3 | Aftabnagar | 23 | 18:00 | Chuadanga | 71 | 18:30 | Kazla | 74 | 13:00 | Netrakona | 115 | 06:00 | Shyampur | 160 | 07:00
4 | Agargaon | 53 | 13:00 | Coxsbazar | 93 | 18:30 | Keranigonj | 48 | 18:00 | New | 52 | 15:00 | Siddhirganj | 94 | 13:00
5 | Agrabad | 48 | 18:00 | Cumilla(N) | 106 | 18:00 | Khagrachori | 22 | 19:00 | Niamatpur | 90 | 18:30 | Sirajganj | 86 | 19:00
6 | Amnura | 49 | 19:00 | Cumilla(S) | 128 | 14:00 | Khulna | 83 | 18:30 | Noapara | 32.5 | 18:00 | Sonargaon | 92 | 23:00
7 | Ashuganj | 45 | 18:30 | Daudkandi | 103 | 20:00 | Khulshi | 145 | 14:00 | PHP | 10 | 10:00 | Sreemongol | 35 | 22:00
8 | BIPTC | N/A | N/A | Dhaka | 22 | 13:00 | Kishoreganj | 106 | 22:00 | Pabna | 75 | 18:30 | Srinagar | 28.43 | 22:00
9 | BSRM | 112 | 07:00 | Dhamrai | 80 | 08:00 | Kodda | 250 | 15:00 | Palashbari | 104 | 18:30 | Sunamganj | 30 | 22:00
10 | Bagerhat | 71 | 19:30 | Dhanmondi | 96 | 13:00 | Kulaura | 24 | 18:00 | Panchagarh | 52 | 18:30 | Sylhet | 89 | 19:30
11 | Bakulia | 70 | 18:00 | Dohazari | 68 | 20:00 | Kurigram | 58 | 18:30 | Patuakhali | 73 | 21:00 | TK | 20 | 18:00
12 | Banani | 26 | 13:00 | Faridpur | 105 | 19:00 | Kushtia | 82 | 18:30 | Payra | 11 | 14:00 | Tangail | 155 | 19:30
13 | Bangabhaban | 10 | 13:00 | Fatullah | 48 | 10:00 | Lalbag | 67 | 13:00 | Postogola | 29 | 12:00 | Thakurgaon | 70 | 18:30
14 | Barapukuria | 56 | 13:00 | Fenchuganj | 26 | 19:30 | Lalmonirhat | 42 | 08:00 | Purbachal | 13 | 12:00 | Tongi | 81 | 11:00
15 | Barguna | 14 | 18:30 | Feni | 85 | 18:00 | Madanganj | 32 | 00:00 | Purbasadipur | 111 | 18:30 | Ullon | 37 | 13:00
16 | Barishal | 74 | 19:00 | GPH | 85 | 05:00 | Madaripur | 67 | 20:00 | Rahanpur_I | 4.1 | 05:00 | Uttara | 56 | 13:00
17 | Barishal-230 | 62 | 18:30 | Ghorashal | 46 | 01:00 | Madartek | 48 | 21:00 | Rahim | 38 | 06:00 | UttaraNew | 14 | 13:00
18 | Baroaulia | 57 | 14:00 | Goalpara | 20 | 12:00 | Madunaghat | 41 | 18:00 | Rajbari | 44 | 18:00 | Zigatola | 33 | 13:00
19 | Baroirhat | 33 | 18:00 | Gollamari | 28 | 00:00 | Magura | 44 | 18:30 | Rajendrapur | 94 | 13:00
20 | Bashundhara | 103 | 11:00 | Gopalganj | 78.8 | 18:30 | Mahasthangarh | 42 | 18:30 | Rajshahi | 98 | 20:00
21 | BashundharaCement | 1 | 00:00 | Gulshan | 72 | 13:00 | Manikganj | 73 | 22:00 | Rajshahi-230 | 25 | 19:00
22 | Beanibazar | 39 | 21:00 | Halishahar | 85.5 | 15:00 | Maniknagar | 40 | 13:00 | Ramganj | 70 | 20:00
23 | Benapole | 48 | 08:00 | HaripurSBU | 147 | 15:00 | Matarbari | 37 | 18:30 | Rampur | 19 | 19:00
24 | Bhaluka | 108 | 00:00 | Hasnabad | 75 | 14:00 | Matuail | 53 | 10:00 | Rangamati | 9 | 18:00
25 | Bhandaria | 32 | 20:00 | Hathazari | 45 | 18:30 | Millgate | 54 | 09:00 | Rangpur | 124 | 18:30
26 | Bhangura | 20 | 18:30 | Ishurdi | 50 | 18:30 | Mirpur | 90 | 18:30 | Ruppur | 3.2 | 09:00
27 | Bheramara(GK) | 38 | 18:30 | Jaldhaka | 53 | 18:30 | Mirsorai | 2 | 00:00 | SSM | 40 | 19:00
28 | Bhulta | 201 | 00:00 | Jamalpur | 116 | 22:00 | Mithapukur | 26 | 18:00 | Saidpur | 99 | 18:00
29 | Bog-Sherpur | 56 | 17:00 | Jashore | 101 | 09:00 | Modern | 0 | 00:00 | Satkhira | 83 | 19:00
30 | Bogura | 115 | 18:30 | Jhenaidah | 87 | 08:00 | Mogbazar | 90 | 15:00 | Satmasjid | 65 | 13:00
31 | Borhanuddin | 29 | 22:00 | Joydebpur | 132 | 18:00 | Mongla | 25 | 12:00 | Savar | 126 | 16:00
32 | Brahmanbaria | 106 | 19:00 | Joypurhat | 43 | 19:00 | Motijheel | 23 | 13:00 | Shahjadpur | 78 | 18:30
33 | Cantonment | 92 | 13:00 | Juldah | 23 | 00:00 | Munshiganj | 61 | 19:30 | Shahjibazar | 82 | 23:00
34 | Chandpur | 45 | 20:00 | KSRM | 30 | 15:00 | Mymensingh | 183 | 21:00 | Shahmirpur | 30.7 | 00:00
35 | Chandraghona | 24 | 18:00 | Kabirpur | 228 | 16:00 | Naogaon | 108 | 13:00 | Shariatpur | 50 | 21:00
36 | Chapai | 54 | 13:00 | Kachua | 51 | 20:00 | Narail | 39 | 18:30 | Sherpur | 104 | 03:00
37 | Charsaidpur | 47 | 12:00 | Kallyanpur | 66 | 11:00 | Narinda | 49 | 13:00 | Shikalbaha | 21 | 12:00
38 | Chauddagram | 29 | 13:00 | Kalurghat | 23 | 09:00 | Narshingdi | 122 | 08:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-01-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 412 | 04:00 | 393 | 14:00 | Gopalganj_I | N/A | N/A | N/A | N/A
| Bhulta | 393 | 05:00 | 375 | 14:00 | Kaliakoir | 397 | 05:00 | 370 | 12:00
| Bibiana | 405 | 22:00 | 394 | 14:00 | Payra | 420 | 06:00 | 409 | 16:00
| BIPTC | 406 | 03:00 | 392 | 12:00 | Rahanpur_I | 411 | 09:00 | 378 | 07:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 238 | 02:00 | 226 | 14:00 | Hasnabad | 236 | 22:00 | 228 | 11:00
| AKSML | 244 | 20:00 | 223 | 14:00 | Hathazari | 243 | 19:00 | 235 | 00:00
| Aminbazar | 240 | 05:00 | 232 | 12:00 | Ishurdi | 237 | 05:00 | 226 | 13:00
| Ashuganj | 240 | 01:00 | 233 | 12:00 | Jhenaidah | 239 | 01:00 | 226 | 08:00
| Baghabari | 236 | 02:00 | 227 | 13:00 | Kaliakoir | 238 | 05:00 | 223 | 14:00
| Barapukuria | 229 | 09:00 | 215 | 17:00 | Keranigonj | 237 | 02:00 | 226 | 12:00
| Barishal | 246 | 19:00 | 240 | 12:00 | Khulna(S) | 245 | 01:00 | 228 | 08:00
| Bheramara | 235 | 01:00 | 224 | 13:00 | Maniknagar | 237 | 05:00 | 225 | 14:00
| Bhulta | 238 | 03:00 | 226 | 14:00 | Meghnaghat | 242 | 21:00 | 235 | 15:00
| Bibiana | 240 | 22:00 | 230 | 14:00 | Mirsorai | 241 | 00:00 | 231 | 05:00
| BIPTC | 238 | 02:00 | 226 | 12:00 | Rajshahi | 239 | 09:00 | 230 | 12:00
| Bogura | 232 | 22:00 | 224 | 13:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 248 | 00:00 | 245 | 14:00 | Rampura | 236 | 04:00 | 226 | 12:00
| BSRM | 241 | 19:00 | 232 | 12:00 | Shikalbaha | 242 | 16:00 | 231 | 03:00
| Cumilla(N) | 238 | 21:00 | 228 | 14:00 | Shyampur | 236 | 01:00 | 226 | 14:00
| Fenchuganj | 242 | 01:00 | 234 | 12:00 | Siddhirganj | 237 | 00:00 | 228 | 12:00
| Ghorashal | N/A | N/A | N/A | N/A | Sirajgonj | 233 | 01:00 | 226 | 12:00
| GPH | 242 | 19:00 | 231 | 03:00 | Tongi | 235 | 04:00 | 222 | 15:00
| Haripur | 233 | 01:00 | 224 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Aftabnagar | 137 | 01:00 | 130 | 14:00 | Kushtia | 137 | 06:00 | 130 | 12:00
| Agargaon | 138 | 01:00 | 132 | 12:00 | Lalbag | 134 | 04:00 | 127 | 12:00
| Agrabad | 141 | 19:00 | 133 | 04:00 | Lalmonirhat | 130 | 09:00 | 124 | 07:00
| AKS | 140 | 17:00 | 133 | 10:00 | Madanganj | 136 | 03:00 | 129 | 14:00
| Aminbazar | 137 | 05:00 | 130 | 11:00 | Madaripur | 136 | 05:00 | 129 | 14:00
| Amnura | 134 | 15:00 | 125 | 08:00 | Madartek | 138 | 02:00 | 129 | 14:00
| Ashuganj | 138 | 07:00 | 134 | 12:00 | Madunaghat | 141 | 19:00 | 135 | 02:00
| Bagerhat | 138 | 01:00 | 128 | 07:00 | Magura | 138 | 01:00 | 129 | 12:00
| Bakulia | 140 | 19:00 | 135 | 00:00 | Mahasthangarh | 136 | 22:00 | 128 | 07:00
| Banani | 136 | 03:00 | 126 | 14:00 | Manikganj | 132 | 06:00 | 123 | 10:00
| Bangabhaban | 137 | 01:00 | 129 | 12:00 | Maniknagar | 136 | 01:00 | 130 | 13:00
| Barapukuria | 134 | 09:00 | 127 | 13:00 | Matarbari | 135 | 13:00 | 125 | 18:30
| Barguna | 137 | 21:00 | 128 | 18:30 | Matuail | 137 | 22:00 | 130 | 14:00
| Barishal | 138 | 02:00 | 134 | 14:00 | Millgate | 136 | 03:00 | 125 | 14:00
| Barishal-230 | 139 | 19:00 | 135 | 12:00 | Mirpur | 136 | 22:00 | 130 | 12:00
| Baroaulia | 143 | 20:00 | 136 | 14:00 | Mithapukur | 134 | 22:00 | 126 | 11:00
| Baroirhat | 140 | 18:30 | 133 | 04:00 | Modern | 140 | 20:00 | 135 | 01:00
| Bashundhara | 136 | 03:00 | 125 | 12:00 | Mogbazar | 140 | 01:00 | 130 | 12:00
| BashundharaCement | 139 | 17:00 | 129 | 14:00 | Mongla | 135 | 00:00 | 127 | 08:00
| Beanibazar | 134 | 00:00 | 129 | 12:00 | Motijheel | 137 | 01:00 | 129 | 12:00
| Benapole | 137 | 01:00 | 125 | 08:00 | Munshiganj | 137 | 21:00 | 128 | 14:00
| Bhaluka | 125 | 04:00 | 113 | 12:00 | Mymensingh | 126 | 20:00 | 112 | 12:00
| Bhandaria | 139 | 02:00 | 135 | 11:00 | Naogaon | 133 | 09:00 | 125 | 13:00
| Bhangura | 141 | 01:00 | 134 | 13:00 | Narail | 138 | 04:00 | 127 | 08:00
| Bheramara | 136 | 00:00 | 130 | 03:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara(GK) | 138 | 01:00 | 132 | 13:00 | Narshingdi | 135 | 02:00 | 129 | 12:00
| Bhulta | 130 | 09:00 | 123 | 14:00 | Natore | 135 | 02:00 | 129 | 13:00
| Bog-Sherpur | 137 | 04:00 | 130 | 07:00 | Nawabganj | 134 | 01:00 | 126 | 14:00
| Bogura | 136 | 21:00 | 130 | 03:00 | Netrakona | 124 | 09:00 | 108 | 13:00
| Bogura-230 | 137 | 21:00 | 130 | 13:00 | New | 136 | 03:00 | 124 | 13:00
| Brahmanbaria | 134 | 01:00 | 129 | 12:00 | Niamatpur | 132 | 09:00 | 118 | 07:00
| Cantonment | 138 | 01:00 | 130 | 14:00 | Noapara | 139 | 01:00 | 128 | 08:00
| Chandpur | 143 | 22:00 | 135 | 13:00 | Pabna | 139 | 01:00 | 130 | 13:00
| Chandraghona | 142 | 18:30 | 135 | 03:00 | Palashbari | 132 | 22:00 | 124 | 07:00
| Chapai | 134 | 17:00 | 129 | 11:00 | Panchagarh | 137 | 08:00 | 120 | 13:00
| Charsaidpur | 137 | 21:00 | 131 | 12:00 | Patuakhali | 136 | 21:00 | 128 | 08:00
| Chauddagram | 140 | 09:00 | 133 | 14:00 | Payra | 133 | 21:00 | 129 | 07:00
| Chhatak | 134 | 00:00 | 128 | 12:00 | PHP | 141 | 19:00 | 131 | 14:00
| Chowmuhani | 143 | 19:00 | 128 | 14:00 | Postogola | 137 | 21:00 | 130 | 14:00
| Chuadanga | 136 | 03:00 | 125 | 13:00 | Purbachal | 138 | 01:00 | 126 | 14:00
| Coxsbazar | 133 | 13:00 | 124 | 02:00 | Purbasadipur | 133 | 08:00 | 121 | 12:00
| Cumilla(N) | 142 | 19:00 | 134 | 14:00 | Rahim | 138 | 21:00 | 128 | 20:00
| Cumilla(S) | 143 | 22:00 | 129 | 10:00 | Rajbari | 135 | 01:00 | 128 | 13:00
| Daudkandi | 141 | 21:00 | 131 | 14:00 | Rajendrapur | 130 | 05:00 | 116 | 15:00
| Dhaka | 138 | 03:00 | 130 | 14:00 | Rajshahi | 136 | 21:00 | 129 | 07:00
| Dhamrai | 137 | 06:00 | 129 | 12:00 | Rajshahi-230 | 133 | 10:00 | 127 | 07:00
| Dhanmondi | 139 | 22:00 | 131.5 | 14:00 | Ramganj | 141 | 16:00 | 127 | 14:00
| Dohazari | 138 | 19:00 | 131 | 02:00 | Rampur | 139 | 18:00 | 133 | 02:00
| Faridpur | 136 | 01:00 | 130 | 12:00 | Rampura | 138 | 04:00 | 130 | 12:00
| Fatullah | 138 | 22:00 | 130 | 14:00 | Rangamati | 141 | 19:00 | 134 | 02:00
| Fenchuganj | 137 | 00:00 | 134 | 12:00 | Rangpur | 133 | 22:00 | 124 | 07:00
| Feni | 142 | 19:00 | 131 | 14:00 | Ruppur | 138 | 00:00 | 135 | 06:00
| Ghorashal | 140 | 00:00 | 135 | 14:00 | Saidpur | 132 | 08:00 | 122 | 11:00
| Goalpara | 140 | 03:00 | 131 | 13:00 | Satkhira | 139 | 01:00 | 128 | 08:00
| Gollamari | 139 | 01:00 | 131 | 08:00 | Satmasjid | 138 | 01:00 | 131 | 12:00
| Gopalganj | 139 | 19:00 | 131 | 14:00 | Savar | 136 | 03:00 | 128 | 07:00
| Gopalganj-400 | 138 | 04:00 | 132 | 14:00 | Shahjadpur | 146 | 07:00 | 141 | 19:30
| Gopalganj_I | N/A | N/A | N/A | N/A | Shahjibazar | 135 | 02:00 | 133 | 12:00
| Gulshan | 137 | 01:00 | 129 | 14:00 | Shahmirpur | 140 | 15:00 | 134 | 00:00
| Halishahar | 141 | 19:00 | 132 | 02:00 | Shariatpur | 136 | 04:00 | 129 | 12:00
| Haripur | 138 | 21:00 | 131 | 14:00 | Sherpur | 129 | 03:00 | 115 | 00:00
| HaripurSBU | 139 | 15:00 | 131 | 07:00 | Shikalbaha | 141 | 15:00 | 135 | 01:00
| Hasnabad | 136 | 00:00 | 131 | 12:00 | Shikalbaha-230 | 140 | 16:00 | 133 | 02:00
| Hathazari | 142 | 19:00 | 114 | 15:00 | Shitalakhya | 137 | 21:00 | 129 | 14:00
| Ishurdi | 138 | 01:00 | 131 | 13:00 | Sholosohor | 140 | 19:00 | 134 | 00:00
| Jaldhaka | 131 | 09:00 | 120 | 13:00 | Shyampur | 137 | 22:00 | 132 | 12:00
| Jamalpur | 129 | 05:00 | 116 | 00:00 | Shyampur-230 | 136 | 01:00 | 130 | 12:00
| Jashore | 135 | 00:00 | 125 | 08:00 | Siddhirganj | 138 | 21:00 | 131 | 14:00
| Jhenaidah | 139 | 03:00 | 129 | 13:00 | Sirajganj | 137 | 03:00 | 130 | 11:00
| Jhenaidah-230 | 139 | 02:00 | 130 | 08:00 | Sonargaon | 137 | 23:00 | 134 | 00:00
| Joydebpur | 144 | 09:00 | 132 | 15:00 | Sreemongol | 135 | 01:00 | 130 | 13:00
| Joypurhat | 133 | 05:00 | 124 | 13:00 | Srinagar | 135 | 05:00 | 125 | 14:00
| Juldah | 139 | 18:00 | 135 | 00:00 | SSM | 143 | 19:30 | 138 | 13:00
| Kabirpur | 135 | 05:00 | 119 | 12:00 | Sunamganj | 134 | 01:00 | 127 | 14:00
| Kachua | 142 | 17:00 | 133 | 02:00 | Sylhet | 134 | 00:00 | 129 | 14:00
| Kaliakoir | 139 | 05:00 | 121 | 12:00 | Tangail | 130 | 05:00 | 117 | 12:00
| Kallyanpur | 137 | 22:00 | 130 | 12:00 | Thakurgaon | 136 | 08:00 | 118 | 13:00
| Kalurghat | 140 | 15:00 | 133 | 03:00 | TK | 141 | 19:00 | 134 | 06:00
| Kamrangirchar | 134 | 05:00 | 126 | 14:00 | Tongi | 137 | 04:00 | 130 | 10:00
| Kaptai | 140 | 00:00 | 135 | 10:00 | Ullon | 138 | 02:00 | 129 | 14:00
| Kazla | 137 | 04:00 | 129 | 13:00 | Uttara | 137 | 03:00 | 126 | 12:00
| Keranigonj | 134 | 01:00 | 126 | 12:00 | UttaraNew | 137 | 03:00 | 129 | 14:00
| Khagrachori | 141 | 21:00 | 135 | 03:00 | Zigatola | 134 | 03:00 | 126 | 13:00
| Khulna | 140 | 01:00 | 130 | 08:00
| Khulna(S) | 140 | 01:00 | 131 | 08:00
| Khulshi | 139 | 19:00 | 134 | 00:00
| Kishoreganj | 130 | 08:00 | 123 | 12:00
| Kodda | 139 | 19:00 | 119 | 12:00
| KSRM | 141 | 15:00 | 134 | 05:00
| Kulaura | 138 | 04:00 | 133 | 14:00
| Kurigram | 130 | 08:00 | 120 | 07:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-01-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 1150 | 4868 | 3621 | 8489 |  |  |  | QF-LDC-11
0:30 | 1110 | 4716 | 3475 | 8191 | Date: | 2023-01-25
1:00 | 1070 | 4564 | 3329 | 7893
1:30 | 1010 | 4424.5 | 3260 | 7684.5
2:00 | 950 | 4285 | 3191 | 7476
2:30 | 950 | 4232.5 | 3114.5 | 7347 | [5 empty] | Gen. at Eve. Peak | 10048 | 10048 MW (20:00 )
3:00 | 950 | 4180 | 3038 | 7218 | [6 empty] | 20:00
3:30 | 945 | 4253 | 2988.5 | 7241.5 | [5 empty] | Gen. at Day Peak | 9231 | 9231 MW (12:00 )
4:00 | 940 | 4326 | 2939 | 7265 | [6 empty] | 12:00
4:30 | 945 | 4211.5 | 2919 | 7130.5 | [5 empty] | Highest Generation | 10048
5:00 | 950 | 4097 | 2899 | 6996 | [6 empty] | 20:00
5:30 | 910 | 4213.5 | 2913.5 | 7127
6:00 | 870 | 4330 | 2928 | 7258
6:30 | 860 | 4525.5 | 3180 | 7705.5
7:00 | 850 | 4721 | 3432 | 8153
7:30 | 895 | 4742.5 | 3523.5 | 8266
8:00 | 940 | 4764 | 3615 | 8379
8:30 | 917.5 | 4718 | 3666.5 | 8384.5
9:00 | 895 | 4672 | 3718 | 8390
9:30 | 980 | 4751.5 | 3679 | 8430.5
10:00 | 1065 | 4831 | 3640 | 8471
10:30 | 1159.5 | 4907 | 3748.5 | 8655.5
11:00 | 1254 | 4983 | 3857 | 8840
11:30 | 1205.5 | 5053 | 3982.5 | 9035.5
12:00 | 1157 | 5123 | 4108 | 9231
12:30 | 1157 | 5113.5 | 4083.5 | 9197
13:00 | 1157 | 5104 | 4059 | 9163
13:30 | 1170.5 | 5126 | 4010.5 | 9136.5
14:00 | 1184 | 5148 | 3962 | 9110
14:30 | 1103.5 | 5071 | 3880 | 8951
15:00 | 1023 | 4994 | 3798 | 8792
15:30 | 1006.5 | 5004 | 3671 | 8675
16:00 | 990 | 5014 | 3544 | 8558
16:30 | 961 | 5056 | 3579.5 | 8635.5
17:00 | 932 | 5098 | 3615 | 8713
17:30 | 981 | 5292 | 3853 | 9145
18:00 | 1030 | 5486 | 4091 | 9577
18:30 | 1013 | 5568.5 | 4220.5 | 9789
19:00 | 996 | 5651 | 4350 | 10001
19:30 | 870 | 5670 | 4374 | 10044
20:00 | 880 | 5669 | 4379 | 10048 |  |  |  | Executive Engineer
20:30 | 1005 | 5591 | 4321 | 9912 |  |  |  | Network Operation Division
21:00 | 1130 | 5513 | 4263 | 9776
21:30 | 1125 | 5422 | 4172 | 9594
22:00 | 1120 | 5331 | 4081 | 9412 |  |  |  |  | Page 6 of 7
22:30 | 1140 | 5250 | 3916 | 9166
23:00 | 1160 | 5169 | 3751 | 8920
23:30 | 1155 | 5018.5 | 3686 | 8704.5
24:00 | 1150 | 4868 | 3621 | 8489
10048 MW (20:00 )
9231 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-01-25 |  | Energy |  | 208206187
[13 empty] | 2023-01-25 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3316 | 895 | 1433 | 0 | 1065 | 1574 | 30 | 0 | 78 | 98 | 0 | 0
0:30 | 3347.5 | 831 | 1525.5 | 0 | 823 | 1498 | 30 | 0 | 39 | 97 | 0 | 0 | Date: | 2023-01-25
1:00 | 3379 | 767 | 1618 | 0 | 581 | 1422 | 30 | 0 | 0 | 96 | 0 | 0
1:30 | 3380 | 766.5 | 1565 | 0 | 465.5 | 1384.5 | 30 | 0 | 0 | 93 | 0 | 0 | [7 empty] | Total Energy | 208.2062 | Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
2:00 | 3381 | 766 | 1512 | 0 | 350 | 1347 | 30 | 0 | 0 | 90 | 0 | 0 | [7 empty] | Energy not Served | 4.9506
2:30 | 3370.5 | 766 | 1465 | 0 | 332.5 | 1298 | 30 | 0 | 0 | 85 | 0 | 0 | [7 empty] | Energy Requirement | 213.1568
3:00 | 3360 | 766 | 1418 | 0 | 315 | 1249 | 30 | 0 | 0 | 80 | 0 | 0
3:30 | 3410 | 766 | 1412 | 0 | 320 | 1224.5 | 30 | 0 | 0 | 79 | 0 | 0 | [5 empty] | Shortage
4:00 | 3460 | 766 | 1406 | 0 | 325 | 1200 | 30 | 0 | 0 | 78 | 0 | 0
4:30 | 3331.5 | 766 | 1400.5 | 0 | 325 | 1199.5 | 30 | 0 | 0 | 78 | 0 | 0
5:00 | 3203 | 766 | 1395 | 0 | 325 | 1199 | 30 | 0 | 0 | 78 | 0 | 0
5:30 | 3217 | 766.5 | 1418.5 | 0 | 407 | 1199 | 30 | 0 | 4 | 85 | 0 | 0
6:00 | 3231 | 767 | 1442 | 0 | 489 | 1199 | 30 | 0 | 8 | 92 | 0 | 0
6:30 | 3255.5 | 837 | 1558 | 0 | 682 | 1233.5 | 30 | 0 | 15.5 | 92 | 2 | 54.8337 |  |  |  | Coal
7:00 | 3280 | 907 | 1674 | 0 | 875 | 1268 | 30 | 0 | 23 | 92 | 4 | 109.6674
7:30 | 3264.5 | 872.5 | 1683 | 0 | 936 | 1324 | 30 | 0 | 31.5 | 94 | 30.5 | 254.8155 |  |  | Oil |  |  |  | ,
8:00 | 3249 | 838 | 1692 | 0 | 997 | 1380 | 30 | 0 | 40 | 96 | 57 | 399.9636
8:30 | 3164.5 | 838 | 1656.5 | 0 | 1031.5 | 1415 | 30 | 0 | 48.5 | 105 | 95.5 | 534.9743
9:00 | 3080 | 838 | 1621 | 0 | 1066 | 1450 | 30 | 0 | 57 | 114 | 134 | 669.985
9:30 | 3098 | 838 | 1562.5 | 0 | 1096.5 | 1441 | 30 | 0 | 75 | 115 | 174.5 | 640.0338
10:00 | 3116 | 838 | 1504 | 0 | 1127 | 1432 | 30 | 0 | 93 | 116 | 215 | 610.0827
10:30 | 3114.5 | 838 | 1554.5 | 0 | 1197 | 1418.5 | 30 | 0 | 148 | 113 | 242 | 472.768
11:00 | 3113 | 838 | 1605 | 0 | 1267 | 1405 | 30 | 0 | 203 | 110 | 269 | 335.4533
11:30 | 3124.5 | 871 | 1604.5 | 0 | 1325.5 | 1370.5 | 30 | 75 | 238 | 117 | 279.5 | 322.5513
12:00 | 3136 | 904 | 1604 | 0 | 1384 | 1336 | 30 | 150 | 273 | 124 | 290 | 309.6492
12:30 | 3101 | 904 | 1631.5 | 0 | 1374 | 1270.5 | 30 | 204 | 274 | 121 | 287 | 219.3349
13:00 | 3066 | 904 | 1659 | 0 | 1364 | 1205 | 30 | 258 | 275 | 118 | 284 | 129.0205
13:30 | 3066 | 904 | 1659 | 0 | 1364 | 1205 | 30 | 258 | 275 | 118 | 284 | 129.0205
14:00 | 3066 | 904 | 1659 | 0 | 1364 | 1205 | 30 | 258 | 275 | 118 | 284 | 129.0205
14:30 | 3019.5 | 904 | 1602 | 0 | 1326.5 | 1203.5 | 30 | 251.5 | 295 | 118 | 227.5 | 206.4328
15:00 | 2973 | 904 | 1545 | 0 | 1289 | 1202 | 30 | 245 | 315 | 118 | 171 | 283.8451
15:30 | 2994.5 | 904 | 1460.5 | 0 | 1317.5 | 1152 | 30 | 252 | 317.5 | 118 | 129 | 299.5119
16:00 | 3016 | 904 | 1376 | 0 | 1346 | 1102 | 30 | 259 | 320 | 118 | 87 | 315.1787
16:30 | 3025.5 | 904.5 | 1346.5 | 0 | 1425 | 1131 | 30 | 257 | 344.5 | 119 | 52.5 | 280.6196
17:00 | 3035 | 905 | 1317 | 0 | 1504 | 1160 | 30 | 255 | 369 | 120 | 18 | 246.0605
17:30 | 3127.5 | 904.5 | 1315 | 10 | 1758.5 | 1217 | 30 | 257.5 | 394 | 122 | 9 | 272.0303
18:00 | 3220 | 904 | 1313 | 20 | 2013 | 1274 | 30 | 260 | 419 | 124 | 0 | 298
18:30 | 3227 | 882 | 1362.5 | 15 | 2060.5 | 1382 | 30 | 267 | 440 | 123 | 0 | 333
19:00 | 3234 | 860 | 1412 | 10 | 2108 | 1490 | 30 | 274 | 461 | 122 | 0 | 368
19:30 | 3264 | 859 | 1378 | 10 | 2121 | 1574 | 30 | 274 | 414 | 120 | 0 | 316.5
20:00 | 3296 | 859 | 1354 | 10 | 2128 | 1571 | 30 | 273 | 413 | 114 | 0 | 265
20:30 | 3297 | 882.5 | 1373 | 55 | 2036.5 | 1572.5 | 30 | 136.5 | 414 | 115 | 0 | 305
21:00 | 3298 | 906 | 1392 | 100 | 1945 | 1574 | 30 | 0 | 415 | 116 | 0 | 345
21:30 | 3295.5 | 906.5 | 1388.5 | 55 | 1901 | 1574 | 30 | 0 | 331.5 | 112 | 0 | 265.5
22:00 | 3293 | 907 | 1385 | 10 | 1857 | 1574 | 30 | 0 | 248 | 108 | 0 | 186
22:30 | 3300.5 | 906.5 | 1408 | 5 | 1632.5 | 1574 | 30 | 0 | 203.5 | 106 | 0 | 171.5
23:00 | 3308 | 906 | 1431 | 0 | 1408 | 1574 | 30 | 0 | 159 | 104 | 0 | 157
23:30 | 3312 | 900.5 | 1432 | 0 | 1236.5 | 1574 | 30 | 0 | 118.5 | 101 | 0 | 78.5 | Max Temp. in Dhaka |  | 28.5° C
24:00 | 3316 | 895 | 1433 | 0 | 1065 | 1574 | 30 | 0 | 78 | 98 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-01-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 733680
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [5 empty] | 2 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 214376
| Teknaf 20MW PP (Solartech) | [6 empty] | 1 | 6 | 13 | 17 | 20 | 20 | 20 | 17 | 13 | 7 | 1 | [9 empty] | 136350
6 | Sikalbaha 225MW CCPP (Gas) | 233 | 233 | 232 | 230 | 234 | 235 | 238 | 232 | 234 | 234 | 233 | 226 | 217 | 150 | 149 | 150 | 149 | 149 |  | 149 | 154 | 154 | 153 | 152 | 153 | 154 | 4705917
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [5 empty] | 0 | 0 |  |  |  | 0 | 51 | 51 | 67 | 67 | 67 | 67 | 67 |  | 68 | 68 | 68 | 68 | 68 | 68 | 0 | 784428
12 | Hathazari 100 MW peaking PP | [6 empty] | 7 | 24 | 32 | 25 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 31 | 31 | 31 | 23 | 23 | 23 | 490944
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 48 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 34 | 34 | 38 | 48 | 51 | 51 | 66 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1305563
| Daudkandi 200 MW PP (B.Trac) | [17 empty] | 20 |  | 10 | 10 | 10 | 100 | 10 |  |  | 214656
14 | Titas 50 MW Peaking PP | [8 empty] | 9 | 20 | 29 | 29 | 28 | 26 | 18 | 18 | 24 | 18 |  | 20 | 19 | 19 | 19 | 19 | 20 | 7 | 331840
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | [5 empty] | 5 | 32 | 32 | 32 | 43 | 98 | 107 | 114 | 114 | 114 | 112 | 112 | 112 |  | 115 | 115 | 115 | 115 | 115 | 65 | 32 | 1595782
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 190 | 150 | 150 | 150 | 150 | 210 | 210 | 205 | 210 | 210 | 210 | 210 | 210 | 120 | 120 | 120 | 155 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4521000
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 278208
33 | Ashuganj 225 MW CCPP | 200 | 203 | 211 | 205 | 201 | 194 | 203 | 181 | 193 | 204 | 199 | 194 | 190 | 211 | 216 | 220 | 182 | 219 |  | 222 | 222 | 222 | 221 | 218 | 182 | 182 | 4913000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 320 | 320 | 335 | 355 | 360 | 290 | 290 | 285 | 315 | 285 | 330 | 290 | 290 | 290 | 335 |  | 290 | 295 | 285 | 290 | 290 | 290 | 290 | 7688300
| Ashuganj 420 MW CCPP(East) | 307 | 307 | 320 | 320 | 307 | 298 | 320 | 287 | 277 | 305 | 316 | 316 | 287 | 297 | 287 | 298 | 298 | 327 |  | 327 | 327 | 327 | 317 | 317 | 340 | 340 | 7399900
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 336000
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 347 | 345 | 345 | 345 | 346 | 348 | 352 | 347 | 344 | 334 | 331 | 331 | 340 | 345 | 346 | 345 | 344 | 341 |  | 337 | 336 | 336 | 336 | 338 | 350 | 353 | 8359940
40 | Meghnaghat 450 MW CCPP(MPL)
41 | Haripur 360MW CCPP(HPL) | 201 | 186 | 196 | 199 | 196 | 193 | 192 | 193 | 176 | 175 | 173 | 173 | 197 | 196 | 183 | 190 | 186 | 193 |  | 192 | 191 | 182 | 182 | 182 | 193 | 196 | 4538000
42 | RPCL 210MW CCPP | 69 | 85 | 85 | 84 | 83 | 83 | 45 | 45 | 45 | 45 | 44 | 35 | 32 | 35 | 35 | 35 | 35 | 35 |  | 55 | 76 | 104 | 105 | 106 | 106 | 106 | 1430400
43 | Sutiakhali 50 MW Solar PP
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 303 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 986520
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 62 | 62 | 63 | 62 | 62 | 62 | 63 | 40 | 40 | 40 | 48 | 60 | 60 | 61 | 61 | 60 |  | 60 | 62 | 62 | 63 | 63 | 62 | 62 | 1405
48 | Shahjibazar 86MW PP (Shahjibazar) | 86 | 50 | 30 | 30 | 30 | 30 | 60 | 60 | 81 | 81 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | [5 empty] | 84 | 84 | 84 | 84 | 1453440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 157 | 157 | 156 | [11 empty] | 50 | 130 | 140 | 140 |  | 140 | 140 | 140 | 145 | 145 | 145 | 145 | 1602500
51 | Sylhet 20 MW GTPP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 440000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 243180
54 | Hobiganj 11MW PP Cofidence-E
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 14 | 14 | 14 | 14 | 14 | 48 | 48 | 48 | 48 | 48 | 48 | 51 | 51 | 48 | 11 | 14 | 19 |  | 51 | 51 | 51 | 11 | 11 | 11 | 11 | 736200
56 | Shahjahanulla 25 MW PP | [25 empty] | 0 | 0
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 280 | 280 | 310 | 320 | 320 | 330 | 290 | 270 | 290 | 280 | 320 | 290 | 315 | 275 | 290 | 280 |  | 310 | 275 | 260 | 285 | 270 | 290 | 290 | 7141500
| Bibiyana South 400 MW | 393 | 400 | 402 | 400 | 402 | 400 | 401 | 400 | 390 | 400 | 400 | 400 | 400 | 395 | 400 | 360 | 400 | 400 |  | 395 | 400 | 400 | 400 | 388 | 401 | 400 | 9554900
58 | Nababganj 55 MW PP (Southern power ) | 17 |  |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 388662
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 148320
60 | Barabkunda 22 MW PP (Regent)
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 445932
62 | Tangail 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 17 | 17 | 16 | 17 | 16 | 16 | 16 | 16 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 420624
63 | Impoprt (Tripura) | 96 | 90 | 80 | 78 | 78 | 92 | 92 | 96 | 114 | 116 | 110 | 124 | 118 | 128 | 118 | 118 | 120 | 124 |  | 122 | 120 | 114 | 116 | 108 | 104 | 98 | 2520000
64 | Malancha, Ctg. EPZ (United) | 17 | 20 | 31 | 40 | 40 | 40 | 40 | 10 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 3 | 5 | 6 | 3 | 7 | 13 | 13 | 296160
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 499212
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 177660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 28 | 16 | 16 | 16 | 13 | 13 | 8 | 8 | 8 | 14 | 14 | 13 |  | 16 | 16 | 21 | 21 | 25 | 30 | 33 | 515200
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 |  | 20 | 20 | 20 | 20 | 15 | 18 | 20 | 377400
69 | Summit Ashulia | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 | 29 | 28 | 29 | 27 | 25 | 27 | 26 | 27 | 17 |  | 28 | 28 | 28 | 27 | 27 | 21 | 21 | 618120
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 744480
72 | Rupganj 33 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 30 | 29 | 29 | 29 | 29 | 29 | 29 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 713200
73 | Ghorashal 108MW PP (Regent) | 76 | 76 | 32 | 32 | 32 | 74 | 74 | 74 | 74 | 74 | 69 | 74 | 74 | 74 | 68 | 70 | 70 | 70 |  | 74 | 76 | 76 | 76 | 75 | 75 | 75 | 1587000
| Feni Lanka Power | [6 empty] | 17 | 17 | 17 | 17 | 17 | 25 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 331740
| Chowmuhani 113 MW | [5 empty] | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 28 | 61 | 105 | 106 |  | 106 | 108 | 107 | 110 | 110 | 64 | 15 | 909720
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434880
77 | Siddhirganj 100 PP(Dutch Bangla) | [15 empty] | 2 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 |  | 0 | 48000
78 | Gazipur 52 MW PP | [6 empty] | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 8 | 0 | 305280
79 | Kodda 150MW PP | [5 empty] | 8 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 776160
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [5 empty] | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 151354
| Gazipur 100 MW PP | 17 |  |  |  |  | 4 | 30 | 34 | 34 | 70 | 70 | 70 | 50 | 34 | 34 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 34 | 889524
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | 0 | [9 empty] | 25078
| Jodiac Power | 17 |  |  |  |  | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 367029
| Karnaphuli Power Ltd. | 54 | 34 | 34 | 34 | 35 | 36 | 51 | 51 | 54 | 55 | 55 | 55 | 38 | 42 | 61 | 90 | 91 | 91 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1564830
82 | Madanganj 102 PP(Summit) | [20 empty] | 8 | 11 | 17 | 17 | 17 | 17 | 59703
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 142 | 138 | 137 | 135 | 137 | 141 | 138 | 138 | 140 | 138 | 138 |  | 140 | 138 | 138 | 140 | 140 | 140 | 140 | 3396975
87 | Meghnaghat 100 MW(IEL) | 8 | 9 | 9 | 9 | 8 | 9 | 9 | 8 | 9 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 20 | 11 |  | 9 | 9 | 9 | 8 | 8 | 9 | 8 | 209280
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 51 | 51 | 53 | 54 | 55 | 55 | 55 | 54 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 24 | 904320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 435480
92 | Fenchuganj 44MW (Energyprima) | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 50 | 50 | 50 | 47 | 47 | 46 | 46 | 46 | 10 | 10 | 15 |  | 47 | 48 | 49 | 10 | 10 | 10 | 10 | 707544
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 20 | 20 | 20 | 20 | 41 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1172893
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 48 |  | 48 | 48 | 48 | 48 | 48 | 24 | 24 | 604224
95 | Patenga 50MW PP (Baraka) | [6 empty] | 15 | 25 | 27 | 27 | 30 | 33 | 27 | 26 | 26 | 26 | 26 | 31 |  | 32 | 32 | 32 | 32 | 32 | 33 | 33 | 522240
96 | Chattogram 108 MW PP (ECPV) | [16 empty] | 7 | 12 |  | 12 | 12 |  |  |  |  | 0 | 36480
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 28 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 291499
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 35 | 35 |  | 0 | 448680
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 10800
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 265320
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 57 | 57 | 48 | 48 | 58 | 58 | 48 | 48 | 48 | 58 | 50 | 58 | 48 | 48 | 48 |  | 48 | 54 | 57 | 48 | 48 | 57 | 48 | 1226400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 53 | 53 | 54 | 27 | 17 | 18 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 23 | 796464
115 | Juldah 100 MW PP Unit-3 (Acorn) | [5 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 485760
116 | Chandpur 200MW (Desh energy) | 17 |  |  |  |  | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 353760
117 | Ashuganj 150MW PP (Midland) | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 5 |  | 6 | 6 | 6 | 6 | 6 | 5 | 6 | 157236
118 | Bibiyana-III 400 MW CCPP | 366 | 366 | 366 | 366 | 393 | 423 | 412 | 433 | 367 | 366 | 366 | 385 | 370 | 413 | 367 | 355 | 365 | 404 |  | 366 | 367 | 367 | 366 | 366 | 366 | 366 | 9090000
| Jamalpur 115 MW PP (United) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 38 | 38 | 38 |  | 47 | 47 | 47 | 47 | 47 | 47 | 28 | 801600
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 100 | 100 | 105 | 106 | 104 | 104 | 104 | 105 | 105 | 270 |  | 283 | 282 | 284 | 66 | 16 | 16 | 16 | 1972145
| Juldah unit-2 (Acorn) | [5 empty] | 18 | 25 | 25 | 25 | 25 | 25 | 25 | 18 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 459840
| Anlima Energy Ltd. | 107 | 34 | 34 | 34 | 34 | 37 | 85 | 107 | 75 | 68 | 68 | 75 | 105 | 116 | 114 | 116 | 75 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1811564
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 410040
| Spectra Solar Plant Ltd. | [6 empty] | 0 | 3 | 8 | 12 | 15 | 17 | 17 | 14 | 11 | 5 | 1 | [9 empty] | 101605
| Chandpur 115(Doreen) | 35 |  |  |  |  | 24 | 35 | 35 | 35 | 34 | 48 | 53 | 53 | 53 | 53 | 52 | 54 | 94 |  | 94 | 94 | 94 | 94 | 94 | 65 | 35 | 1156800
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432720
| Mirsharai 150 MW (Oil) | [12 empty] | 13 |  |  | 13 | 7 | [8 empty] | 0 | 35127
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 4564 | 4285 | 4180 | 4326 | 4097 | 4330 | 4721 | 4764 | 4672 | 4831 | 4983 | 5123 | 5104 | 5148 | 4994 | 5014 | 5098 | 5486 |  | 5651 | 5670 | 5669 | 5513 | 5331 | 5169 | 4868 | 117210447
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | [5 empty] | 0 | 0 |  |  |  | 0 | 16 | 0 |  |  | 16 | 32 | 32 |  | 32 | 16 | 16 | 16 | 16 |  | 0 | 164160
125 | Khulna 330 MW CCPP (GAS) | [10 empty] | 0
126 | Khulna 330 MW CCPP (OIL) | [11 empty] | 150 | 245 | 240 | 245 | 246 | 248 | 260 |  | 274 | 274 | 273 |  |  |  |  | 2126287
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 10 | 49 |  | 43 | 43 | 43 | 43 |  |  |  | 172320
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [20 empty] | 5 | 17 | 17 | 17 |  | 0 | 47040
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 1 | 13 | 32 | 51 | 64 | 68 | 66 | 55 | 39 | 18 | 5 | [9 empty] | 418320
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | [7 empty] | 17 | 17 | 17 | 17 | 35 | 35 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 108 | 108 | 25 | 0 | 519600
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 220 | 220 | 220 | 182 | 181 | 182 | 214 | 217 | 220 | 220 | 217 | 217 | 212 | 180 | 180 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 111 | 4195827
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [6 empty] | 9 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 282240
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 188 | 188 | 188 | 187 | 186 | 185 | 186 | 181 | 176 | 184 | 184 | 176 | 181 | 176 | 160 | 160 | 180 | 179 |  | 177 | 177 | 177 | 180 | 187 | 188 | 188 | 4420133
140 | Bhola 33 MW PP (Venture) | 21 | 20 | 20 | 19 | 19 | 20 | 20 | 19 | 18 | 17 | 14 | 20 | 21 | 18 | 17 | 17 | 17 | 22 |  | 25 | 25 | 22 | 25 | 25 | 24 | 22 | 480200
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [16 empty] | 8 | 8 |  | 8 | 8 | 8 | 8 |  |  | 0 | 39000
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 42 |  | 86 | 40 | 40 | 40 |  |  |  | 181376
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [5 empty] | 15 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 15 | 15 | 20 | 85 |  | 85 | 85 | 85 | 85 | 105 | 67 | 60 | 1124352
146 | Bheramara HVDC | 767 | 766 | 766 | 766 | 766 | 767 | 907 | 838 | 838 | 838 | 838 | 904 | 904 | 904 | 904 | 904 | 905 | 904 |  | 860 | 859 | 859 | 906 | 907 | 906 | 895 | 20637818
147 | Bheramara 410 MW CCPP
148 | Payra 1320 MW | 1090 | 1020 | 920 | 870 | 870 | 870 | 940 | 1060 | 1130 | 1110 | 1080 | 1010 | 880 | 880 | 880 | 780 | 840 | 940 |  | 1160 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 26585200
149
150 | Barapukuria TPP Unit-1 | 82 | 77 | 79 | 79 | 79 | 79 | 78 | 70 | 70 | 72 | 75 | 76 | 75 | 74 | 72 | 72 | 70 | 84 |  | 80 | 80 | 77 | 80 | 80 | 80 | 80 | 1826618
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 250 | 250 | 250 | 251 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6092200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [14 empty] | 25 | 25 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 |  |  | 245632
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 2 | 3 | 3 | 3 | 3 | 2 | 1 | 0 | [9 empty] | 20820
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 208 | 206 | 205 | 180 | 180 | 180 | 193 | 196 | 182 | 184 | 191 | 193 | 199 | 198 | 187 | 182 | 160 | 168 |  | 182 | 182 | 182 | 183 | 185 | 185 | 184 | 4782964
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 439 | 380 | 360 | 337 | 337 | 335 | 442 | 442 | 418 | 324 | 417 | 416 | 414 | 392 | 372 | 305 | 304 | 370 |  | 365 | 364 | 365 | 371 | 376 | 386 | 386 | 9138109
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [10 empty] | 4 | 4 | 5 | 5 | 6 | 7 | 10 | 6 |  | 7 | 7 | 10 | 12 |  |  |  | 82024
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 471120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 199206
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 8 | 8 | 34 | 50 |  | 50 | 50 | 50 | 50 |  |  |  | 528183
167 | Katakhali 50 MW Peaking PP | [9 empty] | 0 | 16 | 30 | 32 | 32 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 |  |  |  | 337911
168 | Santahar 50 MW Peaking PP | [9 empty] | 0 | 25 | 30 | 30 | 30 | 30 | 34 | 34 | 34 |  | 34 | 34 | 30 | 30 | 6 |  |  | 355971
169 | Natore 52 MW PP (Rajlanka) | [5 empty] | 5 | 8 | 8 | 8 | 8 | 0 | [6 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 76896
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 0 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 50 |  | 50 | 50 | 50 | 50 | 50 |  | 0 | 592280
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [9 empty] | 0 | 18 | 50 | 50 | 50 | 50 | 35 | 38 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 727968
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 95 |  | 95 | 95 | 95 | 95 | 95 | 35 | 35 | 820416
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | [5 empty] | 28 | 40 | 38 | 34 | 38 | 34 | 34 | 34 | 34 | 50 | 65 |  | 70 | 70 | 70 | 70 | 71 | 34 | 34 | 853632
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 4 | 2 | 0 | [9 empty] | 34309
178 | Energypac Power Venture Thakurgaon Ltd. | [5 empty] | 11 | 100 | 115 | 115 | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 20 | 95 |  | 113 | 112 | 112 | 113 | 112 | 114 | 37 | 1383168
| Intraco Solar 30 MW | [6 empty] | 0 | 5 | 10 | 21 | 27 | 29 | 28 | 24 | 16 | 9 | 2 | [9 empty] | 171970
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 2 | 28 | 65 | 105 | 130 | 142 | 139 | 117 | 83 | 43 | 9 | [9 empty] | 860470