## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-03-03 | Friday
|  | Date (day): | 2023-03-03 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10389.6 | MW |  |  | (b) At Evening Peak Hour : |  | 12700 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-03-02 | 2023-03-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 130 | 130 | 130 | 130 | 50 |  | Gas shortage
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 | 365 |  | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 402 | 367 | 370 | 370 | 42 |  | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 347 | 344 | 300 | 344 | 16 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 350 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 41 | 61 | 31 | 60 | 40 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint.
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 90 | 75 | 30 | 75 |  | 27 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 34 | 90 | 90 | 120 |  | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 40 | 47 | 33 | 50 | 50 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 58 | 40 | 58 | 44 |  | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 0 | 35 | 19 |  | Fuel shortage
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 98 | 32 | 98 | 51 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 17 | 55
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 31 | 48 | 51 |  | 29 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 26 | 30 | 30 |  |  | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 25 | 50 | 25 | 50
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 278 | 278 | 280 | 280 |  | 20 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 0 | 0 | 300 |  | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 149 | 140 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 52 | 88 | 52 | 88 |  | 17 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 18 | 19 | 46 | 58 |  | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 129 | 17 | 144 |  | 18 | Engine problem
39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
40 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 17 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6263 | 5847 | 2502 | 2776 | 2497 | 3015 | 2222 | 611
41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
42 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 17 | 25 | 17 | 25
43 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 20 | 0 | 20 | 0
44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 18 | 18 | 32 |  | Fuel shortage
45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 30 | 30 | 30 | 30 | 200 |  | Low Water Level
46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 220 | 200 | 220 | 220
47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 17 | 51 | 34 | 34 | 71 |  | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 38 | 58 | 50 | 60 |  | 38 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 85 | 17 | 85 |  | 17 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 33 | 33 | 33 | 33 |  | 67 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 88 | 100 | 88 | 100
53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 | 7 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 0 | 0 | 0 | 0
54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
56 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 121 | 257 | 120 | 260 | 40 |  | Fuel shortage
57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 36 | 17 | 36 | 18 |  | Fuel shortage
58 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 54 | 62 | 54 | 54 | 56 |  | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 107 | 96 | 107 | 107 |  | 9 | Engine problem
| Mirsharai 150 MW |  | Gas/HSD | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | 0 | 0 | 0
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 932 | 1166 | 945 | 1177 | 892 | 281
61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 190 | 218 | 190 | 220 |  |  | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 330 | 290 | 300 | 300 |  |  | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  | 360 | Macine problem
65 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 350 | 250 | 320 | 320 |  |  | FGMO
66 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 46 | 46 | 45 | 46
67 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 55 | 40 | 5 | 5 | 5 | 50 |  | Gas shortage
68 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
69 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
70 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 40 | 140 | 40 | 150
71 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 30 | 28 | 28 | 30 |  | 22 | Engine problem
72 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
73 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 34 | 92 | 34 | 200
74 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19 |  | 3 | Engine problem
75 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 9 | 9 | 9 |  | 2 | Engine problem
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 138 | 138 | 135 | 153
76 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
77 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 0 | 8 | 44 |  | Fuel shortage
78 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21 |  | 4 | Engine problem
79 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
80 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 80 | 17 | 80 | 34 |  | Fuel shortage
81 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 104 | 9 | 113
82 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | Engine problem
83 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 37 | 72 | 18 | 72 | 43 |  | Fuel shortage
| Cumilla Area Total |  |  |  |  | 3309 | 3285 | 1417 | 1629 | 1299 | 1855 | 692 | 591
84 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 44 | 55 | 70 | 100 | 102 |  | Gas shortage
85 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 19 | 19 | 19 |  |  | Gas shortage
86 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
87 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
88 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 68 | 116 | 68 | 115 | 85 |  | Fuel shortage
89 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 49 | 78 | 47 | 80 | 35 |  | Fuel shortage
90 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 45 | 0 | 50 | 0
91 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 228 | 274 | 261.6 | 320 | 102 | 0
92 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
93 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem
94 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 112 | 0 | 112 |  | 51 | Gas shortage & ST U/M.
95 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
96 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 42 | 30 | 50
97 | Fenchuganj 44MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 46 | 50 | 30 | 50
98 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 8 | 8 |  | 3 | Engine problem
99 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 32 | 32 | 32 |  | 32 | GT-8 Under maint.
100 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 89 | 86 | 86
101 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 214 | 210 | 215 | 215
103 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 19 | 19
104 | Sylhet 50MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Gas shortage
105 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 8 | 8 |  | 17 | Engine problem
106 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 325 | 290 | 300 | 300 |  |  | FGMO
107 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 402 | 367 | 366 | 367 |  |  | FGMO
108 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 8 | 8
109 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 370 | 400 | 400
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1668 | 1690 | 1588 | 1741 | 0 | 607
110 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 888 | 770 | 906 | 906
111 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 80 | 99 | 83 | 99 |  | 16 | Engine problem
112 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 38 | 0 | 38 |  | 16 | Engine problem
113 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 0 | 230 |  | Fuel shortage
114 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 32 | 0 | 75 |  | 34 | Engine problem
115 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 150 | 260 | 150 | 260 | 150 |  | Gas shortage
116 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 40 | 8 | 40 | 0
117 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
118 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 55 | 56 | 56 | 56 | 49 |  | Fuel shortage
119 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 0 | 0 | 0 | 50 |  |  | Line O/L
120 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 89 | 0 | 100 | 0
| Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0
| Khulna Area Total |  |  |  |  | 3005 | 3001 | 1270 | 1295 | 1303 | 1524 | 545 | 66
121 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 0 | 0 | 110 |  | Line O/L
122 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 15 | 19 | 14 | 20 |  | 20 | Engine problem
123 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 176 | 178 | 185 | 185
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
124 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 870 | 1090 | 700 | 1050 |  |  | Transformer and Line O/L
125 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 165 | 220 | 220
126 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 121 | 30 | 100 |  |  | Line O/L
127 | Barisal 307 MW |  | Coal | BCPCL | 307*1 | 307 | 307 | 151 | 179 | 150 | 200
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1432 | 1752 | 1299 | 1775 | 110 | 20
128 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
129 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 30 | 0 | 30 |  | 22 | Engine problem
130 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 20 | 20 | 18 | 20 |  | 51 | Engine problem
131 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
132 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 42 | 42 | 42 | 42 |  | 8 | Engine problem
133 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 30 | 40 | 32 | 40 |  | 10 | Engine problem
134 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
135 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
136 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 220 | 145 | 150 | 150 | 70 |  | Gas shortage
137 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 151 | 171 | 170 | 200 | 214 |  | Gas shortage
138 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 35 | 26 | 35 |  | 15 | Engine problem
139 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 21 | 22 | 22
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
140 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
141 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 8 | 8 | 8 | 44 |  | Fuel shortage
142 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 64 | 86 | 64 | 86 |  | 18 | Enging problem
143 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0 | 200 |  | Fuel shortage
144 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 70 | 50 | 90 | 23 |  | Fuel shortage
145 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 75 | 95 | 75 | 95 | 18 |  | Fuel shortage
146 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 0 | 0 | 0 | 0 | 0 |  | 0 |  |  | On test.
| Rajshahi Area Total |  |  |  |  | 2179 | 2129 | 691 | 774 | 674 | 829 | 1170 | 124
147 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
148 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 250 | 250 | 250 | 250 | 24 |  | Machine problem
149 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
150 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 20 |  | Fuel conservation
151 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 71 | 99 | 70 | 99 |  | 14 | Engine problem
152 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
153 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 37 | 113 | 35 | 115
154 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 25 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 111 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 499 | 462 | 523 | 464 | 149 | 99
| Total |  |  |  |  | 23482 | 22700 | 10639 | 11818 | 10389.6 | 12700 | 5882 | 2399
A. |  | 2023-03-02 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 11818 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
2 | Minimum Generation : |  |  | 8170 | MW at | 5:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11865 | MW
3 | Day peak Generation : |  |  | 10639 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11514.7 | MW
4 | Evening peak Generation : |  |  | 11818 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 43 | MW
5 | Total Energy Generation : |  | 244.4567 | MKWHr | By Solar | 2.1902 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Gas : | 133.394 | MKWHr |  | By Oil: | 46.6424 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 37.6902 | MKWHr |  | By Hydro: | 0.73032 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 5882 | MW | Dhaka | 4292.8 | 4292.8 |  | 0 |  | 18:00 |  | 77
|  |  | For Plants S/D or M/C prob = |  |  | 2399 | MW | Chittagong | 1091.6 | 1091.6 |  | 0 |  | 19:00 |  | 43.314
|  |  | Total = |  |  | 8281 | MW | Khulna | 1378 | 1378 |  | 0 |  | 19:30 |  | 39.6277
7 | Total Gas Supplied : |  |  | 1042.19 | MMCFD |  |  | Rajshahi | 1239.9 | 1239.9 |  | 0 |  | 20:00 |  | 23.0394
8 | Fuel Cost : | i) Gas : | Taka | 140764873.602 | ii) Oil : | Taka | 610962996.78 | Comilla | 1032 | 1032 |  | 0 |  | 21:00 |  | 15
|  | iii) Coal : | Taka | 253343812 | Total | Taka | 1005071682.382 | Mymensingh | 1004 | 961 |  | 43 |  | 22:00 |  | 14.7452
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 403 | 403 |  | 0 |  | 23:00 |  | 14.7452
| ii) During Peak Demand : |  |  | 260 | MW (E to W) at | 19:00 | hrs | Barisal | 300.4 | 300.4 |  | 0 |  | 24:00 |  | 0
| iii) Maximum : |  |  | 170 | MW at | 21:00 | hrs | Rangpur | 773 | 773 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 34.1° C |  |  | Total | 11514.7 | 11471.7 |  | 43
B. |  | 2023-03-03 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12700 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9900 | MW
4 | Reserve(Generation end) |  |  |  | 1700 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 227.5363 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8203 | MW at | 5:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.8269 | MKWHr. | ii) HVDC Flow at Peak Time |  | 770 | MW at | 19:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9827 | MKWHr. | iii) Maximum HVDC Flow : |  | 920 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.39 |  | (b) Today: | 79.27 |  | (c) Rule Curve: |  | 92.68
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-03-02 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 354 | 303 |  | 0 | 370 | 160 | 33 | 0 | 0 | 0 | 0 | 0 | 33 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 28 | 33 | 28 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 46 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 285 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 51 | 0 | 0 | 8 | 19 | 9 | 33 | 21 | 116 | 99 | 0 | 19 | 0 | 43 | 43 | 22 | 50 | 0 | 0 | 63 | 90 | 0 | 212 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 95 | 0 | 0 | 48 | 0 | 107 | 0 | 50 | 34 | 40 | 367 | 9 | 17 | 20 | 0 | 16 | 17 | 54 | 0 | 9 | 87 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 0 | 317 | 0 | 0 |  | 888 | 0 | 200 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 182 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 164 | 17 | 0 | 94 | 0 | 50 | 0 | 0 | 75 | 922 | 165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 |  | 5669 | 3563 | 9232 | 3797 | 888 | 1716 | 0 | 1192 | 1493 | 30 | 0 | 0 | 116 | 0 | 0 | 79.41
2:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 383 | 343 |  | 0 | 390 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 226 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 51 | 0 | 0 | 8 | 19 | 9 | 33 | 21 | 110 | 94 | 0 | 19 | 0 | 43 | 43 | 22 | 30 | 0 | 0 | 63 | 40 | 0 | 212 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 30 | 0 | 0 | 48 | 0 | 34 | 0 | 12 | 34 | 40 | 367 | 9 | 17 | 17 | 0 | 16 | 17 | 54 | 0 | 3 | 23 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 18 | 0 | 317 | 0 | 0 |  | 889 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 171 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 37 | 922 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 |  | 5334 | 3441 | 8775 | 3820 | 889 | 1774 | 0 | 659 | 1493 | 30 | 0 | 0 | 110 | 0 | 0 | 79.41
3:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 400 | 342 |  | 0 | 420 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 285 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 51 | 0 | 0 | 8 | 18 | 9 | 33 | 21 | 108 | 95 | 0 | 19 | 0 | 43 | 43 | 22 | 30 | 0 | 0 | 62 | 10 | 0 | 211 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 20 | 0 | 0 | 48 | 0 | 20 | 0 | 12 | 34 | 40 | 367 | 9 | 17 | 17 | 0 | 16 | 17 | 54 | 0 | 9 | 12 | 400 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 0 | 316 | 0 | 0 |  | 888 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 0 | 172 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 37 | 870 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 |  | 5220 | 3373 | 8593 | 3815 | 888 | 1743 | 0 | 568 | 1441 | 30 | 0 | 0 | 108 | 0 | 0 | 79.4
4:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 400 | 343 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 28 | 33 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 228 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 51 | 0 | 0 | 8 | 18 | 9 | 33 | 21 | 110 | 94 | 0 | 19 | 0 | 43 | 43 | 22 | 30 | 0 | 0 | 63 | 10 | 0 | 212 | 19 | 0 | 8 | 260 | 8 | 8 | 0 | 15 | 0 | 0 | 48 | 0 | 17 | 0 | 12 | 34 | 41 | 367 | 9 | 17 | 17 | 0 | 16 | 17 | 54 | 0 | 9 | 12 | 400 | 16 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 0 | 317 | 0 | 0 |  | 889 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 810 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371 | 0 | 0 | 0 | 0 |  | 5108 | 3228 | 8336 | 3810 | 889 | 1628 | 0 | 488 | 1381 | 30 | 0 | 0 | 110 | 0 | 0 | 79.4
5:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 369 | 303 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 28 | 33 | 31 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 15 | 2 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 10 | 0 | 0 | 8 | 18 | 9 | 33 | 21 | 106 | 95 | 0 | 19 | 0 | 43 | 43 | 11 | 10 | 0 | 0 | 52 | 10 | 0 | 212 | 19 | 0 | 8 | 270 | 8 | 8 | 0 | 15 | 0 | 0 | 48 | 0 | 17 | 0 | 12 | 34 | 40 | 367 | 9 | 17 | 17 | 0 | 16 | 17 | 54 | 0 | 9 | 12 | 360 | 17 | 0 | 17 | 51 | 0 | 17 | 0 | 18 | 0 | 316 | 0 | 0 |  | 890 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 0 | 0 | 0 |  | 4922 | 3248 | 8170 | 3771 | 890 | 1523 | 0 | 488 | 1362 | 30 | 0 | 0 | 106 | 0 | 0 | 79.39
6:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 361 | 302 |  | 0 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 8 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 23 | 28 | 33 | 32 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 10 | 0 | 19 | 15 | 5 | 0 | 0 | 0 | 290 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 10 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 100 | 95 | 0 | 19 | 0 | 43 | 43 | 11 | 10 | 0 | 0 | 52 | 10 | 0 | 212 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 15 | 0 | 0 | 48 | 0 | 19 | 0 | 12 | 34 | 40 | 396 | 9 | 17 | 17 | 0 | 16 | 17 | 55 | 17 | 9 | 12 | 360 | 16 | 0 | 17 | 63 | 0 | 17 | 0 | 18 | 0 | 323 | 0 | 0 |  | 889 | 0 | 165 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 40 | 188 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 164 | 0 | 0 | 3 | 0 | 33 | 0 | 0 | 75 | 790 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 55 | 0 | 0 |  | 5025 | 3523 | 8548 | 3814 | 889 | 1542 | 0 | 696 | 1467 | 30 | 0 | 10 | 100 | 0 | 0 | 79.39
7:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 390 | 343 |  | 0 | 450 | 0 | 5 | 25 | 15 | 0 | 0 | 0 | 15 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 23 | 8 | 33 | 30 | 9 | 0 | 30 | 0 | 0 | 0 | 4 | 227 | 0 | 0 | 0 |  | 6 | 0 | 0 | 33 | 0 | 19 | 15 | 5 | 0 | 0 | 0 | 305 | 0 | 183 | 8 | 0 | 47 | 15 | 0 | 25 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 100 | 46 | 0 | 19 | 0 | 43 | 43 | 31 | 30 | 0 | 0 | 33 | 84 | 0 | 212 | 19 | 0 | 8 | 305 | 8 | 8 | 0 | 26 | 0 | 0 | 48 | 0 | 70 | 2 | 70 | 34 | 38 | 365 | 0 | 52 | 17 | 0 | 16 | 17 | 55 | 17 | 9 | 27 | 400 | 16 | 2 | 17 | 89 | 0 | 17 | 1 | 18 | 0 | 323 | 0 | 0 |  | 794 | 0 | 165 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 40 | 188 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 164 | 13 | 0 | 33 | 0 | 33 | 0 | 0 | 75 | 760 | 222 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 372 | 1 | 129 | 0 | 7 |  | 5507 | 3591 | 9098 | 3778 | 794 | 1726 | 0 | 1109 | 1511 | 30 | 0 | 32 | 100 | 18 | 110.589 | 79.38
8:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 400 | 283 |  | 0 | 450 | 0 | 30 | 75 | 55 | 0 | 0 | 0 | 33 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 19 | 23 | 8 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 227 | 0 | 0 | 0 |  | 6 | 8 | 0 | 44 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 192 | 8 | 0 | 47 | 15 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 116 | 46 | 0 | 11 | 1 | 43 | 43 | 31 | 30 | 0 | 0 | 33 | 50 | 0 | 213 | 19 | 0 | 8 | 265 | 8 | 8 | 0 | 64 | 0 | 0 | 49 | 0 | 126 | 8 | 100 | 34 | 30 | 373 | 9 | 52 | 17 | 2 | 16 | 17 | 55 | 17 | 9 | 98 | 350 | 16 | 12 | 17 | 96 | 0 | 17 | 8 | 18 | 0 | 280 | 0 | 0 |  | 794 | 0 | 165 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 40 | 185 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 165 | 36 | 0 | 35 | 0 | 49 | 0 | 1 | 75 | 710 | 165 | 0 | 0 | 1 | 26 | 0 | 0 | 0 | 372 | 6 | 153 | 0 | 35 |  | 5730 | 3640 | 9370 | 3684 | 794 | 1556 | 0 | 1587 | 1463 | 30 | 0 | 40 | 116 | 100 | 222.0996 | 79.38
9:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 289 |  | 0 | 450 | 0 | 33 | 80 | 55 | 0 | 0 | 0 | 33 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 23 | 8 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 229 | 0 | 0 | 0 |  | 6 | 40 | 0 | 44 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 275 | 0 | 184 | 8 | 0 | 47 | 15 | 0 | 51 | 0 | 26 | 0 | 18 | 9 | 33 | 21 | 114 | 34 | 0 | 11 | 1 | 43 | 43 | 31 | 40 | 0 | 0 | 32 | 84 | 0 | 212 | 19 | 0 | 8 | 280 | 8 | 5 | 0 | 173 | 0 | 0 | 49 | 0 | 135 | 14 | 100 | 34 | 40 | 367 | 9 | 52 | 17 | 3 | 16 | 17 | 54 | 17 | 9 | 100 | 400 | 17 | 25 | 17 | 107 | 0 | 17 | 16 | 17 | 0 | 315 | 0 | 0 |  | 794 | 0 | 165 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 185 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 23 | 0 | 0 | 5 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 166 | 40 | 0 | 45 | 0 | 42 | 0 | 2 | 75 | 710 | 165 | 0 | 0 | 2 | 52 | 0 | 0 | 0 | 373 | 13 | 150 | 0 | 57 |  | 6033 | 3714 | 9747 | 3726 | 794 | 1604 | 0 | 1690 | 1483 | 30 | 0 | 121 | 114 | 185 | 189.8445 | 79.37
10:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 378 | 319 |  | 0 | 450 | 0 | 32 | 85 | 55 | 0 | 0 | 0 | 33 | 41 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 23 | 8 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 228 | 0 | 0 | 0 |  | 6 | 40 | 15 | 44 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 295 | 0 | 184 | 8 | 0 | 46 | 30 | 0 | 51 | 0 | 29 | 0 | 15 | 9 | 33 | 21 | 124 | 35 | 0 | 11 | 2 | 43 | 43 | 31 | 40 | 0 | 0 | 32 | 84 | 0 | 216 | 19 | 0 | 8 | 295 | 8 | 5 | 0 | 278 | 0 | 0 | 49 | 0 | 137 | 0 | 88 | 34 | 41 | 367 | 30 | 52 | 17 | 4 | 16 | 17 | 54 | 17 | 9 | 100 | 370 | 17 | 36 | 17 | 107 | 0 | 17 | 23 | 18 | 0 | 315 | 0 | 0 |  | 888 | 0 | 150 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 24 | 181 | 13 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 42 | 23 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 150 | 55 | 0 | 50 | 0 | 56 | 0 | 3 | 75 | 690 | 165 | 0 | 0 | 3 | 72 | 13 | 0 | 0 | 373 | 19 | 151 | 0 | 82 |  | 6232 | 3846 | 10078 | 3673 | 888 | 1644 | 0 | 1868 | 1464 | 30 | 0 | 143 | 124 | 244 | 77.4123 | 79.37
11:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 396 | 338 |  | 0 | 450 | 0 | 43 | 85 | 55 | 0 | 0 | 0 | 40 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 22 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 219 | 0 | 0 | 0 |  | 2 | 40 | 51 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 295 | 0 | 216 | 8 | 0 | 46 | 30 | 0 | 51 | 0 | 29 | 0 | 15 | 9 | 33 | 21 | 134 | 44 | 0 | 11 | 2 | 43 | 43 | 31 | 46 | 0 | 0 | 30 | 84 | 0 | 214 | 19 | 0 | 8 | 280 | 8 | 5 | 0 | 278 | 0 | 0 | 68 | 0 | 149 | 19 | 88 | 34 | 40 | 401 | 47 | 52 | 17 | 4 | 116 | 17 | 54 | 17 | 8 | 100 | 390 | 17 | 43 | 17 | 107 | 0 | 17 | 28 | 19 | 0 | 349 | 0 | 0 |  | 888 | 0 | 150 | 0 | 81 | 0 | 0 | 0 | 0 | 0 | 24 | 177 | 13 | 0 | 0 | 0 | 0 | 0 | 13 | 50 | 0 | 42 | 24 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 150 | 55 | 0 | 50 | 0 | 62 | 0 | 4 | 75 | 680 | 165 | 0 | 0 | 4 | 84 | 35 | 0 | 0 | 0 | 24 | 152 | 0 | 82 |  | 6615 | 3565 | 10180 | 3798 | 888 | 1654 | 0 | 2061 | 1082 | 30 | 0 | 239 | 134 | 294 | 43.314 | 79.36
12:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 347 |  | 0 | 450 | 0 | 41 | 90 | 55 | 0 | 0 | 0 | 40 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 8 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 38 | 51 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 330 | 0 | 190 | 8 | 0 | 46 | 40 | 0 | 51 | 0 | 30 | 0 | 18 | 9 | 33 | 21 | 138 | 44 | 0 | 14 | 2 | 43 | 43 | 42 | 46 | 0 | 0 | 30 | 84 | 0 | 214 | 18 | 0 | 8 | 325 | 8 | 5 | 0 | 278 | 0 | 0 | 68 | 0 | 149 | 20 | 88 | 34 | 40 | 402 | 49 | 52 | 17 | 4 | 121 | 17 | 54 | 17 | 8 | 100 | 400 | 17 | 45 | 17 | 107 | 0 | 17 | 30 | 37 | 0 | 350 | 0 | 0 |  | 888 | 0 | 150 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 176 | 15 | 0 | 0 | 0 | 0 | 0 | 20 | 64 | 0 | 42 | 30 | 0 | 24 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 151 | 55 | 0 | 50 | 0 | 71 | 0 | 5 | 75 | 870 | 220 | 0 | 0 | 4 | 89 | 37 | 0 | 0 | 0 | 25 | 151 | 0 | 111 |  | 6747 | 3892 | 10639 | 3814 | 888 | 1787 | 0 | 2087 | 1271 | 30 | 0 | 289 | 138 | 335 | 154.8246 | 79.36
13:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 329 |  | 0 | 450 | 0 | 41 | 92 | 55 | 0 | 0 | 97 | 40 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 22 | 23 | 21 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 38 | 75 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 295 | 0 | 202 | 8 | 0 | 45 | 5 | 0 | 51 | 0 | 28 | 0 | 18 | 9 | 0 | 21 | 138 | 35 | 0 | 14 | 2 | 43 | 43 | 42 | 50 | 0 | 0 | 31 | 84 | 0 | 214 | 18 | 0 | 8 | 270 | 8 | 5 | 0 | 278 | 0 | 0 | 68 | 0 | 149 | 18 | 50 | 34 | 38 | 367 | 49 | 52 | 17 | 4 | 123 | 17 | 54 | 17 | 9 | 65 | 390 | 17 | 45 | 17 | 107 | 0 | 17 | 29 | 40 | 3 | 340 | 0 | 0 |  | 888 | 0 | 150 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 16 | 0 | 0 | 0 | 0 | 0 | 29 | 64 | 0 | 42 | 32 | 0 | 32 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 151 | 55 | 0 | 50 | 0 | 77 | 0 | 5 | 75 | 1092 | 220 | 0 | 0 | 3 | 86 | 37 | 0 | 0 | 0 | 24 | 150 | 0 | 110 |  | 6610 | 4101 | 10711 | 3819 | 888 | 1684 | 0 | 2004 | 1492 | 30 | 0 | 330 | 138 | 326 | 294.904 | 79.35
14:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 395 | 289 |  | 0 | 450 | 0 | 38 | 85 | 55 | 0 | 0 | 99 | 40 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 22 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 221 | 0 | 0 | 0 |  | 6 | 38 | 71 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 285 | 0 | 216 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 28 | 0 | 15 | 9 | 33 | 15 | 138 | 35 | 0 | 14 | 2 | 43 | 43 | 42 | 50 | 0 | 0 | 31 | 86 | 0 | 214 | 18 | 0 | 8 | 260 | 8 | 5 | 0 | 278 | 0 | 0 | 69 | 0 | 149 | 0 | 50 | 70 | 38 | 369 | 49 | 52 | 30 | 4 | 123 | 23 | 54 | 17 | 9 | 38 | 400 | 17 | 40 | 17 | 107 | 0 | 17 | 25 | 18 | 17 | 310 | 0 | 0 |  | 889 | 0 | 265 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 16 | 0 | 0 | 0 | 0 | 32 | 29 | 62 | 0 | 42 | 32 | 0 | 32 | 12 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 0 | 208 | 55 | 0 | 50 | 0 | 71 | 0 | 4 | 75 | 1102 | 220 | 0 | 23 | 4 | 79 | 37 | 0 | 0 | 0 | 22 | 150 | 0 | 95 |  | 6526 | 4322 | 10848 | 3920 | 889 | 1705 | 0 | 2033 | 1502 | 30 | 0 | 356 | 138 | 275 | 107.8243 | 79.36
15:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 370 | 255 |  | 0 | 450 | 0 | 41 | 80 | 55 | 0 | 0 | 95 | 43 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 10 | 0 | 23 | 22 | 33 | 28 | 25 | 0 | 50 | 0 | 0 | 0 | 21 | 218 | 0 | 0 | 0 |  | 6 | 22 | 75 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 214 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 28 | 0 | 16 | 9 | 0 | 15 | 134 | 34 | 0 | 17 | 1 | 42 | 43 | 42 | 46 | 10 | 0 | 30 | 86 | 0 | 212 | 18 | 0 | 7 | 285 | 8 | 5 | 0 | 278 | 0 | 0 | 68 | 0 | 149 | 14 | 50 | 100 | 38 | 367 | 49 | 52 | 34 | 3 | 123 | 36 | 58 | 34 | 9 | 38 | 396 | 17 | 29 | 17 | 107 | 0 | 17 | 20 | 18 | 17 | 312 | 0 | 0 |  | 888 | 0 | 290 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 16 | 0 | 0 | 0 | 0 | 32 | 24 | 62 | 0 | 42 | 24 | 8 | 28 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205 | 0 | 201 | 55 | 0 | 50 | 0 | 71 | 0 | 3 | 75 | 1050 | 220 | 0 | 36 | 2 | 58 | 37 | 0 | 0 | 0 | 17 | 151 | 0 | 69 |  | 6537 | 4234 | 10771 | 3870 | 888 | 1699 | 0 | 2136 | 1451 | 50 | 0 | 327 | 134 | 216 | 100.4517 | 79.34
16:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 371 | 284 |  | 0 | 450 | 0 | 46 | 65 | 55 | 0 | 0 | 90 | 53 | 58 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 23 | 22 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 22 | 75 | 33 | 0 | 4 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 216 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 28 | 0 | 17 | 9 | 33 | 21 | 130 | 44 | 0 | 17 | 1 | 43 | 43 | 42 | 45 | 80 | 0 | 31 | 89 | 0 | 212 | 18 | 0 | 7 | 270 | 8 | 5 | 0 | 210 | 0 | 0 | 68 | 0 | 115 | 9 | 50 | 100 | 38 | 369 | 58 | 52 | 40 | 1 | 123 | 36 | 58 | 70 | 9 | 38 | 370 | 17 | 15 | 17 | 107 | 0 | 17 | 12 | 21 | 17 | 310 | 0 | 0 |  | 887 | 0 | 275 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 15 | 0 | 0 | 0 | 0 | 32 | 26 | 62 | 0 | 8 | 24 | 8 | 28 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 192 | 56 | 0 | 60 | 0 | 71 | 0 | 2 | 75 | 990 | 220 | 0 | 54 | 1 | 37 | 37 | 0 | 0 | 0 | 10 | 150 | 0 | 38 |  | 6619 | 4073 | 10692 | 3892 | 887 | 1775 | 0 | 2117 | 1390 | 30 | 0 | 345 | 130 | 126 | 119.8048 | 79.34
17:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 371 | 294 |  | 0 | 450 | 0 | 50 | 34 | 55 | 0 | 0 | 57 | 53 | 58 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 23 | 0 | 33 | 28 | 45 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 40 | 72 | 33 | 0 | 12 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 216 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 31 | 0 | 18 | 9 | 33 | 21 | 108 | 44 | 0 | 19 | 0 | 43 | 43 | 42 | 45 | 80 | 0 | 31 | 30 | 0 | 213 | 18 | 0 | 7 | 280 | 8 | 8 | 0 | 210 | 0 | 0 | 68 | 0 | 100 | 3 | 50 | 68 | 40 | 368 | 58 | 52 | 51 | 0 | 123 | 36 | 63 | 70 | 9 | 38 | 370 | 17 | 5 | 17 | 68 | 0 | 17 | 4 | 36 | 17 | 310 | 0 | 0 |  | 889 | 0 | 270 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 172 | 14 | 0 | 0 | 0 | 0 | 32 | 25 | 62 | 0 | 0 | 24 | 8 | 28 | 17 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 185 | 56 | 0 | 70 | 0 | 85 | 0 | 1 | 50 | 960 | 171 | 0 | 119 | 0 | 12 | 37 | 0 | 0 | 0 | 3 | 151 | 0 | 12 |  | 6467 | 3976 | 10443 | 3813 | 889 | 1679 | 0 | 2161 | 1361 | 30 | 0 | 362 | 108 | 40 | 98.6085 | 79.33
18:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 365 | 294 |  | 0 | 350 | 0 | 56 | 48 | 55 | 0 | 0 | 37 | 46 | 58 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 50 | 22 | 23 | 8 | 33 | 26 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 200 | 0 | 0 | 0 |  | 6 | 46 | 84 | 33 | 0 | 13 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 161 | 8 | 0 | 46 | 5 | 0 | 51 | 0 | 28 | 3 | 19 | 9 | 33 | 21 | 138 | 45 | 0 | 19 | 0 | 43 | 43 | 42 | 49 | 80 | 0 | 20 | 30 | 0 | 214 | 18 | 0 | 8 | 260 | 8 | 8 | 0 | 238 | 0 | 0 | 69 | 0 | 106 | 0 | 65 | 68 | 82 | 343 | 58 | 88 | 51 | 0 | 257 | 36 | 75 | 70 | 50 | 48 | 320 | 18 | 0 | 31 | 68 | 0 | 17 | 0 | 57 | 17 | 250 | 0 | 0 |  | 770 | 0 | 265 | 0 | 98 | 0 | 0 | 0 | 20 | 20 | 40 | 181 | 16 | 0 | 0 | 0 | 0 | 31 | 25 | 82 | 0 | 8 | 40 | 8 | 34 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 176 | 56 | 0 | 70 | 0 | 98 | 0 | 0 | 70 | 950 | 174 | 0 | 150 | 0 | 0 | 107 | 0 | 0 | 0 | 0 | 151 | 0 | 0 |  | 6564 | 4052 | 10616 | 3536 | 770 | 1564 | 0 | 2769 | 1351 | 30 | 0 | 458 | 138 | 0 | 77 | 79.33
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 367 | 344 |  | 0 | 350 | 0 | 61 | 75 | 55 | 0 | 0 | 34 | 47 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 8 | 33 | 26 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 200 | 0 | 0 | 0 |  | 6 | 58 | 85 | 33 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 218 | 8 | 0 | 46 | 5 | 0 | 51 | 0 | 28 | 8 | 19 | 9 | 33 | 21 | 138 | 55 | 0 | 19 | 0 | 43 | 43 | 42 | 50 | 112 | 0 | 32 | 89 | 0 | 210 | 18 | 0 | 8 | 290 | 8 | 8 | 0 | 278 | 0 | 0 | 116 | 0 | 140 | 0 | 100 | 92 | 140 | 367 | 78 | 88 | 51 | 0 | 257 | 36 | 62 | 80 | 104 | 100 | 370 | 18 | 0 | 129 | 96 | 0 | 17 | 0 | 72 | 17 | 250 | 0 | 0 |  | 770 | 0 | 260 | 0 | 99 | 0 | 0 | 0 | 38 | 32 | 40 | 178 | 19 | 0 | 0 | 0 | 0 | 30 | 20 | 86 | 0 | 42 | 40 | 8 | 35 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 171 | 56 | 0 | 70 | 0 | 99 | 0 | 0 | 95 | 1090 | 165 | 0 | 121 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 179 | 0 | 0 |  | 7535 | 4283 | 11818 | 3691 | 770 | 1725 | 0 | 3395 | 1519 | 30 | 0 | 550 | 138 | 0 | 43.314 | 79.31
19:30 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 381 | 304 |  | 0 | 320 | 0 | 62 | 30 | 55 | 0 | 0 | 38 | 47 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 8 | 33 | 29 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 200 | 0 | 0 | 0 |  | 6 | 18 | 34 | 33 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 216 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 28 | 8 | 17 | 9 | 33 | 15 | 134 | 78 | 0 | 19 | 0 | 43 | 43 | 42 | 50 | 80 | 0 | 31 | 89 | 0 | 212 | 18 | 0 | 8 | 290 | 8 | 8 | 0 | 225 | 0 | 0 | 116 | 0 | 149 | 0 | 100 | 136 | 150 | 367 | 79 | 88 | 51 | 0 | 265 | 36 | 62 | 52 | 116 | 100 | 400 | 18 | 0 | 144 | 107 | 0 | 17 | 0 | 72 | 17 | 250 | 0 | 0 |  | 769 | 0 | 260 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 8 | 0 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 173 | 56 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 1220 | 175 | 0 | 121 | 0 | 0 | 74 | 0 | 0 | 0 | 0 | 219 | 0 | 0 |  | 7388 | 4226 | 11614 | 3779 | 769 | 1637 | 0 | 3333 | 1689 | 30 | 0 | 243 | 134 | 0 | 39.6277 | 0
20:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 386 | 345 |  | 0 | 380 | 0 | 61 | 30 | 15 | 0 | 0 | 38 | 47 | 16 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 27 | 33 | 30 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 223 | 0 | 0 | 0 |  | 6 | 0 | 0 | 33 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 295 | 0 | 216 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 0 | 8 | 17 | 9 | 33 | 21 | 132 | 100 | 0 | 19 | 0 | 43 | 43 | 42 | 50 | 80 | 0 | 31 | 89 | 0 | 211 | 18 | 0 | 8 | 290 | 8 | 8 | 0 | 45 | 0 | 0 | 118 | 0 | 149 | 0 | 100 | 136 | 150 | 367 | 79 | 88 | 51 | 0 | 266 | 36 | 69 | 17 | 114 | 100 | 400 | 18 | 0 | 144 | 107 | 0 | 17 | 0 | 72 | 17 | 317 | 0 | 0 |  | 802 | 0 | 255 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 183 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 170 | 56 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 1220 | 175 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 228 | 0 | 0 |  | 7264 | 4074 | 11338 | 3920 | 802 | 1735 | 0 | 2895 | 1698 | 30 | 0 | 126 | 132 | 0 | 23.0394 | 79.32
21:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 398 | 342 |  | 0 | 450 | 0 | 30 | 0 | 15 | 0 | 0 | 96 | 47 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 22 | 23 | 27 | 33 | 30 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 33 | 0 | 20 | 15 | 0 | 0 | 0 | 0 | 320 | 0 | 216 | 8 | 0 | 44 | 5 | 0 | 51 | 0 | 0 | 8 | 19 | 9 | 33 | 21 | 132 | 100 | 0 | 19 | 0 | 43 | 43 | 53 | 50 | 112 | 0 | 31 | 89 | 0 | 211 | 18 | 0 | 8 | 300 | 8 | 8 | 0 | 15 | 0 | 0 | 118 | 0 | 132 | 0 | 100 | 136 | 150 | 367 | 79 | 88 | 51 | 0 | 266 | 36 | 63 | 17 | 55 | 50 | 400 | 17 | 0 | 144 | 107 | 0 | 0 | 0 | 72 | 17 | 315 | 0 | 0 |  | 794 | 0 | 250 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 16 | 183 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 169 | 56 | 0 | 70 | 0 | 99 | 0 | 0 | 95 | 1244 | 222 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 229 | 0 | 0 |  | 7178 | 4035 | 11213 | 4008 | 794 | 1902 | 0 | 2498 | 1723 | 30 | 0 | 126 | 132 | 0 | 15 | 79.31
22:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 302 |  | 0 | 450 | 0 | 23 | 0 | 15 | 0 | 0 | 92 | 47 | 16 | 98 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 22 | 23 | 28 | 33 | 32 | 25 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 33 | 0 | 17 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 218 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 134 | 101 | 0 | 19 | 0 | 43 | 43 | 53 | 50 | 80 | 0 | 32 | 89 | 0 | 214 | 18 | 0 | 8 | 280 | 8 | 8 | 0 | 15 | 0 | 0 | 118 | 0 | 132 | 0 | 100 | 136 | 70 | 367 | 79 | 88 | 51 | 0 | 266 | 36 | 63 | 17 | 55 | 50 | 340 | 17 | 0 | 100 | 107 | 0 | 7 | 0 | 72 | 17 | 320 | 0 | 0 |  | 889 | 0 | 255 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 16 | 169 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 171 | 56 | 0 | 70 | 0 | 97 | 0 | 0 | 95 | 1240 | 212 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 229 | 0 | 0 |  | 6858 | 4077 | 10935 | 3947 | 889 | 1802 | 0 | 2288 | 1719 | 30 | 0 | 126 | 134 | 0 | 14.7452 | 79.31
23:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 374 | 301 |  | 0 | 450 | 0 | 24 | 0 | 15 | 0 | 0 | 97 | 47 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 22 | 23 | 28 | 33 | 32 | 25 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 33 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 218 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 18 | 9 | 33 | 21 | 138 | 101 | 0 | 19 | 0 | 0 | 0 | 53 | 50 | 112 | 0 | 32 | 89 | 0 | 214 | 19 | 0 | 8 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 59 | 0 | 108 | 0 | 100 | 136 | 40 | 367 | 59 | 88 | 51 | 0 | 70 | 36 | 72 | 17 | 26 | 50 | 400 | 18 | 0 | 56 | 107 | 0 | 17 | 0 | 62 | 17 | 320 | 0 | 0 |  | 920 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 163 | 56 | 0 | 70 | 0 | 70 | 0 | 0 | 95 | 1240 | 183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 0 | 0 |  | 6377 | 3930 | 10307 | 3907 | 920 | 1815 | 0 | 1766 | 1671 | 30 | 0 | 60 | 138 | 0 | 14.7452 | 79.3
24:00 | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 374 | 302 |  | 0 | 450 | 0 | 25 | 0 | 15 | 0 | 0 | 94 | 47 | 16 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 22 | 23 | 28 | 33 | 33 | 8 | 0 | 30 | 0 | 0 | 0 | 25 | 221 | 0 | 0 | 0 |  | 6 | 0 | 0 | 33 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 218 | 8 | 0 | 47 | 5 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 21 | 126 | 103 | 0 | 19 | 0 | 0 | 0 | 53 | 49 | 112 | 0 | 62 | 89 | 0 | 214 | 19 | 0 | 8 | 285 | 8 | 8 | 0 | 0 | 0 | 0 | 59 | 0 | 98 | 0 | 100 | 17 | 40 | 367 | 59 | 70 | 51 | 0 | 69 | 36 | 54 | 17 | 11 | 50 | 400 | 17 | 0 | 17 | 107 | 0 | 17 | 0 | 45 | 0 | 320 | 0 | 0 |  | 888 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 28 | 22 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 163 | 55 | 0 | 87 | 0 | 70 | 0 | 0 | 95 | 1180 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 0 | 229 | 0 | 0 |  | 6093 | 4049 | 10142 | 3918 | 888 | 1800 | 0 | 1494 | 1826 | 30 | 0 | 60 | 126 | 0 | 0 | 79.3
KWH | 0 | 0 | 3119094 | 4378500 | 0 | 0 | 0 | 9334780 | 7496000 |  | 0 | 9755500 | 493789 | 713280 | 891977 | 812250 | 0 | 0 | 948000 | 800640 | 621792 | 900000 | 0 | 0 | 0 | 0 | 157320 | 400456 | 383975 | 437004 | 541000 | 486000 | 835100 | 724400 | 584640 | 0 | 730320 | 0 | 0 | 0 | 381092 | 5234212 | 0 | 0 | 0 |  | 144240 | 411696 | 636282 | 738120 | 0 | 305280 | 355632 | 37440 | 0 | 0 | 0 | 7492300 | 0 | 4797000 | 200727 | 0 | 1089144 | 348960 | 0 | 1152826 | 0 | 314304 | 70944 | 414000 | 244080 | 786500 | 456360 | 2982720 | 1559040 | 0 | 384444 | 12200 | 941000 | 937200 | 842400 | 990144 | 891982 | 0 | 908448 | 1610880 | 0 | 5246160 | 433000 | 0 | 190080 | 6938500 | 193200 | 171552 | 0 | 3367198 | 0 | 0 | 1615200 | 0 | 2530368 | 103815 | 1613760 | 1588320 | 1344872 | 8916000 | 946800 | 1252800 | 766945 | 30121 | 2348509 | 646475 | 1441048 | 587100 | 610680 | 1362240 | 9169100 | 405120 | 297420 | 933120 | 2307109 | 0 | 426600 | 194545 | 828480 | 187560 | 7542300 | 0 | 0 |  | 20826909 | 0 | 5209056 | 0 | 1223040 | 0 | 0 | 0 | 40320 | 35200 | 320250 | 4380279 | 385700 | 0 | 0 | 0 | 0 | 181568 | 212171 | 561648 | 0 | 396601 | 272291 | 82114 | 352658 | 391680 | 0 | 252576 | 0 | 0 | 5692600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4796864 | 0 | 4096509 | 952320 | 0 | 1392768 | 0 | 1380192 | 0 | 33795 | 1630944 | 24775800 | 4857600 | 0 | 589200 | 28440 | 604080 | 640512 | 0 | 0 | 4210909 | 164940 | 3010900 | 0 | 720800 |  | 149753511 | 94703234 | 244456745 | 92713325 | 20826909 | 40680717 | 0 | 42724251 | 37690209 | 730320 | 0 | 3918138 | 2982720 | 2190156 | 0
Fuel Cost | 0 | 0 | 4553877.24 | 6523965 | 0 | 0 | 0 | 9801519 | 8095680 |  | 0 | 10633495 | 548105.79 | 7974470.4 | 11818695.25 | 10762312.5 | 0 | 0 | 1659000 | 11705356.8 | 8748613.44 | 14589000 | 0 | 0 | 0 | 0 | 2001110.4 | 5406156 | 5149104.75 | 327753 | 405750 | 0 | 0 | 0 | 9944726.4 | 0 | 197186.4 | 0 | 0 | 0 | 6230854.2 | 5443580.48 | 0 | 0 | 0 |  | 1882332 | 6867089.28 | 10829519.64 | 9972001.2 | 0 | 3532089.6 | 451652.64 | 124675.2 | 0 | 0 | 0 | 8316453 | 0 | 5564520 | 258937.83 | 0 | 1230732.72 | 519950.4 | 0 | 1925219.42 | 0 | 5428030.08 | 954196.8 | 567180 | 183060 | 1376375 | 342270 | 21415929.6 | 1699353.6 | 0 | 522843.84 | 194468 | 1289170 | 1237104 | 1465776 | 1712949.12 | 1025779.3 | 0 | 1762389.12 | 3672806.4 | 0 | 5298621.6 | 930950 | 0 | 376358.4 | 6938500 | 144900 | 130379.52 | 0 | 45962252.7 | 0 | 0 | 21772896 | 0 | 35045596.8 | 1213597.35 | 16654003.2 | 21696451.2 | 17846451.44 | 8202720 | 11513088 | 18115488 | 9701854.25 | 0 | 27571495.66 | 7040112.75 | 15318340.24 | 7966947 | 7871665.2 | 16047187.2 | 8435572 | 5246304 | 4297719 | 11841292.8 | 26254900.42 | 0 | 5571396 | 2324812.75 | 12402345.6 | 2470165.2 | 0 | 0 | 0 |  | 62480727 | 0 | 5834142.72 | 0 | 12731846.4 | 0 | 0 | 0 | 726163.2 | 633600 | 4601992.5 | 4905912.48 | 748258 | 0 | 0 | 0 | 0 | 3044895.36 | 3710870.79 | 8784174.72 | 0 | 6567712.56 | 4604440.81 | 1119213.82 | 5949340.46 | 810777.6 | 0 | 191200.032 | 0 | 0 | 30113854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5564362.24 | 0 | 4055543.91 | 12799180.8 | 0 | 16476445.44 | 0 | 17528438.4 | 0 | 373434.75 | 19799660.16 | 223229958 | 4954752 | 0 | 4360080 | 321656.4 | 7085858.4 | 9819048.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 621049530.12 | 483927541.912 | 1104977072.032 | 92897309.232 | 62480727 | 47867564.37 | 0 | 545795872.44 | 253343812 | 197186.4 | 0 | 65167124.34 | 21415929.6 | 15811546.65 | 0
Yesterday Day Peak | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 402 | 347 |  | 0 | 450 | 0 | 41 | 90 | 55 | 0 | 0 | 0 | 40 | 58 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 23 | 8 | 33 | 28 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 |  | 6 | 38 | 51 | 33 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 330 | 0 | 190 | 8 | 0 | 46 | 40 | 0 | 51 | 0 | 30 | 0 | 18 | 9 | 33 | 21 | 138 | 44 | 0 | 14 | 2 | 43 | 43 | 42 | 46 | 0 | 0 | 30 | 84 | 0 | 214 | 18 | 0 | 8 | 325 | 8 | 5 | 0 | 278 | 0 | 0 | 68 | 0 | 149 | 20 | 88 | 34 | 40 | 402 | 49 | 52 | 17 | 4 | 121 | 17 | 54 | 17 | 8 | 100 | 400 | 17 | 45 | 17 | 107 | 0 | 17 | 30 | 37 | 0 | 350 | 0 | 0 |  | 888 | 0 | 150 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 8 | 176 | 15 | 0 | 0 | 0 | 0 | 0 | 20 | 64 | 0 | 42 | 30 | 0 | 24 | 0 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 151 | 55 | 0 | 50 | 0 | 71 | 0 | 5 | 75 | 870 | 220 | 0 | 0 | 4 | 89 | 37 | 0 | 0 | 0 | 25 | 151 | 0 | 111 |  | 10639 | DayPeak
Yesterday Evening Peak | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 367 | 344 | 0 | 0 | 350 | 0 | 61 | 75 | 55 | 0 | 0 | 34 | 47 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 8 | 33 | 26 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 200 | 0 | 0 | 0 | 0 | 6 | 58 | 85 | 33 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 290 | 0 | 218 | 8 | 0 | 46 | 5 | 0 | 51 | 0 | 28 | 8 | 19 | 9 | 33 | 21 | 138 | 55 | 0 | 19 | 0 | 43 | 43 | 42 | 50 | 112 | 0 | 32 | 89 | 0 | 210 | 18 | 0 | 8 | 290 | 8 | 8 | 0 | 278 | 0 | 0 | 116 | 0 | 140 | 0 | 100 | 92 | 140 | 367 | 78 | 88 | 51 | 0 | 257 | 36 | 62 | 80 | 104 | 100 | 370 | 18 | 0 | 129 | 96 | 0 | 17 | 0 | 72 | 17 | 250 | 0 | 0 |  | 770 | 0 | 260 | 0 | 99 | 0 | 0 | 0 | 38 | 32 | 40 | 178 | 19 | 0 | 0 | 0 | 0 | 30 | 20 | 86 | 0 | 42 | 40 | 8 | 35 | 21 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 171 | 56 | 0 | 70 | 0 | 99 | 0 | 0 | 95 | 1090 | 165 | 0 | 121 | 0 | 0 | 113 | 0 | 0 | 0 | 0 | 179 | 0 | 0 |  | 11818 | EvPeak
Forecast for Evening | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 370 | 344 | 0 | 0 | 450 | 0 | 60 | 75 | 55 | 0 | 0 | 90 | 50 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 23 | 28 | 33 | 30 | 50 | 0 | 30 | 0 | 0 | 0 | 25 | 220 | 0 | 0 | 0 | 0 | 6 | 60 | 85 | 33 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 300 | 0 | 220 | 8 | 0 | 46 | 5 | 0 | 51 | 0 | 30 | 8 | 19 | 9 | 33 | 21 | 153 | 100 | 0 | 19 | 0 | 43 | 43 | 50 | 50 | 112 | 0 | 32 | 86 | 0 | 215 | 19 | 0 | 8 | 300 | 8 | 8 |  | 280 | 0 | 0 | 115 | 0 | 149 | 0 | 100 | 200 | 150 | 367 | 80 | 88 | 34 | 0 | 260 | 36 | 54 | 80 | 113 | 100 | 400 | 46 | 0 | 144 | 107 | 0 | 17 |  | 72 | 17 | 320 |  |  |  | 906 | 0 | 260 |  | 99 | 0 | 0 | 0 | 38 | 75 | 40 | 185 | 20 | 0 | 0 | 0 | 0 | 30 | 20 | 86 | 0 | 42 | 40 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 150 | 0 | 200 | 56 | 0 | 90 | 50 | 99 | 0 | 0 | 95 | 1050 | 220 |  | 100 |  |  | 115 | 0 |  | 0 |  | 200 | 0
Forecast for Day | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 370 | 300 | 0 | 0 | 450 | 0 | 31 | 30 | 55 | 0 | 0 | 90 | 33 | 40 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 22 | 23 | 25 | 33 | 30 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 220 | 0 | 0 | 0 | 0 | 6 | 50 | 17 | 33 | 0 | 18 | 15 | 0 | 0 | 0 | 0 | 300 | 0 | 190 | 8 | 0 | 45 | 5 | 0 | 51 | 0 | 28 | 0 | 19 | 9 | 33 | 21 | 135 | 70 | 0 | 19 | 1.6 | 43 | 43 | 30 | 30 | 0 | 0 | 32 | 86 | 0 | 215 | 19 | 0 | 8 | 300 | 8 | 8 | 0 | 280 | 0 | 0 | 68 | 0 | 149 | 20 | 88 | 34 | 40 | 366 | 47 | 52 | 34 | 5 | 120 | 17 | 54 | 17 | 9 | 100 | 400 | 19 | 50 | 17 | 107 | 0 | 17 | 30 | 18 | 17 | 320 |  |  |  | 906 | 0 | 150 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 185 | 14 | 0 | 0 | 0 | 0 | 0 | 18 | 64 | 0 | 42 | 32 | 8 | 26 | 22 | 0 | 11 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 0 | 170 | 56 | 0 | 50 | 0 | 70 | 0 | 8 | 75 | 700 | 220 |  | 30 | 6 | 100 | 35 | 0 |  | 0 | 30 | 150 |  | 130 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 130 | 180 | 0 | 0 | 0 | 353 | 252 | 0 | 0 | 450 | 0 | 34 | 0 | 55 | 0 | 0 | 92 | 32 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 23 | 25 | 33 | 33 | 25 | 0 | 30 | 0 | 0 | 0 | 17 | 227 | 0 | 0 | 0 | 0 | 6 | 32 | 0 | 22 | 0 | 19 | 15 | 0 | 0 | 0 | 0 | 310 | 0 | 183 | 8 | 0 | 44 | 12 | 0 | 51 | 0 | 0 | 0 | 19 | 9 | 33 | 15 | 100 | 51 | 0 | 17 | 1 | 0 | 0 | 0 | 0 | 80 | 0 | 32 | 10 | 0 | 217 | 19 | 0 | 8 | 290 | 8 | 8 | 0 | 65 | 0 | 0 | 47 | 0 | 91 | 7 | 38 | 17 | 41 | 352 | 9 | 52 | 34 | 1 | 16 | 17 | 54 | 17 | 19 | 50 | 385 | 18 | 13 | 17 | 107 | 0 | 17 | 8 | 17 | 0 | 350 | 0 | 0 | 0 | 795 | 0 | 255 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 18 | 0 | 11 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 0 | 180 | 35 | 0 | 50 | 0 | 49 | 0 | 0 | 57 | 620 | 220 | 0 | 0 | 1 | 24 | 0 | 0 | 0 | 372 | 6 | 150 | 0 | 30 | 0 |  |  |  | 133.394 | 20.8269 | 46.6424 | 37.6902 | 0.73032 | 2.9827 | 2.1902
244.4567
| Minimum Generation |  | 8170 | 5:00
| Highest Generation |  | 11818 | 19:00
| Day Peak Generation |  | 10639 | 12:00
| Evening Peak Generation |  | 11818 | 19:00
| HVDC Max Flow |  | 920 | 23:00
| HVDC EvPeak Flow |  | 770 | 19:00
| Load factor L.F |  | 86.19% | [161 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-03-03
Till now the maximum generation is : - |  |  |  | 14782 | 21:00 | Hrs on | 2022-04-16
The Summary of Yesterday's |  |  | 2023-03-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 10639 | MW Hour : | 12:00 | Min. Gen. at | 5:00 | 8203
Evening Peak Generation : |  |  | 11818 | MW Hour : | 19:00 | Available Max Generation : |  | 12700
E.P. Demand (at gen end) : |  |  | 11865 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 11000
Maximum Generation : |  |  | 11818 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1700
Total Gen. (MKWH) : |  |  | 244.4567 | System Load Factor : | 86.19% | Load Shed : |  | 0
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 170 | MW at | 21:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-03-03
Actual : |  | 79.27 | Ft.(MSL) , | Rule curve : | 92.68 | Ft.( MSL )
Gas Consumed : |  | Total = | 1042.19 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 140764873.602
: |  |  | Coal : | 253343812 | Oil : | 610962996.78 | Total : | 1005071682.382
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 0 | 0:00 | 4047.4117 |  |  | 0 | 0%
Chittagong Area |  | 0 | 0:00 | 1118.4033 |  |  | 0 | 0%
Khulna Area |  | 0 | 0:00 | 1469.8011 |  |  | 0 | 0%
Rajshahi Area |  | 0 | 0:00 | 1296.3347 |  |  | 0 | 0%
Cumilla Area |  | 0 | 0:00 | 1107.0207 |  |  | 0 | 0%
Mymensingh Area |  | 43 | 1032:00 | 909.6507 |  |  | 0 | 0%
Sylhet Area |  | 0 | 0:00 | 411.3395 |  |  | 0 | 0%
Barisal Area |  | 0 | 0:00 | 331.6075 |  |  | 0 | 0%
Rangpur Area |  | 0 | 0:00 | 718.2807 |  |  | 0 | 0%
Total |  | 43 |  | 11409.85 |  |  | 0
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Ashuganj-5
4) Baghabari-100 MW & 71 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar 330 MW
8) Sirajganj-1 & 2
9) Kushiara 163 MW ST
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:14 | Tangail 132/33kV S/S Tr-4 LT is restored.
08:43 | 12:43 | Cumilla(N)-Daudkandi 132 kV Ckt-1 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to to remove
wavetrap and from Daudkandi 132/33kV end Due to Maintenance work
08:58 | 17:36 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 LT Scheduled S/D Due to Maintenance work
08:59 | 17:35 | Aminbazar 400/230/132kV S/S 230/132kv Tr-02 HT Scheduled S/D Due to Maintenance work
09:17 | 17:29 | Hathazari 230/132/33kV S/S MT-02 HT Scheduled S/D Due to Annual maintenance
09:17 | 17:29 | Hathazari 230/132/33kV S/S MT-02 LT Scheduled S/D Due to Annual maintenance
09:52 |  | Kamrangichar-Zigatola 132 kV ckt-2 scheduled shutdown due to annual maintenance.
10:18 |  | Banani shifted to Rampura due to Tongi 230/132kV transformer O/L.
| 10:38 | Aminbazar-Mirpur 132kV Ckt-2 is restored.
10:58 |  | Rampal 1320 MW (BIFPCL) unit-1 tripped. | [5 empty] | 380.0MW load interrup
11:40 | 12:14 | Bakulia-Khulshi 132 kV Ckt-1 Tripped from Khulshi 132/33kV
end showing Dist. PRO Trip Fault Loop: Ic_N Fault
Location: 2.865 Km Ic=11.45 KA relays Due to Unknown
12:00 |  | Day peak gen: 10639 MW.
12:09 |  | Siddhirganj GT:Unit-1 was sync.
12:45 | 15:08 | Cumilla(N)-Daudkandi 132 kV Ckt-2 Scheduled S/D from Cumilla(N) 230/132/33kV end Due to To remove wave
trap. and from Daudkandi 132/33kVend.
13:01 | 14:24 | Kodda 132/33kV S/S Tr-3 (426T) LT Scheduled S/D Due to line DS work
| 13:52 | Siddhirganj 132/33kV S/S 120MW EGCB GT2 is restored.
14:48 |  | Kushiara 163MW GT was sync.
| 15:22 | Shahmirpur-Sikalbaha 132kV Ckt-2 is restored.
15:22 |  | Kamrangirchar-Zigatola ckt-2 was switched on.
| 17:05 | Bhandaria 132/33kV S/S Transformer-1 HT is restored.
| 17:06 | Bhandaria 132/33kV S/S Transformer-1 LT is restored.
| 17:30 | Niamatpur 132/33kV S/S 426T HT is restored.
| 17:35 | Niamatpur 132/33kV S/S 426T LT is restored.
18:08 |  | Bogura 400 kv GIS-Bogura 4 - 230kv ckt syn.
| 18:20 | Kabirpur -Kodda 132kV Ckt-1 is restored.
19:00 |  | Evening Peak Gen. 11818 MW
| 19:28 | Barapukuria-Bogura 230 kV Ckt-2 is restored.
19:28 |  | Bogura 400 kv GIS - Baropukuria - 230 kv ckt 2 syn.
23:21 |  | Rampal Unit-1 Sync
05:00 |  | Minimum Generation = 8,203MW
06:12 | 06:24 | Sreemongol 132/33kV S/S 132/33kv T-3 LT Tripped showing relays Due to 33KV vunobir feeder fault(O/C,E/F) | [5 empty] | 18.0MW load interrup
06:12 | 06:18 | Sreemongol 132/33kV S/S 132/33kv T-2 HT Tripped showing relays Due to for 33 kv vunibir feeder fault.
06:12 | 06:18 | Sreemongol 132/33kV S/S 132/33kv T-3 HT Tripped showing relays Due to 33KV vunobir fedder fault
06:45 |  | Coxsbazar 132/33kV S/S 415T-T2 HT Project Work S/D | [5 empty] | 20.0MW load interrup
07:25 |  | Niamatpur 132/33kV S/S 426T LT Scheduled S/D Due to Project work. | [5 empty] | 5.0MW load interrup
07:26 |  | Niamatpur 132/33kV S/S 426T HT Scheduled S/D Due to Project work.
07:29 |  | Aminbazar-Mirpur 132kV Ckt-1 Project Work S/D from Mirpur 132/33kV end Due to Line shifting work to ERS Tower
07:30 |  | Chowmuhani-Feni 132 kV Ckt-1 Project Work S/D from Feni 132/33kV end Due to ESPCN strengthing work.
07:34 |  | Chowmuhani-Feni 132 kV Ckt-2 Project Work S/D from Feni 132/33kV end Due to ESPCN Strengthen work.
07:37 |  | Bhandaria 132/33kV S/S Transformer-1 HT Project Work S/D Due to G2G project work
07:37 |  | Bhandaria 132/33kV S/S Transformer-1 LT Project Work S/D Due to G2G project work

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-03-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 130 | 3119094
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 367 | 9334780 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 344 | 7496000 | gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 350 | 9755500 | gas shortage
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 61 | 713280 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 493789 | FGMO
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 75 | 891977 | Fuel shortage
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 55 | 812250
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 0 | 0 | 0 | Contract Expired
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 437004
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 34 | 948000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 47 | 800640 | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 0 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 58 | 621792 | Fuel shortage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 157320 | Fuel shortage
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 900000 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 400456
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 383975
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 1027000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 835100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 26 | 724400 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 50 | 584640 | 0:00
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 278 | 3367198 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Fuel shortage
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 100 | 0 | 0 | Fuel shortage
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Fuel shortage
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 140 | 2530368 | Fuel shortage
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 88 | 1252800 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 18 | 405120 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 129 | 933120
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 194545
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 17 | 187560 | Fuel shortage
| Dhaka area Total |  |  |  | 5847 | 2776 | 53686208
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 381092
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 103815
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 305280 | Fuel shortage
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 30 | 730320 | Low water level
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 200 | 5234212
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 766945 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 58 | 411696 | Engine problem
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 636282 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 33 | 738120 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1613760
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 15 | 355632 | Gas shortage
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 0 | 37440
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 257 | 2348509 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 646475 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 62 | 1441048 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1362240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 96 | 2307109 | Engine problem
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 0 | 0 | 0 | On test.
| Chattogram area Total |  |  |  | 2382 | 1166 | 19450096
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 218 | 4797000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 290 | 7492300 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 250 | 7542300 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 46 | 1089144 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 55 | 5 | 348960 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1152826
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 1344872
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 28 | 314304 | Engine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200MW (Desh energy) |  | IPP | 12*18.4 | 200 | 92 | 1588320 | Fuel shortage
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 414000 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 9 | 244080 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 2982720
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 786500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 70944 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 21 | 456360 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Fuel shortage
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 80 | 587100 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 610680
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 426600 | Engine problem
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 72 | 828480 | Fuel shortage
| Cumilla Area Total |  |  |  | 3285 | 1629 | 33278217
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 55 | 1559040 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 384444 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12200
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 116 | 1615200 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 78 | 946800 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 297420
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 144240 | Engine problem
| Mymensingh Area Total |  |  |  | 614 | 274 | 4959344
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 941000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 937200 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 112 | 891982 | Sync. at 18:45 & ST U/M.
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 42 | 842400 | Engine problem
| Fenchuganj 44MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 50 | 990144
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 171552 | Engine problem
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 908448
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 89 | 1610880
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 210 | 5246160
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 433000
| Sylhet 50MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Gas shortage
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 193200 | Gas shortage
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 6938500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 8916000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 190080 | Engine problem
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 370 | 9169100
| Sylhet Area Total |  |  |  | 2427 | 1690 | 38379646
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 770 | 20826909
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 99 | 1223040 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 38 | 40320 | Line O/L
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Fuel conservation
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 32 | 35200 | Line O/L
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 5209056 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 40 | 320250 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Fuel shortage
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 56 | 952320 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 0 | 0 | Line O/L
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 604080
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 0 | 0 | 0 | On test.
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 4210909 | On test.
| Khulna Area Total |  |  |  | 3001 | 1295 | 33422084
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 19 | 385700 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 178 | 4380279
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1090 | 24775800
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 165 | 4857600
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 121 | 589200 | Line O/L
| Barisal 307 MW |  | BCPCL | 307*1 | 307 | 179 | 3010900 | Transformer O/L
| Barisal Area Total |  |  |  | 2265 | 1752 | 37999479
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 30 | 181568 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 212171 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 0 | 0 | 0 | Contract Expired
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 396601 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 272291 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 145 | 4796864 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 171 | 4096509 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 352658 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 391680
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252576
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 82114 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 86 | 561648 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel shortage
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 70 | 1392768 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1630944 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28440
| Adani Power Jharkhanda Ltd |  | Import | 0 | 0 | 0 | 0 | On test.
| Rajshahi Area Total |  |  |  | 2129 | 774 | 14648832
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 250 | 5692600 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 99 | 1380192 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 33795
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 113 | 640512
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 164940
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 720800
| Rangpur Area Total |  |  |  | 750 | 462 | 8632839
| Total |  |  |  | 22700 | 11818 | 244456745
| Eastern Grid Total |  |  |  | 14555 | 7535 | 149753511
| Western Grid Total |  |  |  | 8145 | 4283 | 94703234
| National Grid Total |  |  |  | 22700 | 11818 | 244456745
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-03-02
| (a) ENTIRE EASTERN GRID : |  | 7780.4 | MW | (b) ENTIRE WESTERN GRID : |  | 3691.3 | MW
| i) Dhaka area |  | 4292.8 | MW | i) Khulna area |  | 1378 | MW
| ii) Chittagong area |  | 1091.6 | MW | ii) Rajshahi area |  | 1239.9 | MW
| iii) Comilla area |  | 1032 | MW | iii) Barisal area |  | 300.4 | MW
| iv) Mymensingh area |  | 961 | MW | iv) Rangpur area |  | 773 | MW
| v) Sylhet area |  | 403 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 11471.7 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 11 | 21:00 | Chhatak | 22 | 20:00 | Kamrangirchar | 52 | 18:30 | Natore | 120 | 18:30 | Shitalakhya | 114 | 16:00
2 | AKSML | 10.9 | 23:00 | Chowmuhani | 160 | 18:30 | Kaptai | 3.5 | 18:00 | Nawabganj | 33.4 | 15:00 | Sholosohor | 27 | 15:00
3 | Aftabnagar | 31 | 19:00 | Chuadanga | 82 | 19:00 | Kazla | 84 | 13:00 | Netrakona | 107 | 21:00 | Shyampur | 166 | 00:00
4 | Agargaon | 69 | 13:00 | Coxsbazar | 95 | 20:00 | Keranigonj | 60 | 18:30 | New | 69 | 12:00 | Siddhirganj | 100 | 18:00
5 | Agrabad | 58 | 18:00 | Cumilla(N) | 124 | 18:30 | Khagrachori | 26 | 18:30 | Niamatpur | 95 | 19:00 | Sirajganj | 85 | 19:00
6 | Amnura | 57 | 19:00 | Cumilla(S) | 148 | 18:30 | Khulna | 83 | 19:00 | Noapara | 39 | 19:00 | Sonargaon | 98 | 00:00
7 | Ashuganj | 63 | 13:00 | Daudkandi | 105 | 19:00 | Khulshi | 142 | 15:00 | PHP | 9 | 22:00 | Sreemongol | 45 | 18:30
8 | BIPTC | N/A | N/A | Dhaka | 34 | 12:00 | Kishoreganj | 110 | 19:00 | Pabna | 86 | 18:30 | Srinagar | 32 | 19:00
9 | BSRM | 106 | 09:00 | Dhamrai | 102 | 15:00 | Kodda | 294 | 14:00 | Palashbari | 108 | 08:00 | Sunamganj | 35 | 18:00
10 | Bagerhat | 80 | 19:00 | Dhanmondi | 118 | 13:00 | Kulaura | 30 | 18:30 | Panchagarh | 51 | 18:30 | Sylhet | 105 | 18:30
11 | Bakulia | 82 | 18:30 | Dohazari | 88 | 21:00 | Kurigram | 64 | 18:30 | Patuakhali | 67 | 18:30 | TK | 18 | 00:00
12 | Banani | 38 | 14:00 | Faridpur | 117 | 19:00 | Kushtia | 112 | 19:00 | Payra | 12.4 | 18:30 | Tangail | 193 | 19:00
13 | Bangabhaban | 17 | 10:00 | Fatullah | 61 | 12:00 | Lalbag | 73 | 13:00 | Postogola | 35 | 13:00 | Thakurgaon | 73 | 19:00
14 | Barapukuria | 54 | 13:00 | Fenchuganj | 32 | 19:00 | Lalmonirhat | 39 | 07:00 | Purbachal | 16 | 12:00 | Tongi | 116 | 15:00
15 | Barguna | 12 | 00:00 | Feni | 100 | 18:30 | Madanganj | 30 | 11:00 | Purbasadipur | 109 | 18:30 | Ullon | 39 | 18:30
16 | Barishal | 79 | 18:30 | GPH | 86 | 06:00 | Madaripur | 78 | 19:00 | Rahanpur_I | 17 | 23:00 | Uttara | 68 | 13:00
17 | Barishal-230 | 64 | 18:30 | Ghorashal | 58 | 12:00 | Madartek | 60 | 21:00 | Rahim | 30 | 09:00 | UttaraNew | 16 | 11:00
18 | Baroaulia | 57 | 10:00 | Goalpara | 22 | 12:00 | Madunaghat | 46 | 18:30 | Rajbari | 52 | 19:00 | Zigatola | 65 | 13:00
19 | Baroirhat | 35 | 18:30 | Gollamari | 40 | 19:00 | Magura | 50 | 19:00 | Rajendrapur | 104 | 15:00
20 | Bashundhara | 132 | 19:00 | Gopalganj | 86 | 19:00 | Mahasthangarh | 58 | 18:30 | Rajshahi | 114 | 19:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 96 | 13:00 | Manikganj | 90 | 19:30 | Rajshahi-230 | 28 | 19:00
22 | Beanibazar | 45 | 18:30 | Halishahar | 88 | 12:00 | Maniknagar | 58 | 13:00 | Ramganj | 74 | 18:30
23 | Benapole | 64 | 19:00 | HaripurSBU | 144 | 15:00 | Matarbari | 35 | 19:00 | Rampur | 23 | 18:30
24 | Bhaluka | 106 | 07:00 | Hasnabad | 69 | 18:30 | Matuail | 60 | 12:00 | Rangamati | 12 | 18:30
25 | Bhandaria | 34 | 19:30 | Hathazari | 53 | 18:30 | Millgate | 72 | 16:00 | Rangpur | 116 | 19:00
26 | Bhangura | 34 | 19:00 | Ishurdi | 55 | 19:00 | Mirpur | 112 | 18:30 | Ruppur | 4.6 | 15:00
27 | Bheramara(GK) | 45 | 18:30 | Jaldhaka | 56 | 18:30 | Mirsorai | 3 | 10:00 | SSM | 0 | 00:00
28 | Bhulta | 239 | 23:00 | Jamalpur | 145 | 19:00 | Mithapukur | 32 | 07:00 | Saidpur | 105 | 11:00
29 | Bog-Sherpur | 66 | 19:00 | Jashore | 100 | 13:00 | Modern | 0 | 00:00 | Satkhira | 118 | 19:00
30 | Bogura | 126 | 19:00 | Jhenaidah | 106 | 18:30 | Mogbazar | 113 | 13:00 | Satmasjid | 71 | 13:00
31 | Borhanuddin | 36 | 21:00 | Joydebpur | 145 | 18:30 | Mongla | 22 | 09:00 | Savar | 170 | 14:00
32 | Brahmanbaria | 132 | 18:30 | Joypurhat | 60 | 19:30 | Motijheel | 30 | 13:00 | Shahjadpur | 95 | 10:00
33 | Cantonment | 114 | 19:00 | Juldah | 24 | 00:00 | Munshiganj | 89 | 21:00 | Shahjibazar | 94 | 19:00
34 | Chandpur | 44 | 19:30 | KSRM | 32 | 04:00 | Mymensingh | 204 | 18:30 | Shahmirpur | 30.9 | 16:00
35 | Chandraghona | 24 | 19:00 | Kabirpur | 266 | 11:00 | Naogaon | 108 | 19:00 | Shariatpur | 50 | 19:00
36 | Chapai | 55 | 07:00 | Kachua | 66 | 18:30 | Narail | 44 | 18:30 | Sherpur | 136 | 20:00
37 | Charsaidpur | 46.5 | 16:00 | Kallyanpur | 84 | 19:00 | Narinda | 62 | 13:00 | Shikalbaha | 27 | 16:00
38 | Chauddagram | 36 | 19:00 | Kalurghat | 30 | 16:00 | Narshingdi | 149 | 20:00 | Shikalbaha-230 | N/A | N/A
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-03-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 401 | 07:00 | 384 | 12:00 | Kaliakoir | 392 | 08:00 | 380 | 11:00
| Bhulta | 393 | 07:00 | 380 | 12:00 | Madunaghat_I | 418 | 19:30 | 396 | 04:00
| Bibiana | 405 | 05:00 | 397 | 15:00 | Payra | 414 | 00:00 | 406 | 23:00
| BIPTC | 401 | 03:00 | 391 | 13:00 | Rahanpur_I | 416 | 00:00 | 386 | 08:00
| Gopalganj | 417 | 00:00 | 387 | 12:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 232 | 06:00 | 222 | 12:00 | Hasnabad | 233 | 07:00 | 224 | 15:00
| AKSML | 243 | 18:00 | 219 | 12:00 | Hathazari | 242 | 19:00 | 232 | 11:00
| Aminbazar | 235 | 19:00 | 226 | 11:00 | Ishurdi | 236 | 18:00 | 224 | 12:00
| Ashuganj | 238 | 00:00 | 230 | 11:00 | Jhenaidah | 238 | 00:00 | 224 | 12:00
| Baghabari | 234 | 18:00 | 223 | 07:00 | Kaliakoir | 232 | 05:00 | 225 | 15:00
| Barapukuria | 223 | 00:00 | 205 | 07:00 | Keranigonj | 231 | 07:00 | 221 | 12:00
| Barishal | 238 | 04:00 | 233 | 12:00 | Khulna(S) | 241 | 18:00 | 228 | 13:00
| Bheramara | 234 | 00:00 | 227 | 14:00 | Madunaghat_I | 241 | 18:30 | 230 | 04:00
| Bhulta | 234 | 03:00 | 224 | 12:00 | Maniknagar | 232 | 04:00 | 221 | 12:00
| Bibiana | 239 | 05:00 | 234 | 10:00 | Meghnaghat | 240 | 00:00 | 230 | 11:00
| BIPTC | 237 | 00:00 | 223 | 12:00 | Mirsorai | 240 | 19:00 | 226 | 03:00
| Bogura | 232 | 04:00 | 215 | 07:00 | Rajshahi | 238 | 18:00 | 224 | 12:00
| Borhanuddin | 242 | 05:00 | 239 | 12:00 | Rampur | N/A | N/A | N/A | N/A
| BSRM | 239 | 18:00 | 228 | 02:00 | Rampura | 231 | 00:00 | 223 | 12:00
| Cumilla(N) | 235 | 19:00 | 226 | 12:00 | Shikalbaha | 242 | 18:30 | 228 | 02:00
| Fenchuganj | 242 | 18:30 | 236 | 12:00 | Shyampur | 232 | 07:00 | 223 | 15:00
| Ghorashal | N/A | N/A | N/A | N/A | Siddhirganj | 234 | 05:00 | 225 | 12:00
| GPH | 242 | 19:00 | 230 | 05:00 | Sirajgonj | 232 | 04:00 | 225 | 14:00
| Haripur | 231 | 00:00 | 224 | 11:00 | Tongi | 228 | 18:00 | 200 | 10:00
| 132 kV | KV |  | KV
| Aftabnagar | 134 | 00:00 | 127 | 12:00 | Lalbag | 134 | 05:00 | 126 | 12:00
| Agargaon | 135 | 07:00 | 127 | 12:00 | Lalmonirhat | 131 | 00:00 | 125 | 04:00
| Agrabad | 139 | 19:00 | 131 | 01:00 | Madanganj | 135 | 07:00 | 128 | 12:00
| AKS | 137 | 19:00 | 129 | 01:00 | Madaripur | 134 | 02:00 | 127 | 12:00
| Aminbazar | 135 | 19:00 | 127 | 11:00 | Madartek | 134 | 04:00 | 127 | 11:00
| Amnura | 134 | 18:00 | 121 | 08:00 | Madunaghat | 140 | 18:00 | 133 | 02:00
| Ashuganj | 138 | 04:00 | 132 | 15:00 | Magura | 135 | 03:00 | 126 | 14:00
| Bagerhat | 138 | 00:00 | 131 | 12:00 | Mahasthangarh | 134 | 00:00 | 120 | 07:00
| Bakulia | 139 | 19:00 | 131 | 05:00 | Manikganj | 137 | 01:00 | 118 | 11:00
| Banani | 134 | 22:00 | 127 | 10:00 | Maniknagar | 133 | 01:00 | 126 | 12:00
| Bangabhaban | 133 | 07:00 | 126 | 12:00 | Matarbari | 130 | 13:00 | 123 | 01:00
| Barapukuria | 136 | 00:00 | 122 | 07:00 | Matuail | 135 | 19:00 | 129 | 12:00
| Barguna | 137 | 17:00 | 126 | 00:00 | Millgate | 134 | 18:30 | 123 | 12:00
| Barishal | 134 | 00:00 | 130 | 12:00 | Mirpur | 134 | 19:00 | 124 | 12:00
| Barishal-230 | 136 | 04:00 | 131 | 11:00 | Mithapukur | 134 | 00:00 | 118 | 07:00
| Baroaulia | 142 | 19:00 | 134 | 12:00 | Modern | 139 | 07:00 | 131 | 02:00
| Baroirhat | 137 | 18:00 | 129 | 12:00 | Mogbazar | 136 | 05:00 | 128 | 12:00
| Bashundhara | 135 | 07:00 | 123 | 12:00 | Mongla | 137 | 00:00 | 128 | 18:30
| BashundharaCement | 135 | 07:00 | 128 | 12:00 | Motijheel | 133 | 07:00 | 126 | 12:00
| Beanibazar | 134 | 00:00 | 131 | 12:00 | Munshiganj | 134 | 18:30 | 129 | 11:00
| Benapole | 133 | 00:00 | 123 | 12:00 | Mymensingh | 133 | 22:00 | 110 | 20:00
| Bhaluka | 126 | 00:00 | 105 | 18:30 | Naogaon | 129 | 00:00 | 114 | 07:00
| Bhandaria | 135 | 03:00 | 129 | 14:00 | Narail | 133 | 00:00 | 122 | 12:00
| Bhangura | 138 | 00:00 | 129 | 10:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 135 | 00:00 | 127 | 10:00 | Narshingdi | 131 | 07:00 | 121 | 11:00
| Bheramara(GK) | 136 | 00:00 | 128 | 10:00 | Natore | 133 | 18:00 | 124 | 07:00
| Bhulta | 126 | 01:00 | 118 | 12:00 | Nawabganj | 135 | 07:00 | 126 | 12:00
| Bog-Sherpur | 135 | 00:00 | 124 | 07:00 | Netrakona | 125 | 00:00 | 109 | 15:00
| Bogura | 135 | 01:00 | 121 | 07:00 | New | 134 | 00:00 | 123 | 12:00
| Bogura-230 | 137 | 04:00 | 123 | 18:30 | Niamatpur | 127 | 01:00 | 109 | 07:00
| Brahmanbaria | 134 | 04:00 | 128 | 12:00 | Noapara | 137 | 00:00 | 126 | 13:00
| Cantonment | 135 | 07:00 | 127 | 12:00 | Pabna | 137 | 21:00 | 125 | 12:00
| Chandpur | 140 | 18:00 | 128 | 12:00 | Palashbari | 132 | 00:00 | 115 | 07:00
| Chandraghona | 141 | 18:00 | 132 | 02:00 | Panchagarh | 133 | 00:00 | 110 | 07:00
| Chapai | 132 | 00:00 | 123 | 08:00 | Patuakhali | 136 | 17:00 | 125 | 23:00
| Charsaidpur | 135 | 07:00 | 129 | 12:00 | Payra | 133 | 18:00 | 127 | 12:00
| Chauddagram | 140 | 19:00 | 129 | 12:00 | PHP | 137 | 18:00 | 129 | 11:00
| Chhatak | 134 | 00:00 | 132 | 12:00 | Postogola | 134 | 07:00 | 128 | 11:00
| Chowmuhani | 137 | 18:00 | 126 | 13:00 | Purbachal | 134 | 00:00 | 127 | 12:00
| Chuadanga | 131 | 00:00 | 121 | 12:00 | Purbasadipur | 134 | 00:00 | 112 | 07:00
| Coxsbazar | 127 | 18:30 | 121 | 02:00 | Rahim | 135 | 18:00 | 131 | 11:00
| Cumilla(N) | 139 | 18:00 | 132 | 11:00 | Rajbari | 133 | 04:00 | 125 | 12:00
| Cumilla(S) | 139 | 19:00 | 126 | 15:00 | Rajendrapur | 138 | 00:00 | 131 | 12:00
| Daudkandi | 134 | 18:00 | 127 | 12:00 | Rajshahi | 133 | 18:00 | 125 | 08:00
| Dhaka | 135 | 07:00 | 127 | 12:00 | Rajshahi-230 | 133 | 18:00 | 124 | 10:00
| Dhamrai | 133 | 01:00 | 126 | 12:00 | Ramganj | 137 | 19:00 | 125 | 12:00
| Dhanmondi | 136 | 07:00 | 129.5 | 12:00 | Rampur | 137 | 18:00 | 130 | 01:00
| Dohazari | 138 | 07:00 | 129 | 12:00 | Rampura | 134 | 00:00 | 127 | 12:00
| Faridpur | 132 | 00:00 | 130 | 19:30 | Rangamati | 140 | 19:00 | 132 | 02:00
| Fatullah | 135 | 19:00 | 129 | 11:00 | Rangpur | 133 | 00:00 | 120 | 07:00
| Fenchuganj | 138 | 05:00 | 134 | 10:00 | Ruppur | 136 | 00:00 | 129 | 10:00
| Feni | 140 | 18:00 | 130 | 12:00 | Saidpur | 133 | 00:00 | 120 | 07:00
| Ghorashal | 140 | 00:00 | 135 | 13:00 | Satkhira | 137 | 00:00 | 128 | 12:00
| Goalpara | 140 | 00:00 | 130 | 12:00 | Satmasjid | 134 | 04:00 | 127 | 12:00
| Gollamari | 130 | 04:00 | 124 | 15:00 | Savar | 136 | 19:00 | 123 | 15:00
| Gopalganj | 131 | 00:00 | 124 | 12:00 | Shahjadpur | 143 | 00:00 | 134 | 07:00
| Gopalganj-400 | 133 | 02:00 | 127 | 12:00 | Shahjibazar | 135 | 00:00 | 130 | 15:00
| Gulshan | 134 | 02:00 | 126 | 12:00 | Shahmirpur | 138 | 18:00 | 131 | 05:00
| Halishahar | 139 | 07:00 | 131 | 15:00 | Shariatpur | 132 | 00:00 | 126 | 12:00
| Haripur | 135 | 18:00 | 131 | 11:00 | Sherpur | 132 | 19:30 | 112 | 11:00
| HaripurSBU | 136 | 19:00 | 131 | 15:00 | Shikalbaha | 140 | 18:30 | 133 | 04:00
| Hasnabad | 138 | 11:00 | 128 | 13:00 | Shikalbaha-230 | 139 | 08:00 | 131 | 02:00
| Hathazari | 142 | 19:00 | 130 | 19:30 | Shitalakhya | 135 | 07:00 | 128 | 12:00
| Ishurdi | 137 | 18:00 | 128 | 08:00 | Sholosohor | 139 | 07:00 | 131 | 03:00
| Jaldhaka | 132 | 00:00 | 112 | 07:00 | Shyampur | 134 | 19:00 | 129 | 12:00
| Jamalpur | 134 | 19:30 | 116 | 11:00 | Shyampur-230 | 134 | 07:00 | 128 | 12:00
| Jashore | 134 | 00:00 | 122 | 13:00 | Siddhirganj | 135 | 07:00 | 129 | 12:00
| Jhenaidah | 135 | 00:00 | 130 | 05:00 | Sirajganj | 136 | 00:00 | 126 | 07:00
| Jhenaidah-230 | 135 | 00:00 | 126 | 12:00 | Sonargaon | 135 | 02:00 | 127 | 12:00
| Joydebpur | 140 | 07:00 | 132 | 11:00 | Sreemongol | 134 | 00:00 | 131 | 11:00
| Joypurhat | 127 | 00:00 | 112 | 07:00 | Srinagar | 133 | 05:00 | 126 | 12:00
| Juldah | 138 | 19:00 | 132 | 01:00 | SSM | 142 | 18:00 | 138 | 03:00
| Kabirpur | 139 | 13:00 | 119 | 12:00 | Sunamganj | 133 | 00:00 | 130 | 11:00
| Kachua | 140 | 19:00 | 129 | 12:00 | Sylhet | 135 | 00:00 | 133 | 10:00
| Kaliakoir | 140 | 08:00 | 136 | 02:00 | Tangail | 136 | 00:00 | 124 | 06:00
| Kallyanpur | 135 | 19:00 | 125 | 12:00 | Thakurgaon | 135 | 18:00 | 110 | 07:00
| Kalurghat | 139 | 18:00 | 132 | 02:00 | TK | 140 | 19:00 | 132 | 04:00
| Kamrangirchar | 134 | 03:00 | 126 | 12:00 | Tongi | 135 | 04:00 | 126 | 11:00
| Kaptai | 140 | 18:00 | 134 | 11:00 | Ullon | 134 | 00:00 | 127 | 12:00
| Kazla | 133 | 08:00 | 126 | 12:00 | Uttara | 134 | 19:30 | 122 | 12:00
| Keranigonj | 133 | 07:00 | 126 | 12:00 | UttaraNew | 134 | 19:00 | 124 | 12:00
| Khagrachori | 139 | 19:00 | 131 | 03:00 | Zigatola | 133 | 00:00 | 126 | 12:00
| Khulna | 139 | 00:00 | 130 | 12:00
| Khulna(S) | 139 | 00:00 | 131 | 13:00
| Khulshi | 138 | 17:00 | 131 | 01:00
| Kishoreganj | 130 | 00:00 | 119 | 15:00
| Kodda | 140 | 13:00 | 130 | 13:00
| KSRM | 140 | 18:00 | 133 | 12:00
| Kulaura | 136 | 00:00 | 134 | 15:00
| Kurigram | 134 | 00:00 | 112 | 07:00
| Kushtia | 136 | 00:00 | 126 | 12:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2023-03-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 828 | 6093 | 4049 | 10142 |  |  |  | QF-LDC-11
0:30 | 841 | 5881 | 3806 | 9687 | Date: | 2023-03-02
1:00 | 854 | 5669 | 3563 | 9232
1:30 | 837 | 5501.5 | 3502 | 9003.5
2:00 | 820 | 5334 | 3441 | 8775
2:30 | 825 | 5277 | 3407 | 8684 | [5 empty] | Gen. at Eve. Peak | 11818 | 9664 MW (19:00 )
3:00 | 830 | 5220 | 3373 | 8593 | [6 empty] | 19:00
3:30 | 825 | 5164 | 3300.5 | 8464.5 | [5 empty] | Gen. at Day Peak | 10639 | 8717 MW (12:00 )
4:00 | 820 | 5108 | 3228 | 8336 | [6 empty] | 12:00
4:30 | 825 | 5015 | 3238 | 8253 | [5 empty] | Highest Generation | 11818
5:00 | 830 | 4922 | 3248 | 8170 | [6 empty] | 19:00
5:30 | 835 | 4973.5 | 3385.5 | 8359
6:00 | 840 | 5025 | 3523 | 8548
6:30 | 655 | 5266 | 3557 | 8823
7:00 | 470 | 5507 | 3591 | 9098
7:30 | 545 | 5618.5 | 3615.5 | 9234
8:00 | 620 | 5730 | 3640 | 9370
8:30 | 640 | 5881.5 | 3677 | 9558.5
9:00 | 660 | 6033 | 3714 | 9747
9:30 | 785 | 6132.5 | 3780 | 9912.5
10:00 | 910 | 6232 | 3846 | 10078
10:30 | 847 | 6423.5 | 3705.5 | 10129
11:00 | 784 | 6615 | 3565 | 10180
11:30 | 777 | 6681 | 3728.5 | 10409.5
12:00 | 770 | 6747 | 3892 | 10639
12:30 | 765 | 6678.5 | 3996.5 | 10675
13:00 | 760 | 6610 | 4101 | 10711
13:30 | 842 | 6568 | 4211.5 | 10779.5
14:00 | 924 | 6526 | 4322 | 10848
14:30 | 1009 | 6531.5 | 4278 | 10809.5
15:00 | 1094 | 6537 | 4234 | 10771
15:30 | 1057 | 6578 | 4153.5 | 10731.5
16:00 | 1020 | 6619 | 4073 | 10692
16:30 | 1008 | 6543 | 4024.5 | 10567.5
17:00 | 996 | 6467 | 3976 | 10443
17:30 | 925 | 6515.5 | 4014 | 10529.5
18:00 | 854 | 6564 | 4052 | 10616
18:30 | 557 | 7049.5 | 4167.5 | 11217
19:00 | 260 | 7535 | 4283 | 11818
19:30 | 250 | 7388 | 4226 | 11614
20:00 | 226 | 7264 | 4074 | 11338 |  |  |  | Executive Engineer
20:30 | 198 | 7221 | 4054.5 | 11275.5 |  |  |  | Network Operation Division
21:00 | 170 | 7178 | 4035 | 11213
21:30 | 327 | 7018 | 4056 | 11074
22:00 | 484 | 6858 | 4077 | 10935 |  |  |  |  | Page 6 of 7
22:30 | 536 | 6617.5 | 4003.5 | 10621
23:00 | 588 | 6377 | 3930 | 10307
23:30 | 708 | 6235 | 3989.5 | 10224.5
24:00 | 828 | 6093 | 4049 | 10142
9664 MW (19:00 )
8717 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-03-02 |  | Energy |  | 244456745
[13 empty] | 2023-03-02 |  |  |  |  | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | SHORTAGE
0:00 | 3918 | 888 | 1800 | 0 | 1494 | 1826 | 30 | 0 | 60 | 126 | 0 | 0
0:30 | 3857.5 | 888 | 1758 | 0 | 1343 | 1659.5 | 30 | 0 | 30 | 121 | 0 | 0 | Date: | 2023-03-02
1:00 | 3797 | 888 | 1716 | 0 | 1192 | 1493 | 30 | 0 | 0 | 116 | 0 | 0
1:30 | 3808.5 | 888.5 | 1745 | 0 | 925.5 | 1493 | 30 | 0 | 0 | 113 | 0 | 0 | [7 empty] | Total Energy | 244.4567 | Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
2:00 | 3820 | 889 | 1774 | 0 | 659 | 1493 | 30 | 0 | 0 | 110 | 0 | 0 | [7 empty] | Energy not Served | 1.4596
2:30 | 3817.5 | 888.5 | 1758.5 | 0 | 613.5 | 1467 | 30 | 0 | 0 | 109 | 0 | 0 | [7 empty] | Energy Requirement | 245.9164
3:00 | 3815 | 888 | 1743 | 0 | 568 | 1441 | 30 | 0 | 0 | 108 | 0 | 0
3:30 | 3812.5 | 888.5 | 1685.5 | 0 | 528 | 1411 | 30 | 0 | 0 | 109 | 0 | 0 | [5 empty] | Shortage
4:00 | 3810 | 889 | 1628 | 0 | 488 | 1381 | 30 | 0 | 0 | 110 | 0 | 0
4:30 | 3790.5 | 889.5 | 1575.5 | 0 | 488 | 1371.5 | 30 | 0 | 0 | 108 | 0 | 0
5:00 | 3771 | 890 | 1523 | 0 | 488 | 1362 | 30 | 0 | 0 | 106 | 0 | 0
5:30 | 3792.5 | 889.5 | 1532.5 | 0 | 592 | 1414.5 | 30 | 0 | 5 | 103 | 0 | 0
6:00 | 3814 | 889 | 1542 | 0 | 696 | 1467 | 30 | 0 | 10 | 100 | 0 | 0
6:30 | 3796 | 841.5 | 1634 | 0 | 902.5 | 1489 | 30 | 0 | 21 | 100 | 9 | 55.2945 |  |  |  | Coal
7:00 | 3778 | 794 | 1726 | 0 | 1109 | 1511 | 30 | 0 | 32 | 100 | 18 | 110.589
7:30 | 3731 | 794 | 1641 | 0 | 1348 | 1487 | 30 | 0 | 36 | 108 | 59 | 166.3443 |  |  | Oil |  |  |  | ,
8:00 | 3684 | 794 | 1556 | 0 | 1587 | 1463 | 30 | 0 | 40 | 116 | 100 | 222.0996
8:30 | 3705 | 794 | 1580 | 0 | 1638.5 | 1473 | 30 | 0 | 80.5 | 115 | 142.5 | 205.972
9:00 | 3726 | 794 | 1604 | 0 | 1690 | 1483 | 30 | 0 | 121 | 114 | 185 | 189.8445
9:30 | 3699.5 | 841 | 1624 | 0 | 1779 | 1473.5 | 30 | 0 | 132 | 119 | 214.5 | 133.6284
10:00 | 3673 | 888 | 1644 | 0 | 1868 | 1464 | 30 | 0 | 143 | 124 | 244 | 77.4123
10:30 | 3735.5 | 888 | 1649 | 0 | 1964.5 | 1273 | 30 | 0 | 191 | 129 | 269 | 60.3632
11:00 | 3798 | 888 | 1654 | 0 | 2061 | 1082 | 30 | 0 | 239 | 134 | 294 | 43.314
11:30 | 3806 | 888 | 1720.5 | 0 | 2074 | 1176.5 | 30 | 0 | 264 | 136 | 314.5 | 99.0693
12:00 | 3814 | 888 | 1787 | 0 | 2087 | 1271 | 30 | 0 | 289 | 138 | 335 | 154.8246
12:30 | 3816.5 | 888 | 1735.5 | 0 | 2045.5 | 1381.5 | 30 | 0 | 309.5 | 138 | 330.5 | 131.3244
13:00 | 3819 | 888 | 1684 | 0 | 2004 | 1492 | 30 | 0 | 330 | 138 | 326 | 107.8243
13:30 | 3819 | 888 | 1684 | 0 | 2004 | 1492 | 30 | 0 | 330 | 138 | 326 | 107.8243
14:00 | 3819 | 888 | 1684 | 0 | 2004 | 1492 | 30 | 0 | 330 | 138 | 326 | 107.8243
14:30 | 3844.5 | 888 | 1691.5 | 0 | 2070 | 1471.5 | 40 | 0 | 328.5 | 136 | 271 | 104.138
15:00 | 3870 | 888 | 1699 | 0 | 2136 | 1451 | 50 | 0 | 327 | 134 | 216 | 100.4517
15:30 | 3881 | 887.5 | 1737 | 0 | 2126.5 | 1420.5 | 40 | 0 | 336 | 132 | 171 | 110.1282
16:00 | 3892 | 887 | 1775 | 0 | 2117 | 1390 | 30 | 0 | 345 | 130 | 126 | 119.8048
16:30 | 3852.5 | 888 | 1727 | 0 | 2139 | 1375.5 | 30 | 0 | 353.5 | 119 | 83 | 109.2066
17:00 | 3813 | 889 | 1679 | 0 | 2161 | 1361 | 30 | 0 | 362 | 108 | 40 | 98.6085
17:30 | 3674.5 | 829.5 | 1621.5 | 0 | 2465 | 1356 | 30 | 0 | 410 | 123 | 20 | 87.8043
18:00 | 3536 | 770 | 1564 | 0 | 2769 | 1351 | 30 | 0 | 458 | 138 | 0 | 77
18:30 | 3613.5 | 770 | 1644.5 | 0 | 3082 | 1435 | 30 | 0 | 504 | 138 | 0 | 60.157
19:00 | 3691 | 770 | 1725 | 0 | 3395 | 1519 | 30 | 0 | 550 | 138 | 0 | 43.314
19:30 | 3779 | 769 | 1637 | 0 | 3333 | 1689 | 30 | 0 | 243 | 134 | 0 | 33.1767
20:00 | 3920 | 802 | 1735 | 0 | 2895 | 1698 | 30 | 0 | 126 | 132 | 0 | 23.0394
20:30 | 3964 | 798 | 1818.5 | 0 | 2696.5 | 1710.5 | 30 | 0 | 126 | 132 | 0 | 19.0197
21:00 | 4008 | 794 | 1902 | 0 | 2498 | 1723 | 30 | 0 | 126 | 132 | 0 | 15
21:30 | 3977.5 | 841.5 | 1852 | 0 | 2393 | 1721 | 30 | 0 | 126 | 133 | 0 | 14.8726
22:00 | 3947 | 889 | 1802 | 0 | 2288 | 1719 | 30 | 0 | 126 | 134 | 0 | 14.7452
22:30 | 3927 | 904.5 | 1808.5 | 0 | 2027 | 1695 | 30 | 0 | 93 | 136 | 0 | 14.7452
23:00 | 3907 | 920 | 1815 | 0 | 1766 | 1671 | 30 | 0 | 60 | 138 | 0 | 14.7452
23:30 | 3912.5 | 904 | 1807.5 | 0 | 1630 | 1748.5 | 30 | 0 | 60 | 132 | 0 | 7.3726 | Max Temp. in Dhaka |  | 34.1° C
24:00 | 3918 | 888 | 1800 | 0 | 1494 | 1826 | 30 | 0 | 60 | 126 | 0 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 193.080 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 193.080 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-03-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 730320
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [6 empty] | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 381092
| Teknaf 20MW PP (Solartech) | [6 empty] | 2 | 8 | 14 | 0 | 19 | 20 | 18 | 0 | 14 | 9 | 3 | 0 | [8 empty] | 103815
6 | Sikalbaha 225MW CCPP (Gas) | 228 | 226 | 227 | 228 | 227 | 227 | 227 | 227 | 229 | 228 | 219 | 220 | 220 | 221 | 218 | 221 | 221 | 200 |  | 200 | 200 | 223 | 221 | 221 | 221 | 221 | 5234212
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [8 empty] | 0 | 15 | 51 | 51 | 75 | 71 | 75 | 75 | 72 | 84 |  | 85 | 34 |  |  |  |  | 0 | 636282
12 | Hathazari 100 MW peaking PP | [7 empty] | 8 | 40 | 40 | 40 | 38 | 38 | 38 | 22 | 22 | 40 | 46 |  | 58 | 18 | [5 empty] | 411696
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 34 | 40 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 766945
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [7 empty] | 0 | 26 | 29 | 29 | 30 | 28 | 28 | 28 | 28 | 31 | 28 |  | 28 | 28 |  |  |  |  | 0 | 314304
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [11 empty] | 0 | 97 | 99 | 95 | 90 | 57 | 37 |  | 34 | 38 | 38 | 96 | 92 | 97 | 94 | 948000
17 | Siddhirganj 335 MW CCPP
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 30 | 20 | 15 | 15 | 15 | 26 | 64 | 173 | 278 | 278 | 278 | 278 | 278 | 278 | 210 | 210 | 238 |  | 278 | 225 | 45 | 15 | 15 |  | 0 | 3367198
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3119094
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 46 | 46 | 46 | 45 | 44 | 44 | 44 | 44 | 46 |  | 46 | 44 | 44 | 44 | 47 | 47 | 47 | 1089144
33 | Ashuganj 225 MW CCPP | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 192 | 184 | 184 | 216 | 190 | 202 | 216 | 214 | 216 | 216 | 161 |  | 218 | 216 | 216 | 216 | 218 | 218 | 218 | 4797000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 285 | 290 | 285 | 290 | 290 | 290 | 305 | 290 | 275 | 295 | 295 | 330 | 295 | 285 | 290 | 290 | 290 | 290 |  | 290 | 290 | 295 | 320 | 310 | 310 | 310 | 7492300
| Ashuganj 420 MW CCPP(East) | 317 | 317 | 316 | 317 | 316 | 323 | 323 | 280 | 315 | 315 | 349 | 350 | 340 | 310 | 312 | 310 | 310 | 250 |  | 250 | 250 | 317 | 315 | 320 | 320 | 320 | 7542300
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 30 | 30 | 40 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 348960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 354 | 383 | 400 | 400 | 369 | 361 | 390 | 400 | 402 | 378 | 396 | 402 | 402 | 395 | 370 | 371 | 371 | 365 |  | 367 | 381 | 386 | 398 | 402 | 374 | 374 | 9334780
40 | Meghnaghat 450 MW CCPP(MPL) | 370 | 390 | 420 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 350 |  | 350 | 320 | 380 | 450 | 450 | 450 | 450 | 9755500
41 | Haripur 360MW CCPP(HPL) | 303 | 343 | 342 | 343 | 303 | 302 | 343 | 283 | 289 | 319 | 338 | 347 | 329 | 289 | 255 | 284 | 294 | 294 |  | 344 | 304 | 345 | 342 | 302 | 301 | 302 | 7496000
42 | RPCL 210MW CCPP | 99 | 94 | 95 | 94 | 95 | 95 | 46 | 46 | 34 | 35 | 44 | 44 | 35 | 35 | 34 | 44 | 44 | 45 |  | 55 | 78 | 100 | 100 | 101 | 101 | 103 | 1559040
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 2 | 12 | 25 | 36 | 43 | 45 | 45 | 40 | 29 | 15 | 5 | [9 empty] | 297420
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 0 |  | 941000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 0 |  | 937200
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 63 | 63 | 62 | 63 | 52 | 52 | 33 | 33 | 32 | 32 | 30 | 30 | 31 | 31 | 30 | 31 | 31 | 20 |  | 32 | 31 | 31 | 31 | 32 | 32 | 62 | 908448
48 | Shahjibazar 86MW PP (Shahjibazar) | 90 | 40 | 10 | 10 | 10 | 10 | 84 | 50 | 84 | 84 | 84 | 84 | 84 | 86 | 86 | 89 | 30 | 30 |  | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 1610880
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 212 | 211 | 212 | 212 | 212 | 212 | 213 | 212 | 216 | 214 | 214 | 214 | 214 | 212 | 212 | 213 | 214 |  | 210 | 212 | 211 | 211 | 214 | 214 | 214 | 5246160
51 | Sylhet 20 MW GTPP | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 433000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190080
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 171552
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 22 | 22 | 22 | 11 | 11 | 31 | 31 | 31 | 31 | 31 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 53 | 53 | 53 | 53 | 842400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193200
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 290 | 270 | 260 | 270 | 290 | 305 | 265 | 280 | 295 | 280 | 325 | 270 | 260 | 285 | 270 | 280 | 260 |  | 290 | 290 | 290 | 300 | 280 | 300 | 285 | 6938500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 360 | 360 | 400 | 350 | 400 | 370 | 390 | 400 | 390 | 400 | 396 | 370 | 370 | 320 |  | 370 | 400 | 400 | 400 | 340 | 400 | 400 | 9169100
58 | Nababganj 55 MW PP (Southern power ) | [6 empty] | 17 | 17 | 0 | [5 empty] | 10 | 17 | 35 | 50 |  | 55 | 55 | 55 | 35 | 35 | 35 | 35 | 383975
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 2 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 144240
60 | Barabkunda 22 MW PP (Regent) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 355632
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 0 | 0 | 22 |  |  | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 437004
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 11 | 11 | 11 | 11 | 14 | 14 | 14 | 17 | 17 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 384444
63 | Impoprt (Tripura) | 116 | 110 | 108 | 110 | 106 | 100 | 100 | 116 | 114 | 124 | 134 | 138 | 138 | 138 | 134 | 130 | 108 | 138 |  | 138 | 134 | 132 | 132 | 134 | 138 | 126 | 2982720
64 | Malancha, Ctg. EPZ (United) |  |  |  |  | 2 | 5 | 5 | 0 | [17 empty] | 0 | 37440
65 | Feni 22MW PP (Doreen) | 19 | 19 | 18 | 18 | 18 | 18 | 19 | 19 | 18 | 15 | 15 | 18 | 18 | 15 | 16 | 17 | 18 | 19 |  | 19 | 17 | 17 | 19 | 19 | 18 | 19 | 414000
66 | Feni 11 MW PP (Doreen) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 244080
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 |  | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 786500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 21 | 21 | 21 |  | 21 | 15 | 21 | 21 | 21 | 21 | 21 | 456360
69 | Summit Ashulia | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 541000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 8 | 8 | 8 | 8 | 22 | 8 | 21 | 22 | 22 | 22 | 0 | 8 |  | 8 | 8 | 27 | 27 | 28 | 28 | 28 | 486000
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 835100
72 | Rupganj 33 MW PP(Summit) | 28 | 30 | 30 | 30 | 31 | 32 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 26 |  | 26 | 29 | 30 | 30 | 32 | 32 | 33 | 724400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 70 | 70 | 70 |  | 80 | 52 | 17 | 17 | 17 | 17 | 17 | 587100
| Chowmuhani 113 MW | 9 | 3 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 50 |  | 104 | 116 | 114 | 55 | 55 | 26 | 11 | 610680
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 31 |  | 129 | 144 | 144 | 144 | 100 | 56 | 17 | 933120
77 | Siddhirganj 100 PP(Dutch Bangla) | 33 | 14 | 8 | 8 | 8 | 8 | 15 | 33 | 33 | 33 | 40 | 40 | 40 | 40 | 43 | 53 | 53 | 46 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 800640
78 | Gazipur 52 MW PP | [6 empty] | 9 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 45 | 50 |  | 50 | 50 | 50 | 50 | 25 | 25 | 8 | 584640
79 | Kodda 150MW PP | [5 empty] | 10 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 48 | 48 | 48 |  | 98 | 98 | 98 | 98 | 98 | 32 | 32 | 900000
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | [12 empty] | 3 |  | 8 | 8 | 8 | 8 |  |  |  | 70944
| Gazipur 100 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 1252800
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 1 | 0 | [9 empty] | 30121
| Jodiac Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 646475
| Karnaphuli Power Ltd. | 54 | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 54 | 54 | 54 | 54 | 54 | 54 | 58 | 58 | 63 | 75 |  | 62 | 62 | 69 | 63 | 63 | 72 | 54 | 1441048
82 | Madanganj 102 PP(Summit) | [6 empty] | 25 | 75 | 80 | 85 | 85 | 90 | 92 | 85 | 80 | 65 | 34 | 48 |  | 75 | 30 | 30 |  |  |  | 0 | 891977
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac)
86 | Meghnaghat CCPP ( Summit) | 160 | 145 | 135 | 0 | [21 empty] | 0 | 493789
87 | Meghnaghat 100 MW(IEL) | 33 | [5 empty] | 5 | 30 | 33 | 32 | 43 | 41 | 41 | 38 | 41 | 46 | 50 | 56 |  | 61 | 62 | 61 | 30 | 23 | 24 | 25 | 713280
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 16 | 17 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 18 | 17 | 17 | 18 | 17 | 405120
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 46 | 10 | 10 | 10 | 10 | 10 | 33 | 44 | 44 | 44 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 738120
92 | Fenchuganj 44MW (Energyprima) | 50 | 30 | 30 | 30 | 10 | 10 | 30 | 30 | 40 | 40 | 46 | 46 | 50 | 50 | 46 | 45 | 45 | 49 |  | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 990144
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 10 | 10 | 25 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1152826
94 | Gagnagar 102 MW PP (Digital Power) | 16 |  |  |  |  | 8 | 24 | 24 | 24 | 41 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 |  | 58 | 58 | 16 | 16 | 16 | 16 | 16 | 621792
95 | Patenga 50MW PP (Baraka) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 0 | [6 empty] | 4 | 12 | 13 |  | 18 | 20 | 20 | 20 | 17 | 19 | 19 | 305280
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [6 empty] | 15 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 15 | 15 | 15 | 15 | 15 | 812250
100 | Manikganj 55 MW PP (Northern) | [5 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 55 | 55 | 55 | 35 | 17 | 17 | 0 | 400456
101 | Kushiara 163 MW CCPP (KP) | [14 empty] | 10 | 80 | 80 | 80 |  | 112 | 80 | 80 | 112 | 80 | 112 | 112 | 891982
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12200
103 | Kamalaghat 54 MW PP(Banco Energy) | [15 empty] | 17 | 17 | 17 |  | 35 | 35 | 35 | 17 | 17 |  | 0 | 157320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 49 | 49 | 49 | 68 | 68 | 68 | 69 | 68 | 68 | 68 | 69 |  | 116 | 116 | 118 | 118 | 118 | 59 | 59 | 1615200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 107 | 34 | 20 | 17 | 17 | 19 | 70 | 126 | 135 | 137 | 149 | 149 | 149 | 149 | 149 | 115 | 100 | 106 |  | 140 | 149 | 149 | 132 | 132 | 108 | 98 | 2530368
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 12 | 12 | 12 | 12 | 12 | 70 | 100 | 100 | 88 | 88 | 88 | 50 | 50 | 50 | 50 | 50 | 65 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1613760
116 | Chandpur 200MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 70 | 100 | 100 | 68 | 68 |  | 92 | 136 | 136 | 136 | 136 | 136 | 17 | 1588320
117 | Ashuganj 150MW PP (Midland) | 40 | 40 | 40 | 41 | 40 | 40 | 38 | 30 | 40 | 41 | 40 | 40 | 38 | 38 | 38 | 38 | 40 | 82 |  | 140 | 150 | 150 | 150 | 70 | 40 | 40 | 1344872
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 367 | 367 | 367 | 396 | 365 | 373 | 367 | 367 | 401 | 402 | 367 | 369 | 367 | 369 | 368 | 343 |  | 367 | 367 | 367 | 367 | 367 | 367 | 367 | 8916000
| Jamalpur 115 MW PP (United) | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 30 | 47 | 49 | 49 | 49 | 49 | 58 | 58 | 58 |  | 78 | 79 | 79 | 79 | 79 | 59 | 59 | 946800
| Anwara 300 MW PP (United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 116 | 121 | 123 | 123 | 123 | 123 | 123 | 257 |  | 257 | 265 | 266 | 266 | 266 | 70 | 69 | 2348509
| Juldah unit-2 (Acorn) | 87 | 23 | 12 | 12 | 12 | 12 | 27 | 98 | 100 | 100 | 100 | 100 | 65 | 38 | 38 | 38 | 38 | 48 |  | 100 | 100 | 100 | 50 | 50 | 50 | 50 | 1362240
| Anlima Energy Ltd. | 107 | 107 | 51 | 51 | 51 | 63 | 89 | 96 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 68 | 68 |  | 96 | 107 | 107 | 107 | 107 | 107 | 107 | 2307109
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 |  | 7 | 17 | 17 | 426600
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 8 | 16 | 23 | 28 | 30 | 29 | 25 | 20 | 12 | 4 | 0 | [8 empty] | 194545
| Chandpur 115(Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 19 | 37 | 40 | 18 | 18 | 21 | 36 | 57 |  | 72 | 72 | 72 | 72 | 72 | 62 | 45 | 828480
| Kanchan Purbachal Power Generation Ltd. | [11 empty] | 0 | 3 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 187560
| Mirsharai 150 MW (Oil) | [25 empty] | 0 | 0
Mirsharai 150 MW (Gas)
120 | Eastern Zone Total | 5669 | 5334 | 5220 | 5108 | 4922 | 5025 | 5507 | 5730 | 6033 | 6232 | 6615 | 6747 | 6610 | 6526 | 6537 | 6619 | 6467 | 6564 |  | 7535 | 7388 | 7264 | 7178 | 6858 | 6377 | 6093 | 149753511
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 |  |  |  |  | 9 | 49 | 83 | 83 | 83 | 81 | 80 | 63 | 64 | 64 | 66 | 80 | 98 |  | 99 | 99 | 99 | 49 | 39 | 16 | 16 | 1223040
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL)
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 20 |  | 38 | [6 empty] | 40320
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [5 empty] | 13 | 36 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 952320
130 | Mongla Orion 100 MW Solar PP | [6 empty] | 5 | 26 | 52 | 72 | 84 | 89 | 86 | 79 | 58 | 37 | 12 | [9 empty] | 604080
131 | Rampal 1320 MW (BIFPCL) | 371 | 371 | 371 | 371 | 372 | 372 | 372 | 372 | 373 | 373 | 0 | [14 empty] | 217 | 4210909
132 | United Payra Power Ltd. | [13 empty] | 23 | 36 | 54 | 119 | 150 |  | 121 | 121 | 0 |  |  |  | 0 | 589200
133 | Bhola Nutan Biddut BD LTD (GAS) | 165 | 222 | 222 | 222 | 222 | 222 | 222 | 165 | 165 | 165 | 165 | 220 | 220 | 220 | 220 | 220 | 171 | 174 |  | 165 | 175 | 175 | 222 | 212 | 183 | 184 | 4857600
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | [5 empty] | 55 | 129 | 153 | 150 | 151 | 152 | 151 | 150 | 150 | 151 | 150 | 151 | 151 |  | 179 | 219 | 228 | 229 | 229 | 231 | 229 | 3010900
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 182 | 183 | 174 | 168 | 183 | 188 | 188 | 185 | 185 | 181 | 177 | 176 | 169 | 176 | 178 | 178 | 172 | 181 |  | 178 | 183 | 183 | 183 | 169 | 183 | 163 | 4380279
140 | Bhola 33 MW PP (Venture) | 18 | 17 | 16 | 15 | 15 | 15 | 14 | 13 | 12 | 13 | 13 | 15 | 16 | 16 | 16 | 15 | 14 | 16 |  | 19 | 20 | 20 | 21 | 21 | 20 | 19 | 385700
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [5 empty] | 40 | 40 | 40 | 32 | 24 | 24 | 8 | 0 |  |  |  | 8 | 40 |  | 40 | 40 | 40 | 16 | 16 |  | 0 | 320250
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 20 |  | 32 | [5 empty] | 0 | 35200
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 888 | 889 | 888 | 889 | 890 | 889 | 794 | 794 | 794 | 888 | 888 | 888 | 888 | 889 | 888 | 887 | 889 | 770 |  | 770 | 769 | 802 | 794 | 889 | 920 | 888 | 20826909
147 | Bheramara 410 MW CCPP | 200 | 200 | 200 | 180 | 180 | 165 | 165 | 165 | 165 | 150 | 150 | 150 | 150 | 265 | 290 | 275 | 270 | 265 |  | 260 | 260 | 255 | 250 | 255 | 250 | 250 | 5209056
148 | Payra 1320 MW | 922 | 922 | 870 | 810 | 790 | 790 | 760 | 710 | 710 | 690 | 680 | 870 | 1092 | 1102 | 1050 | 990 | 960 | 950 |  | 1090 | 1220 | 1220 | 1244 | 1240 | 1240 | 1180 | 24775800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 200 | 200 | 200 | 200 | 200 | 250 | 250 | 228 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 200 | 200 | 5692600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [13 empty] | 32 | 32 | 32 | 32 | 31 |  | 30 | [6 empty] | 181568
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 4 | 2 | 1 | 0 | 0 | [8 empty] | 28440
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 168 | 161 | 155 | 168 | 196 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 215 | 205 | 193 | 174 | 130 |  | 145 | 165 | 164 | 164 | 164 | 164 | 164 | 4796864
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 164 | 171 | 172 | 172 | 167 | 164 | 164 | 165 | 166 | 150 | 150 | 151 | 151 | 208 | 201 | 192 | 185 | 176 |  | 171 | 173 | 170 | 169 | 171 | 163 | 163 | 4096509
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [8 empty] | 0 | 4 | 13 | 20 | 29 | 29 | 24 | 26 | 25 | 25 |  | 20 | [6 empty] | 212171
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 0 |  |  |  | 12 | 17 | 17 | 17 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 391680
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252576
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern) | [6 empty] | 16 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 8 |  | 8 |  | 42 | 8 | [5 empty] | 396601
167 | Katakhali 50 MW Peaking PP | [8 empty] | 23 | 23 | 24 | 30 | 32 | 32 | 24 | 24 | 24 | 40 |  | 40 | [6 empty] | 272291
168 | Santahar 50 MW Peaking PP | [10 empty] | 0 | 24 | 32 | 32 | 28 | 28 | 28 | 34 |  | 35 | 35 | 28 | 28 | 28 | 28 | 28 | 352658
169 | Natore 52 MW PP (Rajlanka) | [6 empty] | 8 | 8 | 0 | [5 empty] | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 82114
170 | Chapainawabganj 100 MW Peaking PP | [9 empty] | 0 | 50 | 64 | 64 | 62 | 62 | 62 | 62 | 82 |  | 86 | 30 | [5 empty] | 561648
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 35 | 35 |  |  | 3 | 33 | 35 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 60 | 70 | 70 |  | 70 | 94 | 94 | 70 | 70 | 70 | 87 | 1392768
172 | Confidence Power Bogura Unit-1 113 MW | 75 | 37 | 37 |  |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 50 | 70 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1630944
173 | Rangpur 20 MW GTPP | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 50 |  |  |  |  | 33 | 33 | 49 | 42 | 56 | 62 | 71 | 77 | 71 | 71 | 71 | 85 | 98 |  | 99 | 99 | 99 | 99 | 97 | 70 | 70 | 1380192
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 33795
178 | Energypac Power Venture Thakurgaon Ltd. | [8 empty] | 0 | 13 | 35 | 37 | 37 | 37 | 37 | 37 | 37 | 107 |  | 113 | 74 | 55 | 55 | 35 |  | 0 | 640512
| Intraco Solar 30 MW | [6 empty] | 1 | 6 | 13 | 19 | 24 | 25 | 24 | 22 | 17 | 10 | 3 | 0 | [8 empty] | 164940
Adani Power Jharkhanda Ltd
178 | Teesta Solar Limited | [6 empty] | 7 | 35 | 57 | 82 | 82 | 111 | 110 | 95 | 69 | 38 | 12 | 0 | [8 empty] | 720800