## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:June 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-06-01 |  | 2023-05-01 |  | 2022-06-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14655 | 2023-06-08 | 14511 | 2023-05-30 | 14038 | 2022-06-08 | 15648 | 2023-04-19
|  |  | 20:00 |  | 21:00 |  | 23:00 |  | 21:00
2 | Minimum Generation (MW) | 7589 | 2023-06-28 | 4959 | 2023-05-18 | 8231 | 2022-06-17 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14655 | 2023-06-08 | 14511 | 2023-05-30 | 14004 | 2022-06-06 | 15648 | 2023-04-19
|  |  | 20:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 12677 | 2023-06-08 | 15395 | 2023-05-08 | 12226 | 2022-06-08 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15800 | 2023-06-30 | 15600 | 2023-05-31 | 14038 | 2022-06-08 | 16096 | 2023-04-19
|  |  | 20:00 |  | 21:00 |  | 23:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 13225.3 |  | 12886.871 |  | 13051.7667 |  | - | -
7 | Average Generation (MW) at Day Peak | 11423.9667 |  | 11447.9032 |  | 11161.4333 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 930 | 2023-06-25 | 961 | 2023-05-05 | 933 | 2022-06-07 | 956 | 27/3/2019
|  |  | 7:30 |  | 22:30 |  | 2:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 184 | 2023-06-13 | 180 | 2023-05-28 | 188 | 2022-06-08 | 194 | 12/06/19
|  |  | 19:00 |  | 16:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1945 | 2023-06-06 | 1995 | 2023-05-15 | - | - | 4395 | 04/10/2022
|  |  | 21:00 |  | 20:00 |  | - |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13763 | 2023-06-06 | 11496 | 2023-05-15 | - | - | 13200 | 04/10/2022
|  | - | 21:00 |  | 20:00 | - | - |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-06-09 | 0 | 2023-05-01 | - | - | - | -
|  |  | - |  | 21:00 |  |  | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12699 | 2023-06-09 | 11274 | 2023-05-01 | - | - | - | -
|  |  | 21:00 |  | 21:00 |  |  | - | -
14 | Maximum Load Shed (MW) at Day Peak | 2675 | 2023-06-05 | 2489 | 2023-05-16 | - | - | - | -
|  |  | 12:00 |  | 12:00 |  |  | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12099 | 2023-06-05 | 10144 | 2023-05-16 | - | - | - | -
|  |  | 12:00 |  | 12:00 |  |  | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-06-27 | 0 | 2023-05-01 | - | - | - | -
|  |  | - |  | 21:00 |  |  | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 12099 | 2023-06-05 | 9578 | 2023-05-01 | - | - | - | -
|  |  | 12:00 |  | 21:00 |  |  | - | -
18 | Nos. of Days Load Shed at Evening Peak | 22 |  | 23 |  | - |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 26 |  | 25 |  | - |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1745.3811 |  | 1885.6965 |  | 1590.9771 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 88.4927 |  | 62.0427 |  | 84.3577 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1656.8884 |  | 1823.6538 |  | 1506.6194 |  | - | -
23 | Net Generation of IPP (MKWH) | 4513.7304 |  | 4615.9365 |  | 5289.635 |  | - | -
24 | Net Generation of REB (MKWH) | 121.3394 |  | 122.5788 |  | 122.8415 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 364.0404 |  | 357.0366 |  | 624.4748 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6655.9986 |  | 6919.2058 |  | 7543.5707 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4651.8044 |  | 4252.0612 |  | 4234.9012 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 299.6883 |  | 161.3514 |  | 491.7382 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1291.3754 |  | 1442.64 |  | 2164.1587 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 25.8407 |  | 9.6847 |  | 52.8346 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 34.6981 |  | 48.4734 |  | 25.0967 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 441.0844 |  | 1067.0377 |  | 659.199 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 737.9119 |  | 766.1342 |  | 738.4142 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 78.4931 |  | 80.7771 |  | 88.6952 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:June 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
Sl.No | Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period Generation Period | MW | 14655 | 2023-06-08 | 20:00
a) | Dhaka | MW | 4932.34
| Chattogram | MW | 1345.2
| Cumilla | MW | 1317
| Mymensingh | MW | 1017
| Sylhet | MW | 616
| Total supply in East zone | MW | 9227.54
b) | Khulna | MW | 1911
| Barisal | MW | 456.2
| Rajshahi | MW | 1511.6
| Rangpur | MW | 905
| Total supply in West zone | MW | 4783.8
c) | Total supply in both zone ( a+b) | MW | 14011.34
Ref: | 27.21.0000.603.16.087.20.690 | Date: 23/07/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 560 | 2023-06-30 | 4:00
| b) Ishurdi end | MW | 314 | 2023-06-18 | 12:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1160 | 2023-06-18 | 10:00
| b) Ishurdi end | MW | 100 | 2023-06-16 | 19:30
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.71566
| b) Ishurdi end | MKWH | 113.2001
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 109.8041
| b) Ishurdi end | MKWH | 0.69482
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 210
| b)Sirajganj end | MW | 620 | 2023-06-09 | 1:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 350 | 2023-06-18 | 11:00
| b)Sirajganj end | MW | 34 | 2023-06-29 | 4:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Sreepur end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.089
| b)Sirajganj end | MKWH | 273.92
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 270.0018
| b)Sirajganj end | MKWH | 0.09
30 | Transmission loss of EWI /NO-2 | % | 1.432
31 | Daily Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 1928 | 2023-06-04 | 14:30
| b) Gopalganj end | MW | 1122 | 2023-06-04 | 14:30
32 | Daily Maximum power Import through EWI/ NO-3
| a) Aminbazar end | AMPS | 1852 | 2023-06-04 | 12:00
| b) Aminbazar end | MW | 1084 | 2023-06-04 | 12:00
33 | Daily Maximum Energy Export through EWI/ NO-3
| a) Gopalganj end | MKWH
| b) Aminbazar end | MKWH
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MKWH
| b) Aminbazar end | MKWH
35 | Total Energy Export through EWI/ NO-3
| a) Gopalganj end | MKWH | 286.02
| b) Aminbazar end | MKWH | 0.705
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MKWH | 0.64557
| b) Aminbazar end | MKWH | 285.83
37 | Transmission loss of EWI/ NO-3 | % | -
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi. The energy meter of Ghorasal end is out of order.
* *Total energy export from Sreepur end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* ** Total energy export from Gopalganj end and import from Aminbazar end.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: June 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Manikganj | 132/33 kV transformer GT-4 | 2023-06-04 09:32 | 2023-06-04 12:27 | 2:55 | E/O | Due to red hot maintenance. | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer GT-4 (50/75 MVA) HT | 2023-06-04 09:33 | 2023-06-04 12:27 | 2:54 | E/O | Due to red hot maintenance. | 0 | 0 | No interruption
Kishoreganj | 132/33kV transformer T3 Bus | 2023-06-04 19:52 | 2023-06-04 19:57 | 0:05 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Joydebpur | 132/33kV transformer GT-3 HT | 2023-06-07 08:45 | 2023-06-07 09:43 | 0:58 | E/O | Due to red hot maintenance.at 33 kV side | 0 | 0 | No interruption
Tangail | 132/33kV transformer Tr-2 LT | 2023-06-09 12:40 | 2023-06-09 13:39 | 0:59 | T | Due to 33 kV feeder fault | 15 | 14.75 | Power interruption
Tangail | 132/33kV transformer Tr-1 LT | 2023-06-09 12:40 | 2023-06-09 13:40 | 1:00 | T | Due to 33 kV feeder fault | 15 | 15 | Power interruption
Sreepur | 132/33kV transformer- 03 HT | 2023-06-11 11:49 | 2023-06-11 13:29 | 1:40 | T | Tripped showing OSR trip,86.1,86.2 Master pro.relay | 0 | 0 | No interruption
Manikganj | Cap. Bank -1 & 2 | 2023-06-13 10:30 | 2023-06-13 11:50 | 1:20 | E/O | Due to Emergency work | 0 | 0 | No interruption
Sherpur | 132/33kV transformer Tr-3 LT | 2023-06-13 11:20 | 2023-06-13 12:46 | 1:26 | T | Tripped showing O/C relay. | 20 | 28.6667 | Power interruption
Manikganj | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-06-15 10:41 | 2023-06-15 10:44 | 0:03 | T | Tripped showing df/dt relays Due to df/dt signal | 32 | 1.6 | Power interruption
Manikganj | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-06-15 10:41 | 2023-06-15 10:44 | 0:03 | T | Tripped showing df/dt relays Due to df/dt signal | 16 | 0.8 | Power interruption
Jamalpur | 132/33kV transformer T-2 LT & HT | 2023-06-16 11:49 | 2023-06-16 13:37 | 1:48 | E/O | Due to red hot maintenance.at 33 kV side | 20 | 36 | Power interruption
Tangail | 132/33kV transformer Tr-4 LT | 2023-06-17 16:34 | 2023-06-17 17:18 | 0:44 | E/O | Due to Emergency work | 0 | 0 | No interruption
Bhaluka | 132/33kV transformer T-02 LT & T01 | 2023-06-17 17:14 | 2023-06-17 17:32 | 0:18 | E/O | Due to CT burst of feeder no 4 y phase | 0 | 0 | No interruption
Kodda | 132/33kV transformer Tr-2 | 2023-06-17 18:31 | 2023-06-17 18:55 | 0:24 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Kodda | 132/33kV transformer Tr-4 (436T) LT | 2023-06-17 18:31 | 2023-06-17 19:01 | 0:30 | T | Tripped showing Over current | 0 | 0 | No interruption
Kabirpur | 132/33kV transformer XFR, T-2 HT | 2023-06-20 17:40 | 2023-06-20 19:14 | 1:34 | E/O | Due to Emergency work at 33 kV feeder fault | 95 | 148.8333 | Power interruption
Kabirpur | 132/33kV transformer XFR, T-3 HT | 2023-06-20 21:11 | 2023-06-20 22:18 | 1:07 | E/O | Due to Emergency work at 33 kV feeder fault | 50 | 55.8333 | Power interruption
Tangail | 132/33kV transformer Tr-4 LT | 2023-06-21 15:16 | 2023-06-21 15:48 | 0:32 | T | Due to Tr-4 132 kV CB Trip. | 0 | 0 | No interruption
Joydebpur | 132/33kV transformer GT-4 HT | 2023-06-21 15:33 | 2023-06-21 15:58 | 0:25 | E/O | Due to GT-4 33KV GIS CB Gas Felling. | 0 | 0 | No interruption
Kishoreganj | 33 kV T2 Bus | 2023-06-21 08:42 | 2023-06-21 09:30 | 0:48 | E/O | Due to Emergency work | 0 | 0 | No interruption
Tongi | 230 kV Bus-2 | 2023-06-23 14:09 | 2023-06-23 14:58 | 0:49 | T | Tripped showing PT Fail relays. | 81 | 66.15 | Power interruption
Tongi | 230 kV Bus-1 & 2 | 2023-06-23 15:30 | 2023-06-23 15:30 | 0:00 | E/O | Due to bursting of PT | 0 | 0 | No interruption
Aminbazar | 400/230/132kV transformer ATR-02 HT | 2023-06-24 11:34 | 2023-06-24 11:43 | 0:09 | T | Tripped showing Differential relays. | 0 | 0 | No interruption
Aminbazar | 400/230/132kV transformer ATR-02 LT | 2023-06-24 11:34 | 2023-06-24 11:44 | 0:10 | T | Tripped showing 86-1, 86-2 relays. | 0 | 0 | No interruption
Tangail | 132/33kV transformer Tr-4 HT | 2023-06-24 12:00 | 2023-06-24 14:10 | 2:10 | E/O | Due to Emergency work at 33 kV side | 0 | 0 | No interruption
Kodda | 132/33kV transformer Tr-2 (416T) LT | 2023-06-24 15:44 | 2023-06-24 17:00 | 1:16 | E/O | Due to Emergency work | 40 | 50.6667 | Power interruption
Kodda | 132/33kV transformer Tr-2 (416T) HT | 2023-06-24 15:45 | 2023-06-24 16:58 | 1:13 | E/O | Due to Emergency work | 0 | 0 | No interruption
Aminbazar | 400/230/132kV transformer ATR-02 HT | 2023-06-24 16:01 | 2023-06-24 20:01 | 4:00 | T | Tripped showing 86 -1 and 86-2 master prot.relay | 0 | 0 | No interruption
Kodda | 132/33kV transformer Tr-2 (416T) HT | 2023-06-26 06:23 | 2023-06-26 07:41 | 1:18 | E/O | Due to Emergency work | 0 | 0 | No interruption
Kodda | 132/33kV transformer Tr-2 (416T) LT | 2023-06-26 06:23 | 2023-06-26 07:43 | 1:20 | E/O | Due to Emergency work | 30 | 40 | Power interruption
Sherpur | 132/33kV transformer T 02 HT | 2023-06-28 22:28 | 2023-06-28 23:15 | 0:47 | E/O | Due to red hot maintanance.at 33 kV side | 18 | 14.1 | Power interruption
Sherpur | 132/33kV transformer T 02 LT | 2023-06-28 22:28 | 2023-06-28 23:16 | 0:48 | E/O | Due to red hot maintanance.at 33 kV side | 0 | 0 | No interruption
Sherpur | 132/33kV transformer T 03 LT | 2023-06-29 08:33 | 2023-06-29 10:07 | 1:34 | T | Tripped showing O/C & E/F.relay | 20 | 31.3333 | Power interruption
|  |  | Total : | 37:07 |  | Unserved Energy: |  | 503.7333
Dhaka (South) Grid Circle :
Ghorashal | 230/132 kV transformer AT-2 | 2022-06-09 05:59 | 2022-06-09 12:32 | 6:33 | E/O | Due to oil leakage | 0 | 0 | No interruption
Shahmirpur | 132/33kV transformer 406T LT | 2023-06-09 08:46 | 2023-06-10 18:20 | 33:34 | E/O | Due to Breaker maint.work | 0 | 0 | No interruption
Shahmirpur | 132/33kV transformer 406T HT | 2023-06-09 08:47 | 2023-06-09 08:47 | 0:00 | E/O | Due to Breaker maint.work | 0 | 0 | No interruption
Sonargaon | 132 kV Bus coupler | 2023-06-10 09:55 | 2023-06-10 11:40 | 1:45 | E/O | Due to Emergency work | 0 | 0 | No interruption
Sonargaon | 132/33kV transformer Tr-1 HT | 2023-06-13 23:20 | 2023-06-14 00:41 | 1:21 | E/O | Due to red hot maintanance. | 62 | 0 | Power interruption
Sonargaon | 132/33kV transformer Tr-1 LT | 2023-06-13 23:20 | 2023-06-14 00:43 | 1:23 | E/O | Due to red hot maintanance. | 62 | 85.7667 | Power interruption
Rampura | 230/132kV Auto transformer - 02 | 2023-06-17 19:41 | 2023-06-17 22:32 | 2:51 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Ghorashal | 132 kV Bus-1 | 2023-06-21 06:35 | 2023-06-21 11:00 | 4:25 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Siddhirganj | 132/33kV transformer T-1 HT & LT | 2023-06-23 05:48 | 2023-06-23 09:44 | 3:56 | E/O | Due to Oil leakage | 30 | 118 | Power interruption
Bhulta | 400/230kV transformer ATR-01 HT | 2023-06-26 20:57 | 2023-06-26 22:17 | 1:20 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Madanganj | 132/33kV transformer GT-2 HT | 2023-06-28 04:09 | 2023-06-30 14:33 | 58:24 | T | Tripped showing Back up protection relay at 33kV fault | 0 | 0 | No interruption
Madanganj | 132/33kV transformer GT-1 HT | 2023-06-28 04:09 | 2023-06-28 06:01 | 1:52 | T | Tripped showing Back up protection relay at 33kV fault | 9 | 16.8 | Power interruption
Madanganj | 132/33kV transformer GT-1 HT | 2023-06-28 06:09 | 2023-06-28 06:09 | 0:00 | T | Tripped showing Back up protection relay at 33kV fault | 0 | 0 | No interruption
Nawabganj | 132/33kV transformer TR-1 | 2023-06-29 11:00 | 2023-06-29 11:42 | 0:42 | T | Tripped showing O/C relay. | 16 | 11.2 | Power interruption
Nawabganj | 132/33kV transformer TR-1 LT | 2023-06-30 15:40 | 2023-06-30 16:57 | 1:17 | T | Tripped showing Lockout relay | 12 | 15.4 | Power interruption
Nawabganj | 132/33kV transformer TR-2 LT | 2023-06-30 15:40 | 2023-06-30 17:00 | 1:20 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
|  |  | Total : | 120:43 |  | Unserved Energy: |  | 247.1667
Chattogram Grid Circle :
Sholosohor | 132/33kV transformer TRAFO-02 HT | 2023-06-06 08:06 | 2023-06-06 08:24 | 0:18 | E/O | Due to Emergency work | 0 | 0 | No interruption
Khagrachori | 132/33kV transformer TR-2 HT | 2023-06-08 09:56 | 2023-06-08 13:59 | 4:03 | T | Tripped showing Differential relay | 0 | 0 | No interruption
Juldah | 132/33 KV transformer T-2 416T HT | 2023-06-09 11:15 | 2023-06-09 12:41 | 1:26 | E/O | Due to Emergency work | 0 | 0 | No interruption
Juldah | 132/33 KV transformer T-2 416T LT | 2023-06-09 11:18 | 2023-06-09 12:46 | 1:28 | E/O | Due to Emergency work | 0 | 0 | No interruption
Halishahar | 132/33kV transformer 413T(TR-2) HT | 2023-06-10 07:23 | 2023-06-10 08:04 | 0:41 | T | Tripped showing O/C relay. | 23 | 0 | Power interruption
Halishahar | 132/33kV transformer 413T(TR-2) LT | 2023-06-10 07:23 | 2023-06-10 08:10 | 0:47 | T | Tripped showing O/C relay. | 23 | 18.0167 | Power interruption
Khagrachori | 132/33kV transformer TR-2 HT | 2023-06-15 10:08 | 2023-06-15 12:16 | 2:08 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Dohazari | 132/33kV transformer -T-1 | 2023-06-17 22:43 | 2023-06-17 23:34 | 0:51 | E/O | Due to red hot maintanance.at 33 kV side | 0 | 0 | No interruption
Dohazari | 230/132 kV transformer MT-04 LT & HT | 2023-06-19 06:40 | 2023-06-19 06:40 | 0:00 | T | Tripped showing RET 670 relays. | 0 | 0 | No interruption
Hathazari | 230/132/kV transformer MT-04 HT & LT | 2023-06-19 07:28 | 2023-06-19 10:37 | 3:09 | T | Tripped showing RET 670 relays. | 0 | 0 | No interruption
Madunaghat | 132/33kV transformer TR-1(507T) HT | 2023-06-25 08:52 | 2023-06-25 10:42 | 1:50 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Madunaghat | 132/33kV transformer TR-2(507T) LT | 2023-06-25 11:44 | 2023-06-25 11:44 | 0:00 | E/O | Due to Emergency work | 0 | 0 | No interruption
Madunaghat | 132/33kV transformer TR-2(507T) HT | 2023-06-25 12:04 | 2023-06-25 16:52 | 4:48 | E/O | Due to Emergency work | 0 | 0 | No interruption
Dohazari | 132/33kV transformer -T-1 LT | 2023-06-26 23:14 | 2023-06-27 00:03 | 0:49 | E/O | Due to red hot maintanance.at 33 kV side | 19 | 0 | Power interruption
Dohazari | 132/33kV transformer -T-1 HT | 2023-06-26 23:15 | 2023-06-27 00:02 | 0:47 | E/O | Due to red hot maintanance.at 33 kV side | 19 | 14.8833 | Power interruption
Dohazari | 132/33kV transformer -T-2 LT | 2023-06-27 12:28 | 2023-06-27 13:56 | 1:28 | E/O | Due to Emergency work by BPDB | 18 | 26.4 | Power interruption
Chandraghona | 132/33kV transformer-01(406T) LT | 2023-06-30 10:42 | 2023-06-30 11:33 | 0:51 | T | Tripped showing O/C relay. | 23 | 19.55 | Power interruption
|  |  | Total : | 25:24 |  | Unserved Energy: |  | 78.85
Cumilla Grid Circle :
Sylhet | 132/33kV transformer T4 LT | 2023-06-01 16:48 | 2023-06-01 17:35 | 0:47 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Chandpur | 132/33kV transformer 422T LT & HT | 2023-06-02 07:20 | 2023-06-02 10:16 | 2:56 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformer TR-02 LT | 2023-06-03 06:47 | 2023-06-03 07:06 | 0:19 | T | Tripped showing O/C relay.at 33 kV side | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformer TR-04 LT | 2023-06-03 06:47 | 2023-06-03 07:06 | 0:19 | T | Tripped showing O/C relay.at 33 kV side | 0 | 0 | No interruption
Ashuganj | 230/132/33kV transformer T-3 LT | 2023-06-03 13:05 | 2023-06-03 14:38 | 1:33 | T | Tripped showing Instantaneous relays | 0 | 0 | No interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-05 16:41 | 2023-06-06 01:03 | 8:22 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-06 13:25 | 2023-06-06 14:02 | 0:37 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-06 18:54 | 2023-06-06 21:46 | 2:52 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-07 13:20 | 2023-06-07 13:58 | 0:38 | T | Tripped showing O/C relay. | 0 | 0 | No interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-07 14:58 | 2023-06-07 15:37 | 0:39 | T | Tripped showing 50/51. relays. | 0 | 0 | No interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-07 18:52 | 2023-06-07 18:52 | 0:00 | T | Tripped showing 50/51. relays. | 0 | 0 | No interruption
Beanibazar | 132/33kV transformer TR-02 LT | 2023-06-08 04:24 | 2023-06-08 05:02 | 0:38 | E/O | Due to Emergency maint.work | 23 | 14.5667 | Power interruption
Beanibazar | 132/33kV transformer TR-01 LT | 2023-06-08 04:24 | 2023-06-08 05:02 | 0:38 | E/O | Due to Emergency maint.work | 23 | 14.5667 | Power interruption
Ashuganj | 132kV bus coupler | 2023-06-08 14:33 | 2023-06-08 15:10 | 0:37 | T | Tripped showing no relay | 0 | 0 | No interruption
Chowmuhani | 132/33kV transformer TR2-425T HT | 2023-06-08 20:20 | 2023-06-08 21:40 | 1:20 | E/O | Due to red hot maintanance.at 33 kV side | 25 | 33.3333 | Power interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-08 23:23 | 2023-06-09 02:05 | 2:42 | T | Tripped showing 51/50 relays Due to Over Load | 0 | 0 | No interruption
Kulaura | 132/33kV transformer TR-1 LT | 2023-06-09 07:13 | 2023-06-09 08:35 | 1:22 | E/O | Due to red hot maintanance. | 18 | 24.6 | Power interruption
Kulaura | 132/33kV transformer TR-1 HT | 2023-06-09 07:13 | 2023-06-09 08:34 | 1:21 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Chhatak | 132/33kV transformer T-1 LT | 2023-06-11 20:33 | 2023-06-11 20:38 | 0:05 | T | Tripped showing 33 kV feeder fault | 0 | 0 | No interruption
Fenchuganj | 230/132kV transformer TR-01 | 2023-06-12 09:09 | 2023-06-12 09:15 | 0:06 | T | Tripped showing REC650 relays Due to Bad weather. | 10 | 1 | Power interruption
Feni | 132/33kV transformer T-2(415T) HT | 2023-06-13 15:26 | 2023-06-13 15:50 | 0:24 | E/O | Due to Emergency maint.work | 50 | 20 | Power interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-13 22:29 | 2023-06-13 23:58 | 1:29 | T | Tripped showing 51/50 ( O/C) relay | 0 | 0 | No interruption
Chhatak | 132/33kV transformer T-2 HT | 2023-06-15 21:00 | 2023-06-15 23:17 | 2:17 | E/O | Due to red hot maintanance.at 33 kV side | 0 | 0 | No interruption
Chhatak | 132/33kV transformer T-2 LT | 2023-06-15 21:00 | 2023-06-15 23:18 | 2:18 | E/O | Due to red hot maintanance.at 33 kV side | 1.5 | 3.45 | Power interruption
Sylhet | 132/33kV transformer T1 LT & HT | 2023-06-16 08:22 | 2023-06-16 08:49 | 0:27 | E/O | Due to red hot maintanance.at 33 kV side | 16 | 7.2 | Power interruption
Sreemongol | 132/33kV transformer T-2 LT & HT | 2023-06-16 12:16 | 2023-06-16 12:30 | 0:14 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Sreemongol | 132/33kV transformer T-2 LT | 2023-06-16 14:22 | 2023-06-16 14:48 | 0:26 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Sreemongol | 132/33kV transformer T-2 HT | 2023-06-16 14:48 | 2023-06-16 14:49 | 0:01 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Sreemongol | 132/33kV transformer T-3 HT | 2023-06-16 14:48 | 2023-06-16 14:48 | 0:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Cumilla(S) | 132/33kV transformer TR-1 LT | 2023-06-17 21:18 | 2023-06-17 21:28 | 0:10 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T-05 HT & LT | 2023-06-18 20:33 | 2023-06-18 21:10 | 0:37 | E/O | Due to red hot maintanance.at 33 kV side | 15 | 9.25 | Power interruption
Brahmanbaria | 132/33kV transformer 403T LT | 2023-06-19 13:49 | 2023-06-19 17:02 | 3:13 | E/O | Due to Emergency maint.work at 33 kV feeder fault | 0 | 0 | No interruption
Brahmanbaria | 132/33kV transformer 402T LT | 2023-06-19 13:49 | 2023-06-19 13:56 | 0:07 | E/O | Due to Emergency maint.work at 33 kV feeder fault | 30 | 3.5 | Power interruption
Fenchuganj | 230/132kV transformer TR-02 HT | 2023-06-19 21:50 | 2023-06-20 16:54 | 19:04 | E/O | Tripped showing MCGG relays Due to Cable earth fault | 6 | 15.1 | Power interruption 09:42 to 12:13
Sreemongol | 132/33kV transformer T-2 HT | 2023-06-21 21:36 | 2023-06-21 21:50 | 0:14 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ramganj | 132/33kV transformer -02 LT | 2023-06-24 07:23 | 2023-06-24 09:23 | 2:00 | E/O | Due to red hot maintanance. | 20 | 40 | Power interruption
Sylhet | 132/33kV transformer T4 LT | 2023-06-24 11:31 | 2023-06-24 11:35 | 0:04 | T | Tripped showing 50/51 relays Due to Over current | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T-05 HT | 2023-06-30 10:07 | 2023-06-30 11:32 | 1:25 | E/O | Due to Emergency maint.work | 18 | 25.5 | Power interruption
Chowmuhani | 132/33kV transformer TR-2 425T HT | 2023-06-30 19:55 | 2023-06-30 20:20 | 0:25 | T | Tripped showing Directional O/C relay | 55 | 22.9167 | Power interruption
Chowmuhani | 132/33kV transformer TR1-415T LT | 2023-06-30 19:55 | 2023-06-30 20:20 | 0:25 | T | Tripped showing Instt E/F relay | 0 | 0 | No interruption
Chowmuhani | 132/33kV transformer TR-2 425T HT | 2023-06-30 20:30 | 2023-06-30 20:30 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 63:48 |  | Unserved Energy: |  | 234.9833
Khulna Grid Circle :
Khulna (C) | 132/33 transformer Tr-3 405T LT | 2023-06-01 00:35 | 2023-06-01 00:55 | 0:20 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Bagerhat | 132/33k transformer-3 ( 423 T) LT | 2023-06-01 07:07 | 2023-06-01 08:30 | 1:23 | E/O | Due to red hot maintanance.at 33 kV side | 0 | 0 | No interruption
Bagerhat | 132/33kV transformer-3 ( 423 T) HT | 2023-06-01 07:08 | 2023-06-01 08:29 | 1:21 | E/O | Due to red hot maintanance.at 33 kV side | 0 | 0 | No interruption
Narail | 132/33kV Capacitor Bank | 2023-06-03 19:26 | 2023-06-04 12:52 | 17:26 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Barishal | 230/132kV transformer ATR-2 LT | 2023-06-04 07:19 | 2023-06-04 07:19 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Mongla | 132/33kV transformer T-2 LT | 2023-06-07 19:00 | 2023-06-07 19:43 | 0:43 | T | Tripped showing 50/51(OC/EF) relays Due to Birds burning. | 12.5 | 8.9583 | Power interruption
Mongla | 132/33kV transformer T-1 LT | 2023-06-07 19:00 | 2023-06-07 19:42 | 0:42 | T | Tripped showing 50/51(OC/EF) relays Due to Birds burning. | 12.5 | 8.75 | Power interruption
Noapara | 132/33kV transformer T-2 LT | 2023-06-07 20:36 | 2023-06-07 21:15 | 0:39 | E/O | Due to red hot maintanance.at REB feeder | 17 | 0 | Power interruption
Noapara | 132/33kV transformer T-2 HT | 2023-06-07 20:38 | 2023-06-07 21:13 | 0:35 | E/O | Due to red hot maintanance.at REB feeder | 17 | 9.9167 | Power interruption
Barishal | 230/132kV transformer ATR-2 LT | 2023-06-08 14:29 | 2023-06-08 21:27 | 6:58 | E/O | Due to abnormally rise of temperature | 0 | 0 | No interruption
Barishal | 132/33kV transformers T-1,T-2 LT | 2023-06-12 15:02 | 2023-06-12 15:05 | 0:03 | T | Tripped showing E/F, Deff. O/C relays | 43 | 2.15 | Power interruption
Khulna (C) | 132/33 transformer TR-1 425T HT | 2023-06-13 07:30 | 2023-06-13 08:47 | 1:17 | E/O | Due to Emergency maint.work | 15 | 19.25 | Power interruption
Khulna (C) | 132/33 transformer TR-1 425T LT | 2023-06-13 07:30 | 2023-06-13 08:48 | 1:18 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Narail | 132/33kV transformer TR1 (403-T) LT | 2023-06-13 16:12 | 2023-06-13 18:16 | 2:04 | E/O | Due to red hot maintanance.at PBS | 4 | 8.2667 | Power interruption
Narail | 132/33kV transformer TR1 (403-T) HT | 2023-06-13 16:13 | 2023-06-13 18:14 | 2:01 | E/O | Due to red hot maintanance.at PBS | 4 | 0 | Power interruption
Narail | 132/33kV transformer TR2 (413-T) HT | 2023-06-13 18:18 | 2023-06-13 18:34 | 0:16 | T | Due to 33 kV feeder fault | 5 | 1.3333 | Power interruption
Narail | 132/33kV transformer TR1 (403-T) LT | 2023-06-13 18:18 | 2023-06-13 18:38 | 0:20 | T | Due to 33 kV feeder fault | 5 | 0 | Power interruption
Narail | 132/33kV transformer TR2 (413-T) LT | 2023-06-13 18:18 | 2023-06-13 18:36 | 0:18 | T | Due to 33 kV feeder fault | 5 | 0 | Power interruption
Narail | 132/33kV transformer TR1 (403-T) HT | 2023-06-13 18:18 | 2023-06-13 18:37 | 0:19 | T | Due to 33 kV feeder fault | 5 | 1.5833 | Power interruption
Gopalganj | 132/33kV transformer T2 LT | 2023-06-13 19:42 | 2023-06-13 20:13 | 0:31 | T | Due to PBS kV feeder fault | 25 | 12.9167 | Power interruption
Gopalganj | 132/33kV transformer T1 HT | 2023-06-13 19:42 | 2023-06-14 14:33 | 18:51 | T | Due to PBS kV feeder fault | 25 | 471.25 | Power interruption
Mongla | 132/33kV transformer T-1 LT | 2023-06-14 19:28 | 2023-06-14 19:54 | 0:26 | T | Due to 33 kV feeder fault | 11 | 4.7667 | Power interruption
Mongla | 132/33kV transformer T-2 LT | 2023-06-14 19:28 | 2023-06-14 19:56 | 0:28 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Madaripur | 132/33kV transformerT2-415T LT | 2023-06-15 23:35 | 2023-06-16 00:21 | 0:46 | E/O | Due to red hot maintanance.at 33 kV feeder | 38 | 29.1333 | Power interruption
Madaripur | 132/33kV transformerT2-415T HT | 2023-06-15 23:35 | 2023-06-16 00:20 | 0:45 | E/O | Due to red hot maintanance.at 33 kV feeder | 0 | 0 | No interruption
Gopalganj | 132/33kV transformer T-1 LT | 2023-06-16 07:19 | 2023-06-16 07:31 | 0:12 | T | Tripped showing O/C relay | 25 | 5 | Power interruption
Gopalganj | 132/33kV transformer T-1 HT | 2023-06-16 07:19 | 2023-06-16 07:30 | 0:11 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Barishal | 132/33kV transformer T-1 (405T) LT | 2023-06-17 01:22 | 2023-06-17 01:34 | 0:12 | T | Due to 33 kV feeder fault | 90 | 18 | Power interruption
Barishal | 132/33kV transformer T-2 (415T) HT | 2023-06-17 01:22 | 2023-06-17 01:35 | 0:13 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Barishal | 132/33kV transformer T-2 (415T) LT | 2023-06-17 01:22 | 2023-06-17 01:37 | 0:15 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T2 LT | 2023-06-17 07:07 | 2023-06-17 09:17 | 2:10 | E/O | Due to red hot maint.work | 20 | 43.3333 | Power interruption
Satkhira | 132/33 kV transformer T2 HT | 2023-06-17 07:08 | 2023-06-17 07:08 | 0:00 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Faridpur | 132/33kV transformer-2 LT | 2023-06-17 08:00 | 2023-06-17 10:12 | 2:12 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T2(413) LT | 2023-06-19 14:06 | 2023-06-19 14:51 | 0:45 | E/O | Due to Emergency maint.work | 7 | 5.25 | Power interruption
Madaripur | 132/33kV transformer T1-405T HT | 2023-06-20 07:42 | 2023-06-20 07:42 | 0:00 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Bhandaria | 132/33kV transformer T-2 LT | 2023-06-20 07:55 | 2023-06-20 08:48 | 0:53 | E/O | Due to red hot maint.work | 18 | 15.9 | Power interruption
Madaripur | 132/33kV transformer T2-415T HT | 2023-06-22 17:21 | 2023-06-22 18:15 | 0:54 | E/O | Due to red hot maint.work at 33 kV | 0 | 0 | No interruption
Barishal | 132/33kV transformer T-1 (405T) LT & HT | 2023-06-24 08:05 | 2023-06-24 08:57 | 0:52 | E/O | Due to red hot maint.work at 33 kV | 25 | 21.6667 | Power interruption
Barishal | 230/132kV transformer T-5 HT | 2023-06-26 06:41 | 2023-06-26 08:43 | 2:02 | E/O | Due to red hot maint.work | 20 | 40.6667 | Power interruption
Barishal | 230/132kV transformer T-5 LT | 2023-06-26 06:41 | 2023-06-26 08:45 | 2:04 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Barishal | 230/132kV transformer T-4 LT | 2023-06-26 09:08 | 2023-06-26 11:13 | 2:05 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Barishal | 230/132kV transformer T-4 HT | 2023-06-26 09:08 | 2023-06-26 11:10 | 2:02 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Narail | 132/33kV transformer TR2 (413-T) LT | 2023-06-27 06:38 | 2023-06-27 06:38 | 0:00 | E/O | Due to red hot maint.work at 33 kV | 0 | 0 | No interruption
Narail | 132/33kV transformer TR2 (413-T) HT | 2023-06-27 06:39 | 2023-06-27 08:19 | 1:40 | E/O | Due to red hot maint.work at 33 kV | 18 | 30 | Power interruption
Mongla | 132/33kV transformer T-2 HT | 2023-06-28 00:31 | 2023-06-28 09:32 | 9:01 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Mongla | 132/33kV transformer T-2 LT | 2023-06-28 00:31 | 2023-06-28 09:33 | 9:02 | T | Tripped showing Lockout relay | 0 | 0 | No interruption
Goalpara | 132/33kV transformer T-5 LT | 2023-06-28 18:20 | 2023-06-28 18:20 | 0:00 | E/O | Due to fuse change of 33 kV Bus PT | 0 | 0 | No interruption
Goalpara | 132/33kV transformer T-5 HT | 2023-06-28 18:19 | 2023-06-28 18:20 | 0:01 | E/O | Due to fuse change of 33 kV Bus PT | 0 | 0 | No interruption
Goalpara | 132/33kV transformer T-6 LT | 2023-06-28 18:17 | 2023-06-28 18:17 | 0:00 | E/O | Due to fuse change of 33 kV Bus PT | 0 | 0 | No interruption
Goalpara | 132/33kV transformer T-6 HT | 2023-06-28 18:16 | 2023-06-28 18:16 | 0:00 | E/O | Due to fuse change of 33 kV Bus PT | 0 | 0 | No interruption
Barishal | 132/33kV transformers T-1 & T2 | 2023-06-29 09:12 | 2023-06-29 09:27 | 0:15 | T | Tripped showing O/C & E/F relay | 34 | 8.5 | Power interruption
|  |  | Total : | 113:45 |  | Unserved Energy: |  | 766.5917
HVDC Grid Circle :
Bheramara(GK) | Bheramara(GK) 132/33kV S/S TR-2 HT | 2023-06-01 09:41 | 2023-06-01 10:13 | 0:32 | E/O | Due to Emergency maint.work of 33 kV side | 0 | 0 | No interruption
Bheramara(GK) | Bheramara(GK) 132/33kV S/S TR-2 LT | 2023-06-01 09:42 | 2023-06-01 10:14 | 0:32 | E/O | Due to Emergency maint.work of 33 kV side | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-4(435T) LT | 2023-06-01 14:50 | 2023-06-01 16:05 | 1:15 | E/O | Due to Emergency maint.work of PBS | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-4(435T) HT | 2023-06-01 14:50 | 2023-06-01 16:00 | 1:10 | E/O | Due to Emergency maint.work of PBS | 0 | 0 | No interruption
BIPTC | BIPTC S/S 10CF15 | 2023-06-02 17:21 | 2023-06-02 17:53 | 0:32 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
BIPTC | BIPTC S/S 20DF13 | 2023-06-04 10:53 | 2023-06-04 11:27 | 0:34 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Kushtia | 132/33kV transformer T-1 LT | 2023-06-08 06:35 | 2023-06-08 07:57 | 1:22 | E/O | Due to red hot maint.work | 0 | 0 | Power interruption
Kushtia | 132/33kV transformer T-1 HT | 2023-06-08 06:36 | 2023-06-08 07:56 | 1:20 | E/O | Due to red hot maint.work | 30 | 40 | Power interruption
Jashore | 132/33kV transformer T-3 HT | 2023-06-08 08:11 | 2023-06-08 08:45 | 0:34 | T | Tripped showing O/C relay | 30 | 17 | Power interruption
Ishurdi | 132/33kV transformer T-2 LT & HT | 2023-06-09 07:18 | 2023-06-09 08:35 | 1:17 | E/O | Due to red hot maint. | 56 | 71.8667 | Power interruption
Jhenaidah | 132/33kV transformer T-1 HT | 2023-06-11 06:00 | 2023-06-11 08:29 | 2:29 | E/O | Due to Emergency maint.work | 30 | 74.5 | Power interruption
Jhenaidah | 132/33kV transformer T-1 LT | 2023-06-11 06:00 | 2023-06-11 08:29 | 2:29 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Jhenaidah | 132/33kV transformer T-2 HT | 2023-06-14 17:55 | 2023-06-14 18:13 | 0:18 | T | Tripped showing O/C relay | 0 | 0 | Power interruption
Jhenaidah | 132/33kV transformer T-2 LT | 2023-06-14 17:55 | 2023-06-14 18:13 | 0:18 | T | Tripped showing O/C relay | 20 | 6 | Power interruption
Chuadanga | 132/33kV transformer Tr-1 HT | 2023-06-14 22:22 | 2023-06-14 23:49 | 1:27 | E/O | Due to red hot maint.work | 45 | 65.25 | Power interruption
Shahjadpur | 132/33kV transformer T-2(415T) HT | 2023-06-16 21:25 | 2023-06-16 22:27 | 1:02 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-2(415T) HT | 2023-06-16 21:25 | 2023-06-16 22:29 | 1:04 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
BIPTC | BIPTC 20DF13 | 2023-06-17 10:42 | 2023-06-17 11:12 | 0:30 | T | Due to Tripped by impedance 21R | 0 | 0 | No interruption
Jhenaidah | 132/33kV transformer T-1 HT | 2023-06-18 10:11 | 2023-06-18 10:40 | 0:29 | E/O | Due to Emergency maint.work | 40 | 0 | Power interruption
Jhenaidah | 132 kV Bus-A | 2023-06-18 10:13 | 2023-06-18 10:38 | 0:25 | E/O | Due to Emergency maint.work | 40 | 0 | Power interruption
Jhenaidah | 132 kV Bus-B | 2023-06-18 10:14 | 2023-06-18 10:41 | 0:27 | E/O | Due to Emergency maint.work | 40 | 18 | Power interruption
Ruppur | 132/11kV transformerTR-02 LT | 2023-06-19 11:30 | 2023-06-19 11:30 | 0:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Jashore | 132/33kV transformer T-3 LT | 2023-06-19 12:40 | 2023-06-19 12:40 | 0:00 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ishurdi | 132/33kV transformer T-2 | 2023-06-19 13:14 | 2023-06-19 16:47 | 3:33 | T | Tripped showing no relay | 75 | 266.25 | Power interruption
Ishurdi | 132/33kV transformer T-2 HT | 2023-06-19 13:48 | 2023-06-19 16:47 | 2:59 | E/O | Due to Emergency maint.work | 50 | 149.1667 | Power interruption
Shahjadpur | 132/33kV transformer T-2(415T) HT | 2023-06-19 21:43 | 2023-06-19 22:42 | 0:59 | E/O | Due to red hot maint.work | 0 | 0 | No interruption
Jhenaidah | 132/33kV transformer T-2 HT & LT | 2023-06-20 13:53 | 2023-06-20 14:02 | 0:09 | T | Tripped showing 50/51N OC-gnd relays. | 40 | 6 | Power interruption
Jhenaidha (Old) | 132/33kV transformer T-2 | 2023-06-20 13:53 | 2023-06-20 13:53 | 0:00 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-2(415T) HT & LT | 2023-06-20 16:37 | 2023-06-20 17:09 | 0:32 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-2(415T) LT | 2023-06-21 17:58 | 2023-06-21 21:30 | 3:32 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Chuadanga | 132/33kV transformer T1(416T) HT | 2023-06-22 07:22 | 2023-06-22 08:34 | 1:12 | E/O | Due to Emergency maint.work | 45 | 54 | Power interruption
Jhenaidah | 132/33kV transformer T-1 LT | 2023-06-25 15:31 | 2023-06-25 16:59 | 1:28 | E/O | Due to red hot maint.work at 33 kV side | 30 | 44 | Power interruption
Jhenaidah | 132/33kV transformer T-1 HT | 2023-06-25 15:32 | 2023-06-25 16:59 | 1:27 | E/O | Due to red hot maint.work at 33 kV side | 0 | 0 | No interruption
Jashore | 132/33kV transformer T-1 LT & HT | 2023-06-27 07:20 | 2023-06-27 12:24 | 5:04 | E/O | Due to red hot maint. | 0 | 0 | No interruption
BIPTC | BIPTC 20DF22 | 2023-06-27 18:03 | 2023-06-27 20:37 | 2:34 | T | Due to Capacitor unbalance | 0 | 0 | No interruption
BIPTC | BIPTC 20DF22 | 2023-06-27 20:13 | 2023-06-27 20:37 | 0:24 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-1 LT | 2023-06-30 03:50 | 2023-06-30 07:15 | 3:25 | T | Due to 33 CB fault | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-1(405) HT | 2023-06-30 07:16 | 2023-06-30 20:55 | 13:39 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-1(405) LT | 2023-06-30 07:20 | 2023-06-30 07:20 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 61:03 |  | Unserved Energy: |  | 812.0333
Bogura Grid Circle:
Naogaon | 132/33kV transformer T-1 LT | 2023-06-01 22:02 | 2023-06-01 22:59 | 0:57 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Naogaon | 132/33kV transformerT-1 HT | 2023-06-01 22:03 | 2023-06-01 22:58 | 0:55 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Mahasthangarh | 132/33kV transformer 416T MTR 2 LT | 2023-06-06 11:20 | 2023-06-06 11:46 | 0:26 | T | Due to PBS feeder Fault. | 24 | 10.4 | Power interruption
Mahasthangarh | 132/33kV transformer 416T MTR 1 LT | 2023-06-06 11:20 | 2023-06-06 11:46 | 0:26 | T | Due to PBS feeder Fault. | 0 | 0 | No interruption
Bogura | 230/132kV transformer T-02 HT & LT | 2023-06-07 17:50 | 2023-06-07 18:55 | 1:05 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Niamatpur | 132/33kV transformer 417T LT | 2023-06-07 23:07 | 2023-06-07 23:58 | 0:51 | E/O | Due to red-hot maint.at 33 kV side | 25 | 21.25 | Power interruption
Niamatpur | 132/33kV transformer 417T HT | 2023-06-07 23:08 | 2023-06-07 23:57 | 0:49 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Naogaon | 132/33kV transformer T-2 LT | 2023-06-09 08:45 | 2023-06-09 09:43 | 0:58 | E/O | Due to red-hot maint. | 20 | 0 | Power interruption
Naogaon | 132/33kV transformer T-2 HT | 2023-06-09 08:46 | 2023-06-09 09:42 | 0:56 | E/O | Due to red-hot maint. | 20 | 18.6667 | Power interruption
Joypurhat | 132/33kV transformer T-4 (437 T) HT | 2023-06-10 00:58 | 2023-06-10 01:10 | 0:12 | T | Tripped showing No relay | 0 | 0 | No interruption
Joypurhat | 132/33kV transformer T-4 (437 T) LT | 2023-06-10 01:03 | 2023-06-10 01:12 | 0:09 | T | Tripped showing No relay | 0 | 0 | No interruption
Joypurhat | 132/33kV transformer T-4 (437 T) HT | 2023-06-10 01:20 | 2023-06-10 09:40 | 8:20 | E/O | Due to Breaker problem | 0 | 0 | No interruption
Purbasadipur | 132/33kV transformer T-3 LT | 2023-06-12 06:04 | 2023-06-12 06:54 | 0:50 | T | Tripped showing ALSTOM relay. | 25 | 20.8333 | Power interruption
Purbasadipur | 132/33kV transformer T1 HT | 2023-06-12 06:04 | 2023-06-12 06:58 | 0:54 | T | Tripped showing ALSTOM relay. | 40 | 36 | Power interruption
Sirajganj | 132/33kV transformer T-4 | 2023-06-12 20:07 | 2023-06-12 21:03 | 0:56 | E/O | Due to red-hot maint. | 26 | 24.2667 | Power interruption
Purbasadipur | 132/33kV transformer T-3 LT | 2023-06-13 13:06 | 2023-06-13 13:34 | 0:28 | E/O | Due to bursting of L/A at 33 kV side | 20 | 9.3333 | Power interruption
Purbasadipur | 132/33kV transformer T-1 HT | 2023-06-13 13:06 | 2023-06-13 13:40 | 0:34 | E/O | Due to bursting of L/A at 33 kV side | 40 | 0 | Power interruption
Purbasadipur | 132/33kV transformer T-1 LT | 2023-06-13 13:06 | 2023-06-13 13:48 | 0:42 | E/O | Due to bursting of L/A at 33 kV side | 40 | 28 | Power interruption
Niamatpur | 132/33kV transformer 426T LT | 2023-06-13 23:20 | 2023-06-13 23:40 | 0:20 | T | Tripped showing MiCom P-127 relays Due to stormy rain. | 16 | 5.3333 | Power interruption
Kurigram | 132 kV Capacitor Bank | 2023-06-13 23:32 | 2023-06-13 23:32 | 0:00 | T | Tripped showing ABB SPAJ 160C relay | 0 | 0 | No interruption
Niamatpur | 132/33kV transformer 417T LT | 2023-06-14 00:23 | 2023-06-14 00:45 | 0:22 | T | Tripped showing SIEMENS | 15 | 5.5 | Power interruption
Niamatpur | 132/33kV transformer 417T LT | 2023-06-14 02:16 | 2023-06-14 02:45 | 0:29 | T | Due to 33 kV feeder fault | 3 | 1.45 | Power interruption
Niamatpur | 132/33kV transformer T-2 417T LT | 2023-06-14 10:08 | 2023-06-14 12:25 | 2:17 | E/O | Due to Emergency maint.work at 33 kV feeder | 7 | 15.9833 | Power interruption
Niamatpur | 132/33kV transformer T-2 (425T) HT | 2023-06-14 10:08 | 2023-06-14 12:24 | 2:16 | E/O | Due to Emergency maint.work at 33 kV feeder | 7 | 0 | Power interruption
Chapai | 132/33kV transformer T-3 (425T) HT | 2023-06-14 07:29 | 2023-06-14 14:48 | 7:19 | E/O | Due SF6 gas leakage | 0 | 0 | No interruption
Niamatpur | 132/33kV transformer 426 LT | 2023-06-16 06:10 | 2023-06-16 06:23 | 0:13 | T | Due to 33 kV feeder fault | 16 | 3.4667 | Power interruption
Niamatpur | 132/33kV transformer 417T LT | 2023-06-17 08:05 | 2023-06-17 09:48 | 1:43 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Purbasadipur | 132/33kV transformer T-1 LT | 2023-06-17 11:35 | 2023-06-17 11:42 | 0:07 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Mahasthangarh | 132/33kV transformers T1, & T2 | 2023-06-17 14:05 | 2023-06-17 14:49 | 0:44 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Bogura | 132/33kV transformer T-4 HT | 2023-06-17 20:13 | 2023-06-17 21:17 | 1:04 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Panchagarh | 132KV Capacitor Bank | 2023-06-18 06:05 | 2023-06-18 11:30 | 5:25 | T | Due to storm suddenly. | 0 | 0 | No interruption
Niamatpur | 132/33kV transformer 407T HT & LT | 2023-06-18 07:28 | 2023-06-18 09:54 | 2:26 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Mahasthangarh | 132/33kV transformer 406T MTR1 HT | 2023-06-18 15:08 | 2023-06-18 16:23 | 1:15 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Mahasthangarh | 132/33kV transformer 406T MTR1 LT | 2023-06-18 15:08 | 2023-06-18 16:24 | 1:16 | E/O | Due to Emergency maint.work | 10 | 12.6667 | Power interruption
Rajshahi | 230/132/33kV transformer T-02 (416T) LT | 2023-06-18 15:53 | 2023-06-18 16:53 | 1:00 | T | Tripped showing REF630 relays. | 10 | 10 | Power interruption
Purbasadipur | 132/33kV transformer(423T) T-3 LT | 2023-06-18 17:56 | 2023-06-18 18:38 | 0:42 | T | Tripped showing derectional O/C relay | 18 | 0 | Power interruption
Purbasadipur | 132/33kV transformer T-3 (423T) HT | 2023-06-18 17:56 | 2023-06-18 18:36 | 0:40 | T | Tripped showing Lockout relay | 18 | 12 | Power interruption
Purbasadipur | 132/33kV transformer(423T) T-3 HT | 2023-06-19 07:26 | 2023-06-19 08:38 | 1:12 | T | Tripped showing MCCG,Alstom relays. | 0 | 0 | No interruption
Bog-Sherpur | 132/33kV transformer-1 (404T) HT | 2023-06-19 07:32 | 2023-06-19 09:18 | 1:46 | E/O | Due to red-hot maint.at 33 kV side | 55 | 97.1667 | Power interruption
Bog-Sherpur | 132/33kV transformer-2 (414T) HT | 2023-06-19 07:33 | 2023-06-19 09:19 | 1:46 | E/O | Due to red-hot maint.at 33 kV side | 55 | 97.1667 | Power interruption
Sirajganj | 132/33kV transformer T4-(445) HT | 2023-06-19 08:55 | 2023-06-19 10:10 | 1:15 | E/O | Due to Emergency maint.work | 14 | 17.5 | Power interruption
Naogaon | 132/33kV transformer-2 LT | 2023-06-19 12:11 | 2023-06-19 12:58 | 0:47 | E/O | Due to red-hot maint. | 18 | 14.1 | Power interruption
Naogaon | 132/33kV transformer-2 HT | 2023-06-19 12:12 | 2023-06-19 12:57 | 0:45 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Mahasthangarh | 132/33kV transformer 406T MTR1 LT | 2023-06-19 16:19 | 2023-06-19 17:22 | 1:03 | E/O | Due to Emergency maint.work | 10 | 10.5 | Power interruption
Mahasthangarh | 132/33kV transformer 406T MTR1 HT | 2023-06-19 16:20 | 2023-06-19 17:21 | 1:01 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Palashbari | 132/33kV transformer TR2-(404T) LT & HT | 2023-06-20 07:03 | 2023-06-20 08:13 | 1:10 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Mithapukur | 132/33kV transformer TR2-(414T) LT | 2023-06-21 22:40 | 2023-06-21 23:18 | 0:38 | T | Tripped showing O/C relay | 28 | 17.7333 | Power interruption
Mithapukur | 132/33kV transformer TR1-(414T) LT | 2023-06-21 22:40 | 2023-06-21 23:21 | 0:41 | T | Tripped showing Diff. relay | 28 | 19.1333 | Power interruption
Purbasadipur | 132/33kV transformer T-3 (423T) LT | 2023-06-25 06:45 | 2023-06-25 07:17 | 0:32 | T | Tripped showing ALSTHOM MCGG relays | 22 | 11.7333 | Power interruption
Purbasadipur | 132/33kV transformer T-3 (423T) HT | 2023-06-25 06:45 | 2023-06-25 07:15 | 0:30 | T | Tripped showing ALSTHOM MCGG relays | 0 | 0 | No interruption
Purbasadipur | 132/33kV transformer T-3 (423T) LT | 2023-06-25 11:35 | 2023-06-25 12:52 | 1:17 | E/O | Due to Emergency maint.work at 33 kV feeder | 8 | 10.2667 | Power interruption
Purbasadipur | 132/33kV transformer T-3 (423T) HT | 2023-06-25 12:36 | 2023-06-25 12:50 | 0:14 | E/O | Due to Emergency maint.work at 33 kV feeder | 0 | 0 | No interruption
Panchagarh | 132/33kV transformer 407T HT | 2023-06-25 15:49 | 2023-06-25 17:05 | 1:16 | E/O | Due to red-hot maint.at 33 kV side | 15 | 19 | Power interruption
Panchagarh | 132/33kV transformer 407T LT | 2023-06-25 15:49 | 2023-06-25 17:06 | 1:17 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Panchagarh | 33 kV Bus | 2023-06-25 15:52 | 2023-06-25 16:58 | 1:06 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Naogaon | 132/33kV transformer T2 LT | 2023-06-26 06:27 | 2023-06-26 07:07 | 0:40 | T | Tripped showing Inst. E/F relay | 31 | 20.6667 | Power interruption
Naogaon | 132/33kV transformer T1 LT | 2023-06-26 06:27 | 2023-06-26 07:09 | 0:42 | T | Tripped showing O/C &. E/F relay | 0 | 0 | No interruption
Naogaon | 132/33kV transformer T1 LT | 2023-06-26 10:44 | 2023-06-26 14:29 | 3:45 | E/O | Due to Flashing of T1 132 kV DS 404s. | 0 | 0 | No interruption
Naogaon | 132/33kV transformer T1 HT | 2023-06-26 10:45 | 2023-06-26 14:31 | 3:46 | E/O | Due to Flashing of T1 132 kV DS 404s. | 0 | 0 | No interruption
Natore | 132/33kV transformer TR-1(415) LT | 2023-06-27 07:31 | 2023-06-27 08:40 | 1:09 | E/O | Due to red-hot maint. | 30 | 34.5 | Power interruption
Natore | 132/33kV transformer TR-2(415) LT | 2023-06-27 07:31 | 2023-06-27 08:40 | 1:09 | E/O | Due to red-hot maint. | 30 | 34.5 | Power interruption
Rajshahi | 230/132/33kV transformer T-02 (416T) LT | 2023-06-27 11:54 | 2023-06-27 13:09 | 1:15 | E/O | Due to Emergency maint.work | 15 | 18.75 | Power interruption
Natore | 132/33kV transformer TR-4 LT | 2023-06-28 06:58 | 2023-06-28 06:58 | 0:00 | T | Tripped showing Buccholz relay | 0 | 0 | No interruption
Thakurgaon | 132/33kV transformer 432T HT | 2023-06-28 09:40 | 2023-06-28 16:40 | 7:00 | T | Due to OTI problem | 0 | 0 | No interruption
Natore | 132/33kV transformer TR-4 (435)HT | 2023-06-28 09:51 | 2023-06-28 09:51 | 0:00 | T | Tripped showing Bucholz relay | 0 | 0 | No interruption
Sirajganj | 132/33kV transformer T1(415) LT | 2023-06-29 01:47 | 2023-06-29 17:46 | 15:59 | E/O | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 103:47 |  | Unserved Energy: |  | 657.8667
Others :
Ashuganj | 230/132kV transformer OAT-12 HT | 2023-06-26 06:54 | 2023-06-26 10:55 | 4:01 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Ashuganj | 230/132kV transformer OAT-12 LT | 2023-06-26 06:55 | 2023-06-26 10:54 | 3:59 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
|  |  | Total : | 8:00 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 647:22 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division | [9 empty] | 8801.6
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: June 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bashundhara | Bashundhara-Rampura 132 kV Ckt-1 | 2023-06-01 12:15 | 2023-06-01 12:36 | 0:21 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132kV Ckt-1 | 2023-06-02 14:32 | 2023-06-02 15:05 | 0:33 | T | Tripped showing REC 650 relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132kV Ckt-2 | 2023-06-02 14:32 | 2023-06-02 14:55 | 0:23 | T | Tripped showing REC 650 relay | 157 | 60.1833 | Power interruption
Kaliakoir | Kaliakoir-Tangail both Ckt | 2023-06-02 14:32 | 2023-06-02 14:45 | 0:13 | T | Tripped showing REC 650 relay | 472 | 102.2667 | Power interruption
Kaliakoir | Kaliakoir-Tangail 132kV Ckt-2 | 2023-06-02 14:32 | 2023-06-02 14:55 | 0:23 | T | Tripped showing REC 650 relay | 0 | 0 | No interruption
Kabirpur | Kabirpur - Manikganj 132kV Ckt-1 | 2023-06-04 09:36 | 2023-06-04 12:21 | 2:45 | E/O | Due to red hot maintenance. | 0 | 0 | No interruption
Sreepur | Sreepur 230/132/33kV-Ashuganj Ckt-2 | 2023-06-08 14:33 | 2023-06-08 14:56 | 0:23 | T | Tripped showing Differential Relay | 0 | 0 | No interruption
Sreepur | Sreepur 230/132/33kV-Ashuganj Ckt-1 | 2023-06-08 14:34 | 2023-06-08 14:58 | 0:24 | T | Tripped showing Differential & Distance relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132kV Ckt-1 | 2023-06-09 11:58 | 2023-06-09 12:08 | 0:10 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kodda(300MW) 230kV Ckt-1 | 2023-06-10 11:16 | 2023-06-10 18:08 | 6:52 | E/O | Due to Emergency maint.work | 12 | 82.4 | Power interruption
Kodda | Kodda-Rajendrapur 132kV Ckt-2 | 2023-06-10 14:42 | 2023-06-10 15:28 | 0:46 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Sreepur | Sreepur 230/132/33kV-Ashuganj Ckt-2 | 2023-06-12 12:00 | 2023-06-12 12:23 | 0:23 | T | Tripped showing F21, F87L relays Due to Due to bad weather | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132kV Ckt-1 | 2023-06-13 13:09 | 2023-06-13 13:09 | 0:00 | E/O | Due to red hot maintenance. | 0 | 0 | No interruption
Sreepur | Sreepur-Ashuganj 230 kV Ckt-2 | 2023-06-14 06:13 | 2023-06-14 07:00 | 0:47 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132kV Ckt-2 | 2023-06-14 07:07 | 2023-06-14 07:07 | 0:00 | E/O | Due to red hot maintenance. | 0 | 0 | No interruption
Manikganj P/S | Manikganj PS-Savar 132 Ckt-1 | 2023-06-14 17:18 | 2023-06-14 18:08 | 0:50 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Jamalpur | Jamalpur United (200MW)-Jamalpur 132kV Ckt-2 & 1 | 2023-06-15 19:28 | 2023-06-15 19:42 | 0:14 | T | Tripped showing Distance relay | 85 | 19.8333 | Power interruption
Tangail | Tangail-RPCL 132 kV Ckt-1 | 2023-06-15 19:28 | 2023-06-15 19:37 | 0:09 | T | Tripped showing Relay of RPCL end relays. | 0 | 0 | No interruption
Sreepur | Sreepur-Ashuganj 230 kV Ckt-2 | 2023-06-15 22:18 | 2023-06-15 23:03 | 0:45 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132kV Ckt-02 | 2023-06-16 17:05 | 2023-06-16 17:24 | 0:19 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL 132kV Ckt-01 | 2023-06-16 17:05 | 2023-06-16 17:23 | 0:18 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Tangail | Tangail- RPCL 132kV Ckt-02 | 2023-06-16 17:05 | 2023-06-16 17:24 | 0:19 | T | Tripped showing REL 670 relay | 25 | 7.9167 | Power interruption
Tangail | Tangail- RPCL 132kV Ckt-01 | 2023-06-16 17:05 | 2023-06-16 17:23 | 0:18 | T | Tripped showing REL 670 relay | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132kV Ckt-2 | 2023-06-16 17:10 | 2023-06-16 17:26 | 0:16 | E/O | Due to A-Bus power fail. | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132kV Ckt-1 | 2023-06-16 17:10 | 2023-06-16 17:15 | 0:05 | E/O | Due to A-Bus power fail. | 0 | 0 | No interruption
Kabirpur | Kabirpur -Tongi 132kV Ckt-2 | 2023-06-16 18:57 | 2023-06-16 19:28 | 0:31 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Kodda | Kodda - RPCL 100 MW 132 kV Ckt | 2023-06-16 19:00 | 2023-06-16 19:40 | 0:40 | T | Due to Over voltage | 17 | 11.3333 | Power interruption
Bashundhara | Bashundhara-Rampura 132 kV Ckt-2 | 2023-06-16 19:30 | 2023-06-16 19:49 | 0:19 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Bashundhara | Bashundhara-Rampura 132 kV Ckt-1 | 2023-06-16 19:30 | 2023-06-16 20:29 | 0:59 | T | Tripped showing Distance & prot.relay | 0 | 0 | No interruption
Sreepur | Sreepur 230/132/33kV-Ashuganj Ckt-1 | 2023-06-17 06:21 | 2023-06-17 14:40 | 8:19 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Kabirpur | Kabirpur -Tongi 132kV Ckt-2 |  | 2023-06-17 13:43 |  | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Tangail | Tangail - Kaliakair-132 kV Ckt-1 | 2023-06-17 16:24 | 2023-06-17 17:10 | 0:46 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Tangail | Tangail - RPCL132 kV CKt-2 | 2023-06-17 16:40 | 2023-06-17 17:54 | 1:14 | T | Tripped showing REL670 relays Due to thunderingstrom | 0 | 0 | No interruption
Kabirpur | Kabirpur -Tongi 132kV Ckt-1 | 2023-06-17 17:58 | 2023-06-17 18:29 | 0:31 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Jamalpur | Jamalpur United (20MW)- Sherpur 132kV Ckt-2 | 2023-06-20 03:45 | 2023-06-20 03:54 | 0:09 | T | Tripped showing Micom P443 relays. | 0 | 0 | No interruption
Tangail | Tangail -RPCL-1 132 kV Ckt-1 | 2023-06-21 15:16 | 2023-06-21 15:21 | 0:05 | T | Tripped showing ABB REL 670 relays Due to Bad Weather | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2023-06-21 15:44 | 2023-06-21 18:33 | 2:49 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Tangail | Tangail - RPCL 132 kV Ckt-1 | 2023-06-27 13:35 | 2023-06-27 13:49 | 0:14 | T | Tripped showing Distance relay | 70 | 16.3333 | Power interruption
|  |  | Total : | 34:32 |  | Unserved Energy: |  | 300.2667
Dhaka (South) Grid Circle :
Madnaganj | Madanganj -Shitalakhya 132 kV Ckt | 2023-06-09 10:31 | 2023-06-09 18:02 | 7:31 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132kV Ckt-1 | 2023-06-12 11:35 | 2023-06-12 12:27 | 0:52 | T | Tripped showing OPTIMHO relays Due to Heavy Rainfall | 60 | 52 | Power interruption
Madnaganj | Madanganj -Shitalakhya 132 kV Ckt-1 | 2023-06-14 08:18 | 2023-06-14 15:48 | 7:30 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-1 | 2023-06-16 19:19 | 2023-06-16 20:57 | 1:38 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Sonargaon | Sonargaon - OPSL(IEL-2) | 2023-06-16 19:23 | 2023-06-16 20:07 | 0:44 | T | Due to thunderstorm. | 88 | 64.5333 | Power interruption
Madanganj | Madanganj -Shitalakhya 132 kV Ckt | 2023-06-16 20:24 | 2023-06-17 07:54 | 11:30 | E/O | Due to Order by NLDC for Overload. | 0 | 0 | No interruption
Haripur | Haripur-Narsingdi 132kV Ckt-1 | 2023-06-18 12:00 | 2023-06-18 12:17 | 0:17 | T | Tripped showing OPTIMHO -Z1, BN relay Due to Heavy Rainfall | 70 | 19.8333 | Power interruption
Ghorasal | Ghorasal-Joydeb-B 132kV Ckt-1 | 2023-06-21 06:20 | 2023-06-21 11:11 | 4:51 | E/O | Due to red-hot maint. | 0 | 0 | No interruption
Madanganj | Madanganj -Summit 102 MW 132 kV Ckt | 2023-06-28 23:26 | 2023-06-28 23:26 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132kV Ckt-1 | 2023-06-29 07:22 | 2023-06-29 08:10 | 0:48 | T | Tripped showing Distance relay | 0 | 0 | No interruption
Brahmongaon | Brahmongaon-Hasnabad 132 kV Ckt-2 | 2023-06-29 16:54 | 2023-06-29 20:29 | 3:35 | T | Tripped showing Main.prot.relay | 0 | 0 | No interruption
Madnaganj | Madanganj -Shitalakhya 132 kV Ckt | 2023-06-30 15:58 | 2023-06-30 16:12 | 0:14 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 39:30 |  | Unserved Energy: |  | 136.3667
Chattogram Grid Circle :
AKSML | AKSML-Baroaulia 132 kV Ckt-1 | 2023-06-03 21:40 | 2023-06-04 12:41 | 15:01 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-1 | 2023-06-06 07:35 | 2023-06-06 07:44 | 0:09 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cox'sbazar | Dohazari -Cox'sbazar 132 kV Ckt-1 | 2023-06-06 07:35 | 2023-06-06 07:44 | 0:09 | T | Tripped showing Dist. relay. | 70 | 10.5 | Power interruption
Hathazari | Hathazari-Kaptai 132kV Ckt-2 | 2023-06-06 19:02 | 2023-06-06 21:59 | 2:57 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TKCL 132kV Ckt-1 | 2023-06-06 19:23 | 2023-06-06 20:32 | 1:09 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV Ckt-1 | 2023-06-08 02:06 | 2023-06-08 03:37 | 1:31 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132kV Ckt-2 | 2023-06-08 09:53 | 2023-06-08 14:24 | 4:31 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Hathazari | Bakulia-Sikalbaha 132 kV Ckt-1 | 2023-06-12 08:35 | 2023-06-12 08:55 | 0:20 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Baroaulia | Baroaulia-KSRM 132 kV Ckt-1 | 2023-06-12 16:58 | 2023-06-12 17:18 | 0:20 | T | Tripped showing O/C relay | 20 | 6.6667 | Power interruption
BSRM | BSRM-GPH 230 kV Ckt-1 | 2023-06-15 09:32 | 2023-06-15 09:46 | 0:14 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
BSRM | BSRM-GPH 230 kV Ckt-1 | 2023-06-17 10:15 | 2023-06-17 10:15 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV Ckt-2 | 2023-06-17 10:54 | 2023-06-17 11:32 | 0:38 | T | Tripped showing REL670 relays due to huge lightening . | 0 | 0 | No interruption
Hathazari | Hathazari - AKSML 230 kV Ckt-2 | 2023-06-17 11:27 | 2023-06-17 12:28 | 1:01 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Baroirhat | Baroirhat-Feni 132 kV Ckt-2 | 2023-06-23 08:15 | 2023-06-23 10:39 | 2:24 | E/O | Due to Transformer overload | 0 | 0 | No interruption
Khagrachari | Khagrachari-Rangamati 132kV Ckt-1 | 2023-06-30 02:38 | 2023-06-30 02:51 | 0:13 | T | Tripped showing REL 670 relays Due to Lightening | 0 | 0 | No interruption
BSRM | BSRM-Cumilla(N) 230 kV Ckt-1 | 2023-06-30 17:01 | 2023-06-30 18:22 | 1:21 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 31:58 |  | Unserved Energy: |  | 17.1667
Cumilla Grid Circle :
Cumilla(N) | Cumilla(N)-Meghnaghat 230 kV Ckt-1 | 2023-06-02 04:53 | 2023-06-02 05:08 | 0:15 | T | Tripped showing Dist. Prot. Relay relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132kV Ckt-1 | 2023-06-04 10:32 | 2023-06-04 11:01 | 0:29 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Ramganj 132 kV Ckt-2 | 2023-06-06 10:30 | 2023-06-06 10:30 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chauddagram | Chauddagram-Feni 132 kV Ckt-1 | 2023-06-07 15:40 | 2023-06-07 19:22 | 3:42 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Brahmanbaria 132kV Ckt-2 | 2023-06-08 08:38 | 2023-06-08 09:37 | 0:59 | E/O | Due to CB (R- Phase) Oil Refill Work. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132kV Ckt-1 | 2023-06-08 14:35 | 2023-06-08 14:42 | 0:07 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV Ckt-2 | 2023-06-10 09:40 | 2023-06-10 11:54 | 2:14 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-B.baria 132 kV Ckt-1 | 2023-06-11 23:08 | 2023-06-12 07:13 | 8:05 | E/O | Due to instruction of NLDC for OAT-12 Overload. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sreepur 230 kV Ckt-2 | 2023-06-12 11:59 | 2023-06-12 12:24 | 0:25 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sreepur 230 kV Ckt-2 | 2023-06-14 06:12 | 2023-06-14 07:00 | 0:48 | T | Due to General trip | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemangal 132kV Ckt-2 | 2023-06-14 22:46 | 2023-06-14 22:55 | 0:09 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Chattak- | Chattak-Sunamganj 132 kV Ckt-1 | 2023-06-15 10:27 | 2023-06-15 10:40 | 0:13 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sreepur 230 kV Ckt-2 | 2023-06-15 11:32 | 2023-06-15 14:59 | 3:27 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sreepur 230 kV Ckt-1 | 2023-06-15 15:04 | 2023-06-15 16:14 | 1:10 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-15 23:02 | 2023-06-16 00:02 | 1:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-15 23:09 | 2023-06-16 00:03 | 0:54 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-1 | 2023-06-15 23:14 | 2023-06-15 23:29 | 0:15 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-16 18:40 | 2023-06-16 19:43 | 1:03 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-17 03:18 | 2023-06-17 03:36 | 0:18 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-1 | 2023-06-18 11:54 | 2023-06-18 12:06 | 0:12 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-19 12:16 | 2023-06-19 12:36 | 0:20 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132kV Ckt-1 | 2023-06-20 13:18 | 2023-06-20 13:24 | 0:06 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-20 14:27 | 2023-06-20 14:37 | 0:10 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-1 | 2023-06-20 14:27 | 2023-06-20 14:36 | 0:09 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Feni | Feni-PHP 132kV Ckt-1 | 2023-06-23 08:16 | 2023-06-23 10:39 | 2:23 | E/O | Due to Comilla Transformer over load . | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132kV Ckt-1 | 2023-06-23 07:18 | 2023-06-23 07:18 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Brahmanbaria 132kV Ckt-1 | 2023-06-25 23:58 | 2023-06-26 07:02 | 7:04 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132kV Ckt-1 | 2023-06-25 23:58 | 2023-06-26 07:10 | 7:12 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132kV Ckt-2 | 2023-06-26 13:36 | 2023-06-26 13:59 | 0:23 | T | Tripped showing Dist.relay. | 0 | 0 | No interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2023-06-28 10:55 | 2023-06-28 12:19 | 1:24 | T | Tripped showing E/F.relay. | 62 | 86.8 | Power interruption
Chauddagram | Chauddagram-Feni 132 kV Ckt-2 | 2023-06-28 11:25 | 2023-06-28 12:28 | 1:03 | T | Tripped showing Dist.relay. | 71 | 74.55 | Power interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-1 | 2023-06-28 11:27 | 2023-06-28 12:20 | 0:53 | T | Tripped showing E/F.relay. | 20 | 17.6667 | Power interruption
Chowmuhani | Chowmuhani-Feni 132 kV Ckt-2 | 2023-06-28 11:40 | 2023-06-28 12:17 | 0:37 | E/O | Due to Emergency maint.work | 20 | 12.3333 | Power interruption
|  |  | Total : | 47:29 |  | Unserved Energy: |  | 191.35
Khulna Grid Circle :
Bagerhat | Bagerhat-Mongla 132 kV Ckt-2 | 2023-06-03 16:11 | 2023-06-03 18:42 | 2:31 | E/O | Due to Air leakage in compressor safety valve. | 0 | 0 | No interruption
Narail | Narail 132/33kV S/S Capacitor Bank | 2023-06-03 19:26 | 2023-06-03 19:26 | 0:00 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Narail | Goalpara-Labanchura 132kV Ckt-2 | 2023-06-05 12:38 | 2023-06-05 13:05 | 0:27 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Gopalganj | Gopalganj - 400kV Aminbazar Ckt-1 | 2023-06-06 12:05 | 2023-06-06 13:27 | 1:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Barishal | Barishal-Patuakhali(BargunaTat Bakergonj)132 kV Ckt | 2023-06-12 17:18 | 2023-06-12 17:27 | 0:09 | T | Tripped showing Dist. relay. | 10 | 1.5 | Power interruption
Barishal | Barishal-Bhandaria 132 kV Ckt-1 | 2023-06-13 16:17 | 2023-06-13 16:22 | 0:05 | T | Tripped showing Dist. relay. | 30 | 2.5 | Power interruption
Khulna(S) | Khulna (S)-Satkhira 132kV Ckt-1 | 2023-06-13 18:50 | 2023-06-13 19:56 | 1:06 | T | Tripped showing Dist. relay. | 42 | 46.2 | Power interruption
Khulna(S) | Khulna (S)-Satkhira 132kV Ckt-2 | 2023-06-13 18:50 | 2023-06-14 17:10 | 22:20 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 | 2023-06-15 21:32 | 2023-06-15 22:27 | 0:55 | T | Due to Raining and Thundering. | 0 | 0 | No interruption
Goalpara | Goalpara-Labanchura 132kV Ckt-2 | 2023-06-17 04:18 | 2023-06-17 05:03 | 0:45 | T | Tripped showing Dist. relay. | 9 | 6.75 | Power interruption
Patuakhali | Patuakhali-Payra 132kV Ckt-2 | 2023-06-21 08:18 | 2023-06-21 10:04 | 1:46 | E/O | Due to red hot maintanance. | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2023-06-28 02:00 | 2023-06-28 02:39 | 0:39 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 32:05 |  | Unserved Energy: |  | 56.95
HVDC Grid Circle :
HVDC Bheramera | HVDC Bheramera- Rajshahi 230kV Ckt-2 | 2023-06-11 11:19 | 2023-06-11 13:09 | 1:50 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
BIPTC | BIPTC - Baharampur-2 | 2023-06-18 15:59 | 2023-06-18 17:49 | 1:50 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bheramara | Bheramara P/S-Kustia 132 kV Ckt-1 | 2023-06-28 08:44 | 2023-06-28 16:08 | 7:24 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
|  |  | Total : | 11:04 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Bogura(New) | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-2 | 2023-06-07 14:32 | 2023-06-07 17:28 | 2:56 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Monakasha | Monakasha-Rahanpur 400kV Ckt-1 | 2023-06-09 13:54 | 2023-06-09 14:34 | 0:40 | T | Tripped showing Dist. relay. | 87 | 58 | Power interruption
Rajshahi | Rajshahi S/S - 132 kV 50 MW P/P | 2023-06-10 10:58 | 2023-06-10 14:25 | 3:27 | E/O | Due to 132kV CVT oil leakage | 0 | 0 | No interruption
Rajshahi | Rajshahi S/S - 132 kV 50 MW P/P | 2023-06-11 11:19 | 2023-06-11 17:21 | 6:02 | E/O | Due to 132kV CVT oil leakage | 0 | 0 | No interruption
Adani | Adani-Bogura(N) 400kV Ckt | 2023-06-13 23:03 | 2023-06-13 23:52 | 0:49 | T | Tripped showing no. relay. | 0 | 0 | No interruption
Mahasthangar | Mahasthangar-Palashbari 132kV Ckt-2 | 2023-06-16 21:26 | 2023-06-16 21:48 | 0:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Jaldhaka | Jaldhaka-Saidpur 132kV Ckt-1,2 | 2023-06-18 04:08 | 2023-06-18 04:44 | 0:36 | T | Tripped showing O/C.& E/F relay. | 0 | 0 | No interruption
Rajshahi | Rajshahi -50 MW P/S 132 kV Ckt | 2023-06-19 13:02 | 2023-06-19 13:02 | 0:00 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Panchagar | Panchagar-Thakurgaon 132kV Ckt-1 | 2023-06-20 04:26 | 2023-06-20 04:44 | 0:18 | T | Due to 33 kV feeder fault | 5 | 1.5 | Power interruption
Panchagar | Panchagar-Thakurgaon 132kV Ckt-1 | 2023-06-21 05:21 | 2023-06-21 05:31 | 0:10 | T | Tripped showing N/A. relays due to storm suddenly. | 8 | 1.3333 | Power interruption
Panchagar | Panchagar-Thakurgaon 132kV Ckt-1 | 2023-06-22 01:24 | 2023-06-22 01:42 | 0:18 | T | Tripped showing Dist. relay. | 20 | 6 | Power interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-1 | 2023-06-29 13:38 | 2023-06-29 14:18 | 0:40 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 16:18 |  | Unserved Energy: |  | 66.8333
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 212:56 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: June 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33kV transformer Tr-3 (424T) HT |  | 2023-06-02 13:47 |  | S/O | After maint.work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-A | 2023-06-04 06:49 | 2023-06-04 09:11 | 2:22 | S/O | Due to Project work | 0 | 0 | No interruption
Bhaluka | 132 kV Bus-B | 2023-06-04 09:34 | 2023-06-04 12:12 | 2:38 | S/O | Due to Project work | 0 | 0 | No interruption
Tongi | 230/132/33kV transformer T-3 HT & LT |  | 2023-06-04 18:14 |  | S/O | After maint.work | 0 | 0 | No interruption
Tongi | 230/132/33kV transformer T-3 LT & HT | 2023-06-05 10:40 | 2023-06-05 20:35 | 9:55 | S/O | Due to replacement work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus 02 | 2023-06-05 14:40 | 2023-06-05 14:40 | 0:00 | S/O | Due to Bay Recheck. | 0 | 0 | No interruption
Mymensingh | 132/33kV transformer-3 (424T) HT |  | 2023-06-06 17:28 |  | S/O | After maint.work | 0 | 0 | No interruption
Mymensingh | 132/33kV transformer-3 (424T) HT | 2023-06-08 09:34 | 2023-06-08 16:14 | 6:40 | S/O | Due to maint.work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus 02 | 2023-06-11 16:08 | 2023-06-11 17:08 | 1:00 | S/O | Due to changing work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus 01 | 2023-06-11 17:25 | 2023-06-11 18:10 | 0:45 | S/O | Due to changing work | 0 | 0 | No interruption
Manikganj | Capacitor Bank-1 |  | 2023-06-13 09:16 |  | S/O | After maint.work | 0 | 0 | No interruption
Manikganj | Capacitor Bank-1 |  | 2023-06-13 09:20 |  | S/O | After maint.work | 0 | 0 | No interruption
Dhamrai | 132/33kV transformer T-1 LT | 2023-06-13 12:09 | 2023-06-13 13:28 | 1:19 | S/O | Due to SPMD Work | 0 | 0 | No interruption
Dhamrai | 132/33kV transformer T-1 HT | 2023-06-13 12:10 | 2023-06-13 13:28 | 1:18 | S/O | Due to SPMD Work | 0 | 0 | No interruption
Dhamrai | 132/33kV transformer T-2 LT | 2023-06-13 14:36 | 2023-06-13 15:22 | 0:46 | S/O | Due to Testing by SPMD | 0 | 0 | No interruption
Dhamrai | 132/33kV transformer T-2 HT | 2023-06-13 14:36 | 2023-06-13 15:22 | 0:46 | S/O | Due to Testing by SPMD | 0 | 0 | No interruption
Kaliakoir | 400/230kV transformer TR1 LT | 2023-06-14 09:37 | 2023-06-14 11:25 | 1:48 | S/O | Due to testing work. | 0 | 0 | No interruption
Kaliakoir | 400/230kV transformer TR1 HT | 2023-06-14 09:37 | 2023-06-14 11:24 | 1:47 | S/O | Due to testing work. | 0 | 0 | No interruption
Kallyanpur | 132/33kV transformer GT-1 HT | 2023-06-15 06:22 | 2023-06-15 06:22 | 0:00 | S/O | Due to Corrective Maintenance | 0 | 0 | No interruption
Jamalpur | 132/33kV transformer T-2 LT & HT | 2023-06-18 14:35 | 2023-06-18 15:51 | 1:16 | S/O | Due to replacement work | 0 | 0 | No interruption
Jamalpur | 132/33kV transformer T-1 HT & LT | 2023-06-18 17:18 | 2023-06-18 19:48 | 2:30 | S/O | Due to A/M work | 0 | 0 | No interruption
Jamalpur | 132/33kV transformer T-3 LT | 2023-06-19 09:42 | 2023-06-22 18:15 | 80:33 | S/O | Due to replacement work | 0 | 0 | No interruption
Sherpur | 230/132 kV transformer T-1 LT & HT | 2023-06-19 10:40 | 2023-06-19 15:50 | 5:10 | S/O | Due to Project work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus 02 | 2023-06-20 10:05 | 2023-06-20 11:54 | 1:49 | S/O | Due to loop connection. | 0 | 0 | No interruption
Sreepur | 132/33 kV transformer T-2 LT | 2023-06-20 11:01 | 2023-06-20 14:26 | 3:25 | S/O | Due to Project work | 0 | 0 | No interruption
Sreepur | 132/33 kV transformer T-2 HT | 2023-06-20 11:01 | 2023-06-20 14:25 | 3:24 | S/O | Due to Project work | 0 | 0 | No interruption
Sreepur | 230/132 kV transformer T-2 LT | 2023-06-20 11:39 | 2023-06-20 16:09 | 4:30 | S/O | Due to Project work | 0 | 0 | No interruption
Sreepur | 230/132 kV transformer T-2 LT | 2023-06-20 11:40 | 2023-06-20 16:09 | 4:29 | S/O | Due to Project work | 0 | 0 | No interruption
Aminbazar | 132 kV Bus 01 | 2023-06-20 12:54 | 2023-06-20 14:35 | 1:41 | S/O | After maint.work | 0 | 0 | No interruption
Aminbazar | Aminbazar 400/230/132kV Bus-2 (400kV) | 2023-06-20 13:28 | 2023-06-20 16:08 | 2:40 | S/O | Due to DS Problem. | 0 | 0 | No interruption
Sreepur | 132/33 kV transformer T-2 HT & LT | 2023-06-20 14:48 | 2023-06-20 16:46 | 1:58 | S/O | Due to Project work | 0 | 0 | No interruption
Aminbazar | 400/132kV Interim transformer |  | 2023-06-20 15:12 |  | S/O | After maint.work | 0 | 0 | No interruption
Kallyanpur | 132/33kV transformer GT-3 (132kV) HT | 2023-06-22 07:03 | 2023-06-22 14:52 | 7:49 | S/O | Due to maint.work | 0 | 0 | No interruption
Kallyanpur | 132/33kV transformer GT-3 (132kV) HT | 2023-06-22 16:55 | 2023-06-22 17:40 | 0:45 | S/O | Due to 33 KV PT Fuse Noise. | 0 | 0 | No interruption
Jamalpur | 132/33kV transformer T-3 HT |  | 2023-06-22 17:18 |  | S/O | After maint.work | 0 | 0 | No interruption
Sherpur | 132/33kV transformer T-4 HT |  | 2023-06-22 21:10 |  | S/O | After maint.work | 0 | 0 | No interruption
Tongi | 230/132 transformer T-02 LT |  | 2023-06-23 10:05 |  | S/O | After maint.work | 0 | 0 | No interruption
Tongi | 230/132 transformer T-03 LT |  | 2023-06-23 10:13 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 153:03 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur | 230132kV transformer Auto TR-1 HT | 2023-06-01 06:33 | 2023-06-01 13:13 | 6:40 | S/O | Due to changing work | 0 | 0 | No interruption
Haripur | 230132kV transformer Auto TR-1 LT | 2023-06-01 06:33 | 2023-06-01 13:13 | 6:40 | S/O | Due to changing work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer AT-1 |  | 2023-06-02 09:23 |  | S/O | After maint.work | 0 | 0 | No interruption
Narshingdi | 132/33kV transformer T-3 HT | 2023-06-06 11:02 | 2023-06-06 11:02 | 0:00 | S/O | After maint.work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2023-06-07 09:41 | 2023-06-07 17:37 | 7:56 | S/O | Due to Connection Work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2023-06-08 09:29 | 2023-06-08 16:15 | 6:46 | S/O |  | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer AT-2 | 2023-06-11 07:13 | 2023-06-11 07:32 | 0:19 | S/O | Due to measurements at 132KV side. | 0 | 0 | No interruption
Sonargaon | 132/33kV transformer Tr-1 | 2023-06-12 11:03 | 2023-06-12 12:55 | 1:52 | S/O | Due to Connection Work | 60 | 112 | Power interruption
Haripur | 230/132kV transformer Auto TR-3 LT | 2023-06-17 15:32 | 2023-06-17 16:11 | 0:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Meghnaghat | 230 kV Bus-1 | 2023-06-18 09:51 | 2023-06-18 18:48 | 8:57 | S/O | Due to protection work | 0 | 0 | No interruption
Sonargaon | 132/33kV transformer Tr-2 HT |  | 2023-06-19 13:18 |  | S/O | After maint.work | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer AT-2 |  | 2023-06-21 11:03 |  | S/O | After maint.work | 0 | 0 | No interruption
Sonargaon | 132/33kV transformer Tr-1 | 2023-06-22 11:40 | 2023-06-22 12:36 | 0:56 | S/O | Due to Energy meter work | 0 | 0 | No interruption
Sitalakhya | 132kV Bus coupler | 2023-06-22 16:43 | 2023-06-22 16:43 | 0:00 | S/O | Due to corrective maintenance. | 0 | 0 | No interruption
Meghanghat | 400/230 kV transformer T-1 | 2023-06-24 12:50 | 2023-06-24 12:50 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Ghorashal | 132/33kV transformer T-2 | 2023-06-27 06:15 | 2023-06-27 10:18 | 4:03 | S/O | Due to maint.work | 25 | 101.25 | Power interruption
Ghorashal | 230/132 kv transformer ATr-1 | 2023-06-27 06:16 | 2023-06-27 09:30 | 3:14 | S/O | Due to maint.work | 30 | 97 | Power interruption
|  |  | Total : | 50:59 |  | Unserved Energy: |  | 310.25
Chattogram Grid Circle :
Sholosohor | 132/33kV transformer TRAFO-02 LT |  | 2022-06-06 08:22 |  | S/O | After maint.work | 0 | 0 | No interruption
Juldah | 132/33kV transformer 406T T-1 HT |  | 2022-06-08 12:53 |  | S/O | After maint.work | 0 | 0 | No interruption
Halishahar | 132/33kV transformer 406T MTR1 LT | 2022-06-10 08:11 | 2022-06-10 11:18 | 3:07 | S/O | Due to maint. work | 0 | 0 | No interruption
Halishahar | 132/33kV transformer 406T MTR1 HT | 2022-06-10 08:11 | 2022-06-10 11:17 | 3:06 | S/O | Due to maint. work | 0 | 0 | No interruption
Shahmirpur | 132/33kV transformer 406T HT |  | 2022-06-10 17:54 |  | S/O | After maint.work | 0 | 0 | No interruption
Baroaulia | 132/33kV transformer T-1(405T) HT | 2022-06-11 07:10 | 2022-06-11 09:19 | 2:09 | S/O | Due to Hold Differential relay establish | 0 | 0 | No interruption
Baroaulia | 132/33kV transformer T-2(405T) HT | 2022-06-11 11:49 | 2022-06-11 13:49 | 2:00 | S/O | Due to Hold Differential relay establish | 0 | 0 | No interruption
Shahmirpur | 132/33kV transformer 406T LT | 2022-06-14 08:49 | 2022-06-14 19:37 | 10:48 | S/O | Due to BREB 33KV GIS Extension Work. | 0 | 0 | No interruption
Shahmirpur | 132/33kV transformer 406T HT | 2022-06-14 08:50 | 2022-06-14 19:25 | 10:35 | S/O | Due to BREB 33KV GIS Extension Work. | 0 | 0 | No interruption
Sholosohor | 132/33kV transformer TRAFO-01 HT | 2022-06-15 07:07 | 2022-06-15 10:10 | 3:03 | S/O | Due to maint. work | 0 | 0 | No interruption
Sholosohor | 132/33kV transformer TRAFO-02 HT | 2022-06-15 10:16 | 2022-06-15 12:37 | 2:21 | S/O | Due to Preventing birds from nesting on 33kv structure. | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer AUX.TRAFO-02 LT | 2022-06-15 11:49 | 2022-06-15 12:36 | 0:47 | S/O | Due to maint. work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer AUX.TRAFO-02 HT | 2022-06-15 11:49 | 2022-06-15 12:35 | 0:46 | S/O | Due to maint. work | 0 | 0 | No interruption
Dohazari | 132/33kV transformer -T-2 LT | 2022-06-15 16:32 | 2022-06-15 16:54 | 0:22 | S/O | Due to maint. work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-01(406T) LT & HT | 2022-06-18 07:10 | 2022-06-18 19:03 | 11:53 | S/O | Due to project work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-01(406T) LT | 2022-06-19 08:17 | 2022-06-19 18:44 | 10:27 | S/O | Due to project work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-01(406T) HT | 2022-06-19 08:18 | 2022-06-19 18:43 | 10:25 | S/O | Due to project work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-01(406T) LT & HT | 2022-06-20 08:18 | 2022-06-21 20:15 | 35:57 | S/O | Due to maint. work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-01(406T) HT | 2022-06-22 08:15 | 2022-06-22 16:17 | 8:02 | S/O | Due to project work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-01(406T) LT | 2022-06-22 08:15 | 2022-06-22 16:18 | 8:03 | S/O | Due to project work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformer TR-02 | 2022-06-23 08:14 | 2022-06-23 18:36 | 10:22 | S/O | Due to project work | 0 | 0 | No interruption
Chandraghona | 132/33kV transformerTR-02(416T) HT & LT | 2022-06-24 08:28 | 2022-06-24 21:22 | 12:54 | S/O | Due to project work | 0 | 0 | No interruption
Sholosohor | 132/33kV transformer TRAFO-01 LT | 2022-06-24 09:45 | 2022-06-24 10:45 | 1:00 | S/O | Due to 33kV Bus DS change | 0 | 0 | No interruption
Sholosohor | 132/33kV transformer TRAFO-01 HT | 2022-06-24 09:47 | 2022-06-24 10:45 | 0:58 | S/O | Due to 33kV Bus DS change | 0 | 0 | No interruption
Sholosohor | 132/33kV transformer TRAFO-01 HT & LT | 2022-06-24 21:11 | 2022-06-24 22:00 | 0:49 | S/O | Due to 33kV loop connection | 0 | 0 | No interruption
Sholosohor | 50/75 MVA transformerT-1(405T) HT |  | 2022-06-25 12:23 |  | S/O | After maint.work | 0 | 0 | No interruption
Madunaghat | 132/33kV transformer TR-1(507T) HT | 2022-06-30 10:06 | 2022-06-30 14:33 | 4:27 | S/O | Due to maint. Work by BPDB | 17 | 75.65 | Power interruption
Madunaghat | 132/33kV transformer TR-1(507T) LT | 2022-06-30 10:06 | 2022-06-30 14:05 | 3:59 | S/O | Due to maint. Work by BPDB | 0 | 0 | No interruption
|  |  | Total : | 158:20 |  | Unserved Energy: |  | 75.65
Cumilla Grid Circle :
Brahmanbaria | 132/33kV transformer 403T LT & HT | 2023-06-01 10:14 | 2023-06-01 15:40 | 5:26 | S/O | Due to grounding maintenance . | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformer TR-02 LT | 2023-06-04 07:12 | 2023-06-04 15:55 | 8:43 | S/O | Due to Sky wire disconnected | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformer TR-02 HT | 2023-06-04 07:12 | 2023-06-04 14:39 | 7:27 | S/O | Due to Sky wire disconnected | 0 | 0 | No interruption
Chandpur S/S | 132/33kV transformer T3 | 2023-06-05 13:15 | 2023-06-05 13:15 | 0:00 | S/O | Due to maint. work | 0 | 0 | No interruption
Ramganj | 132/33kV transformer -02 LT | 2023-06-09 07:12 | 2023-06-09 11:59 | 4:47 | S/O | Due to changing work at 33 kV side | 30 | 143.5 | Power interruption
Ramganj | 132/33kV transformer -02 LT | 2023-06-10 06:42 | 2023-06-10 08:20 | 1:38 | S/O | Due to PDB work | 38 | 62.0667 | Power interruption
Fenchuganj | 230/132kV transformer TR-02 | 2023-06-12 09:06 | 2023-06-12 22:22 | 13:16 | S/O | Due to Oil centrifuging | 0 | 0 | No interruption
Cumilla(N) | 230/132kV transformer T-04 LT | 2023-06-14 11:50 | 2023-06-14 12:56 | 1:06 | S/O | Due to maint. work | 0 | 0 | No interruption
Cumilla(N) | 230/132kV transformer T-04 HT | 2023-06-14 11:51 | 2023-06-14 11:55 | 0:04 | S/O | Due to maint. work | 0 | 0 | No interruption
Ashuganj | 132 kV Busbar-1 | 2023-06-16 08:01 | 2023-06-16 17:27 | 9:26 | S/O | Due to maint. work | 0 | 0 | No interruption
Ashuganj | 230/132kV transformer T-04 |  | 2023-06-16 19:04 |  | S/O | After maint. work | 0 | 0 | No interruption
Cumilla(N) | 230/132/33kV transformer T-04 LT | 2023-06-20 15:50 | 2023-06-20 17:43 | 1:53 | S/O | Due to Isolator change | 0 | 0 | No interruption
Cumilla(N) | 230/132/33kV transformer T-04 HT | 2023-06-20 15:51 | 2023-06-20 17:43 | 1:52 | S/O | Due to Isolator change | 0 | 0 | No interruption
Fenchuganj | 230/132kV transformer TR-02 HT |  | 2023-06-20 15:54 |  | S/O | After maint. work | 0 | 0 | No interruption
Ashugonj | 132KV bus-1 | 2023-06-23 06:58 | 2023-06-23 10:12 | 3:14 | S/O | Due to corrective maint. | 0 | 0 | No interruption
Cumilla(N) | 230/132kV transformer T-04 LT | 2023-06-23 14:52 | 2023-06-23 16:24 | 1:32 | S/O | Due to maint.by PDB | 20 | 30.6667 | Power interruption
Chowmuhani | 132/33kV transformer TR-2 (425T) LT | 2023-06-24 12:46 | 2023-06-24 12:46 | 0:00 | S/O | Due to T2 VCB incomer String repair | 0 | 0 | No interruption
Chowmuhani | 132/33kV transformer TR-2 (425T) HT | 2023-06-24 12:48 | 2023-06-24 12:48 | 0:00 | S/O | Due to T2 VCB incomer String repair | 0 | 0 | No interruption
Shahjibazar | 132/33kV transformer TR-2 LT | 2023-06-24 13:20 | 2023-06-24 14:25 | 1:05 | S/O | Due to 33 kV Bus maint. | 35 | 37.9167 | Power interruption
Shahjibazar | 132/33kV transformer TR-2 HT | 2023-06-24 13:21 | 2023-06-24 14:24 | 1:03 | S/O | Due to 33 kV Bus maint. | 0 | 0 | No interruption
|  |  | Total : | 62:32 |  | Unserved Energy: |  | 274.15
Khulna Grid Circle :
Gopalganj | 400/132kV transformer ATR-01 LT | 2023-06-03 08:31 | 2023-06-03 16:38 | 8:07 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV 400kV Bus-02 | 2023-06-03 08:43 | 2023-06-03 17:55 | 9:12 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-02 HT | 2023-06-03 09:02 | 2023-06-03 17:52 | 8:50 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-02 LT | 2023-06-04 08:07 | 2023-06-04 17:51 | 9:44 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-02 HT | 2023-06-04 08:11 | 2023-06-04 17:50 | 9:39 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV 400kV Bus-02 | 2023-06-04 08:14 | 2023-06-04 21:46 | 13:32 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-03 HT | 2023-06-04 18:13 | 2023-06-04 20:27 | 2:14 | S/O | Due to maint.work | 0 | 0 | No interruption
Gopalganj | 400kV Bus-01 | 2023-06-06 07:52 | 2023-06-06 16:40 | 8:48 | S/O | Due to maint.work | 0 | 0 | No interruption
Payra | 400/132/33kV Auto transformer-02 LT | 2023-06-06 09:48 | 2023-06-09 11:26 | 73:38 | S/O | Due to CSD-100 SAS Commissioning. | 0 | 0 | No interruption
Payra | 400/132/33kV Auto transformer-02 HT | 2023-06-06 09:50 | 2023-06-09 11:24 | 73:34 | S/O | Due to CSD-100 SAS Commissioning. | 0 | 0 | No interruption
Gopalganj | 400kV Bus-01 | 2023-06-07 07:35 | 2023-06-07 17:01 | 9:26 | S/O | Due to BBP Commissioning & Testing. | 0 | 0 | No interruption
Gopalganj | 400kV Bus-01 | 2023-06-07 11:36 | 2023-06-07 13:30 | 1:54 | S/O | Due to project work | 0 | 0 | No interruption
Barishal | 230/132kV transformer ATR-2 HT |  | 2023-06-07 12:28 |  | S/O | After maint.work | 0 | 0 | No interruption
Barishal | 230/132kV transformer ATR-2 LT |  | 2023-06-07 12:31 |  | S/O | After maint.work | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-1 LT | 2023-06-09 06:19 | 2023-06-09 08:59 | 2:40 | S/O | Due to maint.work of 33 kV CT clamp | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-1 HT | 2023-06-09 06:19 | 2023-06-09 08:57 | 2:38 | S/O | Due to maint.work of 33 kV CT clamp | 0 | 0 | No interruption
Bhandaria | 132/33kV transformer T-1 LT | 2023-06-09 08:40 | 2023-06-09 09:52 | 1:12 | S/O | Due to project work | 6 | 0 | Power interruption
Bhandaria | 132/33kV transformer T-1 HT | 2023-06-09 08:40 | 2023-06-09 10:50 | 2:10 | S/O | Due to project work | 6 | 13 | Power interruption
Payra | 400/132/33kV Auto transformer-01 LT | 2023-06-09 15:53 | 2023-06-10 12:09 | 20:16 | S/O | Due to project work | 0 | 0 | No interruption
Payra | 400/132/33kV Auto transformer-01 HT | 2023-06-09 15:54 | 2023-06-10 12:08 | 20:14 | S/O | Due to project work | 0 | 0 | No interruption
Payra | 400/132/33kV Auto transformer-01 HT | 2023-06-11 13:15 | 2023-06-11 14:05 | 0:50 | S/O | Due to project work | 0 | 0 | No interruption
Barishal | 230/132kV transformer T-4 LT | 2023-06-13 07:01 | 2023-06-13 08:27 | 1:26 | S/O | Due to maint.work at 33 kV DS | 22 | 31.5333 | Power interruption
Barishal | 230/132kV transformer ATR-5 HT |  | 2023-06-13 08:26 |  | S/O | After maint.work | 0 | 0 | No interruption
Madaripur | 132/33kV transformer T3-426T LT | 2023-06-15 09:38 | 2023-06-15 11:17 | 1:39 | S/O | Due to DC MCB Fault. | 0 | 0 | No interruption
Madaripur | 132/33kV transformer T3-426T HT | 2023-06-15 09:38 | 2023-06-15 11:16 | 1:38 | S/O | Due to DC MCB Fault. | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-02 LT | 2023-06-17 10:31 | 2023-06-17 16:57 | 6:26 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-1 LT | 2023-06-18 09:10 | 2023-06-18 11:43 | 2:33 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-1 HT | 2023-06-18 09:11 | 2023-06-18 11:42 | 2:31 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-01 LT | 2023-06-18 09:26 | 2023-06-18 12:24 | 2:58 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-01 HT | 2023-06-18 09:31 | 2023-06-18 12:20 | 2:49 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-03 LT | 2023-06-18 12:41 | 2023-06-18 16:33 | 3:52 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | 400/132kV transformer ATR-03 HT | 2023-06-18 12:48 | 2023-06-18 16:26 | 3:38 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-2 LT | 2023-06-19 09:06 | 2023-06-19 11:59 | 2:53 | S/O | Due to NLDC control, testing. | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-2 HT | 2023-06-19 09:07 | 2023-06-19 11:58 | 2:51 | S/O | Due to NLDC control, testing. | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-1 LT | 2023-06-19 12:04 | 2023-06-19 13:22 | 1:18 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | 132/33kV transformer Tr-1 HT | 2023-06-19 12:05 | 2023-06-19 13:21 | 1:16 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | 132kV Bus Coupler | 2023-06-21 14:03 | 2023-06-21 16:55 | 2:52 | S/O | Due to NLDC signal testing. | 0 | 0 | No interruption
Madaripur | 132/33kV transformer T2-415T LT | 2023-06-22 17:20 | 2023-06-22 18:16 | 0:56 | S/O | Due to maint. work | 0 | 0 | No interruption
Patuakhali | 132/33kV transformer T3-425T LT | 2023-06-23 16:09 | 2023-06-24 15:37 | 23:28 | S/O | Due to project work | 0 | 0 | No interruption
Patuakhali | 132/33kV transformer T3-425T LT | 2023-06-23 16:09 | 2023-06-24 15:35 | 23:26 | S/O | Due to project work | 0 | 0 | No interruption
Rajbari | 132/33kV transformer T-2 LT | 2023-06-24 07:21 | 2023-06-24 10:48 | 3:27 | S/O | Due to New feeder loop connection. | 3 | 10.35 | Power interruption
Rajbari | 132/33kV transformer T-2 HT | 2023-06-24 07:21 | 2023-06-24 10:48 | 3:27 | S/O | Due to New feeder loop connection. | 0 | 0 | No interruption
Khulna(S) | 230/132kV transformer TR-1 LT | 2023-06-24 09:50 | 2023-06-24 13:02 | 3:12 | S/O | Due to Water Deluge System Tested. | 0 | 0 | No interruption
Khulna(S) | 230/132kV transformer TR-1 HT | 2023-06-24 09:51 | 2023-06-24 13:01 | 3:10 | S/O | Due to Water Deluge System Tested. | 0 | 0 | No interruption
Khulna(S) | 230/132kV transformer TR-2 LT | 2023-06-24 13:08 | 2023-06-24 15:10 | 2:02 | S/O | Due to Water Deluge System Tested. | 0 | 0 | No interruption
Khulna(S) | 230/132kV transformer TR-2 HT | 2023-06-24 13:08 | 2023-06-24 15:09 | 2:01 | S/O | Due to Water Deluge System Tested. | 0 | 0 | No interruption
Rampal | 400kV bus-2 | 2023-06-28 02:27 | 2023-06-28 08:37 | 6:10 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 390:37 |  | Unserved Energy : |  | 54.8833
HVDC Grid Circle
BIPTC | BIPTC S/S 10CF25 |  | 2023-06-02 17:53 |  | S/O | After maint.work | 0 | 0 | No interruption
Baghabari | 230 kV Bus-1 | 2023-06-09 08:39 | 2023-06-15 16:32 | 151:53 | S/O | Due to project work | 0 | 0 | No interruption
Shahjadpur | 132/33kV transformer T-4(435T) LT |  | 2023-06-16 08:36 |  | S/O | After maint.work | 0 | 0 | No interruption
Jhenaidah | 132 kV Bus-B |  | 2023-06-18 01:39 |  | S/O | After maint.work | 0 | 0 | No interruption
Ruppur | 132/11kV transformer TR-02 LT |  | 2023-06-19 11:15 |  | S/O | After maint.work | 0 | 0 | No interruption
Ishurdi | 132/11kV transformer TR-02 HT | 2023-06-22 09:14 | 2023-06-22 10:09 | 0:55 | S/O | Due to A/M work | 60 | 55 | Power interruption
Jashore | 132/33kV transformer T-3 LT |  | 2023-06-24 11:26 |  | S/O | After maint.work | 0 | 0 | No interruption
Jhenaidah | 132 /33kV Bus-B |  | 2023-06-25 16:57 |  | S/O | After maint.work | 0 | 0 | No interruption | 812.0333
Pabna | 132/33kV transformer T-2 HT |  | 2023-06-26 12:32 |  |  | newly commission | 0 | 0 | No interruption | 55
Pabna | 132/33kV transformer T-2 LT |  | 2023-06-26 12:45 |  |  | newly commission |  | 0 | No interruption | 867.0333
|  |  | Total : | 152:48 |  | Unserved Energy : |  | 55
Bogura Grid Circle:
Barapukuria | 230/132/33 kV transformer T-4, 444T LT | 2023-06-02 09:58 | 2023-06-02 12:10 | 2:12 | S/O | Due to maint.work | 40 | 0 | Power interruption
Barapukuria | 230/132/33kV KV transformer T-4, 444T HT | 2023-06-02 10:03 | 2023-06-02 12:09 | 2:06 | S/O | Due to project work | 40 | 84 | Power interruption
Bogra | 132kV main Bus-2 | 2023-06-05 08:05 | 2023-06-05 09:06 | 1:01 | S/O | Due to Conductor string maintenance. | 0 | 0 | No interruption
Bogra | 132kV main Bus-1 | 2023-06-05 09:20 | 2023-06-05 11:39 | 2:19 | S/O |  | 0 | 0 | No interruption
Bogra | 132kV main Bus-2 | 2023-06-05 11:44 | 2023-06-05 12:39 | 0:55 | S/O | Due to Conductor string maintenance. | 0 | 0 | No interruption
Bogra | 132/33kV transformer-1 LT | 2023-06-06 07:46 | 2023-06-06 07:46 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Mithapukur | 132/33kV transformer TR-1(404T) LT | 2023-06-07 12:33 | 2023-06-07 14:34 | 2:01 | S/O | Due to changing work | 0 | 0 | No interruption
Mithapukur | 132/33kV transformer TR-1(404T) HT | 2023-06-07 12:34 | 2023-06-07 14:34 | 2:00 | S/O | Due to changing work | 0 | 0 | No interruption
Mithapukur | 132/33kV transformer TR-2 (414T) HT | 2023-06-07 15:24 | 2023-06-07 16:44 | 1:20 | S/O | Due to changing work | 0 | 0 | No interruption
Mithapukur | 132/33kV transformer TR-2 (414T) LT | 2023-06-07 15:24 | 2023-06-07 16:45 | 1:21 | S/O | Due to changing work | 0 | 0 | No interruption
Sherpur | 132/33kV transformer- 03 HT | 2023-06-09 08:27 | 2023-06-09 15:20 | 6:53 | S/O | Due to loop connection | 0 | 0 | No interruption
Bogra | 132/33kV transformer-2 LT | 2023-06-10 07:20 | 2023-06-10 10:30 | 3:10 | S/O | Due to Junction point temperature reduce work. | 12 | 0 | Power interruption
Bogra | 132/33kV transformer-2 HT | 2023-06-10 07:21 | 2023-06-10 10:30 | 3:09 | S/O | Due to Junction point temperature reduce work. | 12 | 37.8 | Power interruption
Mahasthangarh | 132/33kV transformer 416T MTR 2 LT | 2023-06-10 08:02 | 2023-06-10 12:03 | 4:01 | S/O | Due to 33 kV Bus maint. | 21 | 84.35 | Power interruption
Mahasthangarh | 132/33kV transformer 416T MTR 2 HT | 2023-06-10 08:03 | 2023-06-10 12:05 | 4:02 | S/O | Due to 33 kV Bus maint. | 0 | 0 | No interruption
Rajshahi | 132/33kV transformer T-3 HT | 2023-06-13 07:16 | 2023-06-13 09:06 | 1:50 | S/O | Due to maint.work | 35 | 64.1667 | Power interruption
Rajshahi | 132/33kV transformer T-1 | 2023-06-13 07:16 | 2023-06-13 08:54 | 1:38 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 132/33kV transformer T-2 HT | 2023-06-13 07:16 | 2023-06-13 08:56 | 1:40 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 132/33kV transformer T-2 LT | 2023-06-13 07:16 | 2023-06-13 08:58 | 1:42 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 33 kV BusT-1 | 2023-06-13 07:18 | 2023-06-13 08:55 | 1:37 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 33 kV BusT-2 | 2023-06-13 07:18 | 2023-06-13 08:58 | 1:40 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 33 kV BusT-3 | 2023-06-13 07:18 | 2023-06-13 09:07 | 1:49 | S/O | Due to maint.work | 0 | 0 | No interruption
Rajshahi | 230/132/33kV transformer T-01 (406T) LT | 2023-06-15 08:24 | 2023-06-15 09:56 | 1:32 | S/O | Due to 33 kV maint.work | 0 | 0 | No interruption
Rajshahi | 230/132/33kV transformer T-01 (406T) HT | 2023-06-15 08:25 | 2023-06-15 09:56 | 1:31 | S/O | Due to 33 kV maint.work | 3 | 4.55 | Power interruption
Purbasadipur | 132/33kV transformer T-3 (423T) LT & HT | 2023-06-16 08:25 | 2023-06-16 20:18 | 11:53 | S/O | Due to 33 kV BUS upgradation. | 10 | 118.8333 | Power interruption
Purbasadipur | 132/33kV transformer T-3 | 2023-06-17 10:50 | 2023-06-17 15:38 | 4:48 | S/O | Due to changing work | 0 | 0 | No interruption
Purbasadipur | 132/33kV transformer T-1(403) LT | 2023-06-23 07:33 | 2023-06-23 08:16 | 0:43 | S/O | Due to maint.work | 45 | 0 | Power interruption
Purbasadipur | 132/33kV transformer T-1(403) HT | 2023-06-23 07:35 | 2023-06-23 08:15 | 0:40 | S/O | Due to maint.work | 45 | 30 | Power interruption
Purbasadipur | 132/33kV transformer T-1( 403) LT | 2023-06-24 07:35 | 2023-06-24 08:27 | 0:52 | S/O | Due to maint.work | 0 | 0 | No interruption
Purbasadipur | 132/33kV transformer T-1(403) HT | 2023-06-24 16:15 | 2023-06-24 16:58 | 0:43 | S/O | Due to PBS work | 13 | 9.3167 | Power interruption
Purbasadipur | 132/33kV transformer T-1( 403) LT | 2023-06-24 16:15 | 2023-06-24 16:59 | 0:44 | S/O | Due to PBS work | 0 | 0 | No interruption
Rohonpur | 400KV bus-1 |  | 2023-06-24 17:17 |  |  | is charged for the first time. | 0 | 0 | No interruption
Rohonpur | 400KV bus-2 |  | 2023-06-24 17:24 |  |  | is charged for the first time. | 0 | 0 | No interruption
Rohonpur | 400/132KV, 52MVA, T1 |  | 2023-06-24 17:24 |  |  | is charged for the first time. | 0 | 0 | No interruption
Naogaon | 132/33kV transformer T-1 LT | 2023-06-27 07:10 | 2023-06-27 08:40 | 1:30 | S/O | Due to maint.work | 0 | 0 | No interruption
Naogaon | 132/33kV transformer T-1 HT | 2023-06-27 07:12 | 2023-06-27 08:51 | 1:39 | S/O | Due to maint.work | 0 | 0 | No interruption
|  |  | Total : | 99:17 |  | Unserved Energy : |  | 433.0167
Others :
Ashugonj | Ashugonj 230/132kV OAT-12 | 2023-06-23 07:02 | 2023-06-23 10:21 | 3:19 | S/O | Due to corrective maint. | 0 | 0 | No interruption | 1202.95
|  |  | Total : | 3:19 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1070:55 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: June 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bashundhara | Bashundhara-Rampura 132 kV Ckt-1 | 2023-06-01 12:15 | 2023-06-01 12:36 | 0:21 | S/O | Due to replacement work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132kV Ckt-2 |  | 2023-06-06 09:30 |  | S/O | After maint.work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230kV Ckt-1 | 2023-06-06 11:35 | 2023-06-06 11:35 | 0:00 | S/O | Due to Instalation | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230KV Ckt-2 | 2023-06-08 14:32 | 2023-06-08 16:09 | 1:37 | S/O | Due to maint. work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV Ckt-2 | 2023-06-11 11:10 | 2023-06-11 16:28 | 5:18 | S/O | Due to tree trimming | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132kV Ckt-2 |  | 2023-06-14 09:49 |  | S/O | After maint.work | 0 | 0 | No interruption
Sreepur | Sreepur-Ashuganj 230 kV Ckt-2 | 2023-06-15 11:32 | 2023-06-15 14:58 | 3:26 | S/O | Due to maint. work | 0 | 0 | No interruption
Sreepur | Sreepur-Ashuganj 230 kV Ckt-1 | 2023-06-15 11:32 | 2023-06-15 14:58 | 3:26 | S/O | Due to maint. work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-01 | 2023-06-18 09:13 | 2023-06-18 19:32 | 10:19 | S/O | Due to bus coupler connected | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230kV Ckt-1 |  | 2023-06-21 17:18 |  | S/O | After maint.work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbag 132kV Ckt-1 | 2023-06-22 11:10 | 2023-06-22 13:15 | 2:05 | S/O | Due to maint. work | 0 | 0 | No interruption
Tongi | Tongi 230/132/33-Tongi 80 MW PS | 2023-06-25 10:40 | 2023-06-26 14:53 | 28:13 | S/O | Due to maint. work | 0 | 0 | No interruption
|  |  | Total : | 54:45 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Madanganj | Madanganj -Summit 102 MW 132 kV Ckt |  | 2023-06-01 10:26 |  | S/O | After maint.work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230kV Ckt-2 | 2023-06-06 06:28 | 2023-06-06 06:28 | 0:00 | S/O | Due to Order of NLDC | 0 | 0 | No interruption
Fatullah | Fatullah -Hasnabad 132 kV Ckt | 2023-06-07 09:02 | 2023-06-07 09:02 | 0:00 | S/O | Due to line overload | 0 | 0 | No interruption
Fatullah | Fatullah-Madanganj 132 kV Ckt-2 | 2023-06-08 07:39 | 2023-06-08 16:06 | 8:27 | S/O | Due to Order of NLDC | 0 | 0 | No interruption
Fatullah | Fatullah-Madanganj 132 kV Ckt-2 | 2023-06-09 07:38 | 2023-06-09 21:33 | 13:55 | S/O | Due to changing work | 0 | 0 | No interruption
Fatullah | Fatullah-Madanganj 132 kV Ckt-2 | 2023-06-09 07:27 | 2023-06-10 18:20 | 34:53 | S/O |  | 0 | 0 | No interruption
Fatullah | Fatullah-Madanganj 132 kV Ckt-2 | 2023-06-11 07:31 | 2023-06-11 20:06 | 12:35 | S/O | Due to Order of NLDC | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalakhya 132kV Ckt-1 | 2023-06-13 07:49 | 2023-06-13 17:14 | 9:25 | S/O | Due to Order of NLDC | 0 | 0 | No interruption
Madanganj | Madanganj-Shitalakhya 132kV Ckt- | 2023-06-13 07:51 | 2023-06-13 17:12 | 9:21 | S/O | Due to changing work | 0 | 0 | No interruption
Madanganj | Madanganj -Shitalakhya 132 kV Ckt | 2023-06-14 08:18 | 2023-06-14 15:47 | 7:29 | S/O | Due to maint.work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132kV Ckt-1 | 2023-06-15 08:26 | 2023-06-15 16:04 | 7:38 | S/O | Due to Dur to Insulator checking. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132kV Ckt-1 | 2023-06-16 08:54 | 2023-06-16 18:32 | 9:38 | S/O | Due to Insulator checking | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132kV Ckt-1 | 2023-06-17 08:02 | 2023-06-17 17:56 | 9:54 | S/O | Due to Insulator dick checking. | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Aminbazar 230 kV Ckt-01 | 2023-06-20 08:40 | 2023-06-20 08:40 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Gulshan | Gulshan-Rampura 132kV Ckt-1 | 2023-06-21 15:01 | 2023-06-21 15:03 | 0:02 | S/O | Due to Comand by NLDC. | 0 | 0 | No interruption
Sonargaon | Sonargaon-OPML(IEL-1) 132 kV Ckt | 2023-06-23 08:58 | 2023-06-23 18:25 | 9:27 | S/O | Due to project work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230kV Ckt-2 |  | 2023-06-24 15:34 |  | S/O | After maint.work | 0 | 0 | No interruption
Ghorashal | Ghorashal - Joydevpur 132 kV Ckt-2 | 2023-06-27 06:29 | 2023-06-27 11:15 | 4:46 | S/O | Due to maint.work | 0 | 0 | No interruption
Aggreko | Aggreko-keraniganj 132kV Ckt-1 | 2023-06-28 23:59 | 2023-06-28 23:59 | 0:00 | S/O | Due to Comand by NLDC. | 0 | 0 | No interruption
Hasnabad | Hasnabad -Aggreko Aourahati 132 kV Ckt | 2023-06-29 06:00 | 2023-06-29 06:00 | 0:00 | S/O | Due to Comand by NLDC. | 0 | 0 | No interruption
|  |  | Total : | 137:30 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Banskhali | Banskhali - Matarbari 400KV ckt-2 |  | 2023-06-03 13:03 |  |  | first energized | 0 | 0 | No interruption
Banskhali | Banskhali - Matarbari 400KV ckt-1 |  | 2023-06-03 13:43 |  |  | Due to meter polarity correction | 0 | 0 | No interruption
AKSML | AKSML-Khulshi 132kV Ckt-1 |  | 2023-06-04 12:43 |  | S/O | After maint.work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-2 | 2023-06-06 05:39 | 2023-06-06 18:09 | 12:30 | S/O | Due to maint.work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132kV Ckt-1 | 2023-06-08 11:23 | 2023-06-08 11:23 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132kV Ckt-2 |  | 2023-06-08 14:24 |  | S/O | After maint.work | 0 | 0 | No interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-2 | 2023-06-15 16:16 | 2023-06-15 18:25 | 2:09 | S/O | Due to maint.work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132kV Ckt-1 |  | 2023-06-25 19:16 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 14:39 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Chauddagram | Chauddagram-Cumilla(S) 132 kV Ckt-1 | 2023-06-07 12:14 | 2023-06-07 15:34 | 3:20 | S/O | Due to maint.work | 0 | 0 | No interruption
Chauddagram | Chauddagram-Cumilla(S) 132 kV Ckt-1 | 2023-06-07 12:24 | 2023-06-07 15:38 | 3:14 | S/O | Due to SMD work | 0 | 0 | No interruption
Chauddagram | Chauddagram-Feni 132 kV Ckt-1 | 2023-06-07 16:20 | 2023-06-07 19:23 | 3:03 | S/O | Due to SMD work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Brahmanbaria 132kV Ckt-2 |  | 2023-06-13 22:14 |  | S/O | After maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132kV Ckt-1 | 2023-06-16 06:10 | 2023-06-16 21:53 | 15:43 | S/O | Due to changing work | 0 | 0 | No interruption
Brahmanbaria | Brahmanbaria-Shahibazar 132 kV Ckt-2 | 2023-06-17 03:25 | 2023-06-17 03:42 | 0:17 | S/O | Due to remove fault. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sreepur 230 kV Ckt-1 | 2023-06-17 06:20 | 2023-06-17 06:20 | 0:00 | S/O | Due to OPGW. | 0 | 0 | No interruption
Chattak | Chattak-Sylhet 132 kV Ckt-2 | 2023-06-19 11:25 | 2023-06-19 16:07 | 4:42 | S/O | Due to SPMD work | 0 | 0 | No interruption
Chattak | Chattak-Sylhet 132 kV Ckt-1 | 2023-06-19 16:07 | 2023-06-19 17:22 | 1:15 | S/O | Due to maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132kV Ckt-1 | 2023-06-21 06:25 | 2023-06-21 11:08 | 4:43 | S/O | Due to As per instruction of NLDC. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 | 2023-06-23 08:54 | 2023-06-23 10:23 | 1:29 | S/O | Due to For rely change | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132kV Ckt-1 |  | 2023-06-23 10:52 |  | S/O | After maint.work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132kV Ckt-2 | 2023-06-23 11:21 | 2023-06-23 11:54 | 0:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132kV Ckt-2 | 2023-06-27 08:21 | 2023-06-27 10:27 | 2:06 | S/O | Due to As per instruction of NLDC | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV Ckt-1 |  | 2023-06-29 08:15 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 40:25 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gollamari | Gollamari-Gopalgonj Line - 1 | 2023-06-01 09:59 | 2023-06-01 15:27 | 5:28 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalgonj Line - 2 | 2023-06-01 15:27 | 2023-06-01 15:27 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | Gopalganj 400/132kV - 400kV Aminbazar Ckt-1 | 2023-06-04 08:29 | 2023-06-04 13:28 | 4:59 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | Gopalganj 400/132kV - 400kV Aminbazar Ckt-2 | 2023-06-04 14:19 | 2023-06-04 16:30 | 2:11 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | Gopalganj 400/132kV - 400kV Payra Ckt-2 | 2023-06-06 08:28 | 2023-06-06 16:27 | 7:59 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj | Gopalganj 400/132kV - 400kV Rampal Ckt-2 | 2023-06-06 09:14 | 2023-06-06 16:30 | 7:16 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N) 400/230 kV -Rampal Ckt-2 | 2023-06-06 09:14 | 2023-06-06 16:29 | 7:15 | S/O | Due to SAS Commissioning of Gopalganj end. | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj - 400kV Payra Ckt-1 | 2023-06-07 07:59 | 2023-06-07 16:00 | 8:01 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj 400/132kV - 400kV Rampal Ckt-2 | 2023-06-07 08:00 | 2023-06-07 12:02 | 4:02 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Rampal Ckt-2 | 2023-06-07 08:00 | 2023-06-07 11:57 | 3:57 | S/O | Due to Bus bar Protection Testing. | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Rampal Ckt-1 | 2023-06-07 13:34 | 2023-06-07 17:06 | 3:32 | S/O | Due to Bus bar Protection Testing. | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj 400/132kV - 400kV Rampal Ckt-1 | 2023-06-07 13:42 | 2023-06-07 17:05 | 3:23 | S/O | Due to project work | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj 400/132kV - 400kV Rampal Ckt-1 | 2023-06-09 09:55 | 2023-06-12 15:50 | 77:55 | S/O | Due to maint work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV Ckt-1 | 2023-06-14 10:35 | 2023-06-14 13:26 | 2:51 | S/O | Due to SMD work | 0 | 0 | No interruption
Gopalganj | Gopalganj - 400kV Payra Ckt-2 | 2023-06-16 09:33 | 2023-06-17 16:24 | 30:51 | S/O | Due to maint work | 0 | 0 | No interruption
Gopalganj | Gopalganj - Gallamari 132 kV Ckt-1 | 2023-06-18 12:34 | 2023-06-18 15:04 | 2:30 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalgonj Line - 1 | 2023-06-18 12:37 | 2023-06-18 15:19 | 2:42 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | Gallamari- Khulna (S)132kV Ckt-1 | 2023-06-18 15:25 | 2023-06-18 16:56 | 1:31 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalgonj Line - 2 | 2023-06-19 13:39 | 2023-06-19 15:03 | 1:24 | S/O | Due to project work | 0 | 0 | No interruption
Gollamari | Gallamari- Khulna (S) 132kV Ckt-2 | 2023-06-19 15:06 | 2023-06-19 16:19 | 1:13 | S/O | Due to NLDC control signal testing | 0 | 0 | No interruption
Gopalganj | Gopalganj - Gallamari 132 kV Ckt-1 | 2023-06-20 10:00 | 2023-06-20 15:19 | 5:19 | S/O | Due to NLDC Control signal testing. | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalgonj 132 kV Ckt - 1 | 2023-06-20 10:01 | 2023-06-20 10:01 | 0:00 | S/O | Due to NLDC Control signal testing. | 0 | 0 | No interruption
Gollamari | Gopalganj - Gallamari 132 kV Ckt-1 |  | 2023-06-20 15:19 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj | Gopalganj - Gallamari 132 kV Ckt-2 | 2023-06-20 15:25 | 2023-06-20 16:38 | 1:13 | S/O | Due to NLDC control signal testing | 0 | 0 | No interruption
Gopalganj | Gopalganj -Gopalganj 100 MW 132 kV Ckt | 2023-06-21 07:30 | 2023-06-21 12:13 | 4:43 | S/O | Due to NLDC control signal testing | 0 | 0 | No interruption
Gollamari | Gollamari-Gopalgonj 132 kV Ckt -1 | 2023-06-21 13:56 | 2023-06-21 17:04 | 3:08 | S/O | Due to NLDC Control signal testing. | 0 | 0 | No interruption
|  |  | Total : | 193:23 |  | Unserved Energy: |  | 0
HVDC Grid Circle :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Bogura(New) | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 | 2023-06-05 07:57 | 2023-06-05 07:57 | 0:00 | S/O | Due to maint.work | 0 | 0 | No interruption
Bogura(New) | Bogura(New)-Bogura(Sherpur) 132 kV Ckt-1 | 2023-06-05 08:32 | 2023-06-05 12:53 | 4:21 | S/O | Due to maint.work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 | 2023-06-07 08:33 | 2023-06-07 09:46 | 1:13 | S/O | Due to changing work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-2 | 2023-06-07 09:49 | 2023-06-07 10:41 | 0:52 | S/O | Due to Meter change. | 0 | 0 | No interruption
Mithapukur | Mithapukur-Palashbari 132kV Ckt-1 | 2023-06-07 10:57 | 2023-06-07 11:44 | 0:47 | S/O | Due to meter change. | 0 | 0 | No interruption
Mithapukur | Mithapukur-Palashbari 132kV Ckt-2 | 2023-06-07 11:46 | 2023-06-07 12:26 | 0:40 | S/O | Due to meter change. | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-1 | 2023-06-14 07:07 | 2023-06-14 14:12 | 7:05 | S/O | Due to maint.work | 0 | 0 | No interruption
Rohanpur | Rohanpur-Bogura West 400 KV ckt-2 | 2023-06-22 17:14 | 2023-06-22 17:14 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Rajshahi | Rajshahi-50 MW P/S 132 kV Ckt | 2023-06-24 07:02 | 2023-06-24 22:09 | 15:07 | S/O | Due to maint.work | 0 | 0 | No interruption
Bogura | Bogura-Rohonpur 400KV clkt-2 |  | 2023-06-24 17:12 |  | S/O | After maint.work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur Confidence( 100MW ) 132kV Ckt-1 | 2023-06-27 10:12 | 2023-06-27 19:23 | 9:11 | S/O | Due to project work | 0 | 0 | No interruption
|  |  | Total : | 39:16 |  | Unserved Energy: |  | 0
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 479:58 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June 2023
| Area | Previous Month (May' 2023) |  |  |  | Current Month (June '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 27 | 63 | 60 | 150 | 43 | 29 | 50 | 122
2 | Dhaka (South) Grid Circle. | 16 | 26 | 28 | 70 | 13 | 15 | 37 | 65
3 | Chattogram Grid Circle. | 21 | 14 | 17 | 52 | 19 | 14 | 34 | 67
4 | Cumilla Grid Circle. | 16 | 25 | 20 | 61 | 44 | 30 | 35 | 109
5 | Khulna Grid Circle. | 44 | 50 | 32 | 126 | 28 | 35 | 73 | 136
6 | HVDC Grid Circle | 9 | 21 | 6 | 36 | 11 | 31 | 8 | 50
7 | Bogura Grid Circle. | 20 | 71 | 30 | 121 | 36 | 42 | 44 | 122
8 | Others | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 3
9 | Total | 153 | 270 | 193 | 616 | 196 | 221 | 223 | 674
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June 2023
| Area | Previous Month (May' 2023) |  |  |  | Current Month (June '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 156.83 | 1989.57 | 2356.6 | 4503 | 458.57 | 345.43 | 0 | 804
2 | Dhaka (South) Grid Circle. | 109.03 | 122.6 | 808.75 | 1040.38 | 179.77 | 203.77 | 310.25 | 693.79
3 | Chattogram Grid Circle. | 34.37 | 108 | 69 | 211.37 | 54.74 | 41.28 | 75.65 | 171.67
4 | Cumilla Grid Circle. | 536.02 | 79.64 | 413.4167 | 1029.0767 | 201.94 | 224.4 | 274.15 | 700.49
5 | Khulna Grid Circle. | 449.16 | 364.5 | 366.53 | 1180.19 | 662.49 | 161.05 | 54.88 | 878.42
6 | HVDC Grid Circle | 873.93 | 611.681 | 91.33 | 1576.941 | 295.25 | 516.79 | 55 | 867.04
7 | Bogura Grid Circle. | 191.04 | 933.73 | 936.47 | 2061.24 | 550.45 | 174.25 | 433.02 | 1157.72
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 2350.38 | 4209.721 | 5042.0967 | 11602.1977 | 2460.09 | 2375.79 | 2460.3967 | 5273.13
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June 2023
A) Power Interruption
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 13 | - | 13 | 2 | 3 | 8 | 503.73
2 | Dhaka (South) | 5031.6 | 5 | 3 | 8 | - |  | 8 | 557.42
3 | Chattogram | 2042 | 4 | 1 | 5 |  | 3 | 2 | 154.5
4 | Khulna | 2434 | 21 | 3 | 24 | 8 | 7 | 9 | 821.47
5 | HVDC | 5954.3 | 12 | 1 | 13 | 3 | 1 | 8 | 867.03
6 | Bogura | 3145.6 | 30 | 8 | 38 | 8 | 14 | 16 | 1090.89
7 | Cumilla | 2981 | 15 | 4 | 19 | 5 | 3 | 10 | 509.13
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 4504.17
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.92%
3 | Chattogram | 99.9%
4 | Khulna | 99.64%
5 | HVDC | 99.93% | [6 empty] | Executive Engineer
6 | Bogura | 99.88% | [6 empty] | Information Management Division
7 | Cumilla | 99.97% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 7 | - | 7 | 5 | 1 | 1 | - | 300.27
2 | Dhaka (South) | 990.29 | - | 3 | - | 3 | 1 | 2 | - | - | 136.37
3 | Chattogram | 917 | - | 2 | - | 2 | 2 | - | - | - | 17.17
4 | Khulna | 1238.4 | - | 4 | - | 4 | 2 | 1 | 1 |  | 56.95
5 | HVDC | 1325 | - | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 4 | - | 4 | 3 | 1 | - | - | 66.83
7 | Cumilla | 1648.16 | - | 4 | - | 4 | - | 2 | 2 |  | 191.35
8 | Others | - | - | - | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 768.94
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.89%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.98%
7 | Cumilla | 99.98%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-06-01 | 27 | - | 5 | 05hr49 min | 3 | 07hr49 min | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Tangail | 1 | 0:59 | 14.75
Tangail | 1 | 1:00 | 15
Sherpur | 1 | 1:26 | 28.6667
Manikganj | 1 | 0:03 | 1.6
Manikganj | 1 | 0:03 | 0.8
Jamalpur | 1 | 1:48 | 36
Kabirpur | 1 | 1:34 | 148.8333
Kabirpur | 1 | 1:07 | 55.8333
Tongi | 1 | 0:49 | 66.15
Kodda | 1 | 1:16 | 50.6667
Sherpur | 1 | 0:47 | 40
Sherpur | 1 | 0:48 | 14.1
Sherpur | 1 | 1:34 | 31.3333
Kaliakoir | 1 | 0:23 | 60.1833
Kaliakoir | 1 | 0:13 | 102.2667
Kaliakoir | 1 | 6:52 | 82.4
Jamalpur | 1 | 0:14 | 19.8333
Tangail | 1 | 0:19 | 7.9167
Kodda | 1 | 0:40 | 11.3333
Tangail | 1 | 0:14 | 16.3333
Sonargaon | 1 | 1:23 | 85.7667
Siddhirganj | 1 | 3:56 | 118
Madanganj | 1 | 1:52 | 16.8
Nawabganj | 1 | 0:42 | 11.2
Nawabganj | 1 | 1:17 | 15.4
Haripur | 1 | 0:52 | 52
Sonargaon | 1 | 0:44 | 64.5333
Haripur | 1 | 0:17 | 19.8333
Sonargaon | 1 | 1:52 | 112
Ghorashal | 1 | 4:03 | 101.25
Ghorashal | 1 | 3:14 | 97
Halishahar | 1 | 0:47 | 18.0167
Dohazari | 1 | 0:47 | 14.8833
Dohazari | 1 | 1:28 | 26.4
Chandraghona | 1 | 0:51 | 19.55
Cox'sbazar | 1 | 0:09 | 10.5
Baroaulia | 1 | 0:20 | 6.6667
Madunaghat | 1 | 4:27 | 75.65
Beanibazar | 1 | 0:38 | 14.5667
Beanibazar | 1 | 0:38 | 14.5667
Chowmuhani | 1 | 1:20 | 33.3333
Kulaura | 1 | 1:22 | 24.6
Fenchuganj | 1 | 0:06 | 1
Feni | 1 | 0:24 | 20
Chhatak | 1 | 2:18 | 3.45
Sylhet | 1 | 0:27 | 7.2
Cumilla(N) | 1 | 0:37 | 9.25
Brahmanbaria | 1 | 0:07 | 3.5
Fenchuganj | 1 | 2:31 | 15.1
Ramganj | 1 | 2:00 | 40
Cumilla(N) | 1 | 1:25 | 25.5
Chowmuhani | 1 | 0:25 | 22.9167
Chowmuhani | 1 | 1:24 | 86.8
Chauddagram | 1 | 1:03 | 74.55
Chowmuhani | 1 | 1:12 | 17.6667
Chowmuhani | 1 | 0:46 | 12.3333
Ramganj | 1 | 4:47 | 143.5
Ramganj | 1 | 1:38 | 62.0667
Cumilla(N) | 1 | 1:32 | 30.6667
Shahjibazar | 1 | 1:05 | 37.9167
Mongla | 1 | 0:43 | 8.9583
Mongla | 1 | 0:42 | 8.75
Noapara | 1 | 0:35 | 9.9167
Barishal | 1 | 0:03 | 2.15
Khulna (C) | 1 | 1:17 | 19.25
Narail | 1 | 2:04 | 8.2667
Narail | 1 | 0:16 | 1.3333
Narail | 1 | 0:19 | 1.5833
Gopalganj | 1 | 0:31 | 12.92
Gopalganj | 1 | 18:51 | 471.25
Mongla | 1 | 0:26 | 4.7667
Madaripur | 1 | 0:46 | 29.1333
Gopalganj | 1 | 0:12 | 5
Barishal | 1 | 0:12 | 18
Satkhira | 1 | 2:10 | 43.3333
Bagerhat | 1 | 0:45 | 5.25
Bhandaria | 1 | 0:53 | 15.9
Barishal | 1 | 0:52 | 21.6667
Barishal | 1 | 2:02 | 40.6667
Narail | 1 | 1:40 | 30
Barishal | 1 | 0:15 | 8.5
Barishal | 1 | 0:05 | 2.5
Barishal | 1 | 0:09 | 1.5
Khulna(S) | 1 | 1:06 | 46.2
Goalpara | 1 | 0:45 | 6.75
Bhandaria | 1 | 2:10 | 13
Barishal | 1 | 1:26 | 31.5333
Rajbari | 1 | 3:27 | 10.35
Kushtia | 1 | 1:20 | 40
Jashore | 1 | 0:34 | 17
Ishurdi | 1 | 1:17 | 71.8667
Jhenaidah | 1 | 2:29 | 74.5
Jhenaidah | 1 | 0:18 | 6
Chuadanga | 1 | 1:27 | 65.25
Jhenaidah | 1 | 0:27 | 18
Ishurdi | 1 | 3:33 | 266.25
Ishurdi | 1 | 2:59 | 149.1667
Jhenaidah | 1 | 0:09 | 6
Chuadanga | 1 | 1:12 | 54
Jhenaidah | 1 | 1:28 | 44
Ishurdi | 1 | 0:55 | 55
Mahasthangarh | 1 | 0:26 | 10.4
Niamatpur | 1 | 0:51 | 21.25
Naogaon | 1 | 0:56 | 18.6667
Purbasadipur | 1 | 0:50 | 20.8333
Purbasadipur | 1 | 0:54 | 36
Sirajganj | 1 | 0:56 | 24.2667
Purbasadipur | 1 | 0:28 | 9.3333
Purbasadipur | 1 | 0:42 | 28
Niamatpur | 1 | 0:20 | 5.3333
Niamatpur | 1 | 0:22 | 5.5
Niamatpur | 1 | 0:29 | 1.45
Niamatpur | 1 | 2:17 | 15.9833
Niamatpur | 1 | 0:13 | 3.4667
Mahasthangarh | 1 | 1:16 | 12.6667
Rajshahi | 1 | 1:00 | 10
Purbasadipur | 1 | 0:40 | 12
Bog-Sherpur | 1 | 1:46 | 97.1667
Bog-Sherpur | 1 | 1:46 | 97.1667
Sirajganj | 1 | 1:15 | 17.5
Naogaon | 1 | 0:47 | 14.1
Mahasthangarh | 1 | 1:03 | 10.5
Mithapukur | 1 | 0:38 | 17.7333
Mithapukur | 1 | 0:41 | 19.1333
Purbasadipur | 1 | 0:32 | 11.7333
Purbasadipur | 1 | 1:17 | 10.2667
Panchagarh | 1 | 1:16 | 19
Naogaon | 1 | 0:40 | 20.6667
Natore | 1 | 1:09 | 34.5
Natore | 1 | 1:09 | 34.5
Rajshahi | 1 | 1:15 | 18.75
Monakasha | 1 | 0:40 | 58
Panchagar | 1 | 0:18 | 1.5
Panchagar | 1 | 0:10 | 1.3333
Panchagar | 1 | 0:18 | 6
Barapukuria | 1 | 2:06 | 84
Bogra | 1 | 3:09 | 37.8
Mahasthangarh | 1 | 4:01 | 84.35
Rajshahi | 1 | 1:50 | 64.1667
Rajshahi | 1 | 1:31 | 4.55
Purbasadipur | 1 | 11:53 | 118.8333
Purbasadipur | 1 | 0:40 | 30
Purbasadipur | 1 | 0:52 | 9.3167
Total Unserved energy : | 165 | 197:07 | 5273.1117
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:June 2023
Sl. No | Sub-station | Load (MW) | Time
1 | AKS | 10 | 2023-06-07 09:00
2 | AKSML | 25 | 2023-06-23 07:00
3 | Aftabnagar | 68 | 2023-06-05 19:00
4 | Agargaon | 118 | 2023-06-12 10:00
5 | Agrabad | 82 | 2023-06-01 18:30
6 | Amnura | 75 | 2023-06-16 23:00
7 | Ashuganj | 82 | 2023-06-23 05:00
8 | BIPTC | N/A | N/A
9 | BSRM | 176 | 2023-06-20 19:00
10 | Bagerhat | 103 | 2023-06-15 20:00
11 | Bakulia | 130 | 2023-06-04 20:00
12 | Banani | 98 | 2023-06-21 13:00
13 | Bangabhaban | 26 | 2023-06-04 11:00
14 | Barapukuria | 66 | 2023-06-08 20:00
15 | Barguna | 24 | 2023-06-18 00:00
16 | Barishal | 122 | 2023-06-07 19:00
17 | Barishal-230 | 112 | 2023-06-16 22:00
18 | Baroaulia | 83 | 2023-06-21 12:00
19 | Baroirhat | 73 | 2023-06-05 19:00
20 | Bashundhara | 212 | 2023-06-05 19:00
21 | BashundharaCement | 7 | 2023-06-05 11:00
22 | Beanibazar | 85 | 2023-06-08 21:00
23 | Benapole | 72 | 2023-06-08 23:00
24 | Bhaluka | 160 | 2023-06-05 21:00
25 | Bhandaria | 56 | 2023-06-16 23:00
26 | Bhangura | 49 | 2023-06-15 21:00
27 | Bheramara(GK) | 72 | 2023-06-08 21:00
28 | Bhulta | 279 | 2023-06-14 23:00
29 | Bog-Sherpur | 72 | 2023-06-08 19:30
30 | Bogura | 183 | 2023-06-11 21:00
31 | Borhanuddin | 77 | 2023-06-28 23:00
32 | Brahmanbaria | 195 | 2023-06-02 22:00
33 | Cantonment | 180 | 2023-06-05 19:00
34 | Chandpur | 78 | 2023-06-08 21:00
35 | Chandraghona | 38 | 2023-06-30 13:00
36 | Chapai | 84 | 2023-06-15 21:00
37 | Charsaidpur | 50 | 2023-06-20 12:00
38 | Chauddagram | 65 | 2023-06-08 21:00
39 | Chhatak | 35 | 2023-06-06 20:00
40 | Chowmuhani | 232 | 2023-06-13 22:00
41 | Chuadanga | 121 | 2023-06-16 23:00
42 | Coxsbazar | 133 | 2023-06-06 21:00
43 | Cumilla(N) | 183 | 2023-06-03 22:00
44 | Cumilla(S) | 186 | 2023-06-13 14:00
45 | Daudkandi | 168 | 2023-06-21 19:00
46 | Dhaka | 38 | 2023-06-06 12:00
47 | Dhamrai | 132 | 2023-06-24 19:30
48 | Dhanmondi | 173 | 2023-06-07 12:00
49 | Dohazari | 106 | 2023-06-14 21:00
50 | Faridpur | 169 | 2023-06-08 21:00
51 | Fatullah | 73 | 2023-06-08 16:00
52 | Fenchuganj | 52 | 2023-06-08 14:00
53 | Feni | 123 | 2023-06-15 19:00
54 | GPH | 97 | 2023-06-04 17:00
55 | Ghorashal | N/A | N/A
56 | Goalpara | 42 | 2023-06-06 13:00
57 | Gollamari | 65 | 2023-06-01 23:00
58 | Gopalganj | 112 | 2023-06-08 20:00
59 | Gulshan | 130 | 2023-06-25 14:00
60 | Halishahar | 94 | 2023-06-22 13:00
61 | HaripurSBU | 182 | 2023-06-15 21:00
62 | Hasnabad | 123 | 2023-06-06 15:00
63 | Hathazari | 98 | 2023-06-24 19:00
64 | Ishurdi | 61 | 2023-06-11 19:00
65 | Jaldhaka | 82 | 2023-06-26 20:00
66 | Jamalpur | 168 | 2023-06-02 19:00
67 | Jashore | 161 | 2023-06-08 21:00
68 | Jhenaidah | 147 | 2023-06-08 21:00
69 | Joydebpur | 201 | 2023-06-06 19:00
70 | Joypurhat | 64 | 2023-06-02 21:00
71 | Juldah | 28 | 2023-06-12 23:00
72 | KSRM | 55 | 2023-06-12 18:00
73 | Kabirpur | 321 | 2023-06-06 19:30
74 | Kachua | 89 | 2023-06-22 19:30
75 | Kallyanpur | 162 | 2023-06-22 12:00
76 | Kalurghat | 40 | 2023-06-19 12:00
77 | Kamrangirchar | 72 | 2023-06-07 19:00
78 | Kaptai | N/A | N/A
79 | Kazla | 101 | 2023-06-04 23:00
80 | Keranigonj | 88 | 2023-06-03 19:30
81 | Khagrachori | 38 | 2023-06-13 19:30
82 | Khulna | 111 | 2023-06-15 20:00
83 | Khulshi | 201 | 2023-06-06 18:00
84 | Kishoreganj | 170 | 2023-06-04 21:00
85 | Kodda | 320 | 2023-06-07 21:00
86 | Kulaura | 54 | 2023-06-08 20:00
87 | Kurigram | 70 | 2023-06-26 20:00
88 | Kushtia | 168 | 2023-06-08 19:30
89 | Lalbag | 97 | 2023-06-07 19:00
90 | Lalmonirhat | 58 | 2023-06-26 19:30
91 | Madanganj | 48 | 2023-06-07 18:00
92 | Madaripur | 124 | 2023-06-16 22:00
93 | Madartek | 115.18 | 2023-06-07 23:00
94 | Madunaghat | 61 | 2023-06-01 19:00
95 | Magura | 71 | 2023-06-15 20:00
96 | Mahasthangarh | 74 | 2023-06-02 20:00
97 | Manikganj | 133 | 2023-06-07 20:00
98 | Maniknagar | 112 | 2023-06-04 11:00
99 | Matarbari | 48 | 2023-06-07 22:00
100 | Matuail | 73 | 2023-06-17 12:00
101 | Millgate | 114 | 2023-06-14 16:00
102 | Mirpur | 178 | 2023-06-07 19:00
103 | Mirsorai | 6 | 2023-06-01 15:00
104 | Mithapukur | 48 | 2023-06-16 21:00
105 | Modern | 0 | 2023-06-01 00:00
106 | Mogbazar | 165.8 | 2023-06-07 15:00
107 | Mongla | 44 | 2023-06-11 11:00
108 | Motijheel | 54 | 2023-06-06 15:00
109 | Munshiganj | 123 | 2023-06-07 19:00
110 | Mymensingh | 236 | 2023-06-23 22:00
111 | Naogaon | 150 | 2023-06-15 22:00
112 | Narail | 65 | 2023-06-08 20:00
113 | Narinda | 92 | 2023-06-07 18:30
114 | Narshingdi | 184 | 2023-06-07 20:00
115 | Natore | 166 | 2023-06-15 21:00
116 | Nawabganj | 70.5 | 2023-06-07 21:00
117 | Netrakona | 146 | 2023-06-04 20:00
118 | New | 138 | 2023-06-02 00:00
119 | Niamatpur | 97 | 2023-06-14 22:00
120 | Noapara | 56 | 2023-06-11 14:00
121 | PHP | 12 | 2023-06-26 19:30
122 | Pabna | 123 | 2023-06-08 20:00
123 | Palashbari | 142 | 2023-06-25 23:00
124 | Panchagarh | 70 | 2023-06-24 19:30
125 | Patuakhali | 118 | 2023-06-02 22:00
126 | Payra | 22 | 2023-06-01 20:00
127 | Postogola | 70 | 2023-06-07 19:00
128 | Purbachal | 26 | 2023-06-06 21:00
129 | Purbasadipur | 143 | 2023-06-09 22:00
130 | Rahanpur_I | 21 | 2023-06-08 03:00
131 | Rahim | 137 | 2023-06-25 01:00
132 | Rajbari | 80 | 2023-06-08 19:30
133 | Rajendrapur | 110 | 2023-06-03 20:00
134 | Rajshahi | 183 | 2023-06-15 19:30
135 | Rajshahi-230 | 56 | 2023-06-09 15:00
136 | Ramganj | 128 | 2023-06-08 20:00
137 | Rampur | 41 | 2023-06-14 20:00
138 | Rangamati | 18 | 2023-06-07 19:30
139 | Rangpur | 159 | 2023-06-11 19:30
140 | Ruppur | 6.6 | 2023-06-04 10:00
141 | SSM | 16 | 2023-06-05 11:00
142 | Saidpur | 122 | 2023-06-08 20:00
143 | Satkhira | 148 | 2023-06-08 21:00
144 | Satmasjid | 130 | 2023-06-07 18:30
145 | Savar | 219 | 2023-06-07 19:00
146 | Shahjadpur | 122 | 2023-06-14 21:00
147 | Shahjibazar | 157 | 2023-06-06 21:00
148 | Shahmirpur | 53.2 | 2023-06-15 15:00
149 | Shariatpur | 89 | 2023-06-16 22:00
150 | Sherpur | 150 | 2023-06-04 22:00
151 | Shikalbaha | N/A | N/A
152 | Shitalakhya | 114.8 | 2023-06-07 19:00
153 | Sholosohor | 39 | 2023-06-01 19:00
154 | Shyampur | 180 | 2023-06-22 10:00
155 | Siddhirganj | 134 | 2023-06-07 19:00
156 | Sirajganj | 132 | 2023-06-11 21:00
157 | Sonargaon | 92 | 2023-06-24 22:00
158 | Sreemongol | 70 | 2023-06-06 21:00
159 | Sreepur | 76 | 2023-06-07 19:30
160 | Srinagar | 54.2 | 2023-06-07 21:00
161 | Sunamganj | 64 | 2023-06-06 21:00
162 | Sylhet | 186 | 2023-06-06 19:00
163 | TK | 36.1 | 2023-06-29 23:00
164 | Tangail | 252 | 2023-06-15 19:00
165 | Thakurgaon | 113 | 2023-06-08 20:00
166 | Tongi | 119 | 2023-06-07 18:30
167 | Ullon | 55 | 2023-06-06 23:00
168 | Uttara | 85 | 2023-06-05 19:00
169 | UttaraNew | 67 | 2023-06-06 23:00
170 | Zigatola | 102 | 2023-06-15 16:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:June 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5700.05 | 2023-06-07 | 19:30
Chattogram | 1446 | 2023-06-20 | 20:00
Cumilla | 1383 | 2023-06-22 | 21:00
Mymensingh | 1169 | 2023-06-04 | 21:00
Sylhet | 626 | 2023-06-06 | 21:00
Khulna | 1931.8 | 2023-06-08 | 21:00
Barishal | 487 | 2023-06-15 | 22:00
Rajshahi | 1539 | 2023-06-15 | 21:00
Rangpur | 925 | 2023-06-12 | 19:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:June 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar | 400 | 421 | 2023-06-12 10:00 | 228 | 2023-06-03 10:00
2 | Ashuganj | 400 | N/A | N/A | N/A | N/A
3 | Bhulta | 400 | 406 | 2023-06-28 20:00 | 376 | 2023-06-02 12:00
4 | Bibiana | 400 | 410 | 2023-06-29 09:00 | 376 | 2023-06-18 12:00
5 | BIPTC | 400 | 409 | 2023-06-29 04:00 | 387 | 2023-06-03 15:00
6 | Bogura | 400 | N/A | N/A | N/A | N/A
7 | Gopalganj | 400 | 415 | 2023-06-28 06:00 | 389 | 2023-06-06 14:00
8 | Kaliakoir | 400 | 405 | 2023-06-30 16:00 | 357 | 2023-06-19 12:00
9 | Madunaghat_I | 400 | 425 | 2023-06-10 19:30 | 374 | 2023-06-12 12:00
10 | Payra | 400 | 419 | 2023-06-28 06:00 | 401 | 2023-06-07 11:00
11 | Rahanpur_I | 400 | 425 | 2023-06-13 19:30 | 401 | 2023-06-07 16:00
12 | Rampal | 400 | 414 | 2023-06-24 18:30 | 386 | 2023-06-06 15:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon | 230 | 260 | 2023-06-10 03:00 | 220 | 2023-06-02 14:00
2 | AKSML | 230 | 239 | 2023-06-03 21:00 | 201 | 2023-06-19 12:00
3 | Aminbazar | 230 | 244 | 2023-06-29 10:00 | 222 | 2023-06-18 11:00
4 | Ashuganj | 230 | 240 | 2023-06-28 19:00 | 223 | 2023-06-21 05:00
5 | Ashuganj-400 | 230 | N/A | N/A | N/A | N/A
6 | Baghabari | 230 | 232 | 2023-06-30 16:00 | 227 | 2023-06-30 10:00
7 | Barapukuria | 230 | 248 | 2023-06-29 10:00 | 221 | 2023-06-19 13:00
8 | Barapukuria-230 | 230 | N/A | N/A | N/A | N/A
9 | Barishal | 230 | 242 | 2023-06-08 18:30 | 226 | 2023-06-02 22:00
10 | Bheramara | 230 | 234 | 2023-06-03 23:00 | 226 | 2023-06-11 06:00
11 | Bhulta | 230 | 241 | 2023-06-29 08:00 | 222 | 2023-06-08 09:00
12 | Bibiana | 230 | 242 | 2023-06-30 20:00 | 227 | 2023-06-05 04:00
13 | BIPTC | 230 | 235 | 2023-06-03 23:00 | 221 | 2023-06-08 19:30
14 | Bogura | 230 | 231 | 2023-06-13 01:00 | 206 | 2023-06-26 23:00
15 | Borhanuddin | 230 | 250 | 2023-06-14 17:00 | 223 | 2023-06-08 07:00
16 | BSRM | 230 | 241 | 2023-06-04 21:00 | 226 | 2023-06-11 14:00
17 | Cumilla(N) | 230 | 237 | 2023-06-30 20:00 | 219 | 2023-06-18 12:00
18 | Fenchuganj | 230 | 245 | 2023-06-03 19:30 | 230 | 2023-06-18 06:00
19 | Ghorashal | 230 | N/A | N/A | N/A | N/A
20 | Ghorashal-230 | 230 | N/A | N/A | N/A | N/A
21 | GPH | 230 | 240 | 2023-06-04 21:00 | 212 | 2023-06-20 14:00
22 | Haripur | 230 | 238 | 2023-06-29 11:00 | 223 | 2023-06-13 23:00
23 | Hasnabad | 230 | 240 | 2023-06-28 19:30 | 238 | 2023-06-30 05:00
24 | Hathazari | 230 | 242 | 2023-06-06 19:00 | 215 | 2023-06-12 16:00
25 | Ishurdi | 230 | 236 | 2023-06-17 18:30 | 227 | 2023-06-10 08:00
26 | Jhenaidah | 230 | 236 | 2023-06-28 13:00 | 214 | 2023-06-16 19:30
27 | Kaliakoir | 230 | 239 | 2023-06-14 08:00 | 217 | 2023-06-08 09:00
28 | Keranigonj | 230 | 239 | 2023-06-28 19:00 | 219 | 2023-06-08 09:00
29 | Khulna(S) | 230 | 240 | 2023-06-24 20:00 | 223 | 2023-06-01 19:00
30 | Madunaghat_I | 230 | 244 | 2023-06-23 22:00 | 216 | 2023-06-24 14:00
31 | Maniknagar | 230 | 239 | 2023-06-29 08:00 | 219 | 2023-06-08 11:00
32 | Meghnaghat | 230 | 244 | 2023-06-29 07:00 | 226 | 2023-06-18 09:00
33 | Mirsorai | 230 | 242 | 2023-06-04 21:00 | 214 | 2023-06-19 12:00
34 | Rajshahi | 230 | 236 | 2023-06-07 23:00 | 220 | 2023-06-17 13:00
35 | Rampal | 230 | 237 | 2023-06-13 18:00 | 223 | 2023-06-06 15:00
36 | Rampur | 230 | N/A | N/A | N/A | N/A
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
37 | Rampura | 230 | 239 | 2023-06-29 09:00 | 220 | 2023-06-19 12:00
38 | Shikalbaha | 230 | 240 | 2023-06-06 20:00 | 216 | 2023-06-12 13:00
39 | Shyampur | 230 | 239 | 2023-06-29 11:00 | 224 | 2023-06-13 12:00
40 | Siddhirganj | 230 | 241 | 2023-06-30 19:00 | 223 | 2023-06-23 11:00
41 | Sirajgonj | 230 | 238 | 2023-06-13 07:00 | 227 | 2023-06-26 12:00
42 | Sreepur | 230 | 238 | 2023-06-27 20:00 | 224 | 2023-06-06 19:00
43 | Tongi | 230 | 244 | 2023-06-10 21:00 | 213 | 2023-06-19 11:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar | 132 | 143 | 2023-06-16 19:30 | 127 | 2023-06-02 18:00
15 | Agargaon | 132 | 141 | 2023-06-26 18:00 | 138 | 2023-06-13 01:00
16 | Agrabad | 132 | 140 | 2023-06-06 18:30 | 122 | 2023-06-19 12:00
17 | AKS | 132 | 137 | 2023-06-03 20:00 | 113 | 2023-06-18 03:00
18 | Aminbazar | 132 | 143 | 2023-06-27 19:30 | 113 | 2023-06-04 03:00
19 | Amnura | 132 | 141 | 2023-06-13 19:30 | 123 | 2023-06-16 19:30
20 | Ashuganj | 132 | 141 | 2023-06-29 11:00 | 125 | 2023-06-09 04:00
21 | Bagerhat | 132 | 139 | 2023-06-13 19:30 | 120 | 2023-06-30 21:00
22 | Bakulia | 132 | 141 | 2023-06-23 22:00 | 123 | 2023-06-12 12:00
23 | Banani | 132 | 143 | 2023-06-16 20:00 | 127 | 2023-06-18 11:00
24 | Bangabhaban | 132 | 137 | 2023-06-16 19:30 | 124 | 2023-06-08 11:00
25 | Barapukuria | 132 | 139 | 2023-06-19 07:00 | 120 | 2023-06-29 19:30
26 | Barguna | 132 | 142 | 2023-06-27 00:00 | 108 | 2023-06-04 18:00
27 | Barishal | 132 | 141 | 2023-06-27 00:00 | 113 | 2023-06-22 09:00
28 | Barishal-230 | 132 | 134 | 2023-06-07 21:00 | 124 | 2023-06-02 22:00
29 | Baroaulia | 132 | 141 | 2023-06-04 21:00 | 122 | 2023-06-19 07:00
30 | Baroirhat | 132 | 139 | 2023-06-03 23:00 | 117 | 2023-06-20 14:00
31 | Bashundhara | 132 | 142 | 2023-06-16 19:30 | 120 | 2023-06-02 12:00
32 | BashundharaCement | 132 | 140 | 2023-06-28 18:30 | 127 | 2023-06-08 09:00
33 | Beanibazar | 132 | 138 | 2023-06-14 10:00 | 123 | 2023-06-08 19:30
34 | Benapole | 132 | 137 | 2023-06-13 18:30 | 121 | 2023-06-29 19:00
35 | Bhaluka | 132 | 133 | 2023-06-30 17:00 | 117 | 2023-06-08 11:00
36 | Bhandaria | 132 | 142 | 2023-06-12 17:00 | 121 | 2023-06-16 19:00
37 | Bhangura | 132 | 138 | 2023-06-17 18:00 | 129 | 2023-06-08 20:00
38 | Bheramara | 132 | 135 | 2023-06-06 05:00 | 129 | 2023-06-08 19:00
39 | Bheramara(GK) | 132 | 136 | 2023-06-13 18:00 | 129 | 2023-06-15 12:00
40 | Bhulta | 132 | 133 | 2023-06-28 18:00 | 113 | 2023-06-30 04:00
41 | Bog-Sherpur | 132 | 137 | 2023-06-17 18:00 | 122 | 2023-06-29 19:30
42 | Bogura | 132 | 137 | 2023-06-04 17:00 | 120 | 2023-06-29 20:00
43 | Bogura-230 | 132 | 137 | 2023-06-17 18:00 | 119 | 2023-06-27 17:00
44 | Brahmanbaria | 132 | 139 | 2023-06-30 16:00 | 119 | 2023-06-12 00:00
45 | Cantonment | 132 | 140 | 2023-06-17 20:00 | 123 | 2023-06-08 09:00
46 | Chandpur | 132 | 142 | 2023-06-03 23:00 | 112 | 2023-06-05 02:00
47 | Chandraghona | 132 | 141 | 2023-06-06 19:30 | 125 | 2023-06-12 12:00
48 | Chapai | 132 | 139 | 2023-06-13 19:30 | 113 | 2023-06-15 03:00
49 | Charsaidpur | 132 | 141 | 2023-06-28 19:00 | 124 | 2023-06-20 05:00
50 | Chauddagram | 132 | 138 | 2023-06-03 23:00 | 119 | 2023-06-03 08:00
51 | Chhatak | 132 | 137 | 2023-06-15 05:00 | 124 | 2023-06-11 20:00
52 | Chowmuhani | 132 | 138 | 2023-06-23 22:00 | 113 | 2023-06-30 00:00
53 | Chuadanga | 132 | 140 | 2023-06-17 18:30 | 114 | 2023-06-08 19:30
54 | Coxsbazar | 132 | 135 | 2023-06-10 09:00 | 108 | 2023-06-07 00:00
55 | Cumilla(N) | 132 | 138 | 2023-06-10 20:00 | 130 | 2023-06-16 13:00
56 | Cumilla(S) | 132 | 139 | 2023-06-03 23:00 | 122 | 2023-06-13 12:00
57 | Daudkandi | 132 | 138 | 2023-06-17 20:00 | 124 | 2023-06-15 19:00
58 | Dhaka | 132 | 142 | 2023-06-16 19:30 | 128 | 2023-06-14 12:00
59 | Dhamrai | 132 | 142 | 2023-06-17 19:30 | 124 | 2023-06-08 09:00
60 | Dhanmondi | 132 | 141.3 | 2023-06-29 08:00 | 113 | 2023-06-21 15:00
61 | Dohazari | 132 | 140 | 2023-06-23 22:00 | 112 | 2023-06-09 03:00
62 | Faridpur | 132 | 132 | 2023-06-28 07:00 | 113 | 2023-06-03 10:00
63 | Fatullah | 132 | 140 | 2023-06-29 08:00 | 126 | 2023-06-08 09:00
64 | Fenchuganj | 132 | 139 | 2023-06-14 10:00 | 132 | 2023-06-08 21:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
65 | Feni | 132 | 140 | 2023-06-23 22:00 | 117 | 2023-06-28 07:00
66 | Ghorashal | 132 | N/A | N/A | N/A | N/A
67 | Goalpara | 132 | 140 | 2023-06-06 00:00 | 117 | 2023-06-15 23:00
68 | Gollamari | 132 | 138 | 2023-06-02 18:00 | 127 | 2023-06-30 21:00
69 | Gopalganj | 132 | 137 | 2023-06-13 18:00 | 124 | 2023-06-16 20:00
70 | Gopalganj-400 | 132 | 159 | 2023-06-09 18:30 | 125 | 2023-06-06 14:00
71 | Gulshan | 132 | 141 | 2023-06-16 20:00 | 133 | 2023-06-10 18:00
72 | Halishahar | 132 | 141 | 2023-06-03 19:00 | 122 | 2023-06-12 16:00
73 | Haripur | 132 | 141 | 2023-06-16 19:30 | 130 | 2023-06-01 10:00
74 | HaripurSBU | 132 | 134 | 2023-06-25 01:00 | 130 | 2023-06-01 10:00
75 | Hasnabad | 132 | 143 | 2023-06-29 08:00 | 130 | 2023-06-02 11:00
76 | Hathazari | 132 | 142 | 2023-06-03 19:00 | 127 | 2023-06-12 12:00
77 | Ishurdi | 132 | 137 | 2023-06-17 18:30 | 129 | 2023-06-08 19:30
78 | Jaldhaka | 132 | 135 | 2023-06-15 18:30 | 110 | 2023-06-29 19:30
79 | Jamalpur | 132 | 140 | 2023-06-15 21:00 | 112 | 2023-06-02 00:00
80 | Jashore | 132 | 137 | 2023-06-13 18:30 | 122 | 2023-06-29 22:00
81 | Jhenaidah | 132 | 140 | 2023-06-17 18:30 | 125 | 2023-06-08 19:30
82 | Jhenaidah-230 | 132 | 140 | 2023-06-17 18:30 | 161 | 2023-06-12 15:00
83 | Joydebpur | 132 | 144 | 2023-06-17 19:30 | 114 | 2023-06-29 00:00
84 | Joypurhat | 132 | 139 | 2023-06-30 18:30 | 110 | 2023-06-02 19:30
85 | Juldah | 132 | 142 | 2023-06-23 22:00 | 121 | 2023-06-07 03:00
86 | Kabirpur | 132 | 142 | 2023-06-17 18:30 | 116 | 2023-06-28 15:00
87 | Kachua | 132 | 139 | 2023-06-07 18:00 | 116 | 2023-06-30 00:00
88 | Kaliakoir | 132 | 144 | 2023-06-17 19:00 | 111 | 2023-06-09 01:00
89 | Kallyanpur | 132 | 140 | 2023-06-17 19:30 | 122 | 2023-06-01 19:00
90 | Kalurghat | 132 | 140 | 2023-06-03 19:00 | 123 | 2023-06-12 13:00
91 | Kamrangirchar | 132 | 139 | 2023-06-17 19:30 | 119 | 2023-06-04 11:00
92 | Kaptai | 132 | N/A | N/A | N/A | N/A
93 | Kazla | 132 | 137 | 2023-06-16 19:30 | 123 | 2023-06-08 12:00
94 | Keranigonj | 132 | 140 | 2023-06-28 07:00 | 125 | 2023-06-02 14:00
95 | Khagrachori | 132 | 139 | 2023-06-03 19:30 | 122 | 2023-06-20 14:00
96 | Khulna | 132 | 139 | 2023-06-13 18:30 | 111 | 2023-06-19 16:00
97 | Khulna(S) | 132 | 139 | 2023-06-05 23:00 | 126 | 2023-06-30 22:00
98 | Khulshi | 132 | 139 | 2023-06-23 22:00 | 112 | 2023-06-19 14:00
99 | Kishoreganj | 132 | 135 | 2023-06-30 17:00 | 135 | 2023-06-29 11:00
100 | Kodda | 132 | 142 | 2023-06-17 19:00 | 120 | 2023-06-13 11:00
101 | KSRM | 132 | 141 | 2023-06-06 19:30 | 113 | 2023-06-30 12:00
102 | Kulaura | 132 | 138 | 2023-06-15 10:00 | 130 | 2023-06-10 01:00
103 | Kurigram | 132 | 134 | 2023-06-15 18:30 | 108 | 2023-06-29 19:30
104 | Kushtia | 132 | 137 | 2023-06-28 09:00 | 126 | 2023-06-08 19:00
105 | Lalbag | 132 | 140 | 2023-06-28 07:00 | 124 | 2023-06-17 13:00
106 | Lalmonirhat | 132 | 136 | 2023-06-15 06:00 | 113 | 2023-06-26 23:00
107 | Madanganj | 132 | 140 | 2023-06-28 18:30 | 127 | 2023-06-08 09:00
108 | Madaripur | 132 | 132 | 2023-06-13 18:00 | 125 | 2023-06-08 23:00
109 | Madartek | 132 | 141 | 2023-06-16 19:30 | 127 | 2023-06-18 11:00
110 | Madunaghat | 132 | 142 | 2023-06-23 22:00 | 123 | 2023-06-26 13:00
111 | Magura | 132 | 138 | 2023-06-05 23:00 | 122 | 2023-06-08 19:30
112 | Mahasthangarh | 132 | 136 | 2023-06-17 17:00 | 119 | 2023-06-26 23:00
113 | Manikganj | 132 | 141 | 2023-06-16 18:30 | 120 | 2023-06-13 11:00
114 | Maniknagar | 132 | 137 | 2023-06-02 12:00 | 123 | 2023-06-29 03:00
115 | Matarbari | 132 | 144 | 2023-06-30 03:00 | 103 | 2023-06-15 18:30
116 | Matuail | 132 | 140.7 | 2023-06-29 08:00 | 128.7 | 2023-06-12 11:00
117 | Millgate | 132 | 159 | 2023-06-06 05:00 | 121 | 2023-06-02 12:00
118 | Mirpur | 132 | 142 | 2023-06-27 20:00 | 121 | 2023-06-08 09:00
119 | Mithapukur | 132 | 135 | 2023-06-04 17:00 | 112 | 2023-06-02 19:00
120 | Modern | 132 | 142 | 2023-06-23 22:00 | 123 | 2023-06-12 12:00
121 | Mogbazar | 132 | 143 | 2023-06-16 19:30 | 138 | 2023-06-17 07:00
122 | Mongla | 132 | 138 | 2023-06-13 19:30 | 120 | 2023-06-30 22:00
123 | Motijheel | 132 | 137 | 2023-06-16 19:30 | 124 | 2023-06-08 11:00
124 | Munshiganj | 132 | 140 | 2023-06-29 11:00 | 127 | 2023-06-08 00:00
125 | Mymensingh | 132 | 140 | 2023-06-09 13:00 | 111 | 2023-06-08 09:00
126 | Naogaon | 132 | 132 | 2023-06-17 16:00 | 113 | 2023-06-02 03:00
127 | Narail | 132 | 139 | 2023-06-09 16:00 | 121 | 2023-06-08 19:30
128 | Narinda | 132 | N/A | 2023-06-04 20:00 | N/A | N/A
129 | Narshingdi | 132 | 140 | 2023-06-29 11:00 | 120 | 2023-06-08 10:00
130 | Natore | 132 | 136 | 2023-06-08 01:00 | 112 | 2023-06-11 01:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
131 | Nawabganj | 132 | 139 | 2023-06-28 06:00 | 125 | 2023-06-02 14:00
132 | Netrakona | 132 | 138 | 2023-06-03 10:00 | 113 | 2023-06-05 18:30
133 | New | 132 | 142 | 2023-06-28 05:00 | 121 | 2023-06-08 09:00
134 | Niamatpur | 132 | 134 | 2023-06-14 00:00 | 108 | 2023-06-02 19:30
135 | Noapara | 132 | 139 | 2023-06-13 18:30 | 124 | 2023-06-30 22:00
136 | Pabna | 132 | 135 | 2023-06-08 01:00 | 126 | 2023-06-08 19:30
137 | Palashbari | 132 | 133 | 2023-06-04 17:00 | 112 | 2023-06-27 14:00
138 | Panchagarh | 132 | 141 | 2023-06-19 02:00 | 111 | 2023-06-05 07:00
139 | Patuakhali | 132 | 142 | 2023-06-19 20:00 | 134 | 2023-06-12 13:00
140 | Payra | 132 | 142 | 2023-06-27 00:00 | 134 | 2023-06-06 15:00
141 | PHP | 132 | 140 | 2023-06-03 23:00 | 118 | 2023-06-03 08:00
142 | Postogola | 132 | 143 | 2023-06-29 08:00 | 130 | 2023-06-02 11:00
143 | Purbachal | 132 | 141 | 2023-06-28 09:00 | 119 | 2023-06-08 09:00
144 | Purbasadipur | 132 | 136 | 2023-06-19 07:00 | 118 | 2023-06-28 01:00
145 | Rahim | 132 | 141 | 2023-06-16 19:30 | 124 | 2023-06-19 02:00
146 | Rajbari | 132 | 131 | 2023-06-17 18:30 | 120 | 2023-06-27 10:00
147 | Rajendrapur | 132 | 142 | 2023-06-16 19:00 | 119 | 2023-06-13 11:00
148 | Rajshahi | 132 | 134 | 2023-06-07 23:00 | 112 | 2023-06-16 05:00
149 | Rajshahi-230 | 132 | 159 | 2023-06-11 08:00 | 112 | 2023-06-02 08:00
150 | Ramganj | 132 | 138 | 2023-06-03 23:00 | 111 | 2023-06-29 01:00
151 | Rampur | 132 | 140 | 2023-06-23 22:00 | 122 | 2023-06-12 16:00
152 | Rampura | 132 | 142 | 2023-06-16 20:00 | 134 | 2023-06-05 22:00
153 | Rangamati | 132 | 141 | 2023-06-23 22:00 | 124 | 2023-06-12 12:00
154 | Rangpur | 132 | 135 | 2023-06-15 19:00 | 113 | 2023-06-29 19:30
155 | Ruppur | 132 | 137 | 2023-06-28 09:00 | 129 | 2023-06-08 19:30
156 | Saidpur | 132 | 135 | 2023-06-15 02:00 | 114 | 2023-06-29 19:30
157 | Satkhira | 132 | 138 | 2023-06-13 20:00 | 120 | 2023-06-30 22:00
158 | Satmasjid | 132 | 141 | 2023-06-26 18:00 | 124 | 2023-06-07 19:00
159 | Savar | 132 | 141 | 2023-06-27 20:00 | 120 | 2023-06-08 00:00
160 | Shahjadpur | 132 | 142 | 2023-06-04 04:00 | 130 | 2023-06-11 12:00
161 | Shahjibazar | 132 | 137 | 2023-06-15 23:00 | 127 | 2023-06-12 00:00
162 | Shahmirpur | 132 | 140 | 2023-06-06 19:00 | 110 | 2023-06-10 20:00
163 | Shariatpur | 132 | 132 | 2023-06-13 18:00 | 123 | 2023-06-15 19:30
164 | Sherpur | 132 | 141 | 2023-06-15 19:00 | 112 | 2023-06-10 11:00
165 | Shikalbaha | 132 | N/A | N/A | N/A | N/A
166 | Shikalbaha-230 | 132 | 140 | 2023-06-03 19:30 | 113 | 2023-06-10 20:00
167 | Shitalakhya | 132 | 141 | 2023-06-28 19:00 | 128 | 2023-06-08 09:00
168 | Sholosohor | 132 | 139 | 2023-06-03 19:00 | 121 | 2023-06-20 14:00
169 | Shyampur | 132 | 138 | 2023-06-24 16:00 | 126 | 2023-06-07 09:00
170 | Shyampur-230 | 132 | 139 | 2023-06-28 19:00 | 117 | 2023-06-13 12:00
171 | Siddhirganj | 132 | 141 | 2023-06-29 08:00 | 129 | 2023-06-08 09:00
172 | Sirajganj | 132 | 138 | 2023-06-17 18:00 | 124 | 2023-06-11 15:00
173 | Sonargaon | 132 | 139 | 2023-06-16 20:00 | 127 | 2023-06-01 10:00
174 | Sreemongol | 132 | 137 | 2023-06-15 22:00 | 128 | 2023-06-06 21:00
175 | Sreepur | 132 | 134 | 2023-06-30 17:00 | 122 | 2023-06-08 11:00
176 | Srinagar | 132 | 156 | 2023-06-20 09:00 | 124 | 2023-06-02 14:00
177 | SSM | 132 | 132 | 2023-06-26 10:00 | 120 | 2023-06-24 15:00
178 | Sunamganj | 132 | 135 | 2023-06-14 19:30 | 120 | 2023-06-06 21:00
179 | Sylhet | 132 | 135 | 2023-06-14 09:00 | 128 | 2023-06-11 23:00
180 | Tangail | 132 | 140 | 2023-06-09 13:00 | 113 | 2023-06-30 09:00
181 | Thakurgaon | 132 | 138 | 2023-06-03 16:00 | 109 | 2023-06-26 07:00
182 | TK | 132 | 140 | 2023-06-03 22:00 | 109 | 2023-06-17 00:00
183 | Tongi | 132 | 143 | 2023-06-16 19:00 | 124 | 2023-06-08 09:00
184 | Ullon | 132 | 141 | 2023-06-16 19:30 | 127 | 2023-06-18 11:00
185 | Uttara | 132 | 142 | 2023-06-28 05:00 | 120 | 2023-06-11 11:00
186 | UttaraNew | 132 | 142 | 2023-06-27 20:00 | 126 | 2023-06-07 02:00
187 | Zigatola | 132 | 140 | 2023-06-28 06:00 | 131 | 2023-06-16 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:June 2023
Name of the sub-station | Auto transformer |  | Recorded maximum load |  |  | Time | Remarks
| Name | Capacity (MVA) | MW | Amps ( 230kV side ) | Date
Hasnabad | TR1 | 225 | 67 | 200
| TR2 | 225 | 67 | 200 | 07.06.2023 | 24:00
| TR3 | 225 | 67 | 200
Tongi | TR1 | 225 | 195 | 590 | 13.06.2023
| TR2 | 225 | 195 | 590 |  | 11:00
| TR3 | 225 | 195 | 590
Haripur | TR1 | 225 | 95 | 300 | 15.06.2023
| TR2 | 225 | 95 | 300 |  | 6:00
| TR3 | 225 | 95 | 300
| TR1 | 225 | 208 | 565 | 08.06.2023
| TR2 | 225 | 208 | 565 |  | 13:00
| TR3 | 225 | 208 | 565
Keraniganj | ATR1 | 300 | 173 | 496 | 15.06.2023
| ATR2 | 300 | 0 | 0 |  | 19:00
| ATR3 | 300 | 173 | 496
Aminbazar | TR1 | 225 | 201 | 558 | 15.06.2023
| TR2 | 225 | 201 | 558 |  | 24:00
| TR3 | 225 | 207 | 567
Agargaon | TR1 | 300 | 194 | 540 | 07.06.2023 | 23:00
| TR2 | 300 | 194 | 540
Maniknagar | TR1 | 300 | 180 | 540 | 08.06.2023 | 13:00
| TR2 | 300 | 180 | 540
Cumilla (N) | TR1 | 225 | 193 | 526 | 17.06.2023 | 2:00
| TR2 | 225 | 191 | 520
Fenchuganj | AT2 | 300 | 207 | 521 | 18.06.2023 | 22:00
Hathazari | MT1 | 150 | 120 | 334 | 06.06.2023
| MT2 | 150 | 120 | 334
| MT3 | 150 | 120 | 334 |  | 24:00
| MT4 | 150 | 120 | 334
Ishurdi | TR1 | 225 | 95 | 259 | 16.06.2023
| TR2 | 225 | 95 | 259 |  | 20:57
| TR3 | 225 | 95 | 259
Khulna(S) | TR1 | 225 | 146 | 387 | 16.06.2023
| TR2 | 225 | 146 | 387 |  | 19:30
| TR3 | 300 | 187 | 498
Bogura | TR1 | 225 | 197 | 570 | 02.06.2023
| TR2 | 225 | 197 | 570 |  | 19:30
| TR3 | 225 | 266 | 748
Baghabari | TR1 | 300 | 180 | 400 | 08.06.2023 | 20:00
| TR2 | 225 | 134 | 375
Rajshahi | ATR-01 | 300 | 103 | 274 | 14.06.2023
| ATR-02 | 300 | 103 | 274 |  | 4:00
Barapukuria | TR1 | 225 | 191 | 928 | 26.06.2023 | 19:30 | Due to unavailability of 230 kV side meters
| TR2 | 225 | 175 | 850 | 09.06.2023 |  | 132 kV current is being provided
QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:June 2023
Name of the sub-station | Auto transformer |  | Recorded maximum load |  |  | Time | Remarks
| Name | Capacity (MVA) | MW | Amps ( 230kV side ) | Date
Barapukuria | TR6 | 300 | 229 | 1098 | 09.06.2023
Bheramara | Transformer-1 | 225 | 98 | 238
| Transformer-2 | 225 | 98 | 238 | 08.06.2023 | 19:30
Shyampur | ATR-01 | 300 | 121 | 342 | 22.06.2023
| ATR-02 | 300 | 121 | 342 |  | 10:00
Kaliakoir | TR1 | 300 | 135.2 | 642 | 24.06.2023 | 19:30
Sikalbaha | ATR-1 | 300 | 224.23 | 621.78 | 08.06.2023 | 20:00
| ATR-2 | 300 | 224.23 | 621.78
Jhenaidah | T1(230/132 kV) | 300 | 212 | 673 | 16.06.2023 | 21:00
| T2(230/132 kV) | 300 | 212 | 673
Maximum load of 400/230 & 400/132 kV Transformer
Kaliakoir | TR1(400/230 kV) | 520 | 205 | 319 | 02.06.2023 | 14:45
| TR2(400/230 kV) | 520 | 207.7 | 323
| TR1(400/132 kV) | 325 | 322 | 522 | 05.06.2023 | 0:00
| TR2(400/132 kV) | 325 | 324.6 | 518
Bibiyana | ICT1(400/230 kV) | 520 | 156 | 231 | 13.06.2023 | 22:00
| ICT2(400/230kV) | 520 | 152 | 226
Bhulta | ATR1(400/230 kV) | 520 | 351 | 590 | 06.06.2023 | 6:15
| ATR2(400/230kV) | 520 | 351 | 590
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 362 | 563 | 24.06.2023 | 5:15
Gopalganj | ATR1(400/135 kV) | 325 | 135 | 198 | 16.06.2023 | 19:30
| ATR2(400/135kV) | 325 | 135 | 198
| ATR3(400/135kV) | 325 | 135 | 198
Payra | ART1 400 kV/230/33 | 325 | 120 | 184 | 09.06.2023 | 4:30
| ART2 400 kV/230/33 | 325 | 120 | 181 | 10.06.2023 | 3:30
Rahanpur | AT-1 -Gen 400/132 kV | 235 | 236 | 354 | 16.06.2023 | 7:00
Aminbazar | ATR-02 400/230/132kV | 448 | 362 | 599 | 13.06.2023 | 19:30
| ATR-03 400/230/132kV | 448 | 362 | 599
| 400/230/132kV | 448 | 184 | 298
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## "QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 | POWER GRID COMPANY OF BANGLADESH LTD. | [12 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | Information Management Division, LDC, Dhaka. | [11 empty] | Information Management Division, LDC, Dhaka.
[5 empty] | Report on load shedding | [11 empty] | Report on load shedding
Month: June-2023 | [5 empty] | (For Evening Peak) |  | (For Evening Peak) | [6 empty] | Month: June-2023 |  |  | (For Evening Peak) |  | (For Day Peak)
Date | Peak Hour |  |  |  | Total load shed (SS end) | [8 empty] | Remarks | Date | Peak Hour |  |  | Time | Total load shed (SS end) | [8 empty] | Remarks
| Generation (Gen End) | Demand (Gen End) | Load shed | Time | Areawise load shed (MW) | [10 empty] | Generation (Gen End) | Demand (Gen End) | Load shed |  | Areawise load shed (MW)
| (MW) | (MW) | (MW) |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | (MW) |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
2023-06-01 | 14334 | 15700 | 1305 | 21:00 | 270 | 0 | 260 | 150 | 250 | 170 | 30 | 55 | 120 | - | 2023-06-01 | 12349 | 14250 | 1815 | 12:00 | 830 | 150 | 150 | 130 | 200 | 205 | 30 | 40 | 80 | -
2023-06-02 | 14377 | 14770 | 375 | 21:00 | 0 | 0 | 130 | 35 | 110 | 50 | 0 | 0 | 50 | - | 2023-06-02 | 11960 | 13500 | 1471 | 12:00 | 280 | 210 | 290 | 150 | 240 | 75 | 70 | 46 | 110 | -
2023-06-03 | 13635 | 15500 | 1781 | 21:00 | 340 | 270 | 291 | 200 | 260 | 110 | 90 | 80 | 140 | - | 2023-06-03 | 11647 | 14000 | 2247 | 12:00 | 830 | 300 | 205 | 210 | 257 | 210 | 80 | 35 | 120 | -
2023-06-04 | 13781 | 15700 | 1833 | 21:00 | 456 | 320 | 280 | 190 | 240 | 65 | 85 | 69 | 128 | - | 2023-06-04 | 11905 | 14300 | 2287 | 12:00 | 830 | 354 | 205 | 210 | 257 | 185 | 80 | 46 | 120 | -
2023-06-05 | 13859 | 15700 | 1758 | 21:00 | 290 | 266 | 345 | 198 | 245 | 116 | 96 | 66 | 136 | - | 2023-06-05 | 12099 | 14900 | 2675 | 12:00 | 875 | 350 | 380 | 280 | 340 | 120 | 100 | 60 | 170 | -
2023-06-06 | 13763 | 15800 | 1945 | 21:00 | 500 | 0 | 345 | 285 | 320 | 230 | 0 | 75 | 190 | - | 2023-06-06 | 12166 | 14900 | 2610 | 12:00 | 950 | 300 | 375 | 250 | 290 | 190 | 50 | 45 | 160 | -
2023-06-07 | 13898 | 15500 | 1530 | 21:00 | 0 | 0 | 400 | 220 | 320 | 220 | 100 | 110 | 160 | - | 2023-06-07 | 12407 | 14900 | 2380 | 12:00 | 850 | 210 | 310 | 230 | 295 | 180 | 100 | 45 | 160 | -
2023-06-08 | 14655 | 15147 | 470 | 20:00 | 43 | 0 | 16 | 97 | 0 | 152 | 10 | 0 | 152 | - | 2023-06-08 | 12677 | 14500 | 1741 | 12:00 | 235 | 165 | 340 | 228 | 265 | 205 | 90 | 8 | 205 | -
2023-06-09 | 12699 | 12699 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-09 | 11089 | 12500 | 1348 | 12:00 | 114 | 152 | 265 | 215 | 225 | 187 | 95 | 5 | 90 | -
2023-06-10 | 13897 | 13950 | 51 | 21:00 | 25 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-10 | 11798 | 12500 | 336 | 12:00 | 150 | 50 | 10 | 0 | 50 | 50 | 26 | 0 | 0 | -
2023-06-11 | 13792 | 14100 | 294 | 19:30 | 90 | 0 | 0 | 13 | 8 | 107 | 76 | 0 | 0 | - | 2023-06-11 | 12356 | 12500 | 162 | 12:00 | 120 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | -
2023-06-12 | 13565 | 13850 | 272 | 19:30 | 100 | 0 | 0 | 0 | 17 | 120 | 35 | 0 | 0 | - | 2023-06-12 | 11364 | 11800 | 416 | 11:00 | 100 | 80 | 0 | 0 | 150 | 60 | 26 | 0 | 0 | -
2023-06-13 | 13439 | 14400 | 918 | 21:00 | 180 | 170 | 100 | 140 | 48 | 110 | 20 | 0 | 150 | - | 2023-06-13 | 12230 | 13050 | 783 | 12:00 | 220 | 190 | 0 | 130 | 155 | 40 | 48 | 0 | 0 | -
2023-06-14 | 14129 | 15000 | 832 | 21:00 | 53 | 0 | 250 | 87 | 208 | 68 | 0 | 47 | 119 | - | 2023-06-14 | 11976 | 13300 | 1264 | 12:00 | 340 | 179 | 240 | 170 | 240 | 25 | 5 | 5 | 60 | -
2023-06-15 | 13863 | 14125 | 250 | 21:00 | 20 | 0 | 19 | 0 | 211 | 0 | 0 | 0 | 0 | - | 2023-06-15 | 11687 | 12800 | 1063 | 12:00 | 270 | 50 | 230 | 280 | 103 | 130 | 0 | 0 | 0 | -
2023-06-16 | 11974 | 11974 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-16 | 11780 | 12350 | 554 | 12:00 | 70 | 0 | 0 | 174 | 180 | 0 | 0 | 0 | 120 | -
2023-06-17 | 11886 | 11886 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-17 | 12045 | 12300 | 244 | 12:00 | 50 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | -
2023-06-18 | 13141 | 13267 | 120 | 21:00 | 30 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | - | 2023-06-18 | 11466 | 12000 | 510 | 12:00 | 307 | 0 | 0 | 0 | 135 | 68 | 0 | 0 | 0 | -
2023-06-19 | 13456 | 13540 | 80 | 19:30 | 20 | 0 | 0 | 0 | 10 | 50 | 0 | 0 | 0 | - | 2023-06-19 | 11449 | 11800 | 335 | 12:00 | 115 | 134 | 0 | 0 | 86 | 0 | 0 | 0 | 0 | -
2023-06-20 | 13596 | 13596 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-20 | 11950 | 12600 | 621 | 12:00 | 180 | 170 | 0 | 0 | 170 | 65 | 36 | 0 | 0 | -
2023-06-21 | 14131 | 14168 | 35 | 21:00 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-21 | 11970 | 12730 | 745 | 12:00 | 280 | 190 | 0 | 0 | 145 | 55 | 75 | 0 | 0 | -
2023-06-22 | 13892 | 14250 | 342 | 21:00 | 50 | 0 | 190 | 0 | 20 | 40 | 42 | 0 | 0 | - | 2023-06-22 | 11719 | 13050 | 1271 | 12:00 | 400 | 220 | 136 | 140 | 200 | 50 | 45 | 10 | 70 | -
2023-06-23 | 13733 | 13860 | 121 | 21:00 | 18 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | - | 2023-06-23 | 11519 | 12350 | 794 | 12:00 | 186 | 60 | 115 | 67 | 195 | 86 | 25 | 13 | 47 | -
2023-06-24 | 13906 | 14500 | 567 | 19:30 | 61 | 0 | 96 | 52 | 96 | 144 | 0 | 35 | 83 | - | 2023-06-24 | 11858 | 12070 | 202 | 12:00 | 91 | 0 | 0 | 0 | 0 | 111 | 0 | 0 | 0 | -
2023-06-25 | 13727 | 14600 | 834 | 21:00 | 86 | 0 | 181 | 95 | 170 | 164 | 0 | 0 | 138 | - | 2023-06-25 | 11781 | 13250 | 1403 | 12:00 | 320 | 228 | 62 | 124 | 251 | 145 | 126 | 0 | 147 | -
2023-06-26 | 13364 | 13395 | 30 | 21:00 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | - | 2023-06-26 | 11796 | 12535 | 707 | 12:00 | 278 | 0 | 0 | 0 | 204 | 157 | 68 | 0 | 0 | -
2023-06-27 | 11566 | 11566 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-27 | 9530 | 9530 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-06-28 | 10301 | 10301 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-06-28 | 7917 | 7917 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-06-29 | 10896 | 10896 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-06-29 | 7361 | 7361 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023-06-30 | 9504 | 9504 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 2023-06-30 | 8674 | 8674 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:June 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14655 | 2023-06-08 | 20:00
2 | Maximum Day Peak Genaration | MW | 12677 | 2023-06-08 | 12:00
3 | Maximum Evening Peak Demand | MW | 15800 | 2023-06-30 | 20:00
4 | Minimum Generation | MW | 7589 | 2023-06-28 | 6:00
5 | Average of the daily evening peak Genaration | MW | 13225.3 | - | -
6 | Average of the daily day peak Genaration | MW | 11423.9667 | - | -
7 | Maximum load shed | MW | 2675 | 2023-06-05 | 21:00
8 | Minimum load shed | MW | 0 | 2023-06-27 | -
9 | Total nos. of load shed days | Day | 22 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 524.7667 | - | -
11 | Total Generation | MkWh | 7482.4031 | - | - | 16.6667
12 | Total Generation by BPDB | MkWh | 1745.3811 | % of total Gen. | 23.33%
13 | Total Generation by IPP | MkWh | 2143.9393 | '' | 28.65%
14 | A) Total Generation by Generation Companies | MkWh | 2369.791 | '' | 31.67%
| B) Total Generation by REB | MkWh | 121.3394 | " | 1.622%
| C) Total Generation by RENTAL | MkWh | 364.0404 | " | 4.865%
| D) Total Imported from India (BIPTC) | MkWh | 633.1218 | " | 8.461%
| E) Total Imported from Tripura, India (A.C) | MkWh | 104.7901 | " | 1.4%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4651.8044 | % of total Gen. | 62.17%
| B) Oil | MkWh | 1591.0637 | '' | 21.26%
| C) Hydro | MkWh | 25.8407 | '' | 0.3454%
| D) Solar | MkWh | 34.6981 | '' | 0.4637%
| E) Coal | MkWh | 441.0844 | '' | 5.895%
| F) BIPTC (Import from India) | MkWh | 633.1218 | '' | 8.461%
| G) A.C (Import from Tripura, India) | MkWh | 104.7901 | '' | 1.4%
16 | Maximun of the daily total Generation . | MkWh | 299.7656 | 2023-06-08
17 | Monthly Load factor | % | 78.4931 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 30693.5216 | - | -
| A) Gas | M.Taka | 5204.3386 | - | -
| B) Liquid fuel | M.Taka | 20063.4718 | - | -
| C) Coal | M.Taka | 1746.1999 | - | -
| D) BIPTC (Import from India) | M.Taka | 2925.0225 | - | -
| E) Tripura(Import from India) | M.Taka | 754.4888 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1175.8618 | 2023-06-01
| A) Gas | M.Taka | 184.9097 | 2023-06-17
| B) Liquid fuel | M.Taka | 949.963 | 2023-06-01
| C) Coal | M.Taka | 181.5563 | 2023-06-19
| D) BIPTC (Import from India) | M.Taka | 102.9403 | 2023-06-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 5.8165
| B) Excluding Hydro & Solar | Taka/kWhR | 5.8619
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/06/2023 | 06:00
b) | Actual | FT (MSL) | 73.44 | 30/06/2023 | 6:00
22 | Peak Genaration of June 2022 | MW | 14038 | 08/06/2022 | 23:00
23 | Peak Demand of June 2022 | MW | 14038 | 08/06/2022 | 23:00
24 | Maximum peak Generation recorded upto 30/06/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 30/06/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/06/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month: June-2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
8 | Ashuganj 225 MW CCPP | APSCL | 221 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage