## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:May 2022
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2022-05-01 |  | 2022-04-01 |  | 2021-05-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13954 | 2022-05-16 | 14782 | 2022-04-16 | 13417 | 2021-05-22 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 4396 | 2022-05-21 | 4262 | 2022-04-20 | 6470 | 2021-05-14 | - | -
|  |  | 6:00 |  | 6:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13954 | 2022-05-16 | 14782 | 2022-04-16 | 13417 | 2021-05-22 | 14782 | 2022-04-16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11993 | 2022-05-24 | 12895 | 2022-04-26 | 12021 | 2021-05-23 | 12895 | 2022-04-26
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13954 | 2022-05-16 | 14782 | 2022-04-16 | 13417 | 2021-05-22 | 14782 | 2022-04-16
|  |  | 12:00 |  | 12:00 |  | 19:00 |  | 12:00
6 | Average Generation (MW) at Evening Peak | 12277.0968 |  | 13536.3333 |  | 11615.0323 |  | 13536.33 | 2022-04-27
7 | Average Generation (MW) at Day Peak | 10010.6129 |  | 11233.4 |  | 9675.8387 |  | 11233.4 | 2022-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 934 | 2022-05-26 | 935 | 2022-04-10 | 933 | 2021-04-29 18:00 | 956 | 27/3/2019
|  |  | 7:00 |  | 21:30 |  | 18:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 174 | 2022-05-18 | 172 | 2022-04-03 | 187 | 2021-04-18 | 194 | 12/06/19
|  |  | 18:00 |  | 2:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | 350 | 2022-04-07 | 275 | 2021-04-27 | 1459 | 04/05/2010
|  |  | - |  | 22:00 |  | 20:00 |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | 14008 | 2022-04-07 | 13792 | 2021-04-27 | 13792 | 2021-04-27
|  | - | - | - | 22:00 |  | 20:00 |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | 0 | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | 1 |  | 0
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1760.1344 |  | 1929.4341 |  | 1736.8634 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 75.5671 |  | 88.2498 |  | 108.694
22 | Net Generation of BPDB (MKWH) | 1684.5673 |  | 1841.1843 |  | 1628.1694
23 | Net Generation of IPP (MKWH) | 4686.772 |  | 5255.3957 |  | 4485.1096
24 | Net Generation of REB (MKWH) | 117.2486 |  | 131.5194 |  | 122.6176
24 | Net Generation of Rental Power Plant (MKWH) | 517.426 |  | 614.893 |  | 487.59
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7006.0139 |  | 7842.9924 |  | 6723.4866 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4216.1115 |  | 4240.1479 |  | 4753.881 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 296.4446 |  | 633.9729 |  | 247.9394 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1740.5311 |  | 2365.7466 |  | 1303.8078 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 27.4557 |  | 45.2279 |  | 16.1091 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 33.0386 |  | 36.5217 |  | 21.292 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 767.9994 |  | 609.6252 |  | 489.1513 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 725.8023 |  | 754.5062 |  | 716.5811 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 83.2694 |  | 87.447 |  | 75.6219 |  | 87.45 | April'22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:May 2022
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13954 | 2022-05-16 | 21:00
Generation Period
| Dhaka | MW | 4884.54
| Chattogram | MW | 1439.58
| Cumilla | MW | 1267
| Mymensingh | MW | 1025
| Sylhet | MW | 447
a) | Total supply in East zone | MW | 9063.12
| Khulna | MW | 1666.4
| Barisal | MW | 418
| Rajshahi | MW | 1466.6
| Rangpur | MW | 756
b) | Total supply in West zone | MW | 4307
c) | Total supply in both zone ( a+b) | MW | 13370.12
Ref: | 27.21.0000.603.16.087.20.520 | Date: 19/06/2022
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May 2022
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 680 | 2022-05-05 | 20:00
| b) Ishurdi end | MW | 464 | 2022-05-24 | 1:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1200 | 2022-05-01 | 11:00
| b) Ishurdi end | MW | 266 | 2022-05-05 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | - | -
| b) Ishurdi end | MKWH | - | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | - | -
| b) Ishurdi end | MKWH | - | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 14.13
| b) Ishurdi end | MKWH | 126.81
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 460 | 2022-05-05 | 19:30
| b)Serajganj end | MW | 520 | 2022-05-19 | 9:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 480 | 2022-05-19 | 9:00
| b)Sirajganj end | MW | 470 | 2022-05-05 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 10.014 | 2022-05-07
| b)Sirajganj end | MKWH | 0.14 | 2022-05-29
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 30.58
| b)Sirajganj end | MKWH | 122.9
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 117.84
| b)Sirajganj end | MKWH | 31.14
30 | Transmission loss of EWI /NO-2 | % | 2.933
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65 | 0.83636
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74 | 0.81127
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
| 2nd East-West Interconnector Loss: |  |  |  |  | 99387644.47
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578 |  | 96795991.85
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062 |  | 2308363.67
| Difference (-) : | 3516000 |  |  |  | 2239112.76
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: May2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 230/132 kV transformer T-01 | 2022-05-01 14:32 | 2022-05-01 22:24 | 7:52 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T-1 | 2022-05-02 02:27 | 2022-05-02 02:38 | 0:11 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV transformers T-1,T2 & T3 | 2022-05-04 16:30 | 2022-05-04 16:50 | 0:20 | T | Due to 33 kV feeder fault | 50 | 16.6667 | Power interruption
Kabirpur | 132/33 kV transformers T-1 & T2 | 2022-05-12 14:18 | 2022-05-12 15:20 | 1:02 | T | Due to 33 kV feeder fault | 150 | 155 | Power interruption
| 132/33 kV transformers T-1 | 2022-05-13 19:30 | 2022-05-14 00:54 | 5:24 | T | Tripped showing O/C relay at 33 kV side
| 132/33 kV transformers T-2 | 2022-05-13 19:30 | 2022-05-13 20:02 | 0:32 | T |  | 80 | 42.6667 | Power interruption 19:30 to 20:02
Jamalpur | 132/33 kV transformers T-1 & T2 | 2022-05-18 08:24 | 2022-05-18 10:34 | 2:10 | T | Due to red-hot maint | 60 | 130 | Power interruption
Mymensingh | 132/33 kV transformers T-1 & T2 | 2022-05-18 21:04 | 2022-05-18 21:28 | 0:24 | E/O | Due to bursting of CB | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-2 | 2022-05-19 12:13 | 2022-05-19 14:12 | 1:59 | T | Due to problem at tap changer | 0 | 0 | No interruption
Joydevpur | 132/33 kV transformer T-2 | 2022-05-22 11:57 | 2022-05-22 13:44 | 1:47 | T | Due to red-hot maint | 5 | 8.9167 | Power interruption
Mymensingh | 132/33 kV transformers T-1 & T2 | 2022-05-23 08:17 | 2022-05-23 08:24 | 0:07 | T | Due to 33 kV feeder fault | 84 | 9.8 | Power interruption
Kabirpur | 132/33 kV transformer T-2 | 2022-05-25 00:20 | 2022-05-25 01:10 | 0:50 | T | Due to red-hot maint | 40 | 33.3333 | Power interruption
Mirpur | 132/33 kV transformer T-2 | 2022-05-28 05:47 | 2022-05-28 09:44 | 3:57 | T | Due to red-hot maint | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-3 | 2022-05-28 21:43 | 2022-05-28 22:45 | 1:02 | T | Due to red-hot maint.at 33 kV side | 60 | 62 | Power interruption
Sherpur | 132/33 kV transformer T-3 | 2022-05-29 01:41 | 2022-05-29 02:50 | 1:09 | T | Due to red-hot maint.at 33 kV side | 35 | 40.25 | Power interruption
Jamalpur | 132/33 kV transformer T-3 | 2022-05-31 09:11 | 2022-05-31 13:39 | 4:28 | T | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 33:14 |  | Unserved Energy: |  | 498.6333
Dhaka (South) Grid Circle :
Nawabganj | 132/33 kV transformer T-1 with 33 kV Bus | 2022-05-06 10:25 | 2022-05-06 11:40 | 1:15 | T | Due to red-hot maint. | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-2 & 33 kV Bus | 2022-05-07 17:08 | 2022-05-07 17:30 | 0:22 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T-2 | 2022-05-11 18:34 | 2022-05-11 22:29 | 3:55 | T | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T-2 | 2022-05-13 08:40 | 2022-05-13 12:03 | 3:23 | T | Due to red-hot maint. | 0 | 0 | No interruption
Bhulta | 132/33 kV transformers T-1 & T2 | 2022-05-15 00:48 | 2022-05-15 02:06 | 1:18 | T | Tripped showing O/C relay at 33 kV side | 80 | 104 | Power interruption
Sonargaon | 132/33 kV transformer T-2 | 2022-05-16 16:21 | 2022-05-16 16:58 | 0:37 | T | Due to red-hot maint.at 33 kV side | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-1 | 2022-05-17 12:09 | 2022-05-17 14:06 | 1:57 | T | Due to red-hot maint. | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2022-05-17 15:03 | 2022-05-17 16:23 | 1:20 | T | Due to red-hot maint. | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2022-05-20 09:21 | 2022-05-20 12:52 | 3:31 | E/O | Due to sparking at 33 kV feeder | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformers T-1 & T-5 | 2022-05-20 21:18 | 2022-05-20 21:57 | 0:39 | T | Tripped showing O/C relay | 68 | 44.2 | Power interruption
Maniknagar | 132/33 kV transformer T-1 | 2022-05-21 15:25 | 2022-05-21 16:44 | 1:19 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer AT-2 | 2022-05-24 19:35 | 2022-05-24 21:35 | 2:00 | E/O | Due to air leakage | 80 | 160 | Power interruption
Haripur | 230 kV CB | 2022-05-26 11:05 | 2022-05-26 12:57 | 1:52 | T | Due to red-hot maint. | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-2 | 2022-05-29 23:40 | 2022-05-30 08:35 | 8:55 | E/O | Due to flashing at 33 kV bushing | 0 | 0 | No interruption
|  |  | Total : | 32:23 |  | Unserved Energy: |  | 308.2
Chattogram Grid Circle :
Dohazari | 132/33 kV transformers T1 & T2 | 2022-05-11 13:56 | 2022-05-11 14:17 | 0:21 | T | Due to 33 kV feeder fault | 70 | 24.5 | Power interruption
| 33 kV full Bus | 2022-05-12 06:52 | 2022-05-12 08:05 | 0:21 | T | Due to red-hot maint | 52 | 18.2 | Power interruption
Cox'sbazar | 132/33 kV transformers T1 & T2 | 2022-05-13 07:33 | 2022-05-13 09:02 | 1:29 | T | Due to 33 kV feeder fault | 40 | 59.3333 | Power interruption
| 132/33 kV transformers T1 & T2 | 2022-05-13 16:28 | 2022-05-13 16:40 | 0:12 | T | Tripped showing O/C relay at 33 kV side | 50 | 10 | Power interruption
Dohazari | 132/33 kV transformer T2 | 2022-05-18 22:34 | 2022-05-18 12:00 | 0:12 | T | Due to red-hot maint.at 33 kV side | 70 | 14 | Power interruption
Cox'sbazar | 132/33 kV transformer T1 | 2022-05-20 16:47 | 2022-05-20 17:16 | 0:29 | T | Tripped showing E/F relay | 43 | 20.7833 | Power interruption
| 132/33 kV transformer T3 | 2022-05-21 09:59 | 2022-05-21 13:44 | 3:45 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Juldah | 132/33 kV transformer T2 | 2022-05-22 20:10 | 2022-05-22 21:34 | 3:45 | T | Due to red-hot maint. | 0 | 0 | No interruption
Shahmirpur | 132/33 kV transformer T2 | 2022-05-24 06:43 | 2022-05-24 07:08 | 0:25 | T | Due to 33 kV feeder fault | 22 | 9.1667 | Power interruption
Khagrachari | 132/33 kV transformer T2 with 132 kV bus-1 | 2022-05-28 11:24 | 2022-05-28 13:22 | 0:25 | T | Due to red-hot maint. | 0 | 0 | No interruption
|  |  | Total : | 11:24 |  | Unserved Energy: |  | 155.9833
Cumilla Grid Circle :
B.Baria | 132/33 kV transformers T1 & T2 | 2022-05-01 11:15 | 2022-05-01 11:34 | 0:19 | T | Tripped showing O/C relayat 33 kV side | 110 | 34.8333 | Power interruption
Cumilla (N) | 132/33 kV transformer T1 | 2022-05-03 10:56 | 2022-05-03 11:16 | 0:20 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Ashuganj | 132/33 kV transformers T3 & T4 | 2022-05-03 10:47 | 2022-05-03 10:47 | 0:00 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T1 | 2022-05-04 16:25 | 2022-05-04 18:28 | 2:03 | T | Due to 33 kV cable burst | 29 | 59.45 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-05-07 08:16 | 2022-05-07 09:09 | 0:53 | E/O | Due to red-hot maint | 8 | 7.0667 | Power interruption
Kachua | 132/33 kV transformer T2 | 2022-05-07 21:52 | 2022-05-07 22:32 | 0:40 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T4 | 2022-05-08 08:47 | 2022-05-08 10:24 | 1:37 | E/O | Due to red-hot maint | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T1 | 2022-05-10 05:36 | 2022-05-10 05:49 | 0:13 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
| 132/33 kV transformers T2 | 2022-05-10 05:36 | 2022-05-10 06:04 | 0:28 | T |  | 0 | 0 | No interruption
| 132/33 kV transformers T1 | 2022-05-12 15:52 | 2022-05-12 16:40 | 0:48 | T | Tripped showing O/C & E/F relay | 10 | 8 | Power interruption
| 132/33 kV transformers T2 | 2022-05-12 15:52 | 2022-05-12 18:52 | 3:00 | T
Cumilla (N) | 132/33 kV transformers T3 & T4 | 2022-05-12 17:20 | 2022-05-12 17:44 | 0:24 | E/O | Due to 33 kV Bus insulator got cracked | 8 | 3.2 | Power interruption
Fenchuganj | 230/132 kV transformer T1 | 2022-05-13 14:22 | 2022-05-13 16:40 | 2:18 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T2 | 2022-05-16 13:32 | 2022-05-16 18:38 | 5:06 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T1 & T2 | 2022-05-17 08:37 | 2022-05-17 09:17 | 0:40 | T | Tripped showing E/F relay | 16 | 10.6667 | Power interruption
Ramganj | 33 kV Bus-2 | 2022-05-19 08:01 | 2022-05-19 19:17 | 11:16 | E/O | Due to red-hot maint | 55 | 619.6667 | Power interruption
Cumilla (S) | 132/33 kV transformer T2 | 2022-05-19 08:11 | 2022-05-19 08:31 | 0:20 | E/O | Due to 33 kV feeder fault | 0 | 0 | No interruption
B.Baria | 132/33 kV transformers T1 & T2 | 2022-05-20 05:45 | 2022-05-20 06:02 | 0:17 | E/O | Due to 33 kV feeder fault | 40 | 11.3333 | Power interruption
Cumilla (N) | 132/33 kV transformers T3 & T4 | 2022-05-20 13:35 | 2022-05-20 13:44 | 0:09 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Chowmuhani | 132/33 kV transformer T2 | 2022-05-21 10:20 | 2022-05-21 12:20 | 2:00 | E/O | Due to red-hot maint at 33 kV side | 0 | 0 | No interruption
Cumilla (S) | 132/33 kV transformer T2 | 2022-05-22 07:11 | 2022-05-22 07:32 | 0:21 | T | Tripped showing O/C & E/F relay | 23 | 8.05 | Power interruption
| 132/33 kV transformer T2 | 2022-05-22 14:07 | 2022-05-22 14:19 | 0:12 | T | Tripped showing O/C & E/F relay | 20 | 4 | Power interruption
Cumilla (N) | 132/33 kV transformers T3 | 2022-05-25 16:33 | 2022-05-25 16:49 | 0:16 | T | Tripped showing O/C relay at 33 kV feeder fault
| 132/33 kV transformers T4 | 2022-05-25 16:33 | 2022-05-25 16:45 | 0:12 | T |  | 80 | 16 | Power interruption
B.Baria | 132/33 kV transformer T1 | 2022-05-26 00:08 | 2022-05-26 00:48 | 0:40 | E/O | Due to red-hot maint | 40 | 26.6667 | Power interruption
|  |  | Total : | 34:32 |  |  |  | 808.9333
Khulna Grid Circle :
Goalpara | 132/33 kV transformers T5 | 2022-05-03 10:02 | 2022-05-03 10:35 | 0:33 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV transformers T6 | 2022-05-03 10:02 | 2022-05-03 10:24 | 0:22 | T |  | 0 | 0 | No interruption
Patuakhali | 132/33 kV transformers T1 | 2022-05-03 12:32 | 2022-05-03 12:55 | 0:23 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| 132/33 kV transformers T2 | 2022-05-03 12:32 | 2022-05-03 12:55 | 0:23 | T |  | 0 | 0 | No interruption
Khulna(C) | 132/33 kV transformer T3 | 2022-05-07 16:56 | 2022-05-07 17:11 | 0:15 | T | Tripped showing O/C relay | 27 | 6.75 | Power interruption
Kustia | 132/33 kV transformer T1 | 2022-05-08 17:43 | 2022-05-08 18:56 | 1:13 | E/O | Due to red-hot maint | 20 | 24.3333 | Power interruption
Madaripur | 132/33 kV transformer T1 | 2022-05-09 21:07 | 2022-05-09 21:42 | 0:35 | E/O | Due to red-hot maint | 25 | 14.5833 | Power interruption
Gollamari | 132/33 kV transformer T2 | 2022-05-13 07:26 | 2022-05-13 07:26 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Gopalganj(O) | 132/33 kV transformer T1 | 2022-05-14 07:50 | 2022-05-14 07:50 | 0:00 | E/O | Due to red-hot maint at 33 kV PBS feeder | 0 | 0 | No interruption
Barishal | 132/33 kV transformers T1 & T2 | 2022-05-14 21:10 | 2022-05-14 21:24 | 0:14 | E/O | Due to 33 kV feeder fault | 119 | 27.7667 | Power interruption
Mongla | 132/33 kV transformers T1 & T2 | 2022-05-17 04:54 | 2022-05-17 06:07 | 1:13 | E/O | Due to 33 kV feeder fault | 28 | 34.0667 | Power interruption
Rampal | 400/230 kV transformer |  | 2022-05-17 13:45 |  | T | After Tripped showing PRD relay | 0 | 0 | No interruption
| 400/230 kV transformer | 2022-05-17 15:56 | 2022-05-17 18:28 | 2:32 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Barishal | 132 kV Bus coupler | 2022-05-17 15:56 | 2022-05-17 16:04 | 0:08 | E/O | Due to Oil leakage | 195 | 26 | Power interruption
Madaripur | 132/33 kV transformers T1 | 2022-05-22 00:30 | 2022-05-22 01:03 | 0:33 | T | Tripped showing O/C relay | 76 | 41.8 | Power interruption
| 132/33 kV transformers T2 | 2022-05-22 00:30 | 2022-05-22 01:40 | 1:10 | T
Mongla | 132/33 kV transformer T1 | 2022-05-25 19:43 | 2022-05-25 21:06 | 1:23 | E/O | Due to red-hot maint at 33 kV Bus | 25 | 34.5833 | Power interruption
Bagerhat | 132/33 kV transformer T1 | 2022-05-27 04:58 | 2022-05-27 04:58 | 0:00 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T1 | 2022-05-29 23:17 | 2022-05-30 00:58 | 1:41 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Narail | 132/33 kV transformer T1 | 2022-05-30 07:12 | 2022-05-30 08:07 | 0:55 | E/O | Due to red-hot maint | 16 | 14.6667 | Power interruption
|  |  | Total : | 13:33 |  | Unserved Energy: |  | 224.55
HVDC Grid Circle :
Bottail | 132/33 kV transformerT1 | 2022-05-04 18:32 | 2022-05-04 18:55 | 0:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Ishurdi | 230/132 kV transformer T3 | 2022-05-11 08:59 | 2022-05-11 13:59 | 5:00 | T | Tripped showing OLTC | 0 | 0 | No interruption
Benapole | 132/33 kV transformerT1 | 2022-05-13 07:54 | 2022-05-13 10:50 | 2:56 | T |  | 0 | 0 | No interruption
Bottail | 132/33 kV transformerT1 | 2022-05-19 19:04 | 2022-05-19 19:18 | 0:14 | T | Tripped showing O/C relay at 33 kV side | 75 | 17.5 | Power interruption
Shahjadpur | 132/33 kV transformerT3 | 2022-05-22 20:02 | 2022-05-22 20:27 | 0:25 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
| 132/33 kV transformerT4 | 2022-05-24 20:35 | 2022-05-24 21:34 | 0:59 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Bottail | 132/33 kV transformer T2 with 33 kV Bus | 2022-05-31 22:11 | 2022-05-31 23:02 | 0:51 | E/O | Due to red-hot maint at 33 kV Bus | 45 | 38.25 | Power interruption
|  |  | Total : | 10:48 |  |  |  | 55.75
Bogura Grid Circle:
Rangpur | 132/33 kV transformer T2 | 2022-05-02 06:12 | 2022-05-02 07:25 | 1:13 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Natore | 132/33 kV transformer T2 with 33 kV Bus-2 | 2022-05-06 09:09 | 2022-05-06 10:40 | 1:31 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Palashbari | 132/33 kV transformers T3 & T4 | 2022-05-08 07:10 | 2022-05-08 07:10 | 0:00 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Bogura(Sherpur) | 132/33 kV transformer T1 | 2022-05-09 08:10 | 2022-05-09 09:10 | 1:00 | E/O |  | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T3 | 2022-05-17 11:43 | 2022-05-17 15:35 | 3:52 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Naogaon | 132/33 kV transformer T2 | 2022-05-18 07:29 | 2022-05-18 09:17 | 1:48 | E/O | Due to red-hot maint at 33 kV Bus | 55 | 99 | Power interruption
| 132/33 kV transformer T2 | 2022-05-19 08:54 | 2022-05-19 11:19 | 2:25 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 | 2022-05-19 13:58 | 2022-05-19 15:29 | 1:31 | T | Due to 33 kV feeder fault | 40 | 60.6667 | Power interruption
Purbasadipur | 132/33 kV transformer T1 | 2022-05-20 19:15 | 2022-05-20 19:34 | 0:19 | T | Tripped showing O/C relay | 30 | 9.5 | Power interruption
Bogura | 230/132 kV transformer T1 | 2022-05-21 00:02 | 2022-05-21 08:32 | 8:30 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Bogura(Sherpur) | 132/33 kV transformers T1 & T2 | 2022-05-21 10:13 | 2022-05-21 13:02 | 2:49 | E/O | Due to red-hot maint at 33 kV Bus | 10 | 28.1667 | Power interruption
Saidpur | 132/33 kV transformer T3 | 2022-05-21 19:20 | 2022-05-21 19:20 | 0:00 | T | Tripped showing O/C relay at 33 kV side | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T1 | 2022-05-21 15:51 | 2022-05-21 15:56 | 0:05 | E/O | Due to red-hot maint at 33 kV Bus | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T6 | 2022-05-25 05:06 | 2022-05-25 07:53 | 2:47 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Naogaon | 132/33 kV transformers T1 & T2 | 2022-05-30 00:50 | 2022-05-30 00:58 | 0:08 | T | Tripped showing E/F relay | 122 | 16.2667 | Power interruption
Bogura(O) | 132/33 kV transformer T4 | 2022-05-30 07:36 | 2022-05-30 08:28 | 0:52 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 28:50 |  |  |  | 213.6
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 164:44 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: May2022
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Joydevpur | Joydevpur-Ghorashal 132 kV Ckt-1 | 2022-05-03 10:02 | 2022-05-03 11:03 | 1:01 | T | Tripped showing Dist. relay | 50 | 50.8333 | Power interruption
| Joydevpur-Ghorashal 132 kV Ckt-2 | 2022-05-03 10:04 | 2022-05-03 12:27 | 2:23 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-1 | 2022-05-03 09:42 | 2022-05-03 10:11 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Tongi-Bashundhara 132 kV Ckt-1 | 2022-05-03 09:42 | 2022-05-03 10:03 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV Ckt-2 | 2022-05-04 17:42 | 2022-05-04 19:42 | 2:00 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/S 132 kV Ckt-1 & 2 | 2022-05-06 18:20 | 2022-05-06 20:32 | 2:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV Ckt | 2022-05-07 16:56 | 2022-05-07 17:03 | 0:07 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-1 | 2022-05-10 20:05 | 2022-05-10 22:14 | 2:09 | T | Tripped showing A/R block . relay | 0 | 0 | No interruption
| Mymensingh -Jamalpur 132 kV Ckt-1 | 2022-05-18 17:38 | 2022-05-18 17:56 | 0:18 | T | Tripped showing Dist. relay | 58 | 17.4 | Power interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV Ckt-2 | 2022-05-19 16:24 | 2022-05-19 17:02 | 0:38 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Aminbazar-Manikganj P/S 132 kV Ckt- | 2022-05-21 05:37 | 2022-05-21 08:02 | 2:25 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Bhaluka 132 kV Ckt-2 | 2022-05-21 05:44 | 2022-05-21 10:17 | 4:33 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV Ckt-1 & 2 | 2022-05-23 08:17 | 2022-05-23 08:24 | 0:07 | T | Tripped showing O/V relay | 62 | 7.2333 | Power interruption
Bashundhara | Bashundhara-Tongi 132 kV Ckt-1 | 2022-05-30 16:44 | 2022-05-30 16:55 | 0:11 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 17:53 |  | Unserved Energy: |  | 75.4667
Dhaka (South) Grid Circle :
Rampura | Rampura-Bahundhara 132 kV Ckt-1 | 2022-05-03 09:42 | 2022-05-03 10:11 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption | 89.0333 |  | 120.3333 | 251.2167
| Rampura-Bahundhara 132 kV Ckt-1 | 2022-05-03 09:42 | 2022-05-03 10:03 | 0:21 | T | Tripped showing Dist. relay | 0 | 0 | No interruption | 24.7 |  | 14.7833
Ghorashal | Ghorashal-Narsinghdi 132 kV Ckt-2 | 2022-05-03 10:04 | 2022-05-03 11:51 | 1:47 | T | Tripped showing Dist. relay | 50 | 89.1667 | Power interruption | 113.7333 |  | 135.1167
Aurahati | Aurahati-Hasnabad 132 kV Ckt | 2022-05-03 06:00 | 2022-05-03 08:28 | 2:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-05-10 15:53 | 2022-05-10 16:09 | 0:16 | T | Tripped showing Dist. relay | 100 | 26.6667 | Power interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2022-05-10 15:49 | 2022-05-10 16:00 | 0:11 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-05-11 13:49 | 2022-05-11 14:19 | 0:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Haripur-Sonargaon 132 V Ckt-1 | 2022-05-12 15:10 | 2022-05-12 15:24 | 0:14 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Shyampur | Shyampur-APR 230 kV Ckt | 2022-05-12 14:55 | 2022-05-12 15:07 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV Ckt-1 | 2022-05-12 14:56 | 2022-05-12 15:48 | 0:52 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joyvedpur 132 kV Ckt-2 | 2022-05-15 14:59 | 2022-05-15 15:32 | 0:33 | T | Tripped showing main prot.. relay | 0 | 0 | No interruption
Tangail S/S | Tangail S/S-RPCL P.P 132 kV Ckt-1 | 2022-05-18 18:06 | 2022-05-18 18:25 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-05-20 00:10 | 2022-05-20 00:22 | 0:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2022-05-21 04:25 | 2022-05-21 06:40 | 2:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2022-05-21 05:35 | 2022-05-21 06:05 | 0:30 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Moghbazar | Moghbazar-Rampura 132 kV Ckt-2 | 2022-05-24 23:00 | 2022-05-25 16:07 | 17:07 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Ghorashal | Ghorashal-Bhulta 230 kV Ckt-2 | 2022-05-25 17:14 | 2022-05-25 18:46 | 1:32 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV Ckt | 2022-05-26 11:03 | 2022-05-26 11:33 | 0:30 | T | Tripped showing O/C & E/F. relay | 40 | 20 | Power interruption
Siddhirganj | Siddhirganj-Siddhirganj peaking 132 kV Ckt | 2022-05-26 11:04 | 2022-05-26 11:58 | 0:54 | T | Due to master protection. relay | 0 | 0 | No interruption
|  |  | Total : | 31:12 |  | Unserved Energy: |  | 135.8333
Chattogram Grid Circle :
Sikalbaha | Sikalbaha-T.K chemical 132 kV Ckt | 2022-05-01 01:45 | 2022-05-01 02:27 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Kaptai 132 kV Ckt-2 | 2022-05-03 08:18 | 2022-05-03 10:23 | 2:05 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Baroierhat | Baroierhat - Hathazari132 kV Ckt-1 & 2 | 2022-05-06 10:44 | 2022-05-06 11:02 | 0:18 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Kaptai | Kaptai-Chandraghona 132 kV Ckt-1 | 2022-05-06 13:09 | 2022-05-06 14:59 | 1:50 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV Ckt-2 | 2022-05-07 08:00 | 2022-05-07 16:56 | 8:56 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV Ckt-1 | 2022-05-21 08:22 | 2022-05-21 09:49 | 1:27 | T | Tripped showing Dist. & E/F relay. | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2022-05-21 09:39 | 2022-05-21 12:20 | 2:41 | T | Tripped showing Dist. relay | 26 | 69.7667 | Power interruption
| Dohazari-Cox'sbazar 132 kV Ckt-2 | 2022-05-29 13:03 | 2022-05-29 13:30 | 0:27 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 18:26 |  | Unserved Energy: |  | 69.7667
Cumilla Grid Circle :
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-05-03 10:56 | 2022-05-03 12:14 | 1:18 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV Ckt | 2022-05-05 10:28 | 2022-05-05 15:06 | 4:38 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt-2 | 2022-05-05 12:29 | 2022-05-05 12:49 | 0:20 | T | Tripped showing O/C. relay | 0 | 0 | No interruption
| B.Baria-Shahjibazar 132 kV Ckt-2 | 2022-05-05 13:49 | 2022-05-05 15:35 | 1:46 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-1 | 2022-05-06 10:30 | 2022-05-06 15:05 | 4:35 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV Ckt-2 | 2022-05-06 10:30 | 2022-05-06 11:02 | 0:32 | T |  | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj P/S.132 kV Ckt | 2022-05-10 21:38 | 2022-05-10 22:42 | 1:04 | E/O | Due to bursting of L/A | 0 | 0 | No interruption
| Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-05-12 14:40 | 2022-05-12 14:55 | 0:15 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
B.Baria | B.Baria-Narsinghdi 132 kV Ckt-1 | 2022-05-12 15:19 | 2022-05-12 17:23 | 2:04 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| B.Baria-Narsinghdi 132 kV Ckt-2 | 2022-05-12 15:19 | 2022-05-12 19:03 | 3:44 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Daudkandi 132 kV Ckt-2 | 2022-05-12 16:30 | 2022-05-12 17:20 | 0:50 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Bibiyana S/S | Bibiyana S/S-Bibiyna 400 kV P/S 132 kV Ckt | 2022-05-12 17:10 | 2022-05-12 17:10 | 0:00 | T | Tripped showing general trip. relay. | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bibiyana 230 kV kt-2 | 2022-05-13 14:22 | 2022-05-13 16:47 | 2:25 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
B.Baria | B.Baria-Narsinghdi 132 kV Ckt-1 | 2022-05-13 19:11 | 2022-05-13 20:09 | 0:58 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Cumilla(N) 230 kV Ckt-1 | 2022-05-13 19:40 | 2022-05-13 19:54 | 0:14 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV Ckt | 2022-05-17 07:50 | 2022-05-17 07:50 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur desh P.P 132 kV Ckt-1 | 2022-05-18 10:56 | 2022-05-18 11:18 | 0:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ramganj-Chandpur desh P.P 132 kV Ckt-2 | 2022-05-18 10:56 | 2022-05-18 11:10 | 0:14 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV Ckt-1 | 2022-05-19 03:17 | 2022-05-19 03:24 | 0:07 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2022-05-19 03:20 | 2022-05-19 03:43 | 0:23 | T | Tripped showing Dist. relay. | 11 | 4.2167 | Power interruption
Ashuganj | Ashuganj-B.Baria 132 kV Ckt-1 | 2022-05-19 16:28 | 2022-05-19 19:13 | 2:45 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV Ckt-2 | 2022-05-19 16:28 | 2022-05-19 16:56 | 0:28 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Ashuganj-Ghorashal 132 kV Ckt-1 & 2 | 2022-05-19 16:19 | 2022-05-19 16:48 | 0:29 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV Ckt-2 | 2022-05-19 23:32 | 2022-05-20 00:10 | 0:38 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-1 | 2022-05-21 06:44 | 2022-05-21 07:05 | 0:21 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-2 | 2022-05-21 06:44 | 2022-05-21 06:58 | 0:14 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Cumilla(S) 132 kV Ckt-3 | 2022-05-21 06:44 | 2022-05-21 07:06 | 0:22 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Feni | Feni-Chaddogram 132 kV Ckt-2 | 2022-05-23 03:48 | 2022-05-23 04:32 | 0:44 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV Ckt-2 | 2022-05-26 15:23 | 2022-05-26 16:27 | 1:04 | T | Due to red-hot maint. | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV Ckt-1 & 2 | 2022-05-29 09:43 | 2022-05-29 09:43 | 0:00 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-1 & 2 | 2022-05-29 09:43 | 2022-05-29 09:43 | 0:00 | T |  | 0 | 0 | No interruption
Bibiyana | Bibiyana-Fenchuganj 230 kV Ckt-1 | 2022-05-29 09:43 | 2022-05-29 09:43 | 0:00 | T | Tripped showing O/C. relay. | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV Ckt-2 | 2022-05-30 06:44 | 2022-05-30 07:12 | 0:28 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV Ckt-2 | 2022-05-30 07:25 | 2022-05-30 07:34 | 0:09 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
| Cumilla(N)-BSRM 230 kV Ckt-2 | 2022-05-31 07:56 | 2022-05-31 13:08 | 5:12 | T | Tripped showing Dist. relay. | 0 | 0 | No interruption
|  |  | Total : | 38:43 |  | Unserved Energy: |  | 4.2167
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-1 | 2022-05-03 08:57 | 2022-05-03 13:31 | 4:34 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Goalpara | Goalpara-Orion P.P 132 kV Ckt | 2022-05-03 08:57 | 2022-05-03 12:47 | 3:50 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj P.P 132 kV Ckt-2 | 2022-05-03 09:42 | 2022-05-03 10:26 | 0:44 | T |  | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV Ckt-1 | 2022-05-03 10:43 | 2022-05-03 12:46 | 2:03 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Gopalganj(O) 132 kV Ckt-2 | 2022-05-07 08:00 | 2022-05-08 05:42 | 21:42 | E/O | Due to bursting of CT | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV Ckt-1 & 2 | 2022-05-07 08:01 | 2022-05-08 06:25 | 22:24 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Narail | Narail-Magura 132 kV Ckt-1 | 2022-05-11 12:05 | 2022-05-11 12:33 | 0:28 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barisal(N) | Barisal(N)-Bhola 230 kV Ckt-1 | 2022-05-11 17:26 | 2022-05-11 17:55 | 0:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-1 | 2022-05-12 15:58 | 2022-05-12 19:51 | 3:53 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Rampal 400 kV Ckt-1 | 2022-05-21 08:00 | 2022-05-21 08:42 | 0:42 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Noapara | Noapara-Khulna© 132 kV Ckt-2 | 2022-05-31 16:07 | 2022-05-31 16:16 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
|  |  | Total : | 60:58 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenaidah(O) | Jhenaidah(O)-Magura 132 kV Ckt | 2022-05-10 15:30 | 2022-05-10 15:39 | 0:09 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV Ckt-2 |  | 2022-05-20 09:45 |  | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt-1 | 2022-05-21 06:14 | 2022-05-21 06:14 | 0:00 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Baghabari P/S | Baghabari P/S-Sirajganj 132 kV Ckt | 2022-05-21 05:03 | 2022-05-21 07:55 | 2:52 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Rajbari 132 kV Ckt-2 | 2022-05-23 09:39 | 2022-05-23 09:58 | 0:19 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Ishurdi | Ishurdi-Bheramara 132 kV Ckt-2 | 2022-05-31 08:52 | 2022-05-31 15:35 | 6:43 | E/O | Due to red-hot maint | 0 | 0 | No interruption
| Ishurdi-Bheramara 132 kV Ckt-1 | 2022-05-31 08:55 | 2022-05-31 15:35 | 6:40 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 16:43 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Mithapukur | Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-05-16 00:30 | 2022-05-16 01:24 | 0:54 | T | Due to bad weather | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV both Ckts-2 | 2022-05-16 09:08 | 2022-05-16 09:46 | 0:38 | T | Tripped showing Dist. relay | 147 | 93.1 | Power interruption
| Bogura-Naogaon 132 kV both Ckts-1 | 2022-05-16 09:08 | 2022-05-16 12:56 | 3:48 | T
Rajshahi(O) | Rajshahi(O)-Rajshahi(N) 132 kV Ckt-1 | 2022-05-16 17:45 | 2022-05-16 17:55 | 0:10 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mohastanghor 132 kV Ckt-1 | 2022-05-17 04:22 | 2022-05-17 07:16 | 2:54 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV Ckt-1 | 2022-05-17 04:48 | 2022-05-17 05:13 | 0:25 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Bogura-Confi-1 P.P 132 kV Ckt-1 | 2022-05-17 04:48 | 2022-05-17 05:12 | 0:24 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-05-19 20:00 | 2022-05-19 20:40 | 0:40 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Naogaon 132 kV Ckt-1 | 2022-05-19 20:38 | 2022-05-19 21:19 | 0:41 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Bogura(O)-Naogaon 132 kV Ckt-2 | 2022-05-19 20:40 | 2022-05-19 21:34 | 0:54 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Sherpur 132 kV Ckt-1 | 2022-05-19 20:24 | 2022-05-19 21:36 | 1:12 | T | Tripped showing Dist. relay | 0 | 0 | No interruption |  | 0
| Bogura(N)-Sherpur 132 kV Ckt-2 | 2022-05-19 20:40 | 2022-05-19 20:40 | 0:00 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
| Bogura(N)-B.Pukuria 132 kV Ckt-2 | 2022-05-19 20:32 | 2022-05-19 22:25 | 1:53 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Mohastanghor 132 kV Ckt-1 & 2 | 2022-05-21 03:54 | 2022-05-21 05:09 | 1:15 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Bogura-Naogaon 132 kV Ckt-1 | 2022-05-21 03:55 | 2022-05-21 05:24 | 1:29 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Mohastanghor 132 kV Ckt-2 | 2022-05-21 06:14 | 2022-05-21 06:48 | 0:34 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Bogura(N)-Sherpur 132 kV Ckt-1 | 2022-05-21 03:59 | 2022-05-21 08:16 | 4:17 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Bogura(N)-Confi.P/S 132 kV Ckt-1 | 2022-05-21 03:59 | 2022-05-21 08:14 | 4:15 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Naogaon | Naogaon-Joypurhat 132 kV Ckt | 2022-05-21 03:35 | 2022-05-21 04:37 | 1:02 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Naogaon-Santahar P/S 132 kV Ckt | 2022-05-21 03:35 | 2022-05-21 05:20 | 1:45 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Sirajganj | Sirajganj-Shahjadpur 132 kV Ckt | 2022-05-21 05:44 | 2022-05-21 06:46 | 1:02 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Mahastanghor | Mahastanghor-Palashbari 132 kV Ckt-1 | 2022-05-21 04:05 | 2022-05-21 05:13 | 1:08 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV Ckt-2 | 2022-05-24 10:21 | 2022-05-24 10:38 | 0:17 | T | Tripped showing Dist. relay | 0 | 0 | No interruption
Barapukuria S/S | Barapukuria S/S-Barapukuria P/S 230 kV Ckt-2 | 2022-05-25 05:22 | 2022-05-25 07:41 | 2:19 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bogura(O) | Bogura(O)-Naogaon 132 kV Ckt-1 | 2022-05-26 06:25 | 2022-05-26 06:25 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-05-28 11:20 | 2022-05-28 12:17 | 0:57 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV Ckt-2 | 2022-05-29 05:48 | 2022-05-29 08:53 | 3:05 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 37:58 |  | Unserved Energy: |  | 93.1
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 221:53 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 33 kV Bus-2 | 2022-05-07 20:20 | 2022-05-07 21:04 | 0:44 | S/O | Due to C/M work | 45 | 33 | Power interruption
Kabirpur | 132/33 kV transformer T-1 | 2022-05-12 16:56 | 2022-05-12 19:42 | 2:46 | S/O | Due to PBS work | 40 | 110.6667 | Power interruption
Savar | 33 kV Bus-A | 2022-05-14 07:00 | 2022-05-14 07:00 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-1 |  | 2022-05-15 15:50 |  | S/O | After.maint work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-02 | 2022-05-17 05:26 | 2022-05-17 05:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T-2 | 2022-05-17 08:23 | 2022-05-17 11:44 | 3:21 | S/O | Due to PBS work | 60 | 201 | Power interruption
Tongi | 230/132 kV transformer T-03 | 2022-05-18 05:10 | 2022-05-18 07:30 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T-1 | 2022-05-18 07:04 | 2022-05-18 08:38 | 1:34 | S/O | Due to C/M work | 5 | 7.8333 | Power interruption
Sherpur | 132/33 kV transformer T-1 | 2022-05-18 08:22 | 2022-05-18 17:19 | 8:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV transformer T-1 | 2022-05-18 09:38 | 2022-05-18 13:49 | 4:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV transformer T-01 | 2022-05-19 05:22 | 2022-05-19 08:15 | 2:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T-3 | 2022-05-19 08:11 | 2022-05-19 17:04 | 8:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV transformer T-1 | 2022-05-22 09:07 | 2022-05-22 10:56 | 1:49 | S/O | Due to 33 KV GCB noise | 0 | 0 | No interruption
Kallyanpur | 132 kV main Bus | 2022-05-22 12:19 | 2022-05-22 21:18 | 8:59 | S/O | Due to CB change | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T-2 with 33 kV Bus-2 | 2022-05-22 06:05 | 2022-05-22 07:35 | 1:30 | S/O | Due to C/M work | 35 | 52.5 | Power interruption
Tangail | 132/33 kV transformer T-3 | 2022-05-23 07:45 | 2022-05-23 10:48 | 3:03 | S/O | Due to PBS work | 10 | 30.5 | Power interruption
Sherpur | 132/33 kV transformer T-2 | 2022-05-24 08:18 | 2022-05-24 15:13 | 6:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132 kV main Bus | 2022-05-24 08:10 | 2022-05-24 21:12 | 13:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 33 kV Bus-A | 2022-05-24 07:24 | 2022-05-24 08:54 | 1:30 | S/O | Due to PBS work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-4 | 2022-05-25 11:19 | 2022-05-25 13:35 | 2:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132 kV main Bus | 2022-05-25 15:36 | 2022-05-25 16:20 | 0:44 | S/O | Due to tempature high | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-05-25 15:06 | 2022-05-25 16:26 | 1:20 | S/O | Due to loop changing | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2022-05-28 07:24 | 2022-05-28 07:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 76:47 |  | Unserved Energy: |  | 435.5 |  | 634.8
Dhaka (South) Grid Circle : | [9 empty] | 39.3333
Ghorashal | 132/33 kV transformer T-1 | 2022-05-02 13:23 | 2022-05-02 13:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption | 674.1333
Bhulta | 132/33 kV transformer GT-1 | 2022-05-09 06:19 | 2022-05-09 06:59 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 132/33 kV transformer T-1 | 2022-05-10 11:40 | 2022-05-10 12:14 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Shyampur | 132/33 kV transformer GT-2 | 2022-05-14 09:55 | 2022-05-14 17:30 | 7:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | 230/132 kV transformer AT02 | 2022-05-16 11:33 | 2022-05-16 14:12 | 2:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T02 |  | 2022-05-16 17:28 |  | S/O | After.maint work | 0 | 0 | No interruption
Bhulta | 132/33 kV transformer T-1 | 2022-05-17 22:35 | 2022-05-17 23:34 | 0:59 | S/O | Due to 33 kV Bus maint.work | 45 | 44.25 | Power interruption
Siddhirganj | 230/132 kV transformer MT02 | 2022-05-18 15:45 | 2022-05-18 16:56 | 1:11 | S/O | Due to high temperature | 0 | 0 | No interruption
Sreenagar | 132/33 kV transformer T-1 | 2022-05-21 20:05 | 2022-05-21 22:00 | 1:55 | S/O | Due to 33 kV PBS feeder fault | 15 | 28.75 | Power interruption
Siddhirganj | 132/33 kV transformer T-12 | 2022-05-27 06:32 | 2022-05-27 06:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 15:33 |  | Unserved Energy: |  | 73
Chattogram Grid Circle :
GPH ispat | 132/33 kV transformer T1 | 2022-05-04 11:38 | 2022-05-04 12:13 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV transformer T-1 | 2022-05-08 21:02 | 2022-05-08 21:45 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
T.K Chemical | 132/33 kV transformer T-2 | 2022-05-12 09:10 | 2022-05-12 09:56 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kV transformer T3 | 2022-05-14 05:09 | 2022-05-14 05:09 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-1 | 2022-05-14 09:00 | 2022-05-14 11:56 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
GPH ispat | 230/33/11 kV transformer T1 | 2022-05-14 12:56 | 2022-05-14 12:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kV transformer T-1 | 2022-05-18 22:50 | 2022-05-19 | 1:10 | S/O | Due to DS problem | 0 | 0 | No interruption
Hathazari | 230/132 kV transformer T02 | 2022-05-21 12:20 | 2022-05-21 12:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chanradhona | 132/33 kV transformer T-2 |  | 2022-05-21 12:27 |  |  | After.maint work | 0 | 0 | No interruption
Bakulia | 132/33 kV transformer T-3 | 2022-05-21 13:07 | 2022-05-21 15:28 | 2:21 | S/O | Due to 33 kV Y-φ,DS wire stringing | 25 | 58.75 | No interruption
Chanradhona | 132/33 kV transformer T-1 | 2022-05-27 08:24 | 2022-05-27 17:44 | 9:20 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-05-30 07:24 | 2022-05-30 07:24 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kagrachari | 132/33 kV transformer T-1 | 2022-05-31 09:54 | 2022-05-31 11:16 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-2 | 2022-05-31 11:20 | 2022-05-31 12:40 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
GPH ispat | 230/33 kV transformer T1 | 2022-05-31 11:21 | 2022-05-31 11:39 | 0:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Chanradhona | 132/33 kV transformer T-1 | 2022-05-31 15:07 | 2022-05-31 17:30 | 2:23 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 23:14 |  | Unserved Energy : |  | 58.75
Cumilla Grid Circle :
Sylhet | 132/33 kV transformer T2 | 2022-05-05 06:51 | 2022-05-05 06:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-05-10 05:05 | 2022-05-10 07:51 | 2:46 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2022-05-10 18:28 | 2022-05-10 20:20 | 1:52 | S/O | Due to replacement work at 33 kV side | 45 | 84 | Power interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-05-10 20:26 | 2022-05-10 21:37 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T2 | 2022-05-11 06:17 | 2022-05-11 06:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T1 | 2022-05-12 09:50 | 2022-05-12 10:27 | 0:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-05-14 02:03 | 2022-05-14 03:38 | 1:35 | S/O | Due to C/M work | 10 | 15.8333 | Power interruption
Kachua | 132/33 kV transformer T-3 | 2022-05-14 11:20 | 2022-05-14 12:42 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformers T1 T2 T3 & T4 | 2022-05-15 11:21 | 2022-05-15 12:59 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-05-15 07:00 | 2022-05-15 07:44 | 0:44 | S/O | Due to C/M work | 35 | 25.6667 | Power interruption
Chowddagram | 132/33 kV transformer T1 | 2022-05-16 15:22 | 2022-05-16 17:28 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T1 | 2022-05-16 09:19 | 2022-05-16 09:19 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 400/230 kV transformer IBT1 | 2022-05-19 10:21 | 2022-05-19 13:49 | 3:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 132/33 kV transformer T2 | 2022-05-21 12:47 | 2022-05-21 15:34 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformer T2 | 2022-05-22 16:55 | 2022-05-22 18:02 | 1:07 | S/O | Due to CB maint. Of 33 kV feeder | 15 | 16.75 | Power interruption
Daudkandi | 132/33 kV transformer T1 | 2022-05-23 08:16 | 2022-05-23 16:38 | 8:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-05-23 11:01 | 2022-05-23 12:44 | 1:43 | S/O | Due to C/M work | 65 | 111.5833 | Power interruption
Ashuganj | 132 kV Bus-1 | 2022-05-23 10:10 | 2022-05-23 12:19 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowddagram | 132/33 kV transformer T2 | 2022-05-25 12:18 | 2022-05-25 13:35 | 1:17 | S/O | Due to C/M work | 25 | 32.0833 | Power interruption
Shahjibazar | 132/33 kV transformer T4 | 2022-05-27 08:19 | 2022-05-27 11:31 | 3:12 | S/O | Due to C/M work | 20 | 64 | Power interruption
Cumilla(N) | 132/33 kV transformer T4 | 2022-05-27 08:28 | 2022-05-27 10:53 | 2:25 | S/O | Due to C/M work | 10 | 24.1667 | Power interruption
Ramganj | 132/33 kV transformer T2 | 2022-05-27 08:20 | 2022-05-27 09:24 | 1:04 | S/O | Due to C/M work
| 132/33 kV transformer T1 | 2022-05-27 08:40 | 2022-05-27 09:24 | 0:44 | S/O |  | 40 | 29.3333 | Power interruption
Chattak | 132/33 kV transformer T2 | 2022-05-28 12:59 | 2022-05-28 12:59 | 0:00 | S/O | Due to Oil centrifuging | 0 | 0 | No interruption
Bianibazar | 132/33 kV transformer T1 | 2022-05-31 09:58 | 2022-05-31 11:26 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-05-31 11:28 | 2022-05-31 12:33 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 44:42 |  | Unserved Energy : |  | 403.4167
Khulna Grid Circle :
Goalpara | 132/33 kV transformer T6 | 2022-05-05 08:15 | 2022-05-05 10:55 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T3 | 2022-05-05 15:45 | 2022-05-05 16:45 | 1:00 | S/O | Due to changing work by 33 kV feeder | 15 | 15 | Power interruption
Magura | 132 kV Bus | 2022-05-13 08:30 | 2022-05-13 12:27 | 3:57 | S/O | Due to installation work | 58 | 229.1 | Power interruption
Gopalganj(O) | 132/33 kV transformer T-1 | 2022-05-14 07:51 | 2022-05-14 09:02 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | 132/33 kV transformers T3 & T4 | 2022-05-14 08:52 | 2022-05-15 21:16 | 36:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Faripur | 132/33 kV transformer T3 | 2022-05-14 08:59 | 2022-05-14 12:11 | 3:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-B | 2022-05-14 08:56 | 2022-05-14 12:17 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Shariatpur | 132 kV Bus coupler | 2022-05-14 03:05 | 2022-05-14 12:17 | 9:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | 400/132 kV transformer T02 | 2022-05-15 11:09 | 2022-05-15 16:34 | 5:25 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/132 kV transformer T01 | 2022-05-16 10:01 | 2022-05-16 10:01 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampal | 400/132 kV transformer T01 | 2022-05-17 06:23 | 2022-05-17 06:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | 132/33 kV transformer T4 | 2022-05-17 09:58 | 2022-05-17 14:39 | 4:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Noapara | 132/33 kV transformer T2 | 2022-05-21 08:34 | 2022-05-21 08:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Faripur | 132/33 kV transformer T2 | 2022-05-22 06:56 | 2022-05-22 13:13 | 6:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-05-22 08:32 | 2022-05-22 13:13 | 4:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T-1 | 2022-05-23 07:38 | 2022-05-23 11:48 | 4:10 | S/O | Due to C/M work | 20 | 83.3333 | Power interruption
Rajbari | 132/33 kV transformer T-1 | 2022-05-24 08:59 | 2022-05-24 18:52 | 9:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2022-05-24 09:21 | 2022-05-24 18:54 | 9:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T-1 with 33 kV Bus | 2022-05-25 06:57 | 2022-05-25 09:31 | 2:34 | S/O | Due to C/M work | 10 | 25.6667 | Power interruption
Rajbari | 132/33 kV transformer T-2 | 2022-05-25 08:10 | 2022-05-25 18:08 | 9:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | 132 kV Bus-1 | 2022-05-28 08:50 | 2022-05-28 19:35 | 10:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-1 | 2022-05-29 08:26 | 2022-05-29 19:03 | 10:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-1 | 2022-05-30 07:46 | 2022-05-30 07:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | 132/33 kV transformer T-1 | 2022-05-30 10:50 | 2022-05-30 16:05 | 5:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-3 | 2022-05-31 07:12 | 2022-05-31 08:47 | 1:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | 132/33 kV transformer T-2 | 2022-05-31 08:17 | 2022-05-31 19:03 | 10:46 | S/O | Due to SAS work | 0 | 0 | No interruption
|  |  | Total : | 157:07 |  | Unserved Energy : |  | 353.1
HVDC Grid Circle
Jashore | 132/33 kV transformer T1 | 2022-05-04 10:10 | 2022-05-04 11:26 | 1:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Bottail | 132/33 kV transformer T1 | 2022-05-13 20:26 | 2022-05-13 21:53 | 1:27 | S/O | Due to C/M work | 25 | 36.25 | Power interruption
Jhenaidah | 230 kV Bus coupler | 2022-05-13 10:18 | 2022-05-13 15:46 | 5:28 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV transformer T1 | 2022-05-16 06:51 | 2022-05-16 06:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV transformer T01 | 2022-05-16 09:06 | 2022-05-16 09:06 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230/132 kV transformer T02 | 2022-05-18 08:39 | 2022-05-18 17:46 | 9:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC 230 kV filter 20DF11 | 2022-05-23 06:43 | 2022-05-23 11:20 | 4:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Kustia | 132/33 kV transformer T1 with 33 kV Bus-1 | 2022-05-23 07:03 | 2022-05-23 08:59 | 1:56 | S/O | Due to C/M work | 22 | 42.5333 | Power interruption
Jhenaidah | 132/33 kV transformer T1 | 2022-05-29 08:11 | 2022-05-29 09:50 | 1:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T2 | 2022-05-30 08:45 | 2022-05-30 17:29 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T2 | 2022-05-31 07:17 | 2022-05-31 07:17 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 34:14 |  | Unserved Energy : |  | 78.7833
Bogura Grid Circle:
Bogura(O) | 132/33 kV transformer T3 | 2022-05-01 14:38 | 2022-05-01 15:26 | 0:48 | S/O | Due to 33 kV Bus maint. | 18 | 14.4 | Power interruption
Rajshahi | 132/33 kV transformer T2 | 2022-05-07 07:35 | 2022-05-07 09:20 | 1:45 | S/O | Due to C/M work | 13 | 22.75 | Power interruption
Rajshahi(N) | 132/33 kV transformer T2 | 2022-05-07 14:48 | 2022-05-07 16:50 | 2:02 | S/O | Due to Oil refiling | 0 | 0 | Power interruption
Bogura(O) | 132/33 kV transformer T1 | 2022-05-09 08:27 | 2022-05-09 09:27 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T2 | 2022-05-10 08:33 | 2022-05-10 08:33 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | 132/33 kV transformer T2 | 2022-05-10 09:43 | 2022-05-10 14:47 | 5:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Niyamatpur | 132/33 kV transformer T2 |  | 2022-05-13 16:46 |  | S/O | After maint.work | 0 | 0 | No interruption
| 132/33 kV transformer T3 | 2022-05-14 08:43 | 2022-05-14 17:50 | 9:07 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T2 | 2022-05-15 08:15 | 2022-05-15 10:09 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/11 kV transformer T1 | 2022-05-16 09:10 | 2022-05-16 11:45 | 2:35 | S/O | Due to high temperatrue | 0 | 0 | No interruption
Rangpur | 33 kV Bus-2 | 2022-05-19 06:08 | 2022-05-19 07:12 | 1:04 | S/O | Due to 33kV feeder maint. | 30 | 32 | Power interruption
Panchagaor | 132/33 kV transformer T2 | 2022-05-19 08:01 | 2022-05-19 10:58 | 2:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T2 | 2022-05-20 09:15 | 2022-05-20 09:57 | 0:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV transformer T2 | 2022-05-21 22:10 | 2022-05-21 23:20 | 1:10 | S/O | Due to C/M work by 33 kV feeder maint. | 20 | 23.3333 | Power interruption
Naogaon | 132/33 kV transformer T2 | 2022-05-22 07:50 | 2022-05-22 07:50 | 0:00 | S/O | Due to C/M work by 33 kV feeder maint. | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T3 with 33 kV Bus-2 | 2022-05-23 07:10 | 2022-05-23 16:55 | 9:45 | S/O | Due to C/M work | 10 | 97.5 | Power interruption
Jaldhaka | 132/33 kV transformer T1 | 2022-05-24 09:18 | 2022-05-24 09:18 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV transformer T2 | 2022-05-24 12:20 | 2022-05-24 13:40 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Thakurgaon | 132/33 kV transformerT1 | 2022-05-24 12:05 | 2022-05-24 12:30 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformerT2 | 2022-05-24 12:40 | 2022-05-24 13:15 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformerT3 | 2022-05-24 13:30 | 2022-05-24 14:20 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Panchugarh | 132/33 kV transformerT1 | 2022-05-25 12:09 | 2022-05-25 12:54 | 0:45 | S/O | Due to energy meter test | 0 | 0 | No interruption
| 132/33 kV transformerT2 | 2022-05-25 13:01 | 2022-05-25 13:22 | 0:21 | S/O |  | 0 | 0 | No interruption
Rajshahi | 132/33 kV transformerT2 with 33 kV Bus | 2022-05-28 08:28 | 2022-05-28 11:35 | 3:07 | S/O | Due to replacement work | 0 | 0 | No interruption
Mithapukur | 132/33 kV transformer T1 | 2022-05-28 12:57 | 2022-05-28 13:30 | 0:33 | S/O | Due to replacement work | 0 | 0 | No interruption
Bogura | 132/33 kV transformer T1 | 2022-05-31 07:06 | 2022-05-31 09:54 | 2:48 | S/O | Due to C/M work | 40 | 112 | Power interruption
Rajshahi | 132/33 kV transformer T2 | 2022-05-31 10:08 | 2022-05-31 16:21 | 6:13 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 56:50 |  | Unserved Energy : |  | 301.9833
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 408:27 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: May2022
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-05-08 09:57 | 2022-05-08 14:19 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV Ckt-1 | 2022-05-11 10:09 | 2022-05-11 12:09 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2022-05-12 10:49 | 2022-05-12 13:51 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-1 | 2022-05-14 09:22 | 2022-05-14 13:50 | 4:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh -Kishoreganj 132 kV Ckt-1 | 2022-05-16 14:40 | 2022-05-16 16:01 | 1:21 | S/O | Due to tree trimming | 0 | 0 | No interruption
Tongi | Tongi-Tongi P/S 132 kV Ckt | 2022-05-17 10:42 | 2022-05-17 21:32 | 10:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV Ckt-2 | 2022-05-19 10:01 | 2022-05-19 14:35 | 4:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-1 | 2022-05-22 10:05 | 2022-05-22 10:05 | 0:00 | S/O | Due to 33 kV CB pole change | 0 | 0 | No interruption
Tongi | Tongi-Milgate 132 kV Ckt-1 & 2 | 2022-05-22 11:05 | 2022-05-22 17:27 | 6:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| Tongi-Milgate 132 kV Ckt-1 | 2022-05-23 10:17 | 2022-05-23 16:54 | 6:37 | S/O | Due to C/M work | 0 | 0 | No interruption
| Tongi-Milgate 132 kV Ckt-2 | 2022-05-24 10:47 | 2022-05-24 16:02 | 5:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV Ckt-2 | 2022-05-24 10:51 | 2022-05-24 10:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2022-05-29 10:31 | 2022-05-29 11:59 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 50:19 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Keraniganj | Keraniganj-Kamrangirchar 132 kV Ckt | 2022-05-07 05:59 | 2022-05-07 05:59 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Keraniganj-Srinagar 132 kV Ckt-1 | 2022-05-10 12:08 | 2022-05-10 15:30 | 3:22 | S/O | Due to tree trimming | 0 | 0 | No interruption
Shyampur(O) | Shyampur(O)-Shyampur(N) 132 kV Ckt-1 | 2022-05-11 06:17 | 2022-05-11 06:17 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-1 | 2022-05-11 10:12 | 2022-05-11 16:59 | 6:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-2 | 2022-05-13 09:01 | 2022-05-13 09:01 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Nawabganj 132 kV Ckt-2 | 2022-05-13 09:46 | 2022-05-13 14:42 | 4:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 230 kV Ckt-1 | 2022-05-14 10:05 | 2022-05-14 10:05 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Rampura | Rampura-Dhaka university 132 kV Ckt-1 |  | 2022-05-15 10:14 |  |  | new connection | 0 | 0 | No interruption
| Rampura-Dhaka university 132 kV Ckt-2 |  | 2022-05-15 10:25 |  |  |  | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur EGCB P/P 132 kV Ckt | 2022-05-17 11:12 | 2022-05-17 16:28 | 5:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Charsayedpur 132 kV Ckt-1 | 2022-05-17 15:48 | 2022-05-17 17:10 | 1:22 | S/O | Due to OPGW work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2022-05-18 09:30 | 2022-05-18 14:57 | 5:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-1 | 2022-05-18 11:22 | 2022-05-18 16:15 | 4:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Bashundhara | Bashundhara-Purbachal 132 kV Ckt | 2022-05-22 12:56 | 2022-05-22 12:56 | 0:00 |  | new connection | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-1 | 2022-05-22 13:53 | 2022-05-22 17:48 | 3:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj 335 MW 230 kV Ckt-1 | 2022-05-24 09:20 | 2022-05-24 13:22 | 4:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Hasnabad 230 kV Ckt-2 | 2022-05-25 09:56 | 2022-05-25 12:41 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Rampura 230 kV Ckt-1 | 2022-05-26 13:53 | 2022-05-26 17:48 | 3:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | Madanganj-Madanganj P/S 132 kV Ckt | 2022-05-26 14:37 | 2022-05-26 17:38 | 3:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj -Maniknagar 230 kV Ckt-1 |  | 2022-05-26 11:06 |  |  | After maint.work | 0 | 0 | No interruption
| Siddhirganj -Maniknagar 230 kV Ckt-2 | 2022-05-28 11:14 | 2022-05-28 11:14 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur -Madanganj 132 kV Ckt | 2022-05-30 10:00 | 2022-05-30 11:59 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 51:40 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Madunaghat 132 kV Ckt-1 | 2022-05-09 11:35 | 2022-05-09 11:44 | 0:09 | S/O | Due to removing bird | 0 | 0 | No interruption
| Hathazari-Kaptai 132 kV Ckt-2 | 2022-05-09 11:54 | 2022-05-09 12:01 | 0:07 | S/O |  | 0 | 0 | No interruption
Anwara | Anwara-Sikalbaha 230 kV Ckt-1 | 2022-05-13 09:36 | 2022-05-14 15:25 | 29:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Sikalbaha 132 kV Ckt-1 | 2022-05-16 06:33 | 2022-05-16 06:33 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Dohazari-Sikalbaha 132 kV Ckt-2 | 2022-05-16 08:26 | 2022-05-16 09:48 | 1:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV Ckt-2 | 2022-05-18 06:28 | 2022-05-18 07:46 | 1:18 | S/O | Due to C/M work | 35 | 45.5 | Power interruption
Baraulia | Baraulia-Ak.steel 132 kV Ckt | 2022-05-18 12:20 | 2022-05-18 13:36 | 1:16 | S/O | Due to tree trimming | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV Ckt-1 | 2022-05-20 09:48 | 2022-05-20 12:05 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
| Sikalbaha-Dohazari 132 kV Ckt-2 | 2022-05-20 12:07 | 2022-05-20 14:40 | 2:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Sholoshahar 132 kV Ckt-1 | 2022-05-23 09:52 | 2022-05-23 17:46 | 7:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Sholoshahar 132 kV Ckt-1 | 2022-05-24 11:27 | 2022-05-24 13:24 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madunaghat-Khulshi 132 KV Ckt-2 | 2022-05-24 13:42 | 2022-05-24 18:43 | 5:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| Madunaghat-Sikalbaha 132 kV Ckt | 2022-05-25 10:46 | 2022-05-25 13:12 | 2:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV Ckt-1 | 2022-05-26 06:33 | 2022-05-26 08:18 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Chandraghona 132 kV Ckt-1 | 2022-05-26 10:40 | 2022-05-26 13:15 | 2:35 | S/O | Due to D/W work | 0 | 0 | No interruption
| Madunaghat-Chandraghona 132 kV Ckt-2 | 2022-05-26 13:17 | 2022-05-26 15:09 | 1:52 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV Ckt-1 | 2022-05-28 10:23 | 2022-05-28 13:25 | 3:02 | S/O | Due to telecom work | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV Ckt-1 | 2022-05-28 13:32 | 2022-05-28 15:03 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV Ckt-1 | 2022-05-29 08:38 | 2022-05-29 15:48 | 7:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-Madunaghat 132 kV Ckt-1 | 2022-05-30 08:27 | 2022-05-30 16:43 | 8:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt-2 | 2022-05-31 08:50 | 2022-05-31 16:34 | 7:44 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 90:04 |  | Unserved Energy: |  | 45.5
Cumilla Grid Circle :
Cumilla | Cumilla -Surjamoninagar 132 kV Ckt-1 & 2 | 2022-05-07 06:40 | 2022-05-07 17:52 | 11:12 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2022-05-08 10:44 | 2022-05-08 16:14 | 5:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Shahjibazar 86 MW 132 kV | 2022-05-10 20:30 | 2022-05-10 23:07 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 k Ckt-1 |  | 2022-05-12 17:17 |  |  | After maint.work | 0 | 0 | No interruption
Bibiyana | Bibiyana S/S-Bibiyana -3 P.P 400 Ckt |  | 2022-05-13 15:57 |  | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Kachua 132 kV Ckt-1 | 2022-05-17 10:51 | 2022-05-17 13:07 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kachua 132 k Ckt | 2022-05-17 18:43 | 2022-05-17 21:17 | 2:34 | S/O | Due to Alarm checking | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Kachua 132 k Ckt-1 | 2022-05-18 11:25 | 2022-05-18 12:42 | 1:17 | S/O | Due to SCADA test | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumilla(N) 132 kV Ckt-2 | 2022-05-21 09:50 | 2022-05-21 13:00 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-S.M.Nagar 132 kV Ckt-2 | 2022-05-23 11:40 | 2022-05-23 14:26 | 2:46 | S/O | Due to D/W work | 0 | 0 | No interruption
B.baria | B.baria-Ashuganj 132 kV Ckt-1 & 2 | 2022-05-27 07:00 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV Ckt-3 | 2022-05-28 09:30 | 2022-05-28 10:10 | 0:40 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-Ghorasal 132 kV Ckt-1 | 2022-05-28 10:17 | 2022-05-28 11:38 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ashuganj 230 kV Ckt-1 | 2022-05-30 09:48 | 2022-05-30 15:29 | 5:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Cumilla(N) 230 kV Ckt-1 |  | 2022-05-30 14:29 |  | S/O | After maint.work | 0 | 0 | No interruption
|  |  | Total : | 39:04 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Goalpara | Goalpara-Khulna 225 MW 132 kV Ckt | 2022-05-05 11:07 | 2022-05-05 14:49 | 3:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV Ckt-1 & 2 | 2022-05-06 06:46 | 2022-05-06 06:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalapara S/S | Goalapara S/S- KPCL-1 P.P 132 kV Ckt | 2022-05-08 19:23 | 2022-05-08 19:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Jhenaidah (N) 230 kV Ckt-1 | 2022-05-09 08:14 | 2022-05-09 17:55 | 9:41 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulna (S)-Jhenaidah (N) 230 kV Ckt-2 | 2022-05-10 08:30 | 2022-05-10 16:22 | 7:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Faridpur 132 kV Ckt-1 | 2022-05-14 07:14 | 2022-05-14 12:08 | 4:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Goalpara 132 kV Ckt | 2022-05-15 15:50 | 2022-05-15 17:48 | 1:58 | S/O | Due to removing kite | 0 | 0 | No interruption
Rupsha(Orion) P/P | Rupsha(Orion) P/P-Bagerhat 132 kV Ckt | 2022-05-16 07:34 | 2022-05-16 07:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV Ckt-1 | 2022-05-17 08:59 | 2022-05-17 10:43 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
| Payra-Payra 132 kV S/S 400 Ckt |  | 2022-05-17 16:34 |  | S/O | After maint.work | 0 | 0 | No interruption
| Payra P.P-Payra S/S 132 kV Ckt-3 | 2022-05-18 07:36 | 2022-05-18 07:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Payra P.P-Barisal Electrical 307MW400 kV Ckt | 2022-05-19 15:57 | 2022-05-19 20:54 | 4:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | Satkhira-Khulna(S) 132 kV Ckt-1 | 2022-05-20 06:52 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Patuahkali | Patuahkali-Barisal (S) 132 kV Ckt |  | 2022-05-21 08:37 |  | S/O | After maint.work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV Ckt-1 |  | 2022-05-21 10:05 |  | S/O |  | 0 | 0 | No interruption
| Gopalganj(O)-Gallamari 132 kV Ckt-2 |  | 2022-05-21 11:11 |  | S/O |  | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-1 |  | 2022-05-21 13:01 |  | S/O | After maint.work | 0 | 0 | No interruption
Barishal Electric | Barishal Electric P.P-Payra P.P 400 kV Ckt | 2022-05-22 21:23 | 2022-05-22 21:26 | 0:03 | S/O | new connection | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2022-05-24 08:46 | 2022-05-24 17:56 | 9:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajbari | Rajbari-Faridpur 132 kV Ckt-2 | 2022-05-25 08:29 | 2022-05-25 18:53 | 10:24 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rajbari-Faridpur 132 kV Ckt-1 | 2022-05-26 08:25 | 2022-05-26 17:45 | 9:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-2 | 2022-05-28 07:22 | 2022-05-28 07:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV Ckt | 2022-05-28 07:42 | 2022-05-28 07:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV Ckt-1 | 2022-05-28 16:03 | 2022-05-28 17:32 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Patuakhali 132 kV Ckt | 2022-05-29 08:48 | 2022-05-29 14:44 | 5:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Gopalganj P/S 132 kV Ckt | 2022-05-29 09:04 | 2022-05-29 12:43 | 3:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Payra 132 kV S/S 400 Ckt-3 | 2022-05-31 15:05 | 2022-05-31 17:06 | 2:01 | S/O | Due to D/W work | 0 | 0 | No interruption
| Payra-Payra 132 kV S/S 400 Ckt-4 | 2022-05-31 16:18 | 2022-05-31 17:08 | 0:50 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 77:40 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jhenaidah | Jhenaidah-HVDC 230 kV Ckt-1 | 2022-05-11 09:13 | 2022-05-11 16:40 | 7:27 | S/O | Due to D/W work | 0 | 0 | No interruption
HVDC | HVDC-Jhenaidah 230 kV Ckt-2 | 2022-05-12 09:06 | 2022-05-12 15:08 | 6:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Noapara 132 kV Ckt | 2022-05-18 07:19 |  |  | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(N) | Jhenaidah(N)-Chuadanga 132 kV Ckt | 2022-05-20 08:04 | 2022-05-20 09:53 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah(N) 132 kV Ckt-1 |  | 2022-05-21 14:53 |  |  | After maint.work | 0 | 0 | No interruption
Bheramara HVDC | Bheramara HVDC-Jhenaidah(N) 230 kV Ckt-1 | 2022-05-22 08:47 | 2022-05-22 16:32 | 7:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara HVDC-Rajshahi 230 kV Ckt-2 | 2022-05-22 16:07 | 2022-05-22 17:00 | 0:53 | S/O | Due to removing polythene paper | 0 | 0 | No interruption
| Bheramara HVDC-Jhenaidah(N) 230 kV Ckt-2 | 2022-05-23 08:48 | 2022-05-23 16:48 | 8:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara -Rajbari 132 kV Ckt-1 | 2022-05-24 08:49 | 2022-05-24 17:54 | 9:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara -Rajbari 132 kV Ckt-2 | 2022-05-25 08:23 | 2022-05-25 17:59 | 9:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt-1 | 2022-05-26 09:17 | 2022-05-26 13:14 | 3:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Shahjadpur 132 kV Ckt-1 | 2022-05-27 09:56 | 2022-05-27 15:40 | 5:44 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baghabari-Shahjadpur 132 kV Ckt-2 | 2022-05-27 09:56 | 2022-05-27 15:52 | 5:56 | S/O
Jhenaidah(O) | Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-1 | 2022-05-29 09:33 | 2022-05-30 17:26 | 31:53 | S/O | Due to C/M work | 0 | 0 | No interruption
| Jhenaidah(O)-Jhenaidah (N) 132 kV Ckt-2 | 2022-05-31 09:02 | 2022-05-31 09:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 98:07 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Polashbari | Polashbari-Mohastanghor 132 kV Ckt-1 | 2022-05-01 10:16 | 2022-05-01 12:55 | 2:39 | S/O | Due to R-phase wire armoring | 0 | 0 | No interruption
Thaurgaon | Thaurgaon-Panchugarh 132 kV Ckt | 2022-05-06 06:10 | 2022-05-06 07:14 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur confi.132 kV Ckt-1 | 2022-05-15 08:15 | 2022-05-15 10:09 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasdaipur 132 kV Ckt-2 | 2022-05-18 16:10 | 2022-05-18 17:08 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura (O) | Bogura (O)-Naogaon 132 kV Ckt-1 | 2022-05-21 12:05 | 2022-05-21 14:55 | 2:50 | S/O | Due to OPGW work | 0 | 0 | No interruption
Polashbari | Polashbari-Mohastanghor 132 kV Ckt-2 | 2022-05-22 14:11 | 2022-05-22 15:25 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Santahar 132 kV Ckt | 2022-05-23 10:55 | 2022-05-23 15:15 | 4:20 | S/O | Due to C/M work | 0 | 0 | No interruption
| Naogaon-Joypurhat 132 kV Ckt | 2022-05-23 12:19 | 2022-05-23 13:08 | 0:49 | S/O | Due to maint.work | 0 | 0 | No interruption
Bogura (O) | Bogura (O)-Bogura(N) 132 kV Ckt-2 | 2022-05-26 12:38 | 2022-05-26 13:12 | 0:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Baghabari 132 kV Ckt-2 | 2022-05-27 09:37 | 2022-05-27 15:48 | 6:11 | S/O | Due to D/W work | 0 | 0 | No interruption
C.nawabganj | C.nawabganj-Rohanpur 132 kV Ckt-1 | 2022-05-28 08:52 | 2022-05-28 16:52 | 8:00 | S/O | Due to tap changing | 0 | 0 | No interruption
Saidpur | Saidpur-Barapukuria 132 kV Ckt-2 | 2022-05-30 12:48 | 2022-05-30 15:22 | 2:34 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 33:07 |  | Unserved Energy: |  | 0
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 440:01 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May 2022
| Area | Previous Month (April' 2022) |  |  |  | Current Month (May '2022)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 19 | 2 | 75 | 96 | 27 | 3 | 37 | 67
2 | Dhaka (South) Grid Circle. | 36 |  | 46 | 82 | 27 | 6 | 28 | 61
3 | Chattogram Grid Circle. | 29 | 1 | 51 | 81 | 18 |  | 36 | 54
4 | Cumilla Grid Circle. | 46 | 3 | 24 | 73 | 49 | 10 | 41 | 100
5 | Khulna Grid Circle. | 24 |  | 52 | 76 | 20 | 11 | 54 | 85
6 | HVDC Grid Circle | 9 | 3 | 24 | 36 | 9 | 5 | 26 | 40
7 | Bogura Grid Circle. | 28 | 10 | 37 | 75 | 28 | 15 | 39 | 82
8 | Others | Total number of T: 1; Total number of E/O: 1; Total number of Total: 2; Total number of Total: 0
9 | Total | 192 | 20 | 309 | 521 | 178 | 50 | 261 | 489
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May 2022
| Area | Previous Month (April' 2022) |  |  |  | Current Month (May '2022)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 273.7333 |  | 674.1333 | 947.8667 | 574.1 |  | 435.5 | 1009.6
2 | Dhaka (South) Grid Circle. | 151.33 |  |  | 151.33 | 284.03 | 160 | 73 | 517.03
3 | Chattogram Grid Circle. | 888.2 |  | 324.33 | 1212.53 | 225.75 |  | 104.25 | 330
4 | Cumilla Grid Circle. | 350.2 | 15.87 | 292.92 | 658.99 | 145.22 | 667.94 | 403.42 | 1216.58
5 | Khulna Grid Circle. | 140.1 | 15.6 | 204.55 | 360.25 | 48.55 | 176 | 353.1 | 577.65
6 | HVDC Grid Circle | 18.43 | 66.82 | 331.83 | 417.08 | 17.5 | 38.25 | 78.78 | 134.53
7 | Bogura Grid Circle. | 134.62 | 215.07 | 468.45 | 818.14 | 179.53 | 127.17 | 301.9833 | 608.6833
8 | Others | Energy unserved ( MWH ) due to Total: 0; Energy unserved ( MWH ) due to Total: 0
9 | Total | 1956.6133 | 313.36 | 2296.2133 | 4566.1867 | 1474.68 | 1169.36 | 1750.0333 | 4394.0733
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May 2022
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 9 | 6 | 15 | 2 | 3 | 10 | 934.13
2 | Dhaka (South) | 5031.6 | 3 | 2 | 5 |  | 2 | 3 | 381.2
3 | Chattogram | 2042 | 7 | 1 | 8 | 6 |  | 2 | 214.7333
4 | Khulna | 2434 | 9 | 4 | 13 | 3 | 4 | 6 | 577.65
5 | HVDC | 5954.3 | 2 | 2 | 4 | 1 | 1 | 2 | 134.5333
6 | Bogura | 3145.6 | 5 | 6 | 11 | 2 | 1 | 8 | 515.5833
7 | Cumilla | 2981 | 12 | 9 | 21 | 6 | 6 | 9 | 1212.35
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 3970.18
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.94%
3 | Chattogram | 99.96%
4 | Khulna | 99.96%
5 | HVDC | 99.96% | [6 empty] | Executive Engineer
6 | Bogura | 99.83% | [6 empty] | Information Management Division
7 | Cumilla | 99.86% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May 2022
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 |  | 3 | 2 | - | 1 | 75.47
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 2 |  | 1 | 135.83
3 | Chattogram | 917 | - | 1 | 1 | 2 |  |  | 2 | 115.27
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | - | 1 | - | 1 | - | 1 | - | - | -
6 | Bogura | 1803.3 | - | 3 |  | 3 | 2 | 1 |  | 93.1
7 | Cumilla | 1648.16 | - | 1 |  | 1 | 1 |  |  | 4.2167
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 423.8867
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.92%
4 | Khulna | 99.81%
5 | Bheramara (HVDC) | 99.97% | [7 empty] | Executive Engineer
6 | Bogura | 99.27% | [7 empty] | Information Management Division
7 | Cumilla | 99.77% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May 2022
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2022-05-01 | 12 | - | 4 | 05hr'43 min | - | - | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Tangail | 1 | 0:20 | 50 | 16.6667 | Due to tripping of 132/33 kV transformers T-1 ,T 2 & T3
Kabirpur | 1 | 1:02 | 150 | 155 | Due to tripping of 132/33 kV transformers T-1 ,& T 2
Kabirpur | 1 | 0:32 | 80 | 42.6667 | Due to tripping of 132/33 kV transformer T-2
Jamalpur | 1 | 2:10 | 60 | 130 | Due to tripping of 132/33 kV transformers T-1 ,& T 2
Joydevpur | 1 | 1:47 | 5 | 8.9167 | Due to red-hot maint 132/33 kV Transformer T2
Mymensingh | 1 | 0:07 | 84 | 9.8 | Due to tripping of 33 kV feeder fault
Kabirur | 2 | 0:50 | 40 | 33.3333 | Due to red-hot maint 132/33 kV Transformer T2
Kabirpur |  | 1:02 | 60 | 62
Sherpur | 1 | 1:09 | 35 | 40.25 | Due to red-hot maint 132/33 kV Transformer T3
Joydevpur | 1 | 1:01 | 50 | 50.8333 | Due to tripping of Joydevpur-Ghorashal 132 kV Ckt-1
Mymensingh | 1 | 0:18 | 58 | 17.4 | Due to tripping of Mymensingh -Jamalpur 132 kV Ckt-1
Sherpur | 1 | 0:07 | 62 | 7.2333 | Due to tripping of Sherpur-UMPL 132 kV Ckt-1 & 2
Kishoreganj | 1 | 0:44 | 45 | 33 | Due to S/D of 33 kV Bus
Kabirpur | 2 | 2:46 | 40 | 110.6667 | Due to S/D of 132/33 kV transformer T-2
|  | 3:21 | 60 | 201
Dhamrai | 1 | 1:34 | 5 | 7.8333 | Due to S/D of 132/33 kV transformer T-1
Mymensingh | 1 | 1:30 | 35 | 52.5 | Due to S/D of 132/33 kV transformer T-2
Tangail | 1 | 3:03 | 10 | 30.5 | Due to S/D of 132/33 kV transformer T-3
Bhulta | 2 | 1:18 | 80 | 104 | Due to tripping of 132/33 kV transformers T-1 ,& T 2
Hasnabad |  | 0:39 | 68 | 44.2 | Due to tripping of 132/33 kV transformers T-1,& T 5
Ghorashal | 2 | 2:00 | 80 | 160 | Due to air leakage of 230/132 kV Transformer AT-2
|  | 1:47 | 50 | 89.1667 | Due to tripping of Ghorashal-Narsinghdi 132 kV Ckt-2
Haripur | 1 | 0:16 | 100 | 26.6667 | Due to tripping of Haripur-Bhulta 132 kV Ckt
Matuail | 1 | 0:30 | 40 | 20 | Due to tripping of Matuail-Siddhirganj 132 kV Ckt
Bhulta | 1 | 0:59 | 45 | 44.25 | Due to S/D of 132/33 kV transformer T-1
Sreenagar |  | 1:55 | 15 | 28.75
Dohazari | 2 | 0:21 | 70 | 24.5 | Due to tripping of 132/33 kV transformers T-1 ,& T 2
|  | 0:21 | 52 | 18.2 | Due to red-hot maint of 33 kV full Bus
Cox'sbazar | 2 | 1:29 | 40 | 59.3333 | Due to 33 kV feeder fault
|  | 0:12 | 50 | 10 | Due to tripping of 132/33 kV transformers T-1 ,& T 2
Dohazari | 1 | 0:12 | 70 | 14 | Due to red-hot maint of 132/33 kV Transformer T2
Cox'sbazar | 1 | 0:29 | 43 | 20.7833 | Due to tripping of 132/33 kV transformer T-1
Shahmirpur | 1 | 0:25 | 22 | 9.1667 | Due to 33 kV feeder fault
Dohazari | 1 | 2:41 | 26 | 69.7667 | Due to tripping of Dohazari-Cox'sbazar 132 kV Ckt-1
Bakulia | 1 | 2:21 | 25 | 58.75 | Due to S/D of 132/33 kV transformer T-3
Sikalbaha |  | 1:18 | 35 | 45.5 | Due to S/D of Sikalbaha-Dohazari 132 kV Ckt-2
B.Baria | 1 | 0:19 | 110 | 34.8333 | Due to tripping 132/33 kV transformers T1 & T2
Sylhet | 1 | 2:03 | 29 | 59.45 | Due to 33 kV feeder fault
Shahjibazar | 1 | 0:53 | 8 | 7.0667 | Due to red-hot maint of 132/33 kV Transformer T4
B.Baria | 1 | 0:48 | 10 | 8 | Due to tripping 132/33 kV transformers T1 & T2
Cumilla (N) | 1 | 0:24 | 8 | 3.2 | Due to tripping of 132/33 kV transformers T3 & T4
B.Baria | 1 | 0:40 | 16 | 10.6667 | Due to tripping 132/33 kV transformers T1 & T2
Ramganj | 1 | 11:16 | 55 | 619.6667 | Due to red-hot maint of 33 kV Bus-2
B.Baria | 1 | 0:17 | 40 | 11.3333 | Due to 33 kV feeder fault
Cumilla (S) | 2 | 0:21 | 23 | 8.05 | Due to tripping of 132/33 kV transformer T-2
|  | 0:12 | 20 | 4
Cumilla (N) |  | 0:12 | 80 | 16 | Due to 33 kV feeder fault
B.Baria | 1 | 0:40 | 40 | 26.6667 | Due to red-hot maint of 132/33 kV Transformer T1
Sylhet | 1 | 0:23 | 11 | 4.2167 | Due to tripping of Sylhet-Fenchuganj 132 kV Ckt
B.Baria | 1 | 1:52 | 45 | 84 | Due to S/D of 132/33 kV transformer T-2
Shahjibazar | 2 | 1:35 | 10 | 15.8333 | Due to S/D of 132/33 kV transformer T-4
|  | 0:44 | 35 | 25.6667
Cumilla(S) | 1 | 1:07 | 15 | 16.75 | Due to S/D of 132/33 kV transformer T-2
Cumilla(N) | 1 | 1:43 | 65 | 111.5833 | Due to S/D of 132/33 kV transformer T-4
Chowddagram | 1 | 1:17 | 25 | 32.0833 | Due to S/D of 132/33 kV transformer T-2
Shahjibazar | 1 | 3:12 | 20 | 64 | Due to S/D of 132/33 kV transformer T-4
Cumilla(N) | 1 | 2:25 | 10 | 24.1667
Ramganj | 1 | 0:44 | 40 | 29.3333 | Due to S/D of 132/33 kV transformer T-1
Khulna(C) | 1 | 0:15 | 27 | 6.75 | Due to tripping of 132/33 kV transformer T-3
Kustia | 1 | 1:13 | 20 | 24.3333 | Due to red-hot maint of 132/33 kV Transformer T1
Madaripur | 1 | 0:35 | 25 | 14.5833
Page: 2/2 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May 2022
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Barishal | 1 | 0:14 | 119 | 27.7667 | Due to tripping of 132/33 kV transformers T1 & T2
Mongla | 1 | 1:13 | 28 | 34.0667
Barishal | 1 | 0:08 | 195 | 26 | Due to Oil leakage of 132 kV Bus
Madaripur | 1 | 0:33 | 76 | 41.8 | Due to tripping of 132/33 kV transformerT-1
Mongla | 1 | 1:23 | 25 | 34.5833 | Due to red-hot maint of 33 kV Bus
Narail | 1 | 0:55 | 16 | 14.6667 | Due to red-hot maint of 132/33 kV Transformer T1
Noapara | 1 | 1:00 | 15 | 15 | Due to S/D of 132/33 kV transformer T-3
Magura | 1 | 3:57 | 58 | 229.1 | Due to S/D of 132 kV Bus
Khulna© | 1 | 4:10 | 20 | 83.3333 | Due to S/D of 132/33 kV transformer T-1
Satkhira | 2 | 2:34 | 10 | 25.6667 | Due to S/D of 132/33 kV transformer T-1
Bottail | 3 | 0:14 | 75 | 17.5 | Due to tripping of 132/33 kV transformerT-1
|  | 0:51 | 45 | 38.25 | Due to red-hot maint of 132/33 kV Transformer T2
|  | 1:27 | 25 | 36.25 | Due to S/D of 132/33 kV transformer T-1
Kustia | 1 | 1:56 | 22 | 42.5333 | Due to S/D of 132/33 kV transformer T-1
Naogaon | 1 | 1:48 | 55 | 99 | Due to red-hot maint of 132/33 kV Transformer T2
Bogura | 1 | 1:31 | 40 | 60.6667 | Due to 33 kV feeder fault
Purbasadipur | 1 | 0:19 | 30 | 9.5 | Due to tripping of 132/33 kV transformerT-1
Bogura(Sherpur) | 1 | 2:49 | 10 | 28.1667 | Due to red-hot maint of 132/33 kV Transformers T1 & T2
Naogaon | 1 | 0:08 | 122 | 16.2667 | Due to tripping of 132/33 kV transformers T1 & T2
Bogura | 1 | 0:38 | 147 | 93.1 | Due to tripping of Bogura-Naogaon 132 kV both Ckts-2
Bogura(O) | 1 | 0:48 | 18 | 14.4 | Due to S/D of 132/33 kV transformer T-3
Rajshahi | 1 | 1:45 | 13 | 22.75 | Due to S/D of 132/33 kV transformer T-2
Rangpur | 1 | 1:04 | 30 | 32 | Due to S/D of 33 kV Bus-2
Jaldhaka | 1 | 1:10 | 20 | 23.3333 | Due to S/D of 132/33 kV transformer T-2
Saidpur | 1 | 9:45 | 10 | 97.5 | Due to S/D of 132/33 kV transformer T-3
Bogura | 1 | 2:48 | 40 | 112 | Due to S/D of 132/33 kV transformer T-1
| Total Unserved energy : |  |  | 4394.0667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: May '2022
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Aftabnagar | 34 | 17 | 2022-05-01 | 20:00
2 | Agargaon | 102 | 18 | 2022-05-01 | 13:00
3 | Agrabad | 94 | 25 | 2022-05-01 | 18:30
4 | AKS | 25 | 15 | 2022-05-01 | 12:00
5 | AKSML | 154 | 12 | 2022-05-01 | 16:00
6 | Amnura | 61 | 1 | 2022-05-01 | 21:00
7 | Ashuganj | 53 | 2 | 2022-05-01 | 03:00
8 | Bagerhat | 117 | 17 | 2022-05-01 | 22:00
9 | Bakulia | 136 | 19 | 2022-05-01 | 19:00
10 | Banani | 60 | 26 | 2022-05-01 | 15:00
11 | Bangabhaban | 24 | 16 | 2022-05-01 | 11:00
12 | Barapukuria | 57 | 18 | 2022-05-01 | 21:00
13 | Barguna | 22 | 1 | 2022-05-01 | 23:00
14 | Barishal | 124 | 22 | 2022-05-01 | 19:30
15 | Barishal | 74 | 18 | 2022-05-01 | 23:00
16 | Baroaulia | 83 | 17 | 2022-05-01 | 20:00
17 | Baroirhat | 73 | 15 | 2022-05-01 | 19:30
18 | Bashundhara | 195 | 19 | 2022-05-01 | 16:00
19 | BashundharaCement | 14 | 21 | 2022-05-01 | 16:00
20 | Beanibazar | 73 | 8 | 2022-05-01 | 20:00
21 | Benapole | 66 | 20 | 2022-05-01 | 21:00
22 | Bhaluka | 150 | 18 | 2022-05-01 | 20:00
23 | Bhandaria | 62 | 1 | 2022-05-01 | 21:00
24 | Bhangura | 45 | 1 | 2022-05-01 | 21:00
25 | Bheramara(GK) | 62 | 1 | 2022-05-01 | 22:00
26 | Bhulta | 259 | 31 | 2022-05-01 | 22:00
27 | Bog-Sherpur | 64 | 15 | 2022-05-01 | 20:00
28 | Bogura | 177 | 24 | 2022-05-01 | 21:00
29 | Borhanuddin | 46 | 1 | 2022-05-01 | 19:00
30 | Brahmanbaria | 192 | 1 | 2022-05-01 | 23:00
31 | BSRM | 169 | 30 | 2022-05-01 | 18:00
32 | Cantonment | 162 | 18 | 2022-05-01 | 19:00
33 | Chandpur | 90 | 22 | 2022-05-01 | 23:00
34 | Chandraghona | 34 | 1 | 2022-05-01 | 21:00
35 | Chapai | 80 | 18 | 2022-05-01 | 21:00
36 | Charsaidpur | 45 | 22 | 2022-05-01 | 11:00
37 | Chauddagram | 67 | 1 | 2022-05-01 | 00:00
38 | Chhatak | 33 | 7 | 2022-05-01 | 19:30
39 | Chowmuhani | 232 | 20 | 2022-05-01 | 00:00
40 | Chuadanga | 116 | 23 | 2022-05-01 | 19:30
41 | Coxsbazar | 127 | 18 | 2022-05-01 | 18:30
42 | Cumilla(N) | 177 | 23 | 2022-05-01 | 22:00
43 | Cumilla(S) | 174 | 18 | 2022-05-01 | 19:00
44 | Daudkandi | 168 | 6 | 2022-05-01 | 18:00
45 | Dhaka | 42 | 19 | 2022-05-01 | 15:00
46 | Dhamrai | 132 | 16 | 2022-05-01 | 19:30
47 | Dhanmondi | 190 | 12 | 2022-05-01 | 13:00
48 | Dohazari | 112 | 1 | 2022-05-01 | 19:00
49 | Faridpur | 159 | 18 | 2022-05-01 | 21:00
50 | Fatullah | 71 | 19 | 2022-05-01 | 10:00
51 | Fenchuganj | 52 | 8 | 2022-05-01 | 19:00
52 | Feni | 144 | 1 | 2022-05-01 | 21:00
53 | Ghorashal | 66 | 31 | 2022-05-01 | 22:00
54 | Goalpara | 30 | 17 | 2022-05-01 | 14:00
55 | Gollamari | 64 | 25 | 2022-05-01 | 21:00
56 | Gopalganj | 110.4 | 18 | 2022-05-01 | 22:00
57 | GPH | 96 | 7 | 2022-05-01 | 19:30
58 | Gulshan | 140 | 19 | 2022-05-01 | 16:00
59 | Halishahar | 108 | 18 | 2022-05-01 | 13:00
60 | HaripurSBU | 141 | 16 | 2022-05-01 | 16:00
61 | Hasnabad | 91 | 15 | 2022-05-01 | 22:00
62 | Hathazari | 103 | 17 | 2022-05-01 | 22:00
63 | Ishurdi | 92 | 23 | 2022-05-01 | 19:30
64 | Jaldhaka | 74 | 24 | 2022-05-01 | 19:30
65 | Jamalpur | 164 | 29 | 2022-05-01 | 22:00
66 | Jashore | 135 | 18 | 2022-05-01 | 21:00
67 | Jhenaidah | 128 | 18 | 2022-05-01 | 19:30
68 | Joydebpur | 200 | 18 | 2022-05-01 | 21:00
69 | Joypurhat | 67 | 24 | 2022-05-01 | 21:00
70 | Juldah | 30 | 12 | 2022-05-01 | 12:00
71 | Kabirpur | 310 | 19 | 2022-05-01 | 11:00
72 | Kachua | 86 | 6 | 2022-05-01 | 22:00
73 | Kallyanpur | 114 | 26 | 2022-05-01 | 19:00
74 | Kalurghat | 33 | 20 | 2022-05-01 | 13:00
75 | Kamrangirchar | 77 | 31 | 2022-05-01 | 13:00
76 | Kaptai | 45 | 14 | 2022-05-01 | 19:30
77 | Kazla | 91 | 17 | 2022-05-01 | 19:30
78 | Keranigonj | 90 | 16 | 2022-05-01 | 23:00
79 | Khagrachori | 30 | 7 | 2022-05-01 | 19:30
80 | Khulna | 114 | 31 | 2022-05-01 | 13:00
81 | Khulshi | 209 | 14 | 2022-05-01 | 13:00
82 | Kishoreganj | 150 | 1 | 2022-05-01 | 19:00
83 | Kodda | 349 | 30 | 2022-05-01 | 12:00
84 | KSRM | 39.6 | 12 | 2022-05-01 | 01:00
85 | Kulaura | 48 | 15 | 2022-05-01 | 21:00
86 | Kurigram | 70 | 28 | 2022-05-01 | 20:00
87 | Kushtia | 154 | 19 | 2022-05-01 | 20:00
88 | Lalbag | 99 | 24 | 2022-05-01 | 13:00
89 | Lalmonirhat | 52 | 12 | 2022-05-01 | 00:00
90 | Madanganj | 194 | 18 | 2022-05-01 | 22:00
91 | Madaripur | 121 | 19 | 2022-05-01 | 22:00
92 | Madartek | 89 | 18 | 2022-05-01 | 23:00
93 | Madunaghat | 67 | 15 | 2022-05-01 | 19:00
94 | Magura | 64 | 17 | 2022-05-01 | 20:00
95 | Mahasthangarh | 72 | 15 | 2022-05-01 | 23:00
96 | Manikganj | 94 | 18 | 2022-05-01 | 21:00
97 | Maniknagar | 91 | 18 | 2022-05-01 | 16:00
98 | Matarbari | 48 | 21 | 2022-05-01 | 01:00
99 | Matuail | 68 | 24 | 2022-05-01 | 12:00
100 | Millgate | 64 | 14 | 2022-05-01 | 19:30
101 | Mirpur | 148 | 18 | 2022-05-01 | 19:00
102 | Mirsorai | 3.6 | 3 | 2022-05-01 | 00:00
103 | Mithapukur | 44 | 18 | 2022-05-01 | 21:00
104 | Modern | 0 | 3 | 2022-05-01 | 00:00
105 | Mogbazar | 142 | 19 | 2022-05-01 | 15:00
106 | Mongla | 46 | 26 | 2022-05-01 | 09:00
107 | Motijheel | 41 | 18 | 2022-05-01 | 15:00
108 | Munshiganj | 110 | 17 | 2022-05-01 | 23:00
109 | Mymensingh | 249 | 28 | 2022-05-01 | 20:00
110 | Naogaon | 132 | 16 | 2022-05-01 | 21:00
111 | Narail | 59 | 18 | 2022-05-01 | 22:00
112 | Narinda | 82 | 19 | 2022-05-01 | 13:00
113 | Narshingdi | 190 | 24 | 2022-05-01 | 22:00
114 | Natore | 150 | 14 | 2022-05-01 | 22:00
115 | Nawabganj | 59.1 | 1 | 2022-05-01 | 21:00
116 | Netrakona | 128 | 7 | 2022-05-01 | 21:00
117 | New | 86.2 | 19 | 2022-05-01 | 12:00
118 | Niamatpur | 84 | 14 | 2022-05-01 | 23:00
119 | Noapara | 56 | 17 | 2022-05-01 | 19:30
120 | Pabna | 121 | 14 | 2022-05-01 | 23:00
121 | Palashbari | 127 | 29 | 2022-05-01 | 20:00
122 | Panchagarh | 67 | 8 | 2022-05-01 | 19:30
123 | Patuakhali | 142 | 18 | 2022-05-01 | 22:00
124 | PHP | 11 | 12 | 2022-05-01 | 12:00
125 | Purbachal | 20 | 17 | 2022-05-01 | 21:00
126 | Purbasadipur | 131 | 18 | 2022-05-01 | 21:00
127 | Rahim | 30 | 31 | 2022-05-01 | 08:00
128 | Rajbari | 72 | 1 | 2022-05-01 | 22:00
129 | Rajendrapur | 127 | 26 | 2022-05-01 | 19:30
130 | Rajshahi | 173 | 16 | 2022-05-01 | 21:00
131 | Rajshahi | 71.5 | 4 | 2022-05-01 | 10:00
132 | Ramganj | 126 | 17 | 2022-05-01 | 22:00
133 | Rampur | 22 | 19 | 2022-05-01 | 23:00
134 | Rangamati | 14 | 7 | 2022-05-01 | 19:00
135 | Rangpur | 156 | 30 | 2022-05-01 | 21:00
136 | Ruppur | 19 | 31 | 2022-05-01 | 15:00
137 | Saidpur | 113 | 31 | 2022-05-01 | 20:00
138 | Satkhira | 132 | 18 | 2022-05-01 | 22:00
139 | Satmasjid | 109 | 18 | 2022-05-01 | 19:00
140 | Savar | 199 | 16 | 2022-05-01 | 16:00
141 | Shahjadpur | 116 | 1 | 2022-05-01 | 21:00
142 | Shahjibazar | 126 | 7 | 2022-05-01 | 20:00
143 | Shahmirpur | 52.2 | 11 | 2022-05-01 | 18:30
144 | Shariatpur | 82 | 1 | 2022-05-01 | 23:00
145 | Sherpur | 144 | 25 | 2022-05-01 | 00:00
146 | Shikalbaha | 37 | 14 | 2022-05-01 | 19:30
147 | Shitalakhya | 135 | 17 | 2022-05-01 | 16:00
148 | Sholosohor | 0 | #N/A | 2022-05-01 | #N/A
149 | Shyampur | 188 | 25 | 2022-05-01 | 11:00
150 | Siddhirganj | 124 | 19 | 2022-05-01 | 15:00
151 | Sirajganj | 111 | 18 | 2022-05-01 | 21:00
152 | Sonargaon | 91 | 23 | 2022-05-01 | 22:00
153 | Sreemongol | 64 | 25 | 2022-05-01 | 19:00
154 | Srinagar | 48.07 | 24 | 2022-05-01 | 21:00
155 | SSM | 18 | 22 | 2022-05-01 | 23:00
156 | Sunamganj | 58 | 8 | 2022-05-01 | 22:00
157 | Sylhet | 158 | 31 | 2022-05-01 | 19:00
158 | Tangail | 235 | 18 | 2022-05-01 | 19:00
159 | Thakurgaon | 97 | 10 | 2022-05-01 | 20:00
160 | TK | 32 | 18 | 2022-05-01 | 22:00
161 | Tongi | 148 | 19 | 2022-05-01 | 11:00
162 | Ullon | 44 | 1 | 2022-05-01 | 19:00
163 | Uttara | 107 | 18 | 2022-05-01 | 15:00
164 | UttaraNew | 30 | 29 | 2022-05-01 | 14:00
165 | Zigatola | 51 | 19 | 2022-05-01 | 16:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:May 2022
Area | MW | Date | Hour | Remarks
Dhaka | 5376.31 | 18/05/2022 | 15:00
CTG | 1554.95 | 19/05/2022 | 22:00
Cumilla | 1387 | 2022-01-05 | 23:00
Mymensigh | 1081 | 26/05/2022 | 21:00
Sylhet | 568 | 2022-07-05 | 21:00
Khulna | 1780 | 18/05/2022 | 21:00
Barishal | 454 | 18/05/2022 | 23:00
Rajshahi | 1466.6 | 16/05/2022 | 21:00
Rangpur | 908 | 30/05/2022 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: May '2022
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 416 | 3 | 2022-05-01 | 10:00 | 397 | 2 | 2022-05-01 | 21:00
2 | Bheramara | 400 | 407 | 3 | 2022-05-01 | 7:00 | 389 | 20 | 2022-05-01 | 24:00
3 | Ashuganj(N) | 400 | 409 | 12 | 2022-05-01 | 24:00 | 371 | 29 | 2022-05-01 | 10:00
4 | Payra | 400 | 427 | 3 | 2022-05-01 | 11:00 | 412 | 24 | 2022-05-01 | 22:00
5 | Kaliakoir | 400 | 407 | 3 | 2022-05-01 | 10:00 | 375 | 22 | 2022-05-01 | 8:00
6 | Bhulta | 400 | 407 | 10 | 2022-05-01 | 21:00 | 367 | 29 | 2022-05-01 | 10:00
7 | Gopalganj | 400 | 429 | 3 | 2022-05-01 | 15:00 | 395 | 9 | 2022-05-01 | 1:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2022-05-01 | 20:00 | 227 | 2 | 2022-05-01 | 10:00
2 | Ishurdi | 230 | 244 | 3 | 2022-05-01 | 9:00 | 223 | 5 | 2022-05-01 | 10:00
3 | Ashuganj | 230 | 245 | 10 | 2022-05-01 | 18:30 | 225 | 20 | 2022-05-01 | 9:00
4 | Serajganj | 230 | 240 | 13 | 2022-05-01 | 19:00 | 221 | 4 | 2022-05-01 | 12:00
5 | Baghabari | 230 | 244 | 25 | 2022-05-01 | 21:00 | 227 | 2 | 2022-05-01 | 11:00
6 | Barapukuria | 230 | 236 | 17 | 2022-05-01 | 6:00 | 210 | 29 | 2022-05-01 | 20:00
7 | Bogura | 230 | 236 | 17 | 2022-05-01 | 4:00 | 217 | 29 | 2022-05-01 | 20:00
8 | Rajshahi | 230 | 248 | 3 | 2022-05-01 | 9:00 | 218 | 1 | 2022-05-01 | 22:00
9 | Khulna South | 230 | 244 | 25 | 2022-05-01 | 22:00 | 227 | 2 | 2022-05-01 | 12:00
10 | Rampura | 230 | 233 | 3 | 2022-05-01 | 10:00 | 215 | 23 | 2022-05-01 | 17:00
11 | Haripur | 230 | 232 | 3 | 2022-05-01 | 11:00 | 214 | 24 | 2022-05-01 | 11:00
12 | Hasnabad | 230 | 233 | 3 | 2022-05-01 | 11:00 | 212 | 20 | 2022-05-01 | 11:00
13 | Shyampur | 230 | 244 | 25 | 2022-05-01 | 23:00 | 227 | 2 | 2022-05-01 | 13:00
14 | Aminbazar | 230 | 234 | 3 | 2022-05-01 | 1:00 | 215 | 22 | 2022-05-01 | 2:00
15 | Tongi | 230 | 236 | 3 | 2022-05-01 | 10:00 | 212 | 29 | 2022-05-01 | 10:00
16 | Comilla (N) | 230 | 236 | 11 | 2022-05-01 | 19:00 | 216 | 20 | 2022-05-01 | 11:00
17 | Hathazari | 230 | 244 | 25 | 2022-05-01 | 24:00 | 227 | 2 | 2022-05-01 | 14:00
18 | Megnaghat | 230 | 239 | 3 | 2022-05-01 | 13:00 | 220 | 20 | 2022-05-01 | 7:00
19 | Fenchuganj | 230 | 247 | 12 | 2022-05-01 | 22:00 | 233 | 18 | 2022-05-01 | 13:00
20 | Siddhirganj | 230 | 235 | 3 | 2022-05-01 | 10:00 | 216 | 24 | 2022-05-01 | 11:00
21 | Maniknagar | 230 | 244 | 25 | 2022-05-01 | 25:00 | 227 | 2 | 2022-05-01 | 15:00
22 | Old Airport | 230 | 234 | 3 | 2022-05-01 | 13:00 | 211 | 24 | 2022-05-01 | 11:00
23 | Barisal | 230 | 248 | 27 | 2022-05-01 | 23:00 | 228 | 4 | 2022-05-01 | 22:00
24 | Bhola 225 MW | 230 | 248 | 2 | 2022-05-01 | 4:00 | 228 | 4 | 2022-05-01 | 22:00
25 | AKSML | 230 | 244 | 25 | 2022-05-01 | 26:00 | 227 | 2 | 2022-05-01 | 16:00
26 | BSRM | 230 | 239 | 30 | 2022-05-01 | 9:00 | 217 | 20 | 2022-05-01 | 11:00
27 | Bibiyana | 230 | 245 | 5 | 2022-05-01 | 6:00 | 233 | 26 | 2022-05-01 | 15:00
28 | Bhulta | 230 | 235 | 3 | 2022-05-01 | 10:00 | 217 | 23 | 2022-05-01 | 11:00
29 | Ashuganj (S) | 230 | 244 | 25 | 2022-05-01 | 27:00 | 227 | 2 | 2022-05-01 | 17:00
30 | Kaliakoir | 230 | 234 | 3 | 2022-05-01 | 10:00 | 215 | 22 | 2022-05-01 | 8:00
31 | GPH | 230 | 239 | 13 | 2022-05-01 | 6:00 | 214 | 3 | 2022-05-01 | 10:00
32 | Jhenaidah | 230 | 244 | 25 | 2022-05-01 | 21:00 | 227 | 2 | 2022-05-01 | 11:00
132 KV Substation
1 | Aftabnagar | 132 | 143 | 21 | 2022-05-01 | 06:00 | 124 | 19 | 2022-05-01 | 14:00
2 | Agargaon | 132 | 143 | 21 | 2022-05-01 | 06:00 | 122 | 29 | 2022-05-01 | 10:00
3 | Agrabad | 132 | 142 | 21 | 2022-05-01 | 09:00 | 118 | 19 | 2022-05-01 | 15:00
4 | AKS | 132 | 141 | 27 | 2022-05-01 | 18:30 | 121 | 3 | 2022-05-01 | 10:00
5 | Aminbazar | 132 | 144 | 21 | 2022-05-01 | 07:00 | 122 | 25 | 2022-05-01 | 02:00
6 | Amnura | 132 | 136 | 25 | 2022-05-01 | 18:00 | 119 | 13 | 2022-05-01 | 02:00
7 | Ashuganj | 132 | 143 | 21 | 2022-05-01 | 07:00 | 130 | 6 | 2022-05-01 | 00:00
8 | Bagerhat | 132 | 141 | 2 | 2022-05-01 | 02:00 | 121 | 19 | 2022-05-01 | 22:00
9 | Bakulia | 132 | 143 | 29 | 2022-05-01 | 22:00 | 118 | 19 | 2022-05-01 | 15:00
10 | Banani | 132 | 144 | 21 | 2022-05-01 | 06:00 | 120 | 19 | 2022-05-01 | 15:00
11 | Bangabhaban | 132 | 141 | 21 | 2022-05-01 | 06:00 | 120 | 18 | 2022-05-01 | 13:00
12 | Barapukuria | 132 | 142 | 21 | 2022-05-01 | 06:00 | 122 | 12 | 2022-05-01 | 22:00
13 | Barguna | 132 | 142 | 3 | 2022-05-01 | 10:00 | 127 | 1 | 2022-05-01 | 22:00
14 | Barishal | 132 | 144 | 2 | 2022-05-01 | 04:00 | 125 | 6 | 2022-05-01 | 21:00
15 | Barishal | 132 | 144 | 1 | 2022-05-01 | 05:00 | 127 | 20 | 2022-05-01 | 00:00
16 | Baroaulia | 132 | 142 | 26 | 2022-05-01 | 18:00 | 124 | 3 | 2022-05-01 | 09:00
17 | Baroirhat | 132 | 140 | 21 | 2022-05-01 | 09:00 | 118 | 3 | 2022-05-01 | 10:00
18 | Bashundhara | 132 | 144 | 21 | 2022-05-01 | 06:00 | 122 | 18 | 2022-05-01 | 16:00
19 | BashundharaCement | 132 | 141 | 9 | 2022-05-01 | 21:00 | 124 | 20 | 2022-05-01 | 10:00
20 | Beanibazar | 132 | 139 | 17 | 2022-05-01 | 09:00 | 127 | 24 | 2022-05-01 | 19:00
21 | Benapole | 132 | 143 | 3 | 2022-05-01 | 09:00 | 124 | 1 | 2022-05-01 | 21:00
22 | Bhaluka | 132 | 140 | 19 | 2022-05-01 | 23:00 | 110 | 16 | 2022-05-01 | 19:00
23 | Bhandaria | 132 | 145 | 1 | 2022-05-01 | 00:00 | 121 | 2 | 2022-05-01 | 23:00
24 | Bhangura | 132 | 141 | 10 | 2022-05-01 | 18:30 | 118 | 26 | 2022-05-01 | 06:00
25 | Bheramara | 132 | 142 | 21 | 2022-05-01 | 07:00 | 128 | 3 | 2022-05-01 | 22:00
26 | Bheramara(GK) | 132 | 142 | 10 | 2022-05-01 | 18:30 | 128 | 4 | 2022-05-01 | 22:00
27 | Bhulta | 132 | 136 | 3 | 2022-05-01 | 10:00 | 118 | 24 | 2022-05-01 | 11:00
28 | Bog-Sherpur | 132 | 144 | 21 | 2022-05-01 | 07:00 | 124 | 27 | 2022-05-01 | 15:00
29 | Bogura | 132 | 143 | 21 | 2022-05-01 | 06:00 | 124 | 29 | 2022-05-01 | 23:00
30 | Bogura | 132 | 143 | 21 | 2022-05-01 | 06:00 | 124 | 1 | 2022-05-01 | 09:00
31 | Brahmanbaria | 132 | 139 | 12 | 2022-05-01 | 16:00 | 116 | 27 | 2022-05-01 | 13:00
32 | Cantonment | 132 | 142 | 21 | 2022-05-01 | 06:00 | 120 | 24 | 2022-05-01 | 11:00
33 | Chandpur | 132 | 142 | 18 | 2022-05-01 | 11:00 | 120 | 2 | 2022-05-01 | 13:00
34 | Chandraghona | 132 | 142 | 21 | 2022-05-01 | 10:00 | 120 | 19 | 2022-05-01 | 15:00
35 | Chapai | 132 | 136 | 3 | 2022-05-01 | 10:00 | 119 | 28 | 2022-05-01 | 12:00
36 | Charsaidpur | 132 | 142 | 9 | 2022-05-01 | 21:00 | 125 | 20 | 2022-05-01 | 10:00
37 | Chauddagram | 132 | 139 | 9 | 2022-05-01 | 21:00 | 121 | 2 | 2022-05-01 | 12:00
38 | Chhatak | 132 | 139 | 24 | 2022-05-01 | 19:00 | 126 | 25 | 2022-05-01 | 22:00
39 | Chowmuhani | 132 | 138 | 26 | 2022-05-01 | 18:00 | 115 | 20 | 2022-05-01 | 11:00
40 | Chuadanga | 132 | 141 | 13 | 2022-05-01 | 18:00 | 115 | 26 | 2022-05-01 | 20:00
41 | Coxsbazar | 132 | 140 | 21 | 2022-05-01 | 11:00 | 100 | 1 | 2022-05-01 | 00:00
42 | Cumilla(N) | 132 | 139 | 11 | 2022-05-01 | 13:00 | 124 | 20 | 2022-05-01 | 11:00
43 | Cumilla(S) | 132 | 140 | 11 | 2022-05-01 | 19:00 | 122 | 12 | 2022-05-01 | 11:00
44 | Daudkandi | 132 | 139 | 11 | 2022-05-01 | 13:00 | 122 | 20 | 2022-05-01 | 11:00
45 | Dhaka | 132 | 143 | 21 | 2022-05-01 | 06:00 | 122 | 24 | 2022-05-01 | 11:00
46 | Dhamrai | 132 | 143 | 21 | 2022-05-01 | 06:00 | 122 | 18 | 2022-05-01 | 12:00
47 | Dhanmondi | 132 | 140 | 6 | 2022-05-01 | 18:00 | 125 | 19 | 2022-05-01 | 11:00
48 | Dohazari | 132 | 142 | 21 | 2022-05-01 | 13:00 | 112 | 19 | 2022-05-01 | 15:00
49 | Faridpur | 132 | 143 | 3 | 2022-05-01 | 10:00 | 113 | 15 | 2022-05-01 | 12:00
50 | Fatullah | 132 | 141 | 21 | 2022-05-01 | 06:00 | 125 | 29 | 2022-05-01 | 10:00
51 | Fenchuganj | 132 | 140 | 3 | 2022-05-01 | 13:00 | 132 | 24 | 2022-05-01 | 23:00
52 | Feni | 132 | 139 | 9 | 2022-05-01 | 20:00 | 120 | 2 | 2022-05-01 | 10:00
53 | Ghorashal | 132 | 145 | 21 | 2022-05-01 | 07:00 | 132 | 20 | 2022-05-01 | 10:00
54 | Goalpara | 132 | 144 | 3 | 2022-05-01 | 09:00 | 127 | 18 | 2022-05-01 | 12:00
55 | Gollamari | 132 | 144 | 3 | 2022-05-01 | 10:00 | 126 | 17 | 2022-05-01 | 13:00
56 | Gopalganj | 132 | 145 | 3 | 2022-05-01 | 10:00 | 125 | 8 | 2022-05-01 | 00:00
57 | Gulshan | 132 | 141 | 21 | 2022-05-01 | 06:00 | 122 | 24 | 2022-05-01 | 11:00
58 | Halishahar | 132 | 142 | 21 | 2022-05-01 | 09:00 | 117 | 19 | 2022-05-01 | 15:00
59 | Haripur | 132 | 142 | 21 | 2022-05-01 | 06:00 | 126 | 20 | 2022-05-01 | 10:00
60 | HaripurSBU | 132 | 142 | 21 | 2022-05-01 | 06:00 | 126 | 24 | 2022-05-01 | 11:00
61 | Hasnabad | 132 | 143 | 21 | 2022-05-01 | 06:00 | 128 | 19 | 2022-05-01 | 13:00
62 | Hathazari | 132 | 142 | 21 | 2022-05-01 | 09:00 | 123 | 19 | 2022-05-01 | 15:00
63 | Ishurdi | 132 | 143 | 21 | 2022-05-01 | 07:00 | 128 | 31 | 2022-05-01 | 06:00
64 | Jaldhaka | 132 | 141 | 21 | 2022-05-01 | 04:00 | 111 | 12 | 2022-05-01 | 22:00
65 | Jamalpur | 132 | 145 | 21 | 2022-05-01 | 06:00 | 116 | 4 | 2022-05-01 | 19:00
66 | Jashore | 132 | 142 | 3 | 2022-05-01 | 10:00 | 111 | 3 | 2022-05-01 | 09:00
67 | Jhenaidah | 132 | 137 | 24 | 2022-05-01 | 4:00 | 131 | 29 | 2022-05-01 | 16:00
68 | Joydebpur | 132 | 145 | 21 | 2022-05-01 | 06:00 | 128 | 21 | 2022-05-01 | 03:00
69 | Joypurhat | 132 | 144 | 21 | 2022-05-01 | 07:00 | 114 | 29 | 2022-05-01 | 20:00
70 | Juldah | 132 | 142 | 29 | 2022-05-01 | 22:00 | 119 | 3 | 2022-05-01 | 10:00
71 | Kabirpur | 132 | 145 | 21 | 2022-05-01 | 06:00 | 117 | 19 | 2022-05-01 | 15:00
72 | Kachua | 132 | 139 | 28 | 2022-05-01 | 13:00 | 120 | 3 | 2022-05-01 | 10:00
73 | Kaliakoir | 132 | 0 | #N/A | 2022-05-01 | #N/A | 0 | #N/A | 2022-05-01 | #N/A
74 | Kallyanpur | 132 | 145 | 21 | 2022-05-01 | 06:00 | 124 | 24 | 2022-05-01 | 12:00
75 | Kalurghat | 132 | 142 | 21 | 2022-05-01 | 09:00 | 119 | 19 | 2022-05-01 | 15:00
76 | Kamrangirchar | 132 | 139 | 21 | 2022-05-01 | 06:00 | 124 | 14 | 2022-05-01 | 12:00
77 | Kaptai | 132 | 140 | 23 | 2022-05-01 | 07:00 | 126 | 1 | 2022-05-01 | 01:00
78 | Kazla | 132 | 141 | 21 | 2022-05-01 | 07:00 | 119 | 19 | 2022-05-01 | 12:00
79 | Keranigonj | 132 | 139 | 2 | 2022-05-01 | 04:00 | 124 | 21 | 2022-05-01 | 10:00
80 | Khagrachori | 132 | 143 | 21 | 2022-05-01 | 09:00 | 118 | 19 | 2022-05-01 | 15:00
81 | Khulna | 132 | 143 | 3 | 2022-05-01 | 09:00 | 127 | 2 | 2022-05-01 | 21:00
82 | Khulshi | 132 | 140 | 21 | 2022-05-01 | 09:00 | 117 | 19 | 2022-05-01 | 15:00
83 | Kishoreganj | 132 | 142 | 21 | 2022-05-01 | 06:00 | 120 | 15 | 2022-05-01 | 23:00
84 | Kodda | 132 | 145 | 3 | 2022-05-01 | 10:00 | 120 | 30 | 2022-05-01 | 23:00
85 | KSRM | 132 | 140 | 29 | 2022-05-01 | 21:00 | 123 | 3 | 2022-05-01 | 10:00
86 | Kulaura | 132 | 140 | 3 | 2022-05-01 | 13:00 | 132 | 22 | 2022-05-01 | 19:00
87 | Kurigram | 132 | 139 | 21 | 2022-05-01 | 05:00 | 112 | 31 | 2022-05-01 | 19:30
88 | Kushtia | 132 | 142 | 21 | 2022-05-01 | 06:00 | 127 | 4 | 2022-05-01 | 22:00
89 | Lalbag | 132 | 139 | 2 | 2022-05-01 | 04:00 | 125 | 14 | 2022-05-01 | 12:00
90 | Lalmonirhat | 132 | 138 | 13 | 2022-05-01 | 19:00 | 115 | 29 | 2022-05-01 | 19:30
91 | Madanganj | 132 | 141 | 9 | 2022-05-01 | 21:00 | 124 | 20 | 2022-05-01 | 10:00
92 | Madaripur | 132 | 144 | 2 | 2022-05-01 | 04:00 | 127 | 2 | 2022-05-01 | 23:00
93 | Madartek | 132 | 142 | 21 | 2022-05-01 | 06:00 | 121 | 24 | 2022-05-01 | 11:00
94 | Madunaghat | 132 | 142 | 28 | 2022-05-01 | 21:00 | 121 | 19 | 2022-05-01 | 15:00
95 | Magura | 132 | 143 | 21 | 2022-05-01 | 07:00 | 123 | 26 | 2022-05-01 | 19:30
96 | Mahasthangarh | 132 | 142 | 21 | 2022-05-01 | 06:00 | 122 | 29 | 2022-05-01 | 20:00
97 | Manikganj | 132 | 140 | 3 | 2022-05-01 | 10:00 | 120 | 23 | 2022-05-01 | 08:00
98 | Maniknagar | 132 | 141 | 21 | 2022-05-01 | 07:00 | 120 | 18 | 2022-05-01 | 16:00
99 | Matarbari | 132 | 140 | 21 | 2022-05-01 | 16:00 | 102 | 1 | 2022-05-01 | 00:00
100 | Matuail | 132 | 140 | 6 | 2022-05-01 | 19:30 | 125 | 19 | 2022-05-01 | 15:00
101 | Millgate | 132 | 143 | 21 | 2022-05-01 | 06:00 | 120 | 19 | 2022-05-01 | 15:00
102 | Mirpur | 132 | 144 | 21 | 2022-05-01 | 07:00 | 121 | 24 | 2022-05-01 | 11:00
103 | Mithapukur | 132 | 141 | 21 | 2022-05-01 | 06:00 | 118 | 29 | 2022-05-01 | 19:30
104 | Modern | 132 | 141 | 21 | 2022-05-01 | 09:00 | 121 | 3 | 2022-05-01 | 10:00
105 | Mogbazar | 132 | 145 | 21 | 2022-05-01 | 06:00 | 123 | 24 | 2022-05-01 | 11:00
106 | Mongla | 132 | 145 | 3 | 2022-05-01 | 10:00 | 122 | 6 | 2022-05-01 | 22:00
107 | Motijheel | 132 | 141 | 21 | 2022-05-01 | 06:00 | 120 | 18 | 2022-05-01 | 13:00
108 | Munshiganj | 132 | 142 | 9 | 2022-05-01 | 19:00 | 126 | 20 | 2022-05-01 | 09:00
109 | Mymensingh | 132 | 144 | 21 | 2022-05-01 | 06:00 | 116 | 15 | 2022-05-01 | 23:00
110 | Naogaon | 132 | 142 | 21 | 2022-05-01 | 06:00 | 115 | 23 | 2022-05-01 | 01:00
111 | Narail | 132 | 142 | 3 | 2022-05-01 | 09:00 | 120 | 26 | 2022-05-01 | 20:00
112 | Narinda | 132 | 0 | 1 | 2022-05-01 | 00:00 | 0 | #VALUE! | 2022-05-01 | 00:00
113 | Narshingdi | 132 | 139 | 3 | 2022-05-01 | 10:00 | 117 | 24 | 2022-05-01 | 11:00
114 | Natore | 132 | 139 | 21 | 2022-05-01 | 06:00 | 118 | 26 | 2022-05-01 | 01:00
115 | Nawabganj | 132 | 139 | 2 | 2022-05-01 | 04:00 | 125 | 12 | 2022-05-01 | 12:00
116 | Netrakona | 132 | 144 | 21 | 2022-05-01 | 06:00 | 114 | 15 | 2022-05-01 | 19:00
117 | New | 132 | 144 | 21 | 2022-05-01 | 07:00 | 121 | 19 | 2022-05-01 | 14:00
118 | Niamatpur | 132 | 143 | 21 | 2022-05-01 | 07:00 | 112 | 29 | 2022-05-01 | 20:00
119 | Noapara | 132 | 144 | 3 | 2022-05-01 | 10:00 | 126 | 6 | 2022-05-01 | 22:00
120 | Pabna | 132 | 144 | 21 | 2022-05-01 | 07:00 | 128 | 1 | 2022-05-01 | 15:00
121 | Palashbari | 132 | 141 | 21 | 2022-05-01 | 06:00 | 114 | 21 | 2022-05-01 | 06:00
122 | Panchagarh | 132 | 141 | 19 | 2022-05-01 | 20:00 | 111 | 12 | 2022-05-01 | 22:00
123 | Patuakhali | 132 | 142 | 3 | 2022-05-01 | 11:00 | 128 | 1 | 2022-05-01 | 22:00
124 | PHP | 132 | 140 | 21 | 2022-05-01 | 09:00 | 118 | 3 | 2022-05-01 | 10:00
125 | Purbachal | 132 | 144 | 21 | 2022-05-01 | 06:00 | 119 | 3 | 2022-05-01 | 09:00
126 | Purbasadipur | 132 | 140 | 19 | 2022-05-01 | 20:00 | 116 | 31 | 2022-05-01 | 19:30
127 | Rahim | 132 | 142 | 21 | 2022-05-01 | 06:00 | 114 | 24 | 2022-05-01 | 04:00
128 | Rajbari | 132 | 144 | 21 | 2022-05-01 | 07:00 | 125 | 4 | 2022-05-01 | 22:00
129 | Rajendrapur | 132 | 145 | 21 | 2022-05-01 | 07:00 | 120 | 23 | 2022-05-01 | 09:00
130 | Rajshahi | 132 | 138 | 9 | 2022-05-01 | 04:00 | 120 | 31 | 2022-05-01 | 12:00
131 | Ramganj | 132 | 139 | 21 | 2022-05-01 | 09:00 | 115 | 3 | 2022-05-01 | 08:00
132 | Rampur | 132 | 139 | 27 | 2022-05-01 | 21:00 | 118 | 19 | 2022-05-01 | 15:00
133 | Rampura | 132 | 141 | 21 | 2022-05-01 | 06:00 | 112 | 8 | 2022-05-01 | 06:00
134 | Rangamati | 132 | 142 | 21 | 2022-05-01 | 09:00 | 118 | 19 | 2022-05-01 | 15:00
135 | Rangpur | 132 | 141 | 21 | 2022-05-01 | 06:00 | 114 | 30 | 2022-05-01 | 11:00
136 | Ruppur | 132 | 143 | 21 | 2022-05-01 | 07:00 | 129 | 4 | 2022-05-01 | 18:00
137 | Saidpur | 132 | 140 | 19 | 2022-05-01 | 20:00 | 117 | 29 | 2022-05-01 | 19:30
138 | Satkhira | 132 | 145 | 3 | 2022-05-01 | 10:00 | 118 | 20 | 2022-05-01 | 23:00
139 | Satmasjid | 132 | 143 | 21 | 2022-05-01 | 06:00 | 120 | 24 | 2022-05-01 | 11:00
140 | Savar | 132 | 142 | 10 | 2022-05-01 | 21:00 | 122 | 24 | 2022-05-01 | 11:00
141 | Shahjadpur | 132 | 147 | 14 | 2022-05-01 | 05:00 | 115 | 27 | 2022-05-01 | 14:00
142 | Shahjibazar | 132 | 140 | 13 | 2022-05-01 | 20:00 | 125 | 27 | 2022-05-01 | 13:00
143 | Shahmirpur | 132 | 141 | 21 | 2022-05-01 | 09:00 | 118 | 19 | 2022-05-01 | 15:00
144 | Shariatpur | 132 | 145 | 21 | 2022-05-01 | 08:00 | 125 | 7 | 2022-05-01 | 22:00
145 | Sherpur | 132 | 142 | 19 | 2022-05-01 | 22:00 | 111 | 4 | 2022-05-01 | 19:00
146 | Shikalbaha | 132 | 143 | 29 | 2022-05-01 | 13:00 | 120 | 3 | 2022-05-01 | 09:00
147 | Shikalbaha | 132 | 141 | 27 | 2022-05-01 | 19:30 | 120 | 3 | 2022-05-01 | 10:00
148 | Shitalakhya | 132 | 141 | 3 | 2022-05-01 | 10:00 | 126 | 20 | 2022-05-01 | 09:00
149 | Sholosohor | 132 | 0 | #N/A | 2022-05-01 | #N/A | 0 | #N/A | 2022-05-01 | #N/A
150 | Shyampur | 132 | 142 | 21 | 2022-05-01 | 06:00 | 125 | 19 | 2022-05-01 | 17:00
151 | Shyampur | 132 | 140 | 21 | 2022-05-01 | 07:00 | 125 | 20 | 2022-05-01 | 11:00
152 | Siddhirganj | 132 | 142 | 21 | 2022-05-01 | 06:00 | 125 | 19 | 2022-05-01 | 15:00
153 | Sirajganj | 132 | 142 | 3 | 2022-05-01 | 08:00 | 122 | 27 | 2022-05-01 | 14:00
154 | Sonargaon | 132 | 140 | 6 | 2022-05-01 | 19:30 | 124 | 20 | 2022-05-01 | 10:00
155 | Sreemongol | 132 | 141 | 21 | 2022-05-01 | 04:00 | 130 | 25 | 2022-05-01 | 01:00
156 | Srinagar | 132 | 139 | 2 | 2022-05-01 | 04:00 | 124 | 14 | 2022-05-01 | 12:00
157 | SSM | 132 | 142 | 14 | 2022-05-01 | 20:00 | 118 | 12 | 2022-05-01 | 03:00
158 | Sunamganj | 132 | 137 | 19 | 2022-05-01 | 03:00 | 123 | 31 | 2022-05-01 | 04:00
159 | Sylhet | 132 | 136 | 3 | 2022-05-01 | 13:00 | 130 | 24 | 2022-05-01 | 20:00
160 | Tangail | 132 | 141 | 19 | 2022-05-01 | 23:00 | 121 | 29 | 2022-05-01 | 21:00
161 | Thakurgaon | 132 | 140 | 15 | 2022-05-01 | 23:00 | 113 | 12 | 2022-05-01 | 22:00
162 | TK | 132 | 141 | 20 | 2022-05-01 | 19:00 | 121 | 3 | 2022-05-01 | 09:00
163 | Tongi | 132 | 144 | 3 | 2022-05-01 | 10:00 | 124 | 19 | 2022-05-01 | 15:00
164 | Ullon | 132 | 140 | 21 | 2022-05-01 | 07:00 | 120 | 13 | 2022-05-01 | 18:30
165 | Uttara | 132 | 145 | 21 | 2022-05-01 | 06:00 | 121 | 24 | 2022-05-01 | 11:00
166 | UttaraNew | 132 | 143 | 21 | 2022-05-01 | 07:00 | 122 | 24 | 2022-05-01 | 10:00
167 | Zigatola | 132 | 139 | 2 | 2022-05-01 | 05:00 | 125 | 12 | 2022-05-01 | 12:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: May 2022
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 53 | 153
Hasnabad | TR2 | 225 | 53 | 153 | 20.05.2022 | 07:00
| TR3 | 225 | 53 | 153
| TR1 | 225 | 185 | 550 | 18.05.2022 | 17:00
Tongi | TR2 | 225 | 185 | 550
| TR3 | 225 | 185 | 550
Haripur | TR1 | 225 | 122 | 370
| TR2 | 225 | 122 | 370 | 19.05.2022 | 04:00
| TR3 | 225 | 122 | 370
| TR1 | 225 | 203 | 570
Rampura | TR2 | 225 | 203 | 570 | 18.05.2022 | 16:00
| TR3 | 225 | 203 | 570
Keraniganj | ATR1 | 300 | 122 | 361
| ATR2 | 300 | 122 | 361 | 19.05.2022 | 17:00
| ATR3 | 300 | 122 | 361
| TR1 | 225 | 137 | 391
Aminbazar | TR2 | 225 | 137 | 391 | 14.05.2022 | 9:00
| TR3 | 225 | 145 | 410
Agargaon | TR1 | 300 | 185 | 548
| TR2 | 300 | 185 | 548 | 19.05.2022 | 16:00
Maniknagar | TR1 | 300 | 160 | 500 | 31.05.22 | 13:00
| TR2 | 300 | 160 | 500
Cumilla (N) | TR1 | 225 | 187 | 540 | 03.05.22 | 10:00
| TR2 | 225 | 183 | 527
Fenchuganj | AT2 | 300 | 230 | 575 | 17.05.22 | 8:00
| MT1 | 150 | 107 | 330
Hathazari | MT2 | 150 | 107 | 330 | 17.05.22 | 24:00
| MT3 | 150 | 107 | 330
| MT4 | 150 | 107 | 330
| TR1 | 225 | 129 | 569
Ishurdi | TR2 | 225 | 120 | 316 | 21.05.22 | 14:44
| TR3 | 225 | 117 | 594
Khulna(S) | TR1 | 225 | 128 | 358
| TR2 | 225 | 128 | 358 | 07.05.22 | 21:00
| TR3 | 300 | 165 | 459
Bogura | TR1 | 225 | 121 | 350 | 02.05.22 | 22:00
| TR2 | 225 | 121 | 350
| TR3 | 225 | 164 | 472
Baghabari | TR1 | 300 | 185 | 500 | 01.05.22 | 20:00
| TR2 | 225 | 140 | 380
Rajshahi | ATR-01 | 300 | 126 | 340 | 01.05.2022 | 3:00
| ATR-02 | 300 | 126 | 340
Barapukuria | TR1 | 225 | 160 | 750
| TR2 | 225 | 148 | 700 | 30.05.2022 | 21:00
| TR6 | 300 | 193 | 904
Bheramara | Transformer-1 | 225 | 107 | 263 | 05.05.2022 | 21:00
| Transformer-2 | 225 | 107 | 263
Shyampur | ATR-01 | 300 | 104 | 302 | 21.05.2022 | 15:00
| ATR-02 | 300 | 104 | 302
Kaliakoir | TR1 | 300 | 131.6 | 380 | 18.05.2022 | 14:30
Sikalbaha | ATR-1 | 300 | 223 | 673 | 24.05.2022 | 15:00
| ATR-2 | 300 | 223 | 673
Jhenaidah | T1(230/132 kV) | 300 | 179 | 864 | 07.05.2022 | 21:00
| T2(230/132 kV) | 300 | 179 | 864
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:May 2022
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 332.7 | 514 | 29.05.2022 | 10:30
| TR2(400/230 kV) | 520 | 336 | 523
| TR1(400/132 kV) | 325 | 311.7 | 488 | 30.05.2022 | 19:00
| TR2(400/132 kV) | 325 | 312.2 | 485
Bibiyana | ICT1(400/230 kV) | 520 | 164 | 246 | 02.05.2022 | 12:00
| ICT2(400/230kV) | 520 | 159 | 240
Bhulta | ATR1(400/230 kV) | 520 | 203 | 339 | 19.05.2022 | 8:45
| ATR2(400/230kV) | 520 | 203 | 339
Ashuganj(N) | GSUT1(400/230 kV) | 567 | 373.98 | 584 | 05.05.2022 | 8:21
Gopalganj | ATR1(400/138 kV) | 325 | 286 | 422 | 20.05.2022 | 21:00
| ATR2(400/138kV) | 325 | 286 | 422
Payra | GSUT1 | 270 | 187.3 | 803 | 20.05.2022 | 22:00
| GSUT2 | 270 | 188.33 | 801
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:May 2022 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May 2022 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2022-05-01 | 11978 | 11978 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-01 | 8519 | 8519 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-02 | 10798 | 10798 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-02 | 7540 | 7540 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-03 | 7880 | 7880 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-03 | 6014 | 6014 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-04 | 9610 | 9610 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-04 | 6447 | 6447 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-05 | 10543 | 10543 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-05 | 7943 | 7943 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-06 | 10543 | 10543 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-06 | 7708 | 7708 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-07 | 11937 | 11937 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-07 | 9541 | 9541 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-08 | 12734 | 12734 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-08 | 10901 | 10901 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-09 | 11820 | 11820 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-09 | 10378 | 10378 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-10 | 11472 | 11472 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-10 | 9695 | 9695 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-11 | 11566 | 11566 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-11 | 10204 | 10204 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-12 | 12736 | 12736 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-12 | 10744 | 10744 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-13 | 10889 | 10889 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-13 | 8827 | 8827 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-14 | 13297 | 13297 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-14 | 10184 | 10184 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-15 | 13701 | 13701 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-15 | 10853 | 10853 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-16 | 13954 | 13954 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-16 | 11587 | 11587 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-17 | 13256 | 13256 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-17 | 11026 | 11026 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-18 | 13760 | 13760 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-18 | 11832 | 11832 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-19 | 12907 | 12907 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-19 | 11857 | 11857 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-20 | 11749 | 11749 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-20 | 8660 | 8660 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-21 | 10998 | 10998 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-21 | 7266 | 7266 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-22 | 13456 | 13456 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-22 | 10951 | 10951 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-23 | 13810 | 13810 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-23 | 11466 | 11466 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-24 | 13923 | 13923 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-24 | 11993 | 11993 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-25 | 13024 | 13024 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-25 | 11624 | 11624 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-26 | 13361 | 13361 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-26 | 11753 | 11753 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-27 | 11869 | 11869 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-27 | 10118 | 10118 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-28 | 12348 | 12348 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-28 | 10702 | 10702 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-29 | 13303 | 13303 | - | - | [10 empty] | 2022-04-29 | 11023 | 11023 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-30 | 13713 | 13713 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-04-30 | 11410 | 11410 | - | - | - | - | - | - | - | - | - | - | - | -
2022-05-31 | 13655 | 13655 | - | - | - | - | - | - | - | - | - | - | - | - | 2022-05-31 | 11563 | 11563 | - | - | - | - | - | - | - | - | - | - | - | -
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:May 2022
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13954 | 2022-05-16 | 21:00
2 | Maximum Day Peak Genaration | MW | 11993 | 2022-05-24 | 12:00
3 | Maximum Evening Peak Demand | MW | 13954 | 2022-05-16 | 12:00
4 | Minimum Generation | MW | 4396 | 2022-05-21 | 6:00
5 | Average of the daily evening peak Genaration | MW | 12277.0968
6 | Average of the daily day peak Genaration | MW | 10010.6129
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 7807.3833
12 | Total Generation by BPDB | MkWh | 1760.1344 | % of total Gen. | 22.54%
13 | Total Generation by IPP | MkWh | 2591.286 | '' | 33.19%
14 | A) Total Generation by Generation Companies | MkWh | 2095.486 | '' | 26.84%
| B) Total Generation by REB | MkWh | 117.2486 | " | 1.502%
| C) Total Generation by RENTAL | MkWh | 517.426 | " | 6.627%
| D) Total Imported from India (BIPTC) | MkWh | 653.1207 | " | 8.365%
| E) Total Imported from Tripura, India (A.C) | MkWh | 72.6816 | " | 0.9309%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4216.1115 | % of total Gen. | 54%
| B) Oil | MkWh | 2036.9757 | '' | 26.09%
| C) Hydro | MkWh | 27.4557 | '' | 0.3517%
| D) Solar | MkWh | 33.0386 | '' | 0.4232%
| E) Coal | MkWh | 767.9994 | '' | 9.837%
| F) BIPTC (Import from India) | MkWh | 653.1207 | '' | 8.365%
| G) A.C (Import from Tripura, India) | MkWh | 72.6816 | '' | 0.9309%
16 | Maximun of the daily total Generation . | MkWh | 295.3887 | 2022-05-18
17 | Monthly Load factor | % | 83.2694
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 30562.2093
| A) Gas | M.Taka | 4328.8763
| B) Liquid fuel | M.Taka | 18339.3774
| C) Coal | M.Taka | 4174.2227
| D) BIPTC (Import from India) | M.Taka | 3217.3099
| E) Tripura(Import from India) | M.Taka | 502.4231
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1904.2078 | 2022-05-17
| A) Gas | M.Taka | 159.2457 | 2022-05-01
| B) Liquid fuel | M.Taka | 1531.4392 | 2022-05-17
| C) Coal | M.Taka | 238.5372 | 2022-05-12
| D) BIPTC (Import from India) | M.Taka | 114.1324 | 2022-05-19
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.4959
| B) Excluding Hydro & Solar | Taka/kWhR | 4.5305
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/2022 | 06:00
b) | Actual | FT (MSL) | 74.53 | 31/05/2022 | 06:00
22 | Peak Genaration of May 2021 | MW | 13417 | 2021-05-22 | 21:00
23 | Peak Demand of May 2021 | MW | 13417 | 44338 | 19:00
24 | Maximum peak Generation recorded upto 30/05/2022 | MW | 14782 | 16/04/2022 | 21:00
25 | Maximum peak Demand recorded upto 30/05/2022 | MW | 14782 | 16/04/2022 | 21:00
26 | Maximum load shed recorded upto 30/05/2022 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.