## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2023-08-01 | Tuesday
|  | Date (day): | 2023-08-01 |  | Tuesday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13080.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15307 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2023-07-31 | 2023-08-01 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 210 | 210 | 210 | 210
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Air Compressor problem
| Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 12 | 12 | 12 | 96 |  | Gas shortage
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 362 | 370 | 370 | 42 |  | Gas shortage
7 | Haripur 360 MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 317 | 317 | 320 | 330 | 30 |  | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 450 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 59 | 50 | 64 | 36 |  | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 335 | 335 | 0 | 0 | 0 | 0 | 335 |  | Under maint
11 | Madanganj 102 PP(Summit) |  | HFO | NENP | 6*17 | 102 | 102 | 96 | 51 | 17 | 51 |  | 51 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | HFO | IPP | 3*17.08+1*11.3 | 55 | 55 | 15 | 15 | 15 | 15 | 40 |  | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | NENP | 8*13.45 | 100 | 75 | 0 | 0 | 0 | 0 |  | 75 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 17 | 0 | 17 | 17 |  | 5 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 198 | 195 | 195 | 15
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | NENP | 12*8.9 | 100 | 100 | 50 | 65 | 50 | 72 | 28 |  | Fuel shortage
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 315 | 326 | 330 | 330
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 50 | 102
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 0 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 17 | 34 | 20 |  | Fuel shortage
22 | Kodda 150 MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 130 | 64 | 130 | 19 |  | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 | 20 |  | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 35 | 55
25 | Bosila 108 MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 38 | 41 | 38 | 41 |  | 39 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 15 | 16 | 16 | 24 |  | 9 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | RPCL | 6*8.9 | 52 | 52 | 8 | 25 | 8 | 25 | 27 |  | Fuel shortage
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 | 105 |  | Gas shortage
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 105 | 112 | 112 | 112 | 188 |  | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 63 | 250 | 0 | 200
| Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 114*0.959 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
33 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
34 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 8*18.45+8.97 | 149 | 149 | 71 | 144 | 70 | 149
35 | Gazipur 100 MW PP |  | HFO | RPCL | 6*17.5 | 105 | 105 | 35 | 105 | 35 | 105
36 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 50 | 72 | 53 | 72 | 32 |  | Fuel shortage
37 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 54 | 162 | 54 | 162
38 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 35 | 0
39 | Kanchan Purbachal Power Generation Ltd. |  | HFO | IPP | 18.4*3 | 55 | 55 | 0 | 0 | 17 | 17 | 38 |  | Fuel shortage
| Dhaka area Total |  |  |  |  | 6063 | 5722 | 2933 | 3562 | 2888 | 3592 | 1122 | 939
40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 118 | 117 | 120 | 120 |  | 60
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint
41 | Raozan 25 MW PP |  | HFO | RPCL | 3*8.9 | 25 | 25 | 8 | 25 | 8 | 25
42 | Teknaf 20MW PP (Solartech) |  | Solar | IPP | 20 | 20 | 20 | 13 | 0 | 20 | 0
43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 6 | 46 | 6 | 46
44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 132 | 130 | 130 | 100 |  | Low Water Level
45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*75 | 225 | 225 | 214 | 225 | 220 | 225
46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 6*17.5 | 105 | 105 | 51 | 51 | 51 | 51 | 54 |  | Engine problem
48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 24 | 84 | 40 | 84 | 14 |  | Fuel shortage
49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 34 | 50 | 50 | 50 | 52 |  | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | NENP | 8*13.45 | 100 | 100 | 46 | 80 | 46 | 80 | 20 |  | Fuel shortage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 8*13.5 | 100 | 100 | 37 | 100 | 50 | 100
52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 12 | 12 | 12 | 10 |  | Gas shortage
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 17 | 5 | 25
53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 24 | 0 | 24 | 84 |  | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
55 | Anwara 300 MW PP (United) |  | HFO | IPP | 17*17+24 | 300 | 300 | 121 | 265 | 120 | 300
56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 17 | 36 | 36 | 18 |  | Fuel shortage
57 | Karnaphuli Power Ltd. |  | HFO | IPP | 18.415*6+6.5 | 110 | 110 | 55 | 55 | 54 | 54 | 56 |  | Fuel shortage
58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 38 | 88 | 38 | 88 | 12 |  | Fuel shortage
59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 34 | 68 | 34 | 68 | 48 |  | Fuel shortage
60 | Mirsharai 150 MW |  | Gas/HFO | BPDB-RPCL | 18.5*9 | 163 | 163 | 17 | 142 | 17 | 142 | 21 |  | Fuel shortage
| SS Power I |  | Coal | SS Power | 0 | 0 | 0 | 275 | 310 | 450 | 300 |  |  | On test.
| Cox's Bazar Wind |  | Wind | IPP | 66 | 0 | 0 | 0 | 0 | 20 | 10 |  |  | On test.
| Matarbari 2*600 MW (CPGCL) |  | Coal | CPGCL | 0 | 0 | 0 | 150 | 110 | 150 | 0
| Chattogram area Total |  |  |  |  | 2605 | 2545 | 1390 | 2018 | 1682 | 1970 | 489 | 390
| Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 200 | 207 | 200 | 205 | 16 |  | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 280 | 280 | 280 | 80 |  | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 260 | 260 | 260 | 100 |  | Gas shortage
64 | Ashuganj 420 MW CCPP(East) |  | Gas | APSCL | 284*1+116*1 | 400 | 400 | 230 | 250 | 250 | 250 | 150 |  | Gas shortage
65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 0 | 0 | 5 | 5 | 40 |  | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | Gas | QRPP | 15*4 | 55 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 0 | 0 | 0 | 195 |  | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  |  | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 6 | 48 | 6 | 60 | 90 |  | Fuel shortage
70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 23 | 32 | 44 | 46 |  | 6 | Machine problem
71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under Maint.
72 | Chandpur 200 MW (Desh energy) |  | HFO | IPP | 12*18.4 | 200 | 200 | 71 | 156 | 51 | 150 | 50 |  | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 7 | 8 | 20 | 20
74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 112 | 146 | 169
75 | Jangalia 33 MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 31 | 25 | 33
76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 40 | 43 | 43 |  | 9 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, REB | 3*3.67+2*6.97 | 25 | 25 | 15 | 0 | 20 | 20 |  | 5 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 0 |  |  | Contract Expired
79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 34 | 0 | 106 | 8 |  | Fuel shortage
80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 27 | 57 | 27 | 75 | 38 |  | Fuel shortage
81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 17 | 17 |  | 37 | Engine problem
82 | Chandpur 115(Doreen) |  | HFO | IPP | 4*18.5+2*22.5 | 115 | 115 | 59 | 109 | 72 | 115
| Cumilla Area Total |  |  |  |  | 3159 | 3096 | 1486 | 1713 | 1520 | 1908 | 767 | 220
83 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 33 | 97 | 50 | 98 | 104 |  | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 0 | 18 | 18 |  | 4 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 0 | 0 | 0 | 0 | 0
86 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
87 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 9.78*21 | 200 | 200 | 67 | 86 | 68 | 85 | 115 |  | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 9.78*12 | 115 | 115 | 24 | 84 | 24 | 85 | 30 |  | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 42 | 0 | 50 | 0
90 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 6 | 6 | 6 | 6 | 16 |  | Fuel shortage
| Mymensingh Area Total |  |  |  |  | 717 | 614 | 190 | 273 | 217.6 | 292 | 104 | 4
91 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
92 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint
93 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 112 | 0 | 0 | 0 |  | 163 | ST Under maint.
94 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 0 | 0 | 0 |  | 330 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 42 | 47 | 50 | 50
96 | Fenchuganj 44 MW (Energyprima) |  | Gas | NENP | 12*3.3+5*2 | 50 | 50 | 43 | 45 | 48 | 48
97 | Hobiganj 11 MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
98 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 20 | 20 | 30 |  | 36 | Unit-9 under maint
99 | Shahjibazar 86 MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 86 | 80 | 86
100 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
101 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 181 | 110 | 110 | 115 |  | 116 | Machine problem
102 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 17 | 17
| Sylhet 50 MW PP (EPL) |  | Gas | NENP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 24 | 24
104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 300 | 300 | 300 |  |  | FGMO
105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 285*1+134*1 | 400 | 400 | 386 | 367 | 400 | 400 |  |  | FGMO
106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 303 | 350 | 350
| Sylhet Area Total |  |  |  |  | 2472 | 2427 | 1552 | 1351 | 1450 | 1471 | 0 | 875
108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0 | 16 |  | Fuel conservation
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 913 | 814 | 928 | 928
109 | Khulna 115 PP MW (KPCL-2) |  | HFO | NENP | 7*17 | 115 | 115 | 16 | 16 | 16 | 16 | 99 |  | Fuel shortage
110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 10 | 22 | 20 | 30 |  | 24 | Engine problem
111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 120 | 180 | 50 |  | Fuel shortage
112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 22 | 56 | 40 | 55 |  | 54 | Engine problem
113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 130 | 135 | 155 | 155 | 255 |  | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | NENP | 5*8.5 | 40 | 40 | 8 | 8 | 32 | 40
| Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 0 | 0 | 0 | 0 | 0 | 0
115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 35 | 35 | 35 | 70 |  | Fuel shortage
116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 6*18 | 105 | 105 | 50 | 105 | 50 | 105
117 | Mongla Orion 100 MW Solar PP |  | Solar | IPP | 100 | 100 | 100 | 63 | 0 | 100 | 0
118 | Khulna 330 MW CCPP (OIL) |  | Gas/HSD | BPDB | 1*220+1*110 | 220 | 220 | 226 | 234 | 15 | 234 | 220 |  | ST Under S/D
119 | Rampal 1320 MW (BIFPCL) |  | Coal | NTPC&BPDB | 660*2 | 617 | 617 | 0 | 0 | 0 | 0 | 617 |  | Coal shortage
| Kulna 225 MW CCPP (GAS) |  | Gas | NWPGCL | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test.
| Khulna Area Total |  |  |  |  | 3125 | 3121 | 1593 | 1605 | 1511 | 1778 | 1327 | 78
120 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 64 | 16 | 110
121 | Bhola 33 MW PP (Venture) |  | Gas | NENP | 1*34.50 | 40 | 40 | 25 | 34 | 22 | 34 |  | 6 | Engine problem
122 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 130 | 65 | 120 | 120 |  | 74 | Machine problem
| Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired |  | From 18-3-2022
123 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244
124 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 218 | 220 | 220 | 220
125 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 17 | 150 | 17 | 150
126 | Barisal 307 MW |  | Coal | IPP | 307*1 | 307 | 307 | 250 | 150 | 0 | 0 | 307 |  | Coal shortage
| Barisal Area Total |  |  |  |  | 2265 | 2265 | 1900 | 1927 | 1639 | 1878 | 307 | 80
127 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
128 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 35 | 0 | 35 | 17 |  | Fuel shortage
129 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 25 | 0 | 32 |  | 39 | Engine problem
130 | Amnura 50 MW PP(Sinha) |  | HFO | NENP | 7*7.79 | 50 | 28 | 21 | 21 | 21 | 21
131 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 42 | 0 | 0 | 50 |  | Fuel shortage
132 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 38 | 35 | 0 | 35 | 15 |  | Engine problem
133 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 |  | 210 | Under maint
134 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 160 | 213 | 214 | 220
135 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 143 | 147 | 160 | 181 | 39 |  | Gas shortage
136 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 336 | 344 | 414 | 414
137 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 24 | 0 | 31 | 19 |  | Fuel shortage
138 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| Bogura 20 MW PP (Energyprima) |  | Gas | NENP | 5*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
139 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8 |  | 3 | Engine problem
140 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 8 | 8 |  | 44 | Fuel shortage
141 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 12*8.924 | 104 | 104 | 48 | 90 | 50 | 90 | 14 |  | Fuel shortage
142 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 135*1.6 | 200 | 200 | 0 | 0 | 0 | 0
143 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 6*18.55+7.2 | 113 | 113 | 50 | 75 | 50 | 95 | 18 |  | Fuel shortage
144 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 56 | 35 | 57 | 56 |  | Fuel shortage
145 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
| Adani Power Jharkhanda Ltd |  | Coal | Import | 748*2 | 1496 | 1496 | 765 | 774 | 750 | 750
| Rajshahi Area Total |  |  |  |  | 3675 | 3631 | 1617 | 1897 | 1716 | 1977 | 399 | 296
146 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint
147 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 240 | 220 | 220 | 230
148 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 13 | 0 | 0 | 20
149 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 10 | 0 | 0 | 20
150 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 113 | 34 | 98 | 34 | 98 | 15 |  | Fuel shortage
151 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
152 | Energypac Power Venture Thakurgaon Ltd. |  | HFO | IPP | 115 | 115 | 115 | 35 | 114 | 35 | 113
153 | Intraco Solar 30 MW |  | Solar | IPP | 1*30 | 30 | 30 | 20 | 0 | 30 | 0
| Teesta Solar Limited |  | Solar | BPCL | 16*12.5 | 0 | 0 | 201 | 0 | 130 | 0
| Rangpur Area Total |  |  |  |  | 830 | 750 | 537 | 455 | 457 | 441 | 140 | 85
| Total |  |  |  |  | 24911 | 24171 | 13198 | 14801 | 13080.6 | 15307 | 4655 | 2967
A. |  | 2023-07-31 | (Yesterday) |  |  |  |  | Monday
1 | Highest Generation : |  |  | 14801 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 12165 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 0 | MW
3 | Day peak Generation : |  |  | 13198 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 14390.98 | MW
4 | Evening peak Generation : |  |  | 14801 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 400 | MW
5 | Total Energy Generation : |  | 317.9616 | MKWHr | By Solar | 3.0424 | MKWHr
| By Gas : | 149.1228 | MKWHr |  | By Oil: | 68.5339 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16. Hourly Load Shed during
| By Coal : | 69.2769 | MKWHr |  | By Hydro: | 2.8208 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
[5 empty] | By Wind: | 0.0456 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 4655 | MW | Dhaka | 4935.98 | 4895.98 |  | 40 |  | 18:00 |  | 493.735
|  |  | For Plants S/D or M/C prob = |  |  | 2967 | MW | Chittagong | 1484 | 1484 |  | 0 |  | 19:00 |  | 321.835
|  |  | Total = |  |  | 7622 | MW | Khulna | 1868 | 1868 |  | 0 |  | 19:30 |  | 452.67
7 | Total Gas Supplied : |  |  | 1124.55 | MMCFD |  |  | Rajshahi | 1575 | 1515 |  | 60 |  | 20:00 |  | 437.39
8 | Fuel Cost : | i) Gas : | Taka | 164958992.73 | ii) Oil : | Taka | 922612181.87 | Comilla | 1094 | 1054 |  | 40 |  | 21:00 |  | 400.145
|  | iii) Coal : | Taka | 309892790 | Total | Taka | 1397463964.6 | Mymensingh | 1288 | 1118 |  | 170 |  | 22:00 |  | 514.745
9 | Power flow through E-W Interconnectors : |  |  |  | i) Energy | 0 | MKWHr. | Sylhet | 538 | 538 |  | 0 |  | 23:00 |  | 467.95
| ii) During Peak Demand : |  |  | 504 | MW (E to W) at | 21:00 | hrs | Barisal | 474 | 474 |  | 0 |  | 24:00 |  | 1166.055
| iii) Maximum : |  |  | 390 | MW at | 22:00 | hrs | Rangpur | 1134 | 1044 |  | 90
10 | Maximum Temperature in Dhaka was |  |  |  | 37.1° C |  |  | Total | 14390.98 | 13990.98 |  | 400
B. |  | 2023-08-01 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 37.1° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 15500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 178 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15307 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 14300 | MW
4 | Reserve(Generation end) |  |  |  | - | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 332.9779 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 12246 | MW at | 7:00 | 55 | 22 | 22 | 18 | 18 | 15 | 10 | 5 | 13
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.8945 | MKWHr. | ii) HVDC Flow at Peak Time |  | 814 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2246 | MKWHr. | iii) Maximum HVDC Flow : |  | 913 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.3 |  | (b) Today: | 79.93 |  | (c) Rule Curve: |  | 89
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2023-07-31 | [21 empty] | BR
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108 MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360 MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150 MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108 MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195 MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22 MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33 MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44 MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86 MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50 MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11 MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200 MW (Desh energy) | Ashuganj 150 MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | Chandpur 115(Doreen) | Kanchan Purbachal Power Generation Ltd. | Ashuganj 420 MW CCPP(East) | Mirsharai 150 MW (Oil) | Mirsharai 150 MW (Gas) | SS Power I | Cox's Bazar Wind | Matarbari 2*600 MW (CPGCL) | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | Mongla Orion 100 MW Solar PP | Energypac Power Venture Thakurgaon Ltd. | Khulna 330 MW CCPP (OIL) | Khulna 330 MW CCPP (GAS) | Rampal 1320 MW (BIFPCL) | Intraco Solar 30 MW | Barisal 307 MW | Adani Power Jharkhanda Ltd | Teesta Solar Limited | Kulna 225 MW CCPP (GAS) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | HSD (Private) | HFO (Private) | Coal | Hydro | HSD (Public) | HFO (Public) | Tripura | Solar | Wind | Shortage | Water Level
1:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 364 | 323 |  | 0 | 450 | 0 | 42 | 96 | 15 | 326 | 0 | 182 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 22 | 33 | 23 | 8 | 0 | 76 | 70 | 120 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 58 | 39 | 36 | 0 | 6 | 12 | 29 | 0 | 0 | 0 | 295 | 240 | 167 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 38 | 43 | 19 | 10 | 33 | 20 | 146 | 94 | 0 | 16 | 0 | 30 | 0 | 47 | 47 | 112 | 0 | 20 | 81 | 0 | 185 | 17 | 0 | 10 | 320 | 24 | 5 | 0 | 102 | 300 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 6 | 382 | 19 | 35 | 51 | 0 | 86 | 36 | 74 | 17 | 9 | 38 | 350 | 40 | 0 | 17 | 40 | 0 | 17 | 0 | 22 | 17 | 300 | 17 | 0 | 70 | 0 | 150 |  | 913 | 0 | 130 | 0 | 16 | 120 | 0 | 0 | 10 | 48 | 8 | 130 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 22 | 8 | 31 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 151 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 150 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 250 | 766 | 0 | 0 |  | 7535 | 5364 | 12899 | 4363 | 913 | 2144 | 300 | 1586 | 2510 | 146 | 330 | 311 | 146 | 0 | 0 | 1719.955 | 80.45
2:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 366 | 323 |  | 0 | 450 | 0 | 42 | 96 | 15 | 324 | 0 | 191 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 23 | 8 | 0 | 76 | 55 | 120 | 0 | 8 | 224 | 0 | 0 | 0 |  | 6 | 50 | 50 | 36 | 0 | 6 | 12 | 33 | 0 | 0 | 0 | 300 | 240 | 166 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 38 | 43 | 19 | 10 | 33 | 17 | 140 | 94 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 81 | 0 | 185 | 17 | 0 | 10 | 320 | 24 | 5 | 0 | 115 | 300 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 6 | 390 | 19 | 35 | 51 | 0 | 87 | 36 | 74 | 17 | 9 | 38 | 350 | 36 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 270 | 17 | 0 | 70 | 0 | 150 |  | 912 | 0 | 140 | 0 | 16 | 120 | 0 | 0 | 10 | 48 | 8 | 132 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 199 | 0 | 0 | 150 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 771 | 0 | 0 |  | 7507 | 5202 | 12709 | 4359 | 912 | 2149 | 300 | 1473 | 2515 | 131 | 319 | 261 | 140 | 0 | 0 | 1710.405 | 80.42
3:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 380 | 322 |  | 0 | 450 | 0 | 43 | 96 | 15 | 325 | 0 | 185 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 23 | 8 | 0 | 76 | 55 | 120 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 49 | 50 | 36 | 0 | 6 | 12 | 33 | 0 | 0 | 0 | 280 | 240 | 166 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 38 | 43 | 19 | 10 | 33 | 17 | 136 | 97 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 81 | 0 | 185 | 17 | 0 | 10 | 315 | 24 | 5 | 0 | 115 | 299 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 5 | 367 | 19 | 35 | 51 | 0 | 87 | 36 | 74 | 17 | 9 | 38 | 350 | 35 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 270 | 17 | 0 | 70 | 4 | 150 |  | 913 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 10 | 48 | 8 | 132 | 35 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 153 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 221 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 777 | 0 | 0 |  | 7468 | 5146 | 12614 | 4343 | 913 | 2143 | 299 | 1434 | 2521 | 131 | 280 | 260 | 136 | 0 | 4 | 1657.88 | 80.39
4:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 385 | 322 |  | 0 | 450 | 0 | 47 | 96 | 15 | 323 | 0 | 190 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 23 | 8 | 0 | 76 | 55 | 116 | 0 | 8 | 226 | 0 | 0 | 0 |  | 6 | 41 | 50 | 36 | 0 | 6 | 12 | 35 | 0 | 0 | 0 | 315 | 240 | 170 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 38 | 43 | 19 | 10 | 33 | 17 | 134 | 96 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 81 | 0 | 185 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 112 | 300 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 6 | 397 | 19 | 35 | 51 | 0 | 87 | 36 | 65 | 17 | 9 | 38 | 350 | 35 | 0 | 17 | 34 | 0 | 17 | 0 | 17 | 17 | 270 | 17 | 0 | 70 | 2 | 150 |  | 913 | 0 | 160 | 0 | 16 | 120 | 0 | 0 | 10 | 48 | 8 | 132 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 764 | 0 | 0 |  | 7519 | 5144 | 12663 | 4426 | 913 | 2140 | 300 | 1427 | 2508 | 131 | 280 | 252 | 134 | 0 | 2 | 1563.335 | 80.36
5:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 364 | 321 |  | 0 | 450 | 0 | 50 | 96 | 15 | 320 | 0 | 188 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 23 | 8 | 0 | 76 | 55 | 117 | 0 | 8 | 223 | 0 | 0 | 0 |  | 3 | 41 | 50 | 36 | 0 | 6 | 12 | 36 | 0 | 0 | 0 | 310 | 240 | 168 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 38 | 43 | 19 | 10 | 33 | 17 | 132 | 97 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 78 | 0 | 184 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 112 | 180 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 6 | 400 | 19 | 35 | 51 | 0 | 87 | 36 | 74 | 0 | 7 | 38 | 350 | 47 | 0 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 270 | 17 | 0 | 125 | 0 | 150 |  | 912 | 0 | 170 | 0 | 16 | 120 | 0 | 0 | 10 | 43 | 8 | 134 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 156 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 771 | 0 | 0 |  | 7418 | 5156 | 12574 | 4408 | 912 | 2134 | 180 | 1430 | 2570 | 131 | 280 | 247 | 132 | 0 | 0 | 1361.83 | 80.33
6:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 357 | 321 |  | 0 | 450 | 0 | 50 | 96 | 15 | 324 | 0 | 190 | 45 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 23 | 8 | 0 | 78 | 55 | 120 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 41 | 50 | 36 | 0 | 6 | 12 | 36 | 0 | 0 | 0 | 305 | 240 | 174 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 38 | 43 | 0 | 10 | 33 | 17 | 120 | 97 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 78 | 0 | 185 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 34 | 0 | 25 | 34 | 5 | 387 | 19 | 35 | 51 | 0 | 87 | 36 | 56 | 0 | 9 | 38 | 350 | 52 | 3 | 17 | 34 | 0 | 17 | 0 | 18 | 17 | 270 | 17 | 0 | 145 | 2 | 150 |  | 913 | 0 | 175 | 0 | 16 | 120 | 0 | 0 | 10 | 43 | 8 | 134 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 0 | 35 | 1244 | 222 | 0 | 17 | 0 | 2 | 0 | 0 | 0 | 0 | 1 | 250 | 772 | 10 | 0 |  | 7222 | 5171 | 12393 | 4385 | 913 | 2123 | 0 | 1433 | 2591 | 133 | 280 | 247 | 120 | 16 | 2 | 1248.185 | 80.3
7:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 312 | 322 |  | 0 | 450 | 0 | 50 | 96 | 15 | 329 | 0 | 181 | 50 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 80 | 50 | 120 | 0 | 8 | 223 | 0 | 0 | 0 |  | 6 | 41 | 50 | 36 | 0 | 6 | 12 | 31 | 0 | 0 | 0 | 350 | 240 | 161 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 39 | 43 | 0 | 0 | 33 | 17 | 118 | 46 | 0 | 16 | 0 | 30 | 0 | 47 | 48 | 112 | 0 | 20 | 78 | 0 | 185 | 17 | 0 | 10 | 320 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 34 | 2 | 25 | 34 | 6 | 371 | 19 | 35 | 51 | 0 | 87 | 36 | 56 | 0 | 8 | 38 | 350 | 53 | 13 | 17 | 34 | 0 | 17 | 5 | 17 | 17 | 270 | 17 | 0 | 148 | 0 | 150 |  | 913 | 0 | 165 | 0 | 16 | 120 | 0 | 0 | 10 | 34 | 8 | 132 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 1 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 157 | 0 | 414 | 36 | 0 | 35 | 105 | 34 | 0 | 1 | 35 | 1244 | 225 | 0 | 17 | 0 | 8 | 0 | 0 | 0 | 0 | 7 | 250 | 772 | 27 | 0 |  | 7158 | 5175 | 12333 | 4279 | 913 | 2136 | 0 | 1431 | 2594 | 130 | 280 | 239 | 118 | 63 | 0 | 1114.485 | 80.28
8:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 368 | 323 |  | 0 | 450 | 0 | 50 | 96 | 15 | 335 | 0 | 181 | 50 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 25 | 24 | 8 | 0 | 80 | 50 | 118 | 0 | 8 | 222 | 0 | 0 | 0 |  | 6 | 41 | 34 | 36 | 0 | 6 | 12 | 8 | 0 | 0 | 0 | 280 | 240 | 175 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 39 | 43 | 0 | 0 | 33 | 17 | 122 | 47 | 0 | 16 | 1 | 30 | 0 | 47 | 48 | 112 | 0 | 0 | 78 | 0 | 185 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 36 | 4 | 25 | 35 | 6 | 367 | 19 | 35 | 51 | 2 | 87 | 36 | 55 | 0 | 9 | 38 | 350 | 46 | 25 | 17 | 34 | 0 | 17 | 18 | 18 | 15 | 270 | 17 | 0 | 168 | 0 | 150 |  | 913 | 0 | 160 | 0 | 16 | 120 | 0 | 0 | 10 | 30 | 8 | 131 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 154 | 0 | 403 | 36 | 0 | 35 | 105 | 34 | 0 | 3 | 35 | 1244 | 224 | 0 | 17 | 3 | 28 | 0 | 0 | 0 | 0 | 15 | 250 | 768 | 92 | 0 |  | 7119 | 5248 | 12367 | 4250 | 913 | 2069 | 0 | 1433 | 2610 | 130 | 280 | 219 | 122 | 191 | 0 | 1129.765 | 80.26
9:00 | 0 | 0 | 160 | 180 | 0 | 12 | 0 | 367 | 337 |  | 0 | 450 | 0 | 50 | 96 | 15 | 326 | 0 | 133 | 50 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 17 | 19 | 10 | 25 | 10 | 8 | 0 | 80 | 30 | 120 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 33 | 34 | 36 | 0 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 240 | 179 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 39 | 43 | 0 | 0 | 33 | 15 | 126 | 47 | 0 | 14 | 2 | 30 | 0 | 44 | 48 | 80 | 0 | 0 | 75 | 0 | 183 | 17 | 0 | 10 | 290 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 68 | 16 | 25 | 35 | 5 | 343 | 19 | 35 | 51 | 2 | 88 | 36 | 55 | 0 | 9 | 38 | 350 | 35 | 39 | 17 | 34 | 0 | 17 | 19 | 18 | 0 | 230 | 17 | 0 | 184 | 0 | 150 |  | 912 | 0 | 145 | 0 | 16 | 120 | 0 | 0 | 10 | 20 | 8 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 149 | 0 | 377 | 36 | 0 | 35 | 105 | 34 | 0 | 4 | 35 | 1244 | 225 | 0 | 17 | 3 | 36 | 0 | 0 | 0 | 0 | 22 | 250 | 759 | 133 | 0 |  | 6924 | 5241 | 12165 | 4034 | 912 | 2014 | 0 | 1445 | 2617 | 110 | 280 | 201 | 126 | 276 | 0 | 1418.175 | 80.24
10:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 363 | 326 |  | 0 | 450 | 0 | 50 | 96 | 15 | 318 | 0 | 184 | 50 | 25 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 17 | 19 | 12 | 25 | 16 | 8 | 0 | 80 | 0 | 120 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 33 | 34 | 36 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 315 | 240 | 184 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 40 | 36 | 0 | 11 | 33 | 15 | 134 | 47 | 0 | 14 | 2 | 30 | 0 | 42 | 47 | 0 | 0 | 0 | 75 | 0 | 183 | 17 | 0 | 9 | 300 | 16 | 8 | 0 | 112 | 0 | 0 | 68 | 0 | 71 | 4 | 25 | 44 | 6 | 403 | 22 | 35 | 51 | 2 | 88 | 17 | 55 | 0 | 9 | 38 | 350 | 35 | 44 | 54 | 34 | 0 | 17 | 29 | 28 | 0 | 230 | 17 | 0 | 226 | 0 | 150 |  | 913 | 0 | 140 | 0 | 16 | 120 | 0 | 0 | 10 | 20 | 8 | 130 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 146 | 0 | 355 | 35 | 0 | 35 | 32 | 34 | 0 | 0 | 35 | 1220 | 220 | 0 | 17 | 4 | 59 | 0 | 15 | 0 | 0 | 24 | 250 | 760 | 182 | 0 |  | 7148 | 5197 | 12345 | 4210 | 913 | 1904 | 0 | 1454 | 2637 | 80 | 295 | 218 | 134 | 350 | 0 | 1485.025 | 80.22
11:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 326 |  | 0 | 450 | 0 | 49 | 96 | 15 | 316 | 0 | 185 | 50 | 33 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 5 | 17 | 19 | 19 | 25 | 15 | 8 | 0 | 80 | 35 | 115 | 0 | 8 | 219 | 0 | 0 | 0 |  | 6 | 33 | 34 | 46 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 37 | 0 | 11 | 32 | 15 | 140 | 33 | 0 | 14 | 2 | 30 | 0 | 42 | 43 | 0 | 0 | 0 | 78 | 0 | 183 | 17 | 0 | 9 | 300 | 16 | 8 | 0 | 112 | 100 | 0 | 77 | 0 | 71 | 10 | 37 | 68 | 5 | 368 | 21 | 35 | 51 | 6 | 121 | 17 | 55 | 0 | 9 | 38 | 350 | 35 | 38 | 54 | 34 | 0 | 30 | 27 | 60 | 0 | 230 | 17 | 0 | 246 | 0 | 150 |  | 913 | 0 | 140 | 0 | 16 | 120 | 0 | 0 | 10 | 19 | 8 | 120 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 0 | 15 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 144 | 0 | 348 | 35 | 0 | 50 | 32 | 34 | 0 | 7 | 35 | 1210 | 220 | 0 | 17 | 5 | 65 | 0 | 125 | 0 | 0 | 17 | 250 | 770 | 198 | 0 |  | 7368 | 5409 | 12777 | 4129 | 913 | 1896 | 100 | 1613 | 2706 | 115 | 405 | 235 | 140 | 375 | 0 | 1454.465 | 80.2
12:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 317 |  | 0 | 450 | 0 | 50 | 96 | 15 | 315 | 0 | 180 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 17 | 19 | 19 | 25 | 15 | 8 | 0 | 80 | 35 | 118 | 0 | 8 | 214 | 0 | 0 | 0 |  | 6 | 24 | 34 | 46 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 43 | 7 | 11 | 25 | 15 | 146 | 33 | 0 | 16 | 2 | 30 | 0 | 42 | 43 | 112 | 0 | 0 | 78 | 0 | 181 | 17 | 0 | 9 | 280 | 16 | 8 | 0 | 105 | 63 | 0 | 67 | 0 | 71 | 13 | 37 | 71 | 6 | 386 | 24 | 35 | 51 | 5 | 121 | 17 | 55 | 0 | 27 | 38 | 350 | 50 | 42 | 54 | 34 | 0 | 35 | 34 | 59 | 0 | 230 | 17 | 0 | 275 | 0 | 150 |  | 913 | 0 | 130 | 0 | 16 | 120 | 0 | 0 | 10 | 22 | 8 | 130 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 21 | 0 | 38 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 143 | 0 | 336 | 35 | 0 | 50 | 50 | 34 | 0 | 7 | 35 | 1244 | 218 | 0 | 17 | 5 | 63 | 35 | 226 | 0 | 0 | 20 | 250 | 765 | 201 | 0 |  | 7551 | 5647 | 13198 | 4163 | 913 | 1967 | 63 | 1729 | 2774 | 115 | 506 | 280 | 146 | 392 | 0 | 1291.16 | 80.18
13:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 316 |  | 0 | 450 | 0 | 51 | 96 | 15 | 315 | 0 | 185 | 45 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 12 | 25 | 15 | 8 | 0 | 80 | 35 | 115 | 0 | 8 | 214 | 0 | 0 | 0 |  | 6 | 24 | 50 | 46 | 0 | 6 | 10 | 7 | 0 | 0 | 0 | 305 | 240 | 204 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 43 | 16 | 11 | 32 | 15 | 156 | 33 | 0 | 15 | 2 | 30 | 0 | 41 | 39 | 0 | 0 | 0 | 78 | 0 | 180 | 17 | 0 | 9 | 315 | 16 | 8 | 0 | 110 | 300 | 0 | 66 | 0 | 71 | 8 | 37 | 69 | 5 | 370 | 24 | 35 | 51 | 6 | 123 | 17 | 55 | 0 | 27 | 38 | 350 | 54 | 31 | 54 | 34 | 0 | 35 | 34 | 72 | 0 | 230 | 17 | 0 | 325 | 3 | 150 |  | 913 | 0 | 125 | 0 | 16 | 120 | 0 | 0 | 10 | 35 | 8 | 122 | 25 | 16 | 0 | 0 | 0 | 0 | 5 | 48 | 21 | 0 | 29 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 140 | 0 | 319 | 35 | 0 | 50 | 50 | 34 | 0 | 7 | 35 | 1244 | 217 | 0 | 17 | 5 | 101 | 36 | 225 | 0 | 0 | 18 | 250 | 763 | 200 | 0 |  | 7805 | 5655 | 13460 | 4144 | 913 | 1871 | 300 | 1764 | 2822 | 115 | 505 | 305 | 156 | 412 | 3 | 1231.95 | 80.16
14:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 357 | 333 |  | 0 | 450 | 0 | 50 | 96 | 15 | 331 | 0 | 160 | 42 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 14 | 17 | 15 | 8 | 0 | 70 | 35 | 115 | 0 | 8 | 216 | 0 | 0 | 0 |  | 6 | 33 | 48 | 46 | 4 | 6 | 12 | 14 | 0 | 0 | 0 | 280 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 27 | 43 | 16 | 11 | 31 | 15 | 158 | 33 | 0 | 15 | 2 | 30 | 0 | 41 | 39 | 0 | 0 | 0 | 75 | 0 | 0 | 17 | 0 | 10 | 275 | 0 | 8 | 0 | 112 | 20 | 0 | 66 | 0 | 68 | 13 | 25 | 68 | 6 | 370 | 19 | 35 | 51 | 4 | 124 | 17 | 55 | 17 | 12 | 38 | 350 | 54 | 40 | 54 | 34 | 0 | 35 | 32 | 72 | 12 | 230 | 17 | 0 | 380 | 0 | 150 |  | 912 | 0 | 120 | 0 | 16 | 120 | 0 | 0 | 10 | 21 | 8 | 130 | 28 | 16 | 0 | 0 | 0 | 0 | 5 | 48 | 21 | 0 | 29 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 139 | 0 | 302 | 35 | 0 | 50 | 32 | 33 | 0 | 7 | 35 | 1244 | 217 | 0 | 17 | 3 | 82 | 36 | 225 | 0 | 0 | 22 | 250 | 770 | 126 | 0 |  | 7329 | 5525 | 12854 | 3906 | 912 | 1839 | 20 | 1742 | 2884 | 105 | 505 | 302 | 158 | 331 | 0 | 1571.93 | 80.2
15:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 363 | 336 |  | 0 | 450 | 0 | 50 | 75 | 15 | 318 | 0 | 183 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 14 | 17 | 15 | 8 | 0 | 70 | 34 | 110 | 0 | 9 | 211 | 0 | 0 | 0 |  | 6 | 32 | 48 | 46 | 5 | 6 | 12 | 2 | 0 | 0 | 0 | 320 | 240 | 196 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 34 | 32 | 16 | 11 | 31 | 17 | 160 | 33 | 0 | 15 | 2 | 28 | 0 | 41 | 41 | 0 | 0 | 20 | 75 | 0 | 0 | 17 | 0 | 10 | 310 | 8 | 8 | 0 | 112 | 250 | 0 | 65 | 0 | 62 | 8 | 37 | 68 | 5 | 380 | 24 | 35 | 51 | 4 | 124 | 17 | 55 | 17 | 9 | 38 | 332 | 54 | 47 | 54 | 34 | 0 | 35 | 9 | 72 | 17 | 230 | 17 | 0 | 355 | 0 | 145 |  | 912 | 0 | 115 | 0 | 16 | 120 | 0 | 0 | 10 | 21 | 8 | 124 | 29 | 16 | 0 | 0 | 0 | 0 | 25 | 48 | 21 | 0 | 29 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 139 | 0 | 285 | 35 | 0 | 50 | 32 | 33 | 0 | 6 | 35 | 1244 | 220 | 0 | 17 | 4 | 14 | 36 | 222 | 0 | 0 | 12 | 250 | 769 | 156 | 0 |  | 7594 | 5462 | 13056 | 3957 | 912 | 1854 | 250 | 1731 | 2848 | 104 | 505 | 328 | 160 | 262 | 0 | 1541.37 | 80.12
16:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 364 | 316 |  | 0 | 450 | 0 | 51 | 34 | 15 | 314 | 0 | 185 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 14 | 25 | 15 | 8 | 0 | 70 | 35 | 110 | 0 | 9 | 220 | 0 | 0 | 0 |  | 6 | 36 | 32 | 58 | 5 | 6 | 12 | 2 | 0 | 0 | 0 | 280 | 260 | 199 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 38 | 37 | 17 | 11 | 30 | 17 | 156 | 33 | 0 | 15 | 0 | 28 | 0 | 41 | 38 | 0 | 0 | 25 | 78 | 0 | 30 | 17 | 0 | 10 | 315 | 16 | 5 | 0 | 112 | 26 | 0 | 68 | 0 | 68 | 0 | 36 | 68 | 5 | 393 | 19 | 35 | 51 | 3 | 124 | 17 | 55 | 17 | 9 | 38 | 330 | 53 | 24 | 54 | 34 | 0 | 35 | 1 | 72 | 17 | 250 | 34 | 0 | 355 | 0 | 150 |  | 913 | 0 | 115 | 0 | 16 | 120 | 0 | 0 | 10 | 21 | 8 | 130 | 24 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 0 | 140 | 0 | 334 | 35 | 0 | 50 | 32 | 34 | 0 | 5 | 56 | 1244 | 220 | 0 | 17 | 0 | 18 | 36 | 75 | 0 | 0 | 8 | 250 | 768 | 132 | 0 |  | 7373 | 5282 | 12655 | 4034 | 913 | 1883 | 26 | 1732 | 2847 | 105 | 358 | 260 | 156 | 191 | 0 | 1427.725 | 80.1
17:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 362 | 323 |  | 0 | 450 | 0 | 49 | 34 | 15 | 318 | 0 | 192 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 17 | 19 | 14 | 33 | 15 | 8 | 0 | 70 | 30 | 110 | 0 | 8 | 225 | 0 | 0 | 0 |  | 4 | 60 | 50 | 58 | 22 | 37 | 12 | 16 | 0 | 0 | 0 | 280 | 260 | 203 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 39 | 37 | 17 | 11 | 30 | 12 | 150 | 33 | 0 | 0 | 0 | 28 | 0 | 44 | 39 | 0 | 0 | 25 | 84 | 0 | 110 | 17 | 0 | 10 | 300 | 16 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 72 | 0 | 36 | 70 | 6 | 370 | 19 | 35 | 51 | 0 | 124 | 17 | 55 | 17 | 9 | 38 | 370 | 53 | 12 | 90 | 34 | 0 | 35 | 1 | 72 | 17 | 250 | 17 | 0 | 410 | 14 | 150 |  | 907 | 0 | 120 | 0 | 16 | 120 | 0 | 0 | 10 | 21 | 8 | 62 | 12 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 0 | 17 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0 | 142 | 0 | 334 | 35 | 0 | 50 | 90 | 62 | 0 | 3 | 56 | 1200 | 220 | 0 | 17 | 1 | 2 | 36 | 75 | 0 | 0 | 10 | 250 | 771 | 52 | 0 |  | 7639 | 5129 | 12768 | 4076 | 907 | 1887 | 0 | 1931 | 2811 | 100 | 375 | 286 | 150 | 81 | 14 | 1033.31 | 80.08
18:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 361 | 324 |  | 0 | 450 | 0 | 55 | 34 | 15 | 323 | 0 | 150 | 62 | 74 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 14 | 33 | 15 | 8 | 0 | 70 | 35 | 115 | 0 | 12 | 223 | 0 | 0 | 0 |  | 4 | 74 | 50 | 80 | 24 | 45 | 12 | 17 | 0 | 0 | 0 | 280 | 260 | 202 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 37 | 38 | 17 | 11 | 30 | 12 | 144 | 34 | 0 | 0 | 0 | 30 | 0 | 47 | 44 | 0 | 0 | 25 | 84 | 0 | 110 | 17 | 0 | 10 | 280 | 8 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 83 | 0 | 48 | 90 | 5 | 370 | 19 | 35 | 51 | 0 | 124 | 17 | 55 | 17 | 9 | 38 | 375 | 54 | 2 | 90 | 37 | 0 | 35 | 1 | 72 | 17 | 250 | 17 | 0 | 350 | 9 | 150 |  | 908 | 0 | 120 | 0 | 16 | 120 | 0 | 0 | 14 | 35 | 8 | 62 | 20 | 40 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 5 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 0 | 144 | 0 | 341 | 35 | 0 | 50 | 105 | 76 | 0 | 1 | 56 | 1200 | 220 | 0 | 72 | 0 | 2 | 36 | 75 | 0 | 0 | 3 | 250 | 760 | 12 | 0 |  | 7666 | 5217 | 12883 | 4039 | 908 | 1884 | 0 | 2175 | 2740 | 105 | 392 | 316 | 144 | 21 | 9 | 493.735 | 80.06
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 362 | 327 |  | 0 | 450 | 0 | 58 | 38 | 15 | 320 | 0 | 189 | 65 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 22 | 33 | 15 | 25 | 0 | 70 | 35 | 121 | 0 | 25 | 220 | 0 | 0 | 0 |  | 5 | 84 | 50 | 80 | 24 | 46 | 12 | 25 | 0 | 0 | 0 | 315 | 260 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 38 | 0 | 0 | 33 | 17 | 168 | 48 | 0 | 0 | 0 | 30 | 0 | 47 | 44 | 0 | 0 | 20 | 84 | 0 | 110 | 17 | 0 | 10 | 290 | 16 | 5 | 0 | 112 | 226 | 0 | 86 | 0 | 135 | 0 | 100 | 100 | 11 | 398 | 90 | 88 | 51 | 0 | 257 | 17 | 55 | 34 | 26 | 88 | 370 | 72 | 0 | 90 | 68 | 0 | 35 | 0 | 95 | 0 | 250 | 70 | 0 | 330 | 3 | 150 |  | 908 | 0 | 125 | 0 | 16 | 120 | 0 | 0 | 27 | 50 | 8 | 66 | 29 | 64 | 0 | 0 | 0 | 35 | 20 | 90 | 21 | 8 | 26 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 144 | 0 | 346 | 35 | 0 | 90 | 105 | 77 | 0 | 0 | 56 | 1244 | 220 | 0 | 150 | 0 | 0 | 72 | 234 | 0 | 0 | 0 | 250 | 771 | 0 | 0 |  | 8726 | 5887 | 14613 | 4135 | 908 | 1927 | 226 | 2966 | 2825 | 105 | 564 | 636 | 168 | 0 | 3 | 321.835 | 80.02
19:30 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 327 |  | 0 | 450 | 0 | 59 | 51 | 15 | 324 | 0 | 193 | 65 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 10 | 19 | 22 | 33 | 15 | 25 | 0 | 70 | 35 | 123 | 0 | 25 | 225 | 0 | 0 | 0 |  | 3 | 84 | 50 | 80 | 24 | 46 | 12 | 30 | 0 | 0 | 0 | 280 | 260 | 203 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 38 | 0 | 0 | 30 | 17 | 112 | 76 | 0 | 0 | 0 | 30 | 0 | 47 | 45 | 0 | 0 | 20 | 84 | 0 | 110 | 17 | 0 | 10 | 260 | 16 | 5 | 0 | 112 | 53 | 0 | 86 | 0 | 135 | 0 | 100 | 120 | 25 | 368 | 93 | 88 | 51 | 0 | 257 | 17 | 55 | 34 | 56 | 88 | 385 | 72 | 0 | 162 | 68 | 0 | 35 | 0 | 97 | 0 | 250 | 110 | 0 | 330 | 5 | 150 |  | 908 | 0 | 130 | 0 | 16 | 120 | 0 | 0 | 40 | 55 | 8 | 62 | 29 | 64 | 0 | 0 | 0 | 35 | 20 | 90 | 21 | 8 | 30 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 146 | 0 | 362 | 35 | 0 | 95 | 105 | 77 | 0 | 0 | 56 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 234 | 0 | 0 | 0 | 250 | 769 | 0 | 0 |  | 8669 | 5957 | 14626 | 4139 | 908 | 1919 | 53 | 3166 | 2803 | 105 | 568 | 698 | 112 | 0 | 5 | 452.67 | 0
20:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 361 | 332 |  | 0 | 450 | 0 | 59 | 51 | 15 | 319 | 0 | 187 | 65 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 17 | 19 | 22 | 33 | 16 | 25 | 0 | 70 | 35 | 120 | 0 | 25 | 221 | 0 | 0 | 0 |  | 3 | 84 | 50 | 80 | 24 | 46 | 12 | 30 | 0 | 0 | 0 | 295 | 260 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 30 | 39 | 0 | 0 | 0 | 0 | 44 | 94 | 0 | 0 | 0 | 30 | 0 | 47 | 42 | 0 | 0 | 20 | 85 | 0 | 110 | 17 | 0 | 10 | 280 | 16 | 5 | 0 | 112 | 53 | 0 | 87 | 0 | 135 | 0 | 100 | 135 | 26 | 375 | 84 | 88 | 51 | 0 | 264 | 17 | 55 | 34 | 56 | 88 | 375 | 72 | 0 | 162 | 68 | 0 | 35 | 0 | 96 | 0 | 250 | 142 | 0 | 320 | 3 | 150 |  | 814 | 0 | 135 | 0 | 16 | 120 | 0 | 0 | 25 | 61 | 8 | 66 | 33 | 64 | 0 | 0 | 0 | 35 | 20 | 90 | 21 | 25 | 38 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 147 | 0 | 358 | 35 | 0 | 95 | 105 | 97 | 0 | 0 | 56 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 234 | 0 | 0 | 0 | 250 | 762 | 0 | 0 |  | 8630 | 5912 | 14542 | 4120 | 814 | 1942 | 53 | 3218 | 2796 | 105 | 568 | 729 | 44 | 0 | 3 | 437.39 | 80.03
21:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 362 | 317 |  | 0 | 450 | 0 | 59 | 51 | 15 | 326 | 0 | 198 | 65 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 22 | 33 | 16 | 25 | 0 | 70 | 62 | 117 | 0 | 25 | 225 | 0 | 0 | 0 |  | 6 | 84 | 50 | 80 | 24 | 46 | 12 | 17 | 0 | 0 | 0 | 280 | 260 | 207 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 32 | 40 | 8 | 11 | 31 | 0 | 112 | 97 | 0 | 0 | 0 | 30 | 0 | 47 | 45 | 0 | 0 | 20 | 86 | 0 | 110 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 112 | 250 | 0 | 86 | 0 | 144 | 0 | 100 | 156 | 48 | 367 | 84 | 105 | 51 | 0 | 265 | 17 | 55 | 34 | 57 | 88 | 303 | 72 | 0 | 162 | 68 | 0 | 35 | 0 | 109 | 0 | 250 | 142 | 0 | 310 | 0 | 110 |  | 814 | 0 | 135 | 0 | 16 | 180 | 0 | 0 | 22 | 56 | 8 | 65 | 34 | 64 | 0 | 0 | 0 | 35 | 25 | 90 | 21 | 42 | 35 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 220 | 13 | 10 | 0 | 0 | 0 | 213 | 0 | 0 | 147 | 0 | 344 | 35 | 0 | 75 | 105 | 98 | 0 | 0 | 56 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 234 | 0 | 0 | 0 | 150 | 774 | 0 | 0 |  | 8917 | 5884 | 14801 | 4082 | 814 | 1925 | 250 | 3303 | 2698 | 132 | 650 | 725 | 112 | 0 | 0 | 400.145 | 80.02
22:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 359 | 317 |  | 0 | 450 | 0 | 58 | 96 | 15 | 280 | 0 | 83 | 56 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 14 | 33 | 23 | 0 | 0 | 70 | 62 | 120 | 0 | 25 | 225 | 0 | 0 | 0 |  | 0 | 84 | 50 | 80 | 24 | 46 | 12 | 27 | 0 | 0 | 0 | 280 | 260 | 206 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 47 | 43 | 8 | 11 | 32 | 0 | 116 | 95 | 0 | 0 | 0 | 30 | 0 | 47 | 46 | 0 | 0 | 20 | 81 | 0 | 110 | 17 | 0 | 10 | 260 | 24 | 2 | 0 | 115 | 12 | 0 | 87 | 0 | 149 | 0 | 100 | 156 | 60 | 367 | 84 | 105 | 51 | 0 | 265 | 17 | 55 | 34 | 58 | 88 | 380 | 72 | 0 | 162 | 68 | 0 | 35 | 0 | 115 | 13 | 250 | 142 | 0 | 310 | 0 | 150 |  | 814 | 0 | 140 | 0 | 16 | 180 | 0 | 0 | 22 | 51 | 8 | 63 | 35 | 64 | 0 | 0 | 0 | 35 | 20 | 90 | 21 | 25 | 35 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 220 | 10 | 10 | 0 | 0 | 0 | 140 | 0 | 0 | 152 | 0 | 381 | 35 | 0 | 75 | 105 | 98 | 0 | 0 | 56 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 100 | 0 | 0 | 0 | 150 | 775 | 0 | 0 |  | 8675 | 5686 | 14361 | 4005 | 814 | 1929 | 12 | 3334 | 2699 | 132 | 440 | 730 | 116 | 0 | 0 | 514.745 | 80.01
23:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 364 | 327 |  | 0 | 450 | 0 | 59 | 40 | 15 | 280 | 0 | 193 | 56 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 19 | 19 | 33 | 25 | 2 | 0 | 70 | 62 | 122 | 0 | 8 | 223 | 0 | 0 | 0 |  | 3 | 84 | 50 | 80 | 0 | 46 | 12 | 26 | 0 | 0 | 0 | 325 | 260 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 47 | 43 | 16 | 11 | 32 | 17 | 116 | 92 | 0 | 0 | 0 | 30 | 0 | 47 | 46 | 0 | 0 | 20 | 84 | 0 | 110 | 17 | 0 | 9 | 310 | 24 | 2 | 0 | 112 | 77 | 0 | 68 | 0 | 88 | 0 | 100 | 156 | 65 | 404 | 19 | 105 | 51 | 0 | 267 | 17 | 55 | 34 | 28 | 88 | 383 | 72 | 0 | 162 | 68 | 0 | 17 | 0 | 115 | 17 | 250 | 142 | 0 | 310 | 0 | 150 |  | 777 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 11 | 0 | 8 | 132 | 25 | 64 | 0 | 0 | 0 | 35 | 20 | 90 | 21 | 34 | 36 | 8 | 24 | 0 | 0 | 0 | 0 | 0 | 210 | 10 | 8 | 0 | 0 | 0 | 140 | 0 | 0 | 151 | 0 | 388 | 35 | 0 | 70 | 105 | 98 | 0 | 0 | 94 | 1244 | 222 | 0 | 150 | 0 | 0 | 114 | 100 | 0 | 0 | 0 | 150 | 772 | 0 | 0 |  | 8728 | 5632 | 14360 | 4306 | 777 | 1989 | 77 | 3080 | 2686 | 132 | 378 | 669 | 116 | 0 | 0 | 467.95 | 80
24:00 | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 392 | 332 |  | 0 | 450 | 0 | 45 | 17 | 15 | 336 | 0 | 175 | 41 | 102 | 130 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 14 | 33 | 16 | 8 | 0 | 70 | 60 | 121 | 0 | 8 | 225 | 0 | 0 | 0 |  | 6 | 76 | 50 | 46 | 0 | 46 | 12 | 26 | 0 | 0 | 0 | 275 | 260 | 198 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 46 | 43 | 18 | 11 | 32 | 17 | 138 | 93 | 0 | 15 | 0 | 30 | 0 | 47 | 46 | 0 | 0 | 20 | 84 | 0 | 110 | 17 | 0 | 10 | 310 | 24 | 5 | 0 | 115 | 150 | 0 | 68 | 0 | 47 | 0 | 25 | 115 | 25 | 367 | 18 | 35 | 51 | 0 | 267 | 17 | 55 | 34 | 12 | 50 | 395 | 54 | 0 | 17 | 68 | 0 | 17 | 0 | 93 | 17 | 250 | 17 | 0 | 310 | 5 | 150 |  | 777 | 0 | 150 | 0 | 16 | 120 | 0 | 0 | 11 | 0 | 8 | 124 | 28 | 64 | 0 | 0 | 0 | 0 | 20 | 12 | 21 | 34 | 29 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 182 | 0 | 0 | 151 | 0 | 388 | 35 | 0 | 70 | 15 | 98 | 0 | 0 | 95 | 1244 | 222 | 0 | 150 | 0 | 0 | 35 | 220 | 0 | 0 | 0 | 150 | 771 | 0 | 0 |  | 8113 | 5466 | 13579 | 4320 | 777 | 1998 | 150 | 2313 | 2685 | 130 | 522 | 391 | 138 | 0 | 5 | 1166.055 | 79.99
KWH | 0 | 0 | 4987094 | 4284000 | 0 | 301090 | 0 | 8759300 | 7806000 |  | 0 | 10114500 | 0 | 1210560 | 1676676 | 380041 | 7663603 | 0 | 4448000 | 1104960 | 1203696 | 1782720 | 0 | 0 | 0 | 0 | 387360 | 532617 | 532716 | 320796 | 456000 | 395280 | 664200 | 432500 | 238522 | 0 | 1792800 | 1028000 | 2700000 | 0 | 271168 | 5426131 | 0 | 0 | 0 |  | 129120 | 1224592 | 1075660 | 1172040 | 159360 | 444480 | 266832 | 452640 | 0 | 0 | 0 | 7634300 | 6113000 | 4546000 | 0 | 0 | 43560 | 0 | 0 | 939968 | 0 | 874480 | 971309 | 259092 | 194040 | 742200 | 355990 | 3224640 | 1486080 | 0 | 238428 | 15450 | 706000 | 0 | 1088400 | 1075968 | 1132854 | 0 | 359520 | 1841280 | 0 | 3389250 | 383000 | 0 | 238500 | 7359500 | 448416 | 146640 | 0 | 2722364 | 3000687 | 0 | 1718400 | 0 | 1699488 | 81540 | 1046400 | 1764950 | 344581 | 9153000 | 752400 | 1142400 | 1257055 | 30121 | 3377236 | 617466 | 1432680 | 352260 | 438480 | 1170240 | 8498900 | 1235520 | 362470 | 1556640 | 1062600 | 0 | 650880 | 218086 | 1373760 | 296280 | 6245700 | 935054 | 0 | 5716363 | 45600 | 3003636 |  | 21894545 | 0 | 3559104 | 0 | 379200 | 3115227 | 0 | 0 | 282240 | 787200 | 191625 | 2699000 | 651551 | 711552 | 0 | 0 | 0 | 159259 | 208335 | 662384 | 493220 | 126188 | 312516 | 199421 | 137385 | 0 | 0 | 173520 | 0 | 0 | 4962000 | 43000 | 21000 | 0 | 0 | 0 | 4370091 | 0 | 0 | 3806709 | 0 | 8848727 | 838560 | 0 | 1340640 | 2011680 | 1205817 | 0 | 50432 | 1135392 | 31481000 | 5286655 | 0 | 1418400 | 38280 | 496800 | 876038 | 2187676 | 0 | 0 | 210442 | 5695000 | 18418910 | 1538750 | 0 |  | 184936156 | 133025471 | 317961627 | 101985185 | 21894545 | 47137633 | 3000687 | 47354438 | 69276909 | 2820800 | 9736994 | 8441825 | 3224640 | 3042371 | 45600 | 0
Fuel Cost | 0 | 0 | 7281157.24 | 6383160 | 0 | 400449.7 | 0 | 9197265 | 8430480 |  | 0 | 11024805 | 0 | 13534060.8 | 22215957 | 5035543.25 | 8583235.36 | 0 | 7784000 | 16154515.2 | 16936002.72 | 28897891.2 | 0 | 0 | 0 | 0 | 4927219.2 | 7190329.5 | 7143721.56 | 240597 | 342000 | 0 | 0 | 0 | 4057259.22 | 0 | 484056 | 277560 | 5103000 | 0 | 4433596.8 | 5643176.24 | 0 | 0 | 0 |  | 1685016 | 20426194.56 | 18307733.2 | 15834260.4 | 2020684.8 | 5142633.6 | 338876.64 | 1507291.2 | 0 | 0 | 0 | 8474073 | 6663170 | 5273360 | 0 | 0 | 49222.8 | 0 | 0 | 1569746.56 | 0 | 15102269.6 | 13064106.05 | 354956.04 | 145530 | 1298850 | 266992.5 | 23152915.2 | 1619827.2 | 0 | 324262.08 | 246273 | 967220 | 0 | 1893816 | 1861424.64 | 1302782.1 | 0 | 697468.8 | 4198118.4 | 0 | 3423142.5 | 823450 | 0 | 472230 | 7359500 | 336312 | 111446.4 | 0 | 37160268.6 | 62894399.52 | 0 | 23164032 | 0 | 23537908.8 | 953202.6 | 10798848 | 24109217 | 4572589.87 | 8420760 | 9149184 | 16519104 | 15901745.75 | 0 | 39648750.64 | 6724204.74 | 15229388.4 | 4780168.2 | 5652007.2 | 13785427.2 | 7818988 | 15999984 | 5237691.5 | 19753761.6 | 12092388 | 0 | 8500492.8 | 2606127.7 | 20565187.2 | 3902007.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65683635 | 0 | 3986196.48 | 0 | 3947472 | 51401245.5 | 0 | 0 | 5083142.4 | 14169600 | 2753651.25 | 3022880 | 1264008.94 | 7755916.8 | 0 | 0 | 0 | 2670773.43 | 3643779.15 | 10359685.76 | 3797794 | 2089673.28 | 5284645.56 | 2718108.23 | 2317684.95 | 0 | 0 | 131354.64 | 0 | 0 | 26248980 | 1806860 | 738150 | 0 | 0 | 0 | 76301788.86 | 0 | 0 | 4415782.44 | 0 | 8760239.73 | 11270246.4 | 0 | 15859771.2 | 29068776 | 15313875.9 | 0 | 557273.6 | 13783658.88 | 283643810 | 5392388.1 | 0 | 10496160 | 432946.8 | 5827464 | 13429662.54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 787494028.18 | 715429081.82 | 1502923110 | 109521712.36 | 65683635 | 55437280.37 | 62894399.52 | 603206338.18 | 309892790 | 761616 | 130248044.36 | 126263399.81 | 23152915.2 | 15860979.2 | 0 | 0
Yesterday Day Peak | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 360 | 317 |  | 0 | 450 | 0 | 50 | 96 | 15 | 315 | 0 | 180 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 17 | 19 | 19 | 25 | 15 | 8 | 0 | 80 | 35 | 118 | 0 | 8 | 214 | 0 | 0 | 0 |  | 6 | 24 | 34 | 46 | 0 | 6 | 10 | 2 | 0 | 0 | 0 | 305 | 240 | 200 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 23 | 43 | 7 | 11 | 25 | 15 | 146 | 33 | 0 | 16 | 2 | 30 | 0 | 42 | 43 | 112 | 0 | 0 | 78 | 0 | 181 | 17 | 0 | 9 | 280 | 16 | 8 | 0 | 105 | 63 | 0 | 67 | 0 | 71 | 13 | 37 | 71 | 6 | 386 | 24 | 35 | 51 | 5 | 121 | 17 | 55 | 0 | 27 | 38 | 350 | 50 | 42 | 54 | 34 | 0 | 35 | 34 | 59 | 0 | 230 | 17 | 0 | 275 | 0 | 150 |  | 913 | 0 | 130 | 0 | 16 | 120 | 0 | 0 | 10 | 22 | 8 | 130 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 21 | 0 | 38 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 143 | 0 | 336 | 35 | 0 | 50 | 50 | 34 | 0 | 7 | 35 | 1244 | 218 | 0 | 17 | 5 | 63 | 35 | 226 | 0 | 0 | 20 | 250 | 765 | 201 | 0 |  | 13198 | DayPeak
Yesterday Evening Peak | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 362 | 317 | 0 | 0 | 450 | 0 | 59 | 51 | 15 | 326 | 0 | 198 | 65 | 102 | 130 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 19 | 22 | 33 | 16 | 25 | 0 | 70 | 62 | 117 | 0 | 25 | 225 | 0 | 0 | 0 | 0 | 6 | 84 | 50 | 80 | 24 | 46 | 12 | 17 | 0 | 0 | 0 | 280 | 260 | 207 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 32 | 40 | 8 | 11 | 31 | 0 | 112 | 97 | 0 | 0 | 0 | 30 | 0 | 47 | 45 | 0 | 0 | 20 | 86 | 0 | 110 | 17 | 0 | 10 | 300 | 16 | 0 | 0 | 112 | 250 | 0 | 86 | 0 | 144 | 0 | 100 | 156 | 48 | 367 | 84 | 105 | 51 | 0 | 265 | 17 | 55 | 34 | 57 | 88 | 303 | 72 | 0 | 162 | 68 | 0 | 35 | 0 | 109 | 0 | 250 | 142 | 0 | 310 | 0 | 110 |  | 814 | 0 | 135 | 0 | 16 | 180 | 0 | 0 | 22 | 56 | 8 | 65 | 34 | 64 | 0 | 0 | 0 | 35 | 25 | 90 | 21 | 42 | 35 | 8 | 24 | 0 | 0 | 8 | 0 | 0 | 220 | 13 | 10 | 0 | 0 | 0 | 213 | 0 | 0 | 147 | 0 | 344 | 35 | 0 | 75 | 105 | 98 | 0 | 0 | 56 | 1244 | 220 | 0 | 150 | 0 | 0 | 114 | 234 | 0 | 0 | 0 | 150 | 774 | 0 | 0 |  | 14801 | EvPeak
Forecast for Evening | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 370 | 330 | 0 | 0 | 450 | 0 | 64 | 51 | 15 | 330 | 0 | 195 | 72 | 102 | 130 | 0 | 0 | 0 | 0 | 34 | 35 | 55 | 17 | 19 | 22 | 33 | 24 | 25 | 0 | 70 | 60 | 120 | 0 | 25 | 225 |  | 0 | 0 | 0 | 6 | 84 | 50 | 80 | 24 | 46 | 12 | 25 | 0 | 0 | 0 | 280 | 260 | 205 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 46 | 43 | 20 | 11 | 33 | 20 | 169 | 98 | 0 | 18 | 0 | 30 | 0 | 50 | 48 | 0 | 0 | 30 | 86 | 0 | 115 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 112 | 200 | 0 | 85 | 0 | 149 | 0 | 100 | 150 | 60 | 400 | 85 | 105 | 51 | 0 | 300 | 36 | 54 | 106 | 75 | 88 | 350 | 72 | 0 | 162 | 68 | 0 | 17 |  | 115 | 17 | 250 | 142 |  | 300 | 10 | 0 |  | 928 | 0 | 155 |  | 16 | 180 | 0 | 0 | 30 | 55 | 40 | 120 | 34 | 110 | 0 | 0 | 0 | 35 | 32 | 90 | 21 | 0 | 35 | 8 | 31 | 0 | 0 | 8 | 0 | 0 | 230 | 0 | 0 | 0 |  | 0 | 220 | 0 | 0 | 181 | 0 | 414 | 35 | 0 | 95 | 105 | 98 | 0 | 0 | 57 | 1244 | 220 |  | 150 |  |  | 113 | 234 |  | 0 |  | 0 | 750 |  | 0
Forecast for Day | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 370 | 320 | 0 | 0 | 450 | 0 | 50 | 17 | 15 | 330 | 0 | 195 | 50 | 50 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 70 | 60 | 120 | 0 | 8 | 220 |  | 0 | 0 | 0 | 6 | 40 | 50 | 46 | 0 | 6 | 12 | 5 | 0 | 0 | 0 | 280 | 260 | 200 | 0 | 0 | 5 | 0 | 0 | 43 | 0 | 44 | 43 | 20 | 11 | 25 | 20 | 146 | 50 | 0 | 18 | 1.6 | 30 | 0 | 50 | 48 | 0 | 0 | 20 | 80 | 0 | 110 | 17 | 0 | 10 | 300 | 24 | 11 | 0 | 112 | 0 | 0 | 68 | 0 | 70 | 20 | 50 | 51 | 6 | 400 | 24 | 35 | 51 | 5 | 120 | 36 | 54 | 0 | 27 | 38 | 350 | 53 | 50 | 54 | 34 | 0 | 17 | 35 | 72 | 17 | 250 | 17 |  | 450 | 20 | 150 |  | 928 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 20 | 40 | 32 | 120 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 21 | 0 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 160 | 0 | 414 | 35 | 0 | 50 | 50 | 34 | 0 | 8 | 35 | 1244 | 220 |  | 17 | 6 | 100 | 35 | 15 |  | 0 | 30 | 0 | 750 | 130 | 0 |  |  |  |  | g | h | o | c | h | t | s
Generation at 08:00(Today) | 0 | 0 | 210 | 180 | 0 | 12 | 0 | 397 | 331 | 0 | 0 | 450 | 0 | 44 | 17 | 15 | 327 | 0 | 186 | 33 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 19 | 33 | 16 | 8 | 0 | 70 | 60 | 118 | 0 | 8 | 221 | 0 | 0 | 0 | 0 | 6 | 34 | 50 | 46 | 0 | 6 | 12 | 8 | 0 | 0 | 0 | 300 | 260 | 166 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 37 | 43 | 19 | 11 | 25 | 17 | 120 | 44 | 0 | 16 | 1 | 30 | 0 | 42 | 46 | 0 | 0 | 20 | 72 | 0 | 112 | 17 | 0 | 10 | 305 | 24 | 5 | 0 | 112 | 0 | 0 | 68 | 0 | 35 | 5 | 25 | 34 | 5 | 385 | 19 | 35 | 51 | 1 | 88 | 17 | 55 | 34 | 9 | 38 | 380 | 40 | 27 | 17 | 34 | 0 | 17 | 18 | 17 | 17 | 250 | 17 | 0 | 352 | 26 | 150 | 0 | 911 | 0 | 155 | 0 | 16 | 120 | 0 | 0 | 10 | 20 | 8 | 132 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 214 | 0 | 0 | 152 | 0 | 394 | 36 | 0 | 50 | 15 | 34 | 0 | 3 | 56 | 1244 | 222 | 0 | 17 | 2 | 55 | 36 | 15 | 0 | 0 | 15 | 150 | 776 | 80 | 0 | 0 |  |  |  | 154.3902 | 21.7207 | 57.8071 | 51.1145 | 0.30738 | 3.5482 | 3.5023
292.3904
| Minimum Generation |  | 12165 | 9:00
| Highest Generation |  | 14801 | 21:00
| Day Peak Generation |  | 13198 | 12:00
| Evening Peak Generation |  | 14801 | 21:00
| HVDC Max Flow |  | 913 | 1:00
| HVDC EvPeak Flow |  | 814 | 21:00
| Load factor L.F |  | 89.51% | [164 empty] | 1275.5

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
DAILY REPORT
[7 empty] | Reporting Date : | 2023-08-01
Till now the maximum generation is : - |  |  |  | 15648 | 21:00 | Hrs on | 2023-04-19
The Summary of Yesterday's |  |  | 2023-07-31 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  |  | 13198 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 12246
Evening Peak Generation : |  |  | 14801 | MW Hour : | 21:00 | Available Max Generation : |  | 15307
E.P. Demand (at gen end) : |  |  | 0 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 15500
Maximum Generation : |  |  | 14801 | MW Hour : | 21:00 | Reserve(Generation end) |  | -
Total Gen. (MKWH) : |  |  | 317.9616 | System Load Factor : | 89.51% | Load Shed : |  | 178
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  |  | 390 | MW at | 22:00 | Energy
Import from West grid to East grid :- Maximum |  |  |  | - | MW at | - | Energy | -
|  | Water Level of Kaptai Lake at 6:00 A M on |  | 2023-08-01
Actual : |  | 79.93 | Ft.(MSL) , | Rule curve : | 89 | Ft.( MSL )
Gas Consumed : |  | Total = | 1124.55 | MMCFD. | Oil Consumed (PDB) :
HSD :
FO :
Cost of the Consumed Fuel (PDB+Pvt) : |  |  | Gas : | 164958992.73
: |  |  | Coal : | 309892790 | Oil : | 922612181.87 | Total : | 1397463964.6
Load Shedding & Other Information
Area |  | Yesterday |  |  |  | Today
|  |  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
|  | MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka |  | 40 | 960:00 | 5277.8352 |  |  | 55 | 1.042%
Chittagong Area |  | 0 | 0:00 | 1454.5136 |  |  | 22 | 1.513%
Khulna Area |  | 0 | 0:00 | 2038.779 |  |  | 22 | 1.079%
Rajshahi Area |  | 60 | 1440:00 | 1773.2563 |  |  | 18 | 1.015%
Cumilla Area |  | 40 | 960:00 | 1458.4679 |  |  | 18 | 1.234%
Mymensingh Area |  | 170 | 4080:00 | 1085.3681 |  |  | 15 | 1.382%
Sylhet Area |  | 0 | 0:00 | 607.7026 |  |  | 10 | 1.646%
Barisal Area |  | 0 | 0:00 | 507.0683 |  |  | 5 | 0.9861%
Rangpur Area |  | 90 | 2160:00 | 991.7224 |  |  | 13 | 1.311%
Total |  | 400 |  | 15194.7134 |  |  | 178
Information of the Generating Units under shut down.
|  | Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit- 1,2
2) Ghorasal-3,7
3) Shajibazar 330 MW
4) Baghabari-71,100 MW
5) Raozan unit-2
6) Siddhirganj 210 MW .
7) Shajibazar-9
Outage | Restore | Additional Information of Machines, lines, Interruption / Forced Load shed etc. | [5 empty] | Remark
Time | Time
| 08:13 | Feni 132/33kV S/S T-1(405T) HT is restored.
| 08:14 | Feni 132/33kV S/S T-1(405T) LT is restored.
| 08:16 | Goalpara 132/33kV S/S T-6 HT is restored.
| 08:17 | Goalpara 132/33kV S/S T-6 LT is restored.
08:18 | 09:10 | Shahjibazar 132/33kV S/S TR-04 LT Scheduled S/D Due to Red hot Maintenece work by Habiganj Pbs |  |  |  |  | 40.0MW load interrup.
08:20 | 09:07 | Shahjibazar 132/33kV S/S TR-04 HT Scheduled S/D Due to Red hot Maintenece work by Habiganj Pbs |  |  |  |  | 40.0MW load interrup.
08:38 | 11:25 | Meghnaghat -S.S. power Bashkhali 400 kV ckt was shutdown due to red hot maintenance work by Siemens
at Meghnaghat end.
| 08:45 | Chhatak 132/33kV S/S T-2 HT is restored.
| 08:46 | Chhatak 132/33kV S/S T-2 LT is restored.
09:02 |  | Khulna 330 MW CCPP GT was sync.
| 09:16 | Chandpur 132/33kV S/S 402T HT is restored.
| 09:16 | Chandpur 132/33kV S/S 402T LT is restored.
09:18 |  | Chandpur 132/33kV S/S 200KVA Aux. T-2 LT Scheduled S/D Due to Two station supply transformer LT side MCCB
will be stay close condition at a time. Between two station supply Transformer, Normally one station supply transformer
LT side MCCB will be stay open.
| 09:19 | Chandpur 132/33kV S/S 200KVA Aux. T-1 LT is restored.
09:44 |  | Kushiara 163MW tripped. |  |  |  |  | 110MW generation interrup.
10:08 | 13:55 | Gopalganj(N)-Madaripur 132kV Ckt-3 Project Work S/D from Gopalganj 400/132kV end. and from Madaripur
132/33 kV end Due to Teleprotection work
11:18 | 16:55 | Khulna (S)-Rampal Ckt-1 Scheduled S/D from Khulna(S) 230/132kV end Due to Due to protection test on Rample end
and from Rampal 400/230kV end Due to Remotely switching operation Check from NlDC
11:21 |  | Kushiara 163MW was sync.
12:00 |  | Day peak generation 13198 MW.
12:01 | 12:05 | Shahjibazar-Sreemangal 132kV Ckt-2 Tripped from Shahjibazar 132/33kV end showing Distance Relay relays. and
from Sreemongol 132/33kV end showing Distance Relay
12:30 |  | Kushiara 163MW tripped. |  |  |  |  | 80MW generation interrup.
13:40 |  | Sylhet CCPP 225 MW tripped due to GT flame failure. |  |  |  |  | 180MW generation interrup.
13:46 | 14:15 | Kabirpur - Manikganj 132kV Ckt-1 Forced S/D from Manikganj 132/33kV end Due to work at Kabirpur end
14:13 | 21:47 | Madaripur 132/33kV S/S Gopaganj North CKT-04 Project Work S/D Due to Project work
14:17 | 21:47 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 Project Work S/D
15:52 |  | Sylhet CCPP 225 GT was sync.
16:20 |  | Bhola CCPP GT2 tripped.
16:43 | 18:26 | Hathazari 230/132/33kV S/S T-01 HT Tripped showing Primary 132kV side-Micom relays Due to 33 kV Blue phase
XLPE Cable Punchured
20:14 | 20:58 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Forced S/D Due to For 33KV Bus DS high temperature maintenance. |  |  |  |  | 40.0MW load interrup.
20:56 | 21:30 | Bogura 132/33kV S/S Transformer-1 LT Tripped showing 50 relays Due to O/C |  |  |  |  | 20.0MW load interrup.
20:56 |  | Bogura 132/33kV S/S Transformer-2 LT Tripped showing o/c, E/F relays Due to o/C, E/F |  |  |  |  | 20.0MW load interrup.
20:56 |  | Bogura 132/33kV S/S Transformer-2 HT Tripped showing 50 relays Due to o/C, E/F |  |  |  |  | 80.0MW load interrup.
21:00 |  | Today's peak generation 14801 MW
21:27 | 22:37 | Shahjadpur 132/33kV S/S T-4(435T) HT Forced S/D Due to 33 kV incoming CT (B-Phase) Red-hot maintenance work. |  |  |  |  | 15.0MW load interrup.
21:27 | 22:39 | Shahjadpur 132/33kV S/S T-4(435T) LT Forced S/D Due to 33 kV Incoming CT (B-phase) Red-hot maintenance work. |  |  |  |  | 15.0MW load interrup.
21:46 | 22:20 | Ashuganj-Cumilla(N) 230 kV Ckt-2 Tripped from Cumilla(N) 230/132/33kV end showing Distance
protection B-Phase Earth fault protection Directional earth fault protection relays Due to None and from Ashuganj
230/132/33kV end showing Distance-B phase, V-fail relays.
| 21:47 | Gopalganj 400/132kV S/S 132kV Madaripur Ckt-4 is restored.
22:28 | 23:39 | Sirajganj 132/33kV S/S T2-(425) LT Forced S/D Due to Red Hot has become visible at 33kV BUS DS Y-phase CB |  |  |  |  | 15.0MW load interrup.
side of T-02 Transformer.
22:29 | 23:37 | Sirajganj 132/33kV S/S T2-(425) HT Forced S/D Due to Red Hot has become visible at 33kV BUS DS Y-phase CB
side of T-02 Transformer.
23:49 | 00:36 | Dohazari 132/33kV S/S Power Transformer -T-2 HT Forced S/D Due to SD taken by Keranihut 33KV feeder for Bus |  |  |  |  | 50.0MW load interrup.
DS high temperature maintenance.
06:08 |  | Dohazari-Sikalbaha 132 kV Ckt-2 Scheduled S/D from Dohazari 132/33kV end Due to Bus coupler Bay conductor
change. Doha-sik-01 is on duty. and from Shikalbaha 230/132kV end Due to Maintenance at Dohazari S/S End
07:00 |  | Min. Gen. 12246 MW.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2023-07-31 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 210 | 4987094
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108 MW PP (Regent) |  | IPP | 34*3.35 | 108 | 12 | 301090 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 362 | 8759300 | Machine problem
7 | Haripur 360 MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 317 | 7806000 | Machine problem
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 450 | 10114500
9 | Meghnaghat 100 MW(IEL) |  | NENP | 12*8.9 | 100 | 59 | 1210560 | Fuel shortage
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 335 | 0 | 0 | Under maint.
11 | Madanganj 102 PP(Summit) |  | NENP | 6*17 | 102 | 51 | 1676676 | Engine problem
12 | Madanganj-55 MW PP(Summit) |  | IPP | 3*17.08+1*11.3 | 55 | 15 | 380041 | Fuel shortage
13 | Keraniganj 100 MW PP (Powerpac) |  | NENP | 8*13.45 | 75 | 0 | 0 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 320796 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 198 | 4448000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | NENP | 12*8.9 | 100 | 65 | 1104960 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7663603
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1203696
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 0 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 387360 | Fuel shortage
22 | Kodda 150 MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 130 | 1782720 | Engine problem
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 532617 | Fuel shortage
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 532716
25 | Bosila 108 MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 0 | 0 | 0
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 41 | 851280 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 664200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 432500 | Engine problem
29 | Gazipur 52 MW PP |  | RPCL | 6*8.9 | 52 | 25 | 238522 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 112 | 2722364 | Fuel shortage
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 250 | 3000687
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 114*0.959 | 0 | 0 | 0 | Contract Expired
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | Contract Expired
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 8*18.45+8.97 | 149 | 144 | 1699488
36 | Gazipur 100 MW PP |  | RPCL | 6*17.5 | 105 | 105 | 1142400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1235520 | Fuel shortage
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1556640
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 218086
40 | Kanchan Purbachal Power Generation Ltd. |  | IPP | 18.4*3 | 55 | 0 | 296280 | Fuel shortage
| Dhaka area Total |  |  |  | 5722 | 3562 | 71553696
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 117 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | RPCL | 3*8.9 | 25 | 25 | 271168
43 | Teknaf 20MW PP (Solartech) |  | IPP | 20 | 20 | 0 | 81540
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 444480 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 132 | 2820800
46 | Sikalbaha 225MW |  | PDB | 1*150+1*75 | 225 | 225 | 5426131
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 6*17.5 | 105 | 51 | 1257055 | Fuel shortage
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 84 | 1224592
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 50 | 1075660 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | NENP | 8*13.45 | 100 | 80 | 1172040 | Fuel shortage
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 8*13.5 | 100 | 100 | 1046400
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 12 | 266832 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 17 | 452640
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 24 | 159360 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30121
56 | Anwara 300 MW PP (United) |  | IPP | 17*17+24 | 300 | 265 | 3377236 | Fuel shortage
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 617466 | Fuel shortage
58 | Karnaphuli Power Ltd. |  | IPP | 18.415*6+6.5 | 110 | 55 | 1432680 | Fuel shortage
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 88 | 1170240 | Fuel shortage
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 68 | 1062600 | Fuel shortage
| Mirsharai 150 MW |  | BPDB-RPCL | 18.5*9 | 163 | 142 | 935054 | Fuel shortage
| SS Power I |  | SS Power | 0 | 0 | 310 | 5716363 | On test.
| Cox's Bazar Wind |  | IPP | 66 | 0 | 0 | 45600 | On test.
| Matarbari 2*600 MW (CPGCL) |  | CPGCL | 0 | 0 | 110 | 3003636 | On test.
| Chattogram area Total |  |  |  | 2545 | 2018 | 35789694
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 0 | 0 | 0 | Contract Expired
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 207 | 4546000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7634300 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6113000 | Gas shortage
| Ashuganj 420 MW CCPP(East) |  | APSCL | 284*1+116*1 | 400 | 250 | 6245700 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 0 | 43560 | Gas shortage
66 | Ashuganj 55 MW PP (Precision) |  | QRPP | 15*4 | 0 | 0 | 0 | Contract Expired
67 | Ashuganj 195 MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 0 | 0 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 939968 | Engine problem
69 | Ashuganj 150 MW PP (Midland) |  | IPP | 23*7.015 | 150 | 48 | 344581 | Fuel shortage
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 32 | 874480 | Machine problem
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint.
72 | Chandpur 200 MW (Desh energy) |  | IPP | 12*18.4 | 200 | 156 | 1764950 | Fuel shortage
73 | Feni 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 8 | 259092
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 194040
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 112 | 3224640 | Restriction by India
75 | Jangalia 33 MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 31 | 742200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 40 | 971309 | Fuel shortage
77 | Cumilla 25 MW PP (Summit) |  | SIPP, REB | 3*3.67+2*6.97 | 25 | 0 | 355990 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Contract Expired
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 352260 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 57 | 438480 | Fuel shortage
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 650880 | Fuel shortage
82 | Chandpur 115(Doreen) |  | IPP | 4*18.5+2*22.5 | 115 | 109 | 1373760
| Cumilla Area Total |  |  |  | 3096 | 1713 | 37069190
83 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 97 | 1486080 | Gas shortage
84 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 238428 | Engine problem
85 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 0 | 0 | 0 | Under maint.
86 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15450
87 | Mymensingh 200 MW PP (United) |  | IPP | 9.78*21 | 200 | 86 | 1718400 | Fuel shortage
88 | Jamalpur 115 MW PP (United) |  | IPP | 9.78*12 | 115 | 84 | 752400 | Fuel shortage
89 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 362470
90 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 6 | 129120 | Fuel shortage
| Mymensingh Area Total |  |  |  | 614 | 273 | 4702348
91 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 706000 | Machine problem
92 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
93 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 1132854 | under maint
94 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 0 | 0 | Under maint.
95 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1088400
| Fenchuganj 44 MW (Energyprima) |  | NENP | 12*3.3+5*2 | 50 | 45 | 1075968
96 | Hobiganj 11 MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 146640
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 359520
98 | Shahjibazar 86 MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 86 | 1841280
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 110 | 3389250 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 383000
| Sylhet 50 MW PP (EPL) |  | NENP | 27*2 | 0 | 0 | 0 | Contract Expired
102 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 448416
103 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7359500 | FGMO
104 | Bibiyana-III 400 MW CCPP |  | PDB | 285*1+134*1 | 400 | 367 | 9153000 | FGMO
105 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238500
106 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 303 | 8498900
| Sylhet Area Total |  |  |  | 2427 | 1351 | 35821228
107 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Fuel shortage
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 814 | 21894545
108 | Khulna 115 PP MW (KPCL-2) |  | NENP | 7*17 | 115 | 16 | 379200 | Fuel shortage
109 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 22 | 282240 | Engine problem
110 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 3115227 | Fuel shortage
111 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 56 | 787200 | Engine problem
112 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 135 | 3559104 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | NENP | 5*8.5 | 40 | 8 | 191625 | Fuel shortage
113 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 0 | 0 | 0 | Contract Expired
114 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 838560 | Fuel shortage
115 | Madhumati 100 MW PP |  | NWPGCL | 6*18 | 105 | 105 | 2011680
116 | Mongla Orion 100 MW Solar PP |  | IPP | 100 | 100 | 0 | 496800
| Khulna 330 MW CCPP (OIL) |  | BPDB | 1*220+1*110 | 220 | 234 | 2187676
| Rampal 1320 MW (BIFPCL) |  | NTPC&BPDB | 660*2 | 617 | 0 | 0 | Coal shortage.
| Kulna 225 MW CCPP (GAS) |  | NWPGCL | 0 | 0 | 0 | 0 | On test.
| Khulna Area Total |  |  |  | 3121 | 1605 | 35743857
117 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 711552 | High voltage
118 | Bhola 33 MW PP (Venture) |  | NENP | 1*34.50 | 40 | 34 | 651551 | Engine problem
119 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 2699000 | Machine problem
120 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 0 | 0 | 0 | Contract Expired
121 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 1244 | 31481000
122 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5286655
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1418400
| Barisal 307 MW |  | IPP | 307*1 | 307 | 150 | 5695000 | Coal shortage.
| Barisal Area Total |  |  |  | 2265 | 1927 | 47943158
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 35 | 159259 | Engine problem
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 25 | 208335 | Fuel shortage
127 | Amnura 50 MW PP(Sinha) |  | NENP | 7*7.79 | 28 | 21 | 493220 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 42 | 126188 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 312516 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 213 | 4370091
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 147 | 3806709 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 344 | 8848727 | Gas shortage
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 24 | 137385 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 0 | 0 | 0 | Contract Expired
136 | Bogura 20 MW PP (Energyprima) |  | NENP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 173520 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 199421
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 662384 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 135*1.6 | 200 | 0 | 0 | Fuel conservation
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 6*18.55+7.2 | 113 | 75 | 1340640 | Fuel shortage
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 56 | 1135392 | Fuel shortage
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38280
| Adani Power Jharkhanda Ltd |  | Import | 748*2 | 1496 | 774 | 18418910
| Rajshahi Area Total |  |  |  | 3631 | 1897 | 40430977
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 220 | 4962000 | Machine problem
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 13 | 43000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 10 | 21000
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 9*6.984+7*7.015+3.15*2 | 113 | 98 | 1205817 | Fuel shortage
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50432
150 | Energypac Power Venture Thakurgaon Ltd. |  | IPP | 115 | 115 | 114 | 876038
| Intraco Solar 30 MW |  | IPP | 1*30 | 30 | 0 | 210442
| Teesta Solar Limited |  | BPCL | 16*12.5 | 0 | 0 | 1538750
| Rangpur Area Total |  |  |  | 750 | 455 | 8907479
| Total |  |  |  | 24171 | 14801 | 317961627
| Eastern Grid Total |  |  |  | 14404 | 8917 | 184936156
| Western Grid Total |  |  |  | 9767 | 5884 | 133025471
| National Grid Total |  |  |  | 24171 | 14801 | 317961627
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
| Date: | 2023-07-31
| (a) ENTIRE EASTERN GRID : |  | 9089.98 | MW | (b) ENTIRE WESTERN GRID : |  | 4901 | MW
| i) Dhaka area |  | 4895.98 | MW | i) Khulna area |  | 1868 | MW
| ii) Chittagong area |  | 1484 | MW | ii) Rajshahi area |  | 1515 | MW
| iii) Comilla area |  | 1054 | MW | iii) Barisal area |  | 474 | MW
| iv) Mymensingh area |  | 1118 | MW | iv) Rangpur area |  | 1044 | MW
| v) Sylhet area |  | 538 | MW
|  | SYSTEM TOTAL DEMAND ( a + b ) = |  | 13990.98 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
| Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time | Sub-station | Load (MW) | Time
1 | AKS | 18 | 00:00 | Chhatak | 38 | 21:00 | Kamrangirchar | 57.3 | 13:00 | Natore | 163 | 21:00 | Sholosohor | 41 | 19:30
2 | AKSML | 98 | 15:00 | Chowmuhani | 220 | 22:00 | Kaptai | N/A | N/A | Nawabganj | 53.1 | 22:00 | Shyampur | 120 | 00:00
3 | Aftabnagar | 40 | 00:00 | Chuadanga | 120 | 20:00 | Kazla | 108 | 17:00 | Netrakona | 127 | 21:00 | Siddhirganj | 124 | 15:00
4 | Agargaon | 108 | 13:00 | Coxsbazar | 127 | 18:30 | Keranigonj | 80 | 00:00 | New | 91.4 | 12:00 | Sirajganj | 124 | 19:00
5 | Agrabad | 82 | 17:00 | Cumilla(N) | 190 | 19:30 | Khagrachori | 32 | 22:00 | Niamatpur | 104 | 21:00 | Sonargaon | 82 | 12:00
6 | Amnura | 74 | 21:00 | Cumilla(S) | 168 | 19:00 | Khulna | 103 | 20:00 | Noapara | 44 | 19:30 | Sreemongol | 65 | 00:00
7 | Ashuganj | 80 | 21:00 | Daudkandi | 163 | 20:00 | Khulshi | 199 | 19:00 | PHP | 8 | 19:30 | Sreepur | 80 | 21:00
8 | BIPTC | N/A | N/A | Dhaka | 36 | 13:00 | Kishoreganj | 128 | 21:00 | Pabna | 135 | 21:00 | Srinagar | 46.2 | 19:00
9 | BSRM | 169 | 21:00 | Dhamrai | 124 | 21:00 | Kodda | 274 | 21:00 | Palashbari | 145 | 21:00 | Sunamganj | 46 | 19:30
10 | Bagerhat | 94 | 22:00 | Dhanmondi | 182 | 13:00 | Kulaura | 56 | 21:00 | Panchagarh | 63 | 21:00 | Sylhet | 154 | 20:00
11 | Bakulia | 111 | 14:00 | Dohazari | 94 | 19:00 | Kurigram | 70 | 20:00 | Patuakhali | 114 | 22:00 | TK | 32.5 | 20:00
12 | Banani | 54 | 11:00 | Faridpur | 176 | 22:00 | Kushtia | 156 | 20:00 | Payra | 20 | 05:00 | Tangail | 220 | 20:00
13 | Bangabhaban | 23 | 10:00 | Fatullah | 69 | 11:00 | Lalbag | 83 | 17:00 | Postogola | 66 | 00:00 | Thakurgaon | 100 | 19:00
14 | Barapukuria | 70 | 19:30 | Fenchuganj | 48 | 21:00 | Lalmonirhat | 54 | 20:00 | Purbachal | 24 | 00:00 | Tongi | 120 | 18:30
15 | Barguna | 22 | 22:00 | Feni | 125 | 21:00 | Madanganj | 42 | 19:00 | Purbasadipur | 142 | 21:00 | Ullon | 46 | 01:00
16 | Barishal | 107 | 21:00 | GPH | 87 | 19:00 | Madaripur | 116 | 21:00 | Rahim | 47 | 00:00 | Uttara | 89 | 16:00
17 | Barishal-230 | 106 | 21:00 | Ghorashal | 71 | 21:00 | Madartek | 102.33 | 00:00 | Rajbari | 82 | 20:00 | UttaraNew | 76 | 15:00
18 | Baroaulia | 69 | 11:00 | Goalpara | 36 | 00:00 | Madunaghat | 59 | 20:00 | Rajendrapur | 104 | 21:00 | Zigatola | 100 | 14:00
19 | Baroirhat | 60 | 22:00 | Gollamari | 55 | 13:00 | Magura | 66 | 20:00 | Rajshahi | 190 | 21:00
20 | Bashundhara | 181 | 13:00 | Gopalganj | 115 | 21:00 | Mahasthangarh | 88 | 23:00 | Rajshahi-230 | 44 | 22:00
21 | BashundharaCement | 0 | 00:00 | Gulshan | 156 | 13:00 | Manikganj | 120 | 22:00 | Ramganj | 110 | 22:00
22 | Beanibazar | 86 | 21:00 | Halishahar | 89.5 | 14:00 | Maniknagar | 108 | 13:00 | Rampur | 33 | 00:00
23 | Benapole | 78 | 21:00 | HaripurSBU | 153 | 19:30 | Matarbari | 48 | 21:00 | Rangamati | 18 | 19:00
24 | Bhaluka | 122 | 21:00 | Hasnabad | 95 | 00:00 | Matuail | 72 | 10:00 | Rangpur | 172 | 20:00
25 | Bhandaria | 54 | 22:00 | Hathazari | 81 | 21:00 | Millgate | 106 | 11:00 | Ruppur | 6 | 11:00
26 | Bhangura | 38 | 19:30 | Ishurdi | 80 | 21:00 | Mirpur | 149 | 15:00 | SSM | 14 | 12:00
27 | Bheramara(GK) | 69 | 22:00 | Jaldhaka | 89 | 22:00 | Mirsorai | 6 | 15:00 | Saidpur | 113 | 21:00
28 | Bhulta | 232 | 00:00 | Jamalpur | 151 | 21:00 | Mithapukur | 48 | 20:00 | Satkhira | 135 | 21:00
29 | Bog-Sherpur | 82 | 23:00 | Jashore | 149 | 23:00 | Modern | 0 | 00:00 | Satmasjid | 115 | 00:00
30 | Bogura | 181 | 19:00 | Jhenaidah | 147 | 21:00 | Mogbazar | 154.9 | 15:00 | Savar | 198 | 19:30
31 | Borhanuddin | 63 | 21:00 | Joydebpur | 184 | 20:00 | Mongla | 24 | 00:00 | Shahjadpur | 113 | 20:00
32 | Brahmanbaria | 145 | 22:00 | Joypurhat | 72 | 14:00 | Motijheel | 46 | 16:00 | Shahjibazar | 110 | 19:30
33 | Cantonment | 168 | 13:00 | Juldah | 22 | 09:00 | Munshiganj | 105 | 19:00 | Shahmirpur | 49 | 00:00
34 | Chandpur | 71 | 20:00 | KSRM | 37 | 16:00 | Mymensingh | 240 | 19:00 | Shariatpur | 77 | 23:00
35 | Chandraghona | 34 | 19:00 | Kabirpur | 291 | 18:30 | Naogaon | 148 | 23:00 | Sherpur | 136 | 21:00
36 | Chapai | 84 | 21:00 | Kachua | 84 | 19:30 | Narail | 63 | 22:00 | Shikalbaha | 35 | 19:30
37 | Charsaidpur | 48 | 11:00 | Kallyanpur | 123 | 00:00 | Narinda | 82 | 13:00 | Shikalbaha-230 | N/A | N/A
38 | Chauddagram | 64 | 23:00 | Kalurghat | 34 | 18:00 | Narshingdi | 163 | 19:30 | Shitalakhya | 109.6 | 16:00
| Sub Divisional Engineer |  |  |  | Executive Engineer |  |  |  | Superintendent Engineer
| Network Operation Division |  |  |  | Network Operation Division |  |  |  | Load Despatch Circle
| (1) Honbl. State Minister |  |  |  | (8) Executive Director (O & M) PGCB. |  |  |  | (18) C.E. Transmission (1 & 2) PGCB.
| Ministry of Power,Energy & Mineral |  |  |  | (9) Member,Generation,PDB. |  |  |  | (19) S.E. System Protection,PGCB.
| Resources, GOB. |  |  |  | (10) Member,Distribution,PDB. |  |  |  | (20) Director,Public Relation,PDB.
| (2) Secy (Power Divn.)Ministry of |  |  |  | (11) Member,Transmission & |  |  |  | (21) Director Program, PDB.
| Power,Energy & Mineral Resources. |  |  |  | System Operation,PDB. |  |  |  | (22) S.E. Consumer Affairs,PDB.
| (3) Director General,Power cell |  |  |  | (12) Member,P&D,PDB. |  |  |  | (23) Director,Project Planning,PDB.
| (4) Chairman,BERC |  |  |  | (13) C.E (P & D), PGCB. |  |  |  | (24) Director,System Planning,PDB.
| (5) Chairman, BPDB. |  |  |  | (14) G.M. Commercial Operation |  |  |  | (25) Executive Eng.IMD.
| (6) Managing Director, PGCB. |  |  |  | (15) C.E. Generation,PDB. |  |  |  | (26) Executive Eng. EMD.
| (7) Member(Power & Industry) |  |  |  | (16) C.E, (P & D),PDB. |  |  |  | (27) NLDC
| Planning Commission. |  |  |  | (17) C.E. System Operation,PGCB

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2023-07-31 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV | Hour | 400 KV | KV | Hour | KV | Hour
14 | Aminbazar | 396 | 03:00 | 386 | 12:00 | Gopalganj | 403 | 02:00 | 394 | 12:00
| Ashuganj | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Bhulta | 396 | 21:00 | 386 | 12:00 | Madunaghat_I | 390 | 21:00 | 382 | 10:00
| Bibiana | 403 | 05:00 | 395 | 17:00 | Payra | 409 | 02:00 | 405 | 11:00
| BIPTC | 399 | 06:00 | 390 | 15:00 | Rampal | 405 | 02:00 | 394 | 19:00
| Bogura | N/A | N/A | N/A | N/A
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Agargaon | 231 | 03:00 | 223 | 12:00 | Hasnabad | 230 | 03:00 | 223 | 12:00
| AKSML | 236 | 19:30 | 226 | 10:00 | Hathazari | 234 | 21:00 | 226 | 09:00
| Aminbazar | 233 | 00:00 | 225 | 11:00 | Ishurdi | 234 | 17:00 | 224 | 19:00
| Ashuganj | 233 | 22:00 | 228 | 12:00 | Jhenaidah | 227 | 09:00 | 216 | 18:30
| Ashuganj-400 | N/A | N/A | N/A | N/A | Kaliakoir | N/A | N/A | N/A | N/A
| Baghabari | 229 | 10:00 | 224 | 19:00 | Keranigonj | 230 | 04:00 | 222 | 12:00
| Barapukuria | 219 | 09:00 | 205 | 19:00 | Khulna(S) | 233 | 02:00 | 226 | 17:00
| Barapukuria-230 | N/A | N/A | N/A | N/A | Madunaghat_I | 234 | 19:00 | 228 | 10:00
| Barishal | 238 | 18:30 | 231 | 21:00 | Maniknagar | 231 | 07:00 | 223 | 12:00
| Bheramara | 231 | 09:00 | 222 | 19:00 | Meghnaghat | 239 | 21:00 | 231 | 13:00
| Bhulta | 234 | 07:00 | 226 | 12:00 | Mirsorai | 234 | 21:00 | 224 | 12:00
| Bibiana | 232 | 06:00 | 224 | 21:00 | Rajshahi | 229 | 17:00 | 218 | 19:00
| BIPTC | 233 | 09:00 | 220 | 01:00 | Rampal | 232 | 02:00 | 225 | 19:00
| Bogura | 226 | 09:00 | 217 | 21:00 | Rampur | N/A | N/A | N/A | N/A
| Borhanuddin | 240 | 09:00 | 237 | 04:00 | Rampura | 233 | 22:00 | 224 | 12:00
| BSRM | 234 | 20:00 | 224 | 10:00 | Shikalbaha | 234 | 21:00 | 225 | 15:00
| Cumilla(N) | 232 | 21:00 | 225 | 12:00 | Shyampur | 230 | 03:00 | 223 | 12:00
| Fenchuganj | 236 | 00:00 | 228 | 15:00 | Siddhirganj | 233 | 05:00 | 230 | 18:00
| Ghorashal | 232 | 16:00 | 230 | 00:00 | Sirajgonj | 236 | 09:00 | 231 | 19:00
| Ghorashal-230 | N/A | N/A | N/A | N/A | Sreepur | 230 | 09:00 | 225 | 19:00
| GPH | 233 | 19:00 | 224 | 10:00 | Tongi | 230 | 06:00 | 222 | 12:00
| Haripur | 233 | 21:00 | 225 | 12:00
| 132 kV | KV |  | KV |  | Tongi | KV |  | KV
| Aftabnagar | 135 | 03:00 | 127 | 12:00 | Lalbag | 134 | 03:00 | 128 | 12:00
| Agargaon | 132 | 03:00 | 125 | 12:00 | Lalmonirhat | 127 | 09:00 | 112 | 23:00
| Agrabad | 137 | 19:00 | 131 | 09:00 | Madanganj | 135 | 21:00 | 129 | 12:00
| AKS | 134 | 19:30 | 128 | 10:00 | Madaripur | 131 | 17:00 | 127 | 19:00
| Aminbazar | 134 | 00:00 | 129 | 11:00 | Madartek | 134 | 04:00 | 126 | 12:00
| Amnura | 137 | 00:00 | 122 | 22:00 | Madunaghat | 140 | 19:00 | 132 | 14:00
| Ashuganj | 139 | 21:00 | 136 | 13:00 | Magura | 135 | 00:00 | 126 | 20:00
| Bagerhat | 135 | 02:00 | 129 | 22:00 | Mahasthangarh | 130 | 09:00 | 120 | 19:00
| Bakulia | 141 | 21:00 | 135 | 10:00 | Manikganj | 134 | 22:00 | 126 | 12:00
| Banani | 135 | 22:00 | 126 | 12:00 | Maniknagar | 134 | 22:00 | 127 | 12:00
| Bangabhaban | 134 | 03:00 | 126 | 12:00 | Matarbari | 132 | 17:00 | 120 | 22:00
| Barapukuria | 135 | 09:00 | 123 | 19:30 | Matuail | 136 | 22:00 | 129.4 | 12:00
| Barguna | 137 | 00:00 | 131 | 03:00 | Millgate | 135 | 06:00 | 127 | 12:00
| Barishal | 136 | 00:00 | 130 | 06:00 | Mirpur | 132 | 00:00 | 126 | 12:00
| Barishal-230 | 136 | 18:00 | 132 | 01:00 | Mithapukur | 130 | 09:00 | 116 | 23:00
| Baroaulia | 138 | 21:00 | 130 | 14:00 | Modern | 137 | 21:00 | 131 | 14:00
| Baroirhat | 132 | 18:30 | 125 | 00:00 | Mogbazar | 135 | 01:00 | 127 | 12:00
| Bashundhara | 135 | 05:00 | 125 | 15:00 | Mongla | 135 | 08:00 | 129 | 20:00
| BashundharaCement | 135 | 21:00 | 129 | 12:00 | Motijheel | 134 | 03:00 | 126 | 12:00
| Beanibazar | 128 | 06:00 | 120 | 21:00 | Munshiganj | 136 | 21:00 | 129 | 15:00
| Benapole | 135 | 02:00 | 125 | 20:00 | Mymensingh | 130 | 18:30 | 115 | 19:00
| Bhaluka | 125 | 06:00 | 120 | 13:00 | Naogaon | 125 | 09:00 | 109 | 23:00
| Bhandaria | 134 | 14:00 | 125 | 03:00 | Narail | 137 | 02:00 | 123 | 19:00
| Bhangura | 135 | 00:00 | 130 | 19:00 | Narinda | 0 | 00:00 | N/A | N/A
| Bheramara | 133 | 00:00 | 129 | 19:00 | Narshingdi | 131 | 22:00 | 123 | 11:00
| Bheramara(GK) | 134 | 01:00 | 129 | 19:00 | Natore | 133 | 16:00 | 125 | 19:00
| Bhulta | 127 | 22:00 | 120 | 00:00 | Nawabganj | 135 | 07:00 | 129 | 12:00
| Bog-Sherpur | 132 | 11:00 | 124 | 19:00 | Netrakona | 129 | 18:30 | 116 | 17:00
| Bogura | 134 | 14:00 | 125 | 23:00 | New | 135 | 03:00 | 128 | 12:00
| Bogura-230 | 134 | 16:00 | 125 | 23:00 | Niamatpur | 122 | 09:00 | 101 | 23:00
| Brahmanbaria | 127 | 08:00 | 121 | 12:00 | Noapara | 137 | 02:00 | 130 | 20:00
| Cantonment | 132 | 03:00 | 125 | 12:00 | Pabna | 132 | 00:00 | 126 | 19:00
| Chandpur | 138 | 21:00 | 118 | 08:00 | Palashbari | 128 | 09:00 | 114 | 22:00
| Chandraghona | 138 | 00:00 | 133 | 10:00 | Panchagarh | 131 | 00:00 | 112 | 23:00
| Chapai | 130 | 18:30 | 124 | 22:00 | Patuakhali | 139 | 21:00 | 134 | 02:00
| Charsaidpur | 137 | 21:00 | 130 | 12:00 | Payra | 139 | 00:00 | 136 | 12:00
| Chauddagram | 133 | 19:00 | 124 | 06:00 | PHP | 132 | 21:00 | 122 | 05:00
| Chhatak | 128 | 01:00 | 120 | 14:00 | Postogola | 137 | 21:00 | 130 | 12:00
| Chowmuhani | 130 | 18:30 | 120 | 23:00 | Purbachal | 136 | 05:00 | 126 | 12:00
| Chuadanga | 131 | 17:00 | 117 | 20:00 | Purbasadipur | 127 | 00:00 | 110 | 19:00
| Coxsbazar | 125 | 00:00 | 119 | 18:00 | Rahim | 136 | 21:00 | 130 | 11:00
| Cumilla(N) | 136 | 21:00 | 128 | 05:00 | Rajbari | 127 | 00:00 | 122 | 20:00
| Cumilla(S) | 137 | 21:00 | 122 | 15:00 | Rajendrapur | 135 | 19:30 | 128 | 02:00
| Daudkandi | 138 | 21:00 | 127 | 08:00 | Rajshahi | 133 | 09:00 | 128 | 18:30
| Dhaka | 135 | 07:00 | 127 | 12:00 | Rajshahi-230 | 136 | 17:00 | 126 | 01:00
| Dhamrai | 135 | 04:00 | 129 | 18:00 | Ramganj | 131 | 21:00 | 118 | 00:00
| Dhanmondi | 136 | 22:00 | 128 | 12:00 | Rampur | 137 | 19:30 | 132 | 09:00
| Dohazari | 138 | 17:00 | 129 | 18:00 | Rampura | 135 | 05:00 | 127 | 12:00
| Faridpur | 128 | 01:00 | 124 | 20:00 | Rangamati | 138 | 17:00 | 132 | 10:00
| Fatullah | 131 | 22:00 | 125 | 12:00 | Rangpur | 129 | 09:00 | 113 | 19:00
| Fenchuganj | 133 | 07:00 | 128 | 15:00 | Ruppur | 135 | 17:00 | 130 | 19:30
| Feni | 132 | 18:30 | 123 | 03:00 | Saidpur | 128 | 16:00 | 114 | 23:00
| Ghorashal | 139 | 01:00 | 135 | 14:00 | Satkhira | 136 | 17:00 | 127 | 20:00
| Goalpara | 139 | 09:00 | 133 | 20:00 | Satmasjid | 132 | 04:00 | 125 | 12:00
| Gollamari | 137 | 17:00 | 132 | 20:00 | Savar | 134 | 22:00 | 127 | 12:00
| Gopalganj | 134 | 00:00 | 130 | 10:00 | Shahjadpur | 139 | 17:00 | 133 | 19:00
| Gopalganj-400 | 129 | 00:00 | 127 | 10:00 | Shahjibazar | 129 | 16:00 | 122 | 12:00
| Gulshan | 134 | 01:00 | 126 | 12:00 | Shahmirpur | 140 | 19:00 | 133 | 10:00
| Halishahar | 138 | 19:00 | 131 | 10:00 | Shariatpur | 130 | 17:00 | 126 | 16:00
| Haripur | 136 | 21:00 | 130 | 11:00 | Sherpur | 127 | 18:30 | 112 | 07:00
| HaripurSBU | 136 | 21:00 | 130 | 11:00 | Shikalbaha | 129 | 20:00 | 123 | 10:00
| Hasnabad | 136 | 21:00 | 131 | 10:00 | Shikalbaha-230 | 141 | 19:30 | 135 | 15:00
| Hathazari | 138 | 00:00 | 133 | 09:00 | Shitalakhya | 137 | 22:00 | 129.4 | 15:00
| Ishurdi | 135 | 17:00 | 129 | 19:00 | Sholosohor | 137 | 17:00 | 131 | 10:00
| Jaldhaka | 127 | 09:00 | 110 | 23:00 | Shyampur | 130 | 21:00 | 125 | 01:00
| Jamalpur | 131 | 19:30 | 114 | 17:00 | Shyampur-230 | 130 | 03:00 | 125 | 12:00
| Jashore | 136 | 02:00 | 127 | 19:00 | Siddhirganj | 135 | 22:00 | 130 | 12:00
| Jhenaidah | 137 | 00:00 | 128 | 20:00 | Sirajganj | 132 | 00:00 | 125 | 19:00
| Jhenaidah-230 | 138 | 01:00 | 129 | 20:00 | Sonargaon | 138 | 21:00 | 131 | 00:00
| Joydebpur | 138 | 09:00 | 129 | 16:00 | Sreemongol | 131 | 09:00 | 126 | 01:00
| Joypurhat | 121 | 05:00 | 105 | 23:00 | Sreepur | 128 | 04:00 | 125 | 19:00
| Juldah | 142 | 21:00 | 133 | 10:00 | Srinagar | 134 | 02:00 | 128 | 12:00
| Kabirpur | 136 | 09:00 | 124 | 12:00 | SSM | 142 | 21:00 | 135 | 10:00
| Kachua | 136 | 21:00 | 119 | 00:00 | Sunamganj | 127 | 09:00 | 120 | 14:00
| Kaliakoir | N/A | N/A | N/A | N/A | Sylhet | 130 | 00:00 | 124 | 15:00
| Kallyanpur | 128 | 03:00 | 123 | 12:00 | Tangail | 132 | 00:00 | 121 | 21:00
| Kalurghat | 138 | 17:00 | 132 | 10:00 | Thakurgaon | 126 | 00:00 | 111 | 7:00
| Kamrangirchar | 136 | 04:00 | 121 | 12:00 | TK | 139 | 19:30 | 133 | 06:00
| Kaptai | N/A | N/A | N/A | N/A | Tongi | 136 | 01:00 | 130 | 12:00
| Kazla | 134 | 22:00 | 126 | 13:00 | Ullon | 135 | 03:00 | 127 | 12:00
| Keranigonj | 135 | 06:00 | 129 | 12:00 | Uttara | 133 | 22:00 | 126 | 12:00
| Khagrachori | 138 | 19:30 | 131 | 10:00 | UttaraNew | 132 | 00:00 | 126 | 12:00
| Khulna | 138 | 02:00 | 132 | 20:00 | Zigatola | 134 | 03:00 | 129 | 12:00
| Khulna(S) | 138 | 09:00 | 133 | 19:00
| Khulshi | 136 | 19:00 | 130 | 14:00
| Kishoreganj | 130 | 06:00 | 125 | 13:00
| Kodda | 138 | 22:00 | 126 | 12:00
| KSRM | 138 | 19:00 | 132 | 14:00
| Kulaura | 132 | 09:00 | 127 | 15:00
| Kurigram | 128 | 09:00 | 112 | 22:00
| Kushtia | 134 | 02:00 | 127 | 20:00

## L-Curve
Date | 2023-07-31
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 770 | 8113 | 5466 | 13579 |  |  |  | QF-LDC-11
0:30 | 783 | 7824 | 5415 | 13239 | Date: | 2023-07-31
1:00 | 796 | 7535 | 5364 | 12899
1:30 | 781 | 7521 | 5283 | 12804
2:00 | 766 | 7507 | 5202 | 12709
2:30 | 753 | 7487.5 | 5174 | 12661.5 | [5 empty] | Gen. at Eve. Peak | 14801 | 14801 MW (21:00 )
3:00 | 740 | 7468 | 5146 | 12614 | [6 empty] | 21:00
3:30 | 720 | 7493.5 | 5145 | 12638.5 | [5 empty] | Gen. at Day Peak | 13198 | 13198 MW (12:00 )
4:00 | 700 | 7519 | 5144 | 12663 | [6 empty] | 12:00
4:30 | 685 | 7468.5 | 5150 | 12618.5 | [5 empty] | Highest Generation | 14801
5:00 | 670 | 7418 | 5156 | 12574 | [6 empty] | 21:00
5:30 | 700 | 7320 | 5163.5 | 12483.5
6:00 | 730 | 7222 | 5171 | 12393
6:30 | 745 | 7190 | 5173 | 12363
7:00 | 760 | 7158 | 5175 | 12333
7:30 | 775 | 7138.5 | 5211.5 | 12350
8:00 | 790 | 7119 | 5248 | 12367
8:30 | 770 | 7021.5 | 5244.5 | 12266
9:00 | 750 | 6924 | 5241 | 12165
9:30 | 940 | 7036 | 5219 | 12255
10:00 | 1130 | 7148 | 5197 | 12345
10:30 | 1175 | 7258 | 5303 | 12561
11:00 | 1220 | 7368 | 5409 | 12777
11:30 | 1230 | 7459.5 | 5528 | 12987.5
12:00 | 1240 | 7551 | 5647 | 13198
12:30 | 1180 | 7678 | 5651 | 13329
13:00 | 1120 | 7805 | 5655 | 13460
13:30 | 1140 | 7567 | 5590 | 13157
14:00 | 1160 | 7329 | 5525 | 12854
14:30 | 1185 | 7461.5 | 5493.5 | 12955
15:00 | 1210 | 7594 | 5462 | 13056
15:30 | 1230 | 7483.5 | 5372 | 12855.5
16:00 | 1250 | 7373 | 5282 | 12655
16:30 | 1170 | 7506 | 5205.5 | 12711.5
17:00 | 1090 | 7639 | 5129 | 12768
17:30 | 995 | 7652.5 | 5173 | 12825.5
18:00 | 900 | 7666 | 5217 | 12883
18:30 | 885 | 8196 | 5552 | 13748
19:00 | 870 | 8726 | 5887 | 14613
19:30 | 900 | 8669 | 5957 | 14626
20:00 | 506 | 8630 | 5912 | 14542 |  |  |  | Executive Engineer
20:30 | 505 | 8773.5 | 5898 | 14671.5 |  |  |  | Network Operation Division
21:00 | 504 | 8917 | 5884 | 14801
21:30 | 447 | 8796 | 5785 | 14581
22:00 | 390 | 8675 | 5686 | 14361 |  |  |  |  | Page 6 of 7
22:30 | 520 | 8701.5 | 5659 | 14360.5
23:00 | 650 | 8728 | 5632 | 14360
23:30 | 710 | 8420.5 | 5549 | 13969.5
24:00 | 770 | 8113 | 5466 | 13579
14801 MW (21:00 )
13198 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2023-07-31 |  | Energy |  | 317961627
[15 empty] | 43676 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(HSD) | P.GEN(HFO). | COAL | HYDRO | G.GEN(HSD) | G.GEN(HFO) | TRIPURA | SOLAR | WIND | SHORTAGE
0:00 | 4320 | 777 | 1998 | 150 | 2313 | 2685 | 130 | 522 | 391 | 138 | 0 | 5 | 1166.055
0:30 | 4341.5 | 845 | 2071 | 225 | 1949.5 | 2597.5 | 138 | 426 | 351 | 142 | 0 | 2.5 | 1443.005 |  |  | Date: | 43676
1:00 | 4363 | 913 | 2144 | 300 | 1586 | 2510 | 146 | 330 | 311 | 146 | 0 | 0 | 1719.955
1:30 | 4361 | 912.5 | 2146.5 | 300 | 1529.5 | 2512.5 | 138.5 | 324.5 | 286 | 143 | 0 | 0 | 1715.18 | [9 empty] | Total Energy | 317.9616 | 317.9616 | Total Energy Gen 317.962 MKWHr Energy Not Served 27.538 MKWHr Energy Requirement 345.500 MKWHr
2:00 | 4359 | 912 | 2149 | 300 | 1473 | 2515 | 131 | 319 | 261 | 140 | 0 | 0 | 1710.405 | [9 empty] | Energy not Served | 27.5384 | 27.5384
2:30 | 4351 | 912.5 | 2146 | 299.5 | 1453.5 | 2518 | 131 | 299.5 | 260.5 | 138 | 0 | 2 | 1684.1425 | [9 empty] | Energy Requirement | 345.5 | 345.5
3:00 | 4343 | 913 | 2143 | 299 | 1434 | 2521 | 131 | 280 | 260 | 136 | 0 | 4 | 1657.88
3:30 | 4384.5 | 913 | 2141.5 | 299.5 | 1430.5 | 2514.5 | 131 | 280 | 256 | 135 | 0 | 3 | 1610.6075 | [8 empty] | Shortage
4:00 | 4426 | 913 | 2140 | 300 | 1427 | 2508 | 131 | 280 | 252 | 134 | 0 | 2 | 1563.335
4:30 | 4417 | 912.5 | 2137 | 240 | 1428.5 | 2539 | 131 | 280 | 249.5 | 133 | 0 | 1 | 1462.5825
5:00 | 4408 | 912 | 2134 | 180 | 1430 | 2570 | 131 | 280 | 247 | 132 | 0 | 0 | 1361.83
5:30 | 4396.5 | 912.5 | 2128.5 | 90 | 1431.5 | 2580.5 | 132 | 280 | 247 | 126 | 8 | 1 | 1305.0075
6:00 | 4385 | 913 | 2123 | 0 | 1433 | 2591 | 133 | 280 | 247 | 120 | 16 | 2 | 1248.185
6:30 | 4332 | 913 | 2129.5 | 0 | 1432 | 2592.5 | 131.5 | 280 | 243 | 119 | 39.5 | 1 | 1181.335 | [7 empty] | Coal
7:00 | 4279 | 913 | 2136 | 0 | 1431 | 2594 | 130 | 280 | 239 | 118 | 63 | 0 | 1114.485
7:30 | 4264.5 | 913 | 2102.5 | 0 | 1432 | 2602 | 130 | 280 | 229 | 120 | 127 | 0 | 1122.125 | [6 empty] | Oil
8:00 | 4250 | 913 | 2069 | 0 | 1433 | 2610 | 130 | 280 | 219 | 122 | 191 | 0 | 1129.765
8:30 | 4142 | 912.5 | 2041.5 | 0 | 1439 | 2613.5 | 120 | 280 | 210 | 124 | 233.5 | 0 | 1273.97
9:00 | 4034 | 912 | 2014 | 0 | 1445 | 2617 | 110 | 280 | 201 | 126 | 276 | 0 | 1418.175
9:30 | 4122 | 912.5 | 1959 | 0 | 1449.5 | 2627 | 95 | 287.5 | 209.5 | 130 | 313 | 0 | 1451.6
10:00 | 4210 | 913 | 1904 | 0 | 1454 | 2637 | 80 | 295 | 218 | 134 | 350 | 0 | 1485.025
10:30 | 4169.5 | 913 | 1900 | 50 | 1533.5 | 2671.5 | 97.5 | 350 | 226.5 | 137 | 362.5 | 0 | 1469.745
11:00 | 4129 | 913 | 1896 | 100 | 1613 | 2706 | 115 | 405 | 235 | 140 | 375 | 0 | 1454.465
11:30 | 4146 | 913 | 1931.5 | 81.5 | 1671 | 2740 | 115 | 455.5 | 257.5 | 143 | 383.5 | 0 | 1372.8125
12:00 | 4163 | 913 | 1967 | 63 | 1729 | 2774 | 115 | 506 | 280 | 146 | 392 | 0 | 1291.16
12:30 | 4153.5 | 913 | 1919 | 181.5 | 1746.5 | 2798 | 115 | 505.5 | 292.5 | 151 | 402 | 1.5 | 1431.545
13:00 | 4144 | 913 | 1871 | 300 | 1764 | 2822 | 115 | 505 | 305 | 156 | 412 | 3 | 1571.93
13:30 | 4144 | 913 | 1871 | 300 | 1764 | 2822 | 115 | 505 | 305 | 156 | 412 | 3 | 1571.93
14:00 | 4144 | 913 | 1871 | 300 | 1764 | 2822 | 115 | 505 | 305 | 156 | 412 | 3 | 1571.93
14:30 | 4050.5 | 912.5 | 1862.5 | 275 | 1747.5 | 2835 | 109.5 | 505 | 316.5 | 158 | 337 | 1.5 | 1556.65
15:00 | 3957 | 912 | 1854 | 250 | 1731 | 2848 | 104 | 505 | 328 | 160 | 262 | 0 | 1541.37
15:30 | 3995.5 | 912.5 | 1868.5 | 138 | 1731.5 | 2847.5 | 104.5 | 431.5 | 294 | 158 | 226.5 | 0 | 1484.5475
16:00 | 4034 | 913 | 1883 | 26 | 1732 | 2847 | 105 | 358 | 260 | 156 | 191 | 0 | 1427.725
16:30 | 4055 | 910 | 1885 | 13 | 1831.5 | 2829 | 102.5 | 366.5 | 273 | 153 | 136 | 7 | 1230.5175
17:00 | 4076 | 907 | 1887 | 0 | 1931 | 2811 | 100 | 375 | 286 | 150 | 81 | 14 | 1033.31
17:30 | 4057.5 | 907.5 | 1885.5 | 0 | 2053 | 2775.5 | 102.5 | 383.5 | 301 | 147 | 51 | 11.5 | 763.5225
18:00 | 4039 | 908 | 1884 | 0 | 2175 | 2740 | 105 | 392 | 316 | 144 | 21 | 9 | 493.735
18:30 | 4087 | 908 | 1905.5 | 113 | 2570.5 | 2782.5 | 105 | 478 | 476 | 156 | 10.5 | 6 | 407.785
19:00 | 4135 | 908 | 1927 | 226 | 2966 | 2825 | 105 | 564 | 636 | 168 | 0 | 3 | 321.835
19:30 | 4139 | 908 | 1919 | 53 | 3166 | 2803 | 105 | 568 | 698 | 112 | 0 | 5 | 379.6125
20:00 | 4120 | 814 | 1942 | 53 | 3218 | 2796 | 105 | 568 | 729 | 44 | 0 | 3 | 437.39
20:30 | 4101 | 814 | 1933.5 | 151.5 | 3260.5 | 2747 | 118.5 | 609 | 727 | 78 | 0 | 1.5 | 418.7675
21:00 | 4082 | 814 | 1925 | 250 | 3303 | 2698 | 132 | 650 | 725 | 112 | 0 | 0 | 400.145
21:30 | 4043.5 | 814 | 1927 | 131 | 3318.5 | 2698.5 | 132 | 545 | 727.5 | 114 | 0 | 0 | 457.445
22:00 | 4005 | 814 | 1929 | 12 | 3334 | 2699 | 132 | 440 | 730 | 116 | 0 | 0 | 514.745
22:30 | 4155.5 | 795.5 | 1959 | 44.5 | 3207 | 2692.5 | 132 | 409 | 699.5 | 116 | 0 | 0 | 491.3475
23:00 | 4306 | 777 | 1989 | 77 | 3080 | 2686 | 132 | 378 | 669 | 116 | 0 | 0 | 467.95
23:30 | 4313 | 777 | 1993.5 | 113.5 | 2696.5 | 2685.5 | 131 | 450 | 530 | 127 | 0 | 2.5 | 817.0025 |  |  | Max Temp. in Dhaka |  | 37.1° C
24:00 | 4320 | 777 | 1998 | 150 | 2313 | 2685 | 130 | 522 | 391 | 138 | 0 | 5 | 1166.055
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
SOLAR
Total Energy Gen 317.962 MKWHr Energy Not Served 27.538 MKWHr Energy Requirement 345.500 MKWHr
Shortage
Note on W13: Author:

## Generation
g | 2023-07-31
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 76 | 76 | 76 | 76 | 76 | 78 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1792800
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 55 | 55 | 55 | 55 | 55 | 50 | 50 | 30 | 0 | 35 | 35 | 35 | 35 | 34 | 35 | 30 | 35 |  | 35 | 35 | 35 | 62 | 62 | 62 | 60 | 1028000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 116 | 117 | 120 | 120 | 118 | 120 | 120 | 115 | 118 | 115 | 115 | 110 | 110 | 110 | 115 |  | 121 | 123 | 120 | 117 | 120 | 122 | 121 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 8 | 12 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 271168
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 4 | 16 | 4 | 10 | 13 | 8 | 13 | 8 | 0 |  | 0 | [8 empty] | 81540
6 | Sikalbaha 225MW CCPP (Gas) | 224 | 224 | 226 | 226 | 223 | 222 | 223 | 222 | 225 | 216 | 219 | 214 | 214 | 216 | 211 | 220 | 225 | 223 |  | 220 | 225 | 221 | 225 | 225 | 223 | 225 | 5426131
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 39 | 50 | 50 | 50 | 50 | 50 | 50 | 34 | 34 | 34 | 34 | 34 | 50 | 48 | 48 | 32 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1075660
12 | Hathazari 100 MW peaking PP | 58 | 50 | 49 | 41 | 41 | 41 | 41 | 41 | 33 | 33 | 33 | 24 | 24 | 33 | 32 | 36 | 60 | 74 |  | 84 | 84 | 84 | 84 | 84 | 84 | 76 | 1224592
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1257055
Daudkandi 200 MW PP (B.Trac)
14 | Titas 50 MW Peaking PP | 38 | 38 | 38 | 38 | 38 | 38 | 39 | 39 | 39 | 40 | 23 | 23 | 23 | 27 | 34 | 38 | 39 | 37 |  | 30 | 30 | 30 | 32 | 47 | 47 | 46 | 874480
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 182 | 191 | 185 | 190 | 188 | 190 | 181 | 181 | 133 | 184 | 185 | 180 | 185 | 160 | 183 | 185 | 192 | 150 |  | 189 | 193 | 187 | 198 | 83 | 193 | 175 | 4448000
17 | Siddhirganj 335 MW CCPP | 326 | 324 | 325 | 323 | 320 | 324 | 329 | 335 | 326 | 318 | 316 | 315 | 315 | 331 | 318 | 314 | 318 | 323 |  | 320 | 324 | 319 | 326 | 280 | 280 | 336 | 7663603
18 | Kodda 300 MW PP Unit-2 (Summit) | 102 | 115 | 115 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 105 | 110 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 115 | 112 | 115 | 2722364
19 | Ashuganj 195 MW PP (APSCL-United) | [26 empty] | 0
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 160 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 |  | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 4987094
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24 | Ghorasal 6
25 | Ghorasal 365 MW CCPP Unit-7
26 | SS Power I | 70 | 70 | 70 | 70 | 125 | 145 | 148 | 168 | 184 | 226 | 246 | 275 | 325 | 380 | 355 | 355 | 410 | 350 |  | 330 | 330 | 320 | 310 | 310 | 310 | 310 | 5716363
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | [18 empty] | 43560
33 | Ashuganj 225 MW CCPP | 167 | 166 | 166 | 170 | 168 | 174 | 161 | 175 | 179 | 184 | 200 | 200 | 204 | 200 | 196 | 199 | 203 | 202 |  | 200 | 203 | 200 | 207 | 206 | 200 | 198 | 4546000
34 | Ashuganj 450 MW CCPP(South) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6113000
| Ashuganj 450 MW CCPP(North) | 295 | 300 | 280 | 315 | 310 | 305 | 350 | 280 | 280 | 315 | 280 | 305 | 305 | 280 | 320 | 280 | 280 | 280 |  | 315 | 280 | 295 | 280 | 280 | 325 | 275 | 7634300
| Ashuganj 420 MW CCPP(East) | 300 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 250 | 250 |  | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 6245700
35 | Ashuganj 55 MW PP (Precision)
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 364 | 366 | 380 | 385 | 364 | 357 | 312 | 368 | 367 | 363 | 360 | 360 | 360 | 357 | 363 | 364 | 362 | 361 |  | 362 | 360 | 361 | 362 | 359 | 364 | 392 | 8759300
40 | Meghnaghat 450 MW CCPP(MPL) | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 |  | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 10114500
41 | Haripur 360 MW CCPP(HPL) | 323 | 323 | 322 | 322 | 321 | 321 | 322 | 323 | 337 | 326 | 326 | 317 | 316 | 333 | 336 | 316 | 323 | 324 |  | 327 | 327 | 332 | 317 | 317 | 327 | 332 | 7806000
42 | RPCL 210MW CCPP | 94 | 94 | 97 | 96 | 97 | 97 | 46 | 47 | 47 | 47 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 34 |  | 48 | 76 | 94 | 97 | 95 | 92 | 93 | 1486080
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 13 | 25 | 39 | 44 | 38 | 42 | 31 | 40 | 47 | 24 | 12 | 2 | [8 empty] | 362470
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 28 | 28 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 706000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | [7 empty] | 20 | 25 | 25 | 25 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 359520
48 | Shahjibazar 86 MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 75 | 75 | 78 | 78 | 78 | 75 | 75 | 78 | 84 | 84 |  | 84 | 84 | 85 | 86 | 81 | 84 | 84 | 1841280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 185 | 185 | 185 | 185 | 184 | 185 | 185 | 185 | 183 | 183 | 183 | 181 | 180 |  |  | 30 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3389250
51 | Sylhet 20 MW GTPP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 383000
52 | Sylhet 50 MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 9 | 10 | 238500
54 | Hobiganj 11 MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 |  | 5 | 5 | 5 | 0 | 2 | 2 | 5 | 146640
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 44 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1088400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 |  | 8 | 16 | 16 | 8 |  | 16 | 16 | 16 | 16 | 24 | 24 | 24 | 448416
57 | Bibiana-II 341 MW CCPP (Summit) | 320 | 320 | 315 | 310 | 310 | 305 | 320 | 290 | 290 | 300 | 300 | 280 | 315 | 275 | 310 | 315 | 300 | 280 |  | 290 | 260 | 280 | 300 | 260 | 310 | 310 | 7359500
| Bibiyana South 400 MW | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 332 | 330 | 370 | 375 |  | 370 | 385 | 375 | 303 | 380 | 383 | 395 | 8498900
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 5 | 17 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 532716
59 | Tangail Palli Power Gen 22 MW | 6 | 6 | 6 | 6 | 3 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 4 | 4 |  | 5 | 3 | 3 | 6 | 0 | 3 | 6 | 129120
60 | Barabkunda 22 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 266832
61 | Narshingdi 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 10 | 17 | 0 |  |  | 17 | 320796
62 | Tangail 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 16 | 15 | 15 | 15 | 15 | [9 empty] | 15 | 238428
63 | Impoprt (Tripura) | 146 | 140 | 136 | 134 | 132 | 120 | 118 | 122 | 126 | 134 | 140 | 146 | 156 | 158 | 160 | 156 | 150 | 144 |  | 168 | 112 | 44 | 112 | 116 | 116 | 138 | 3224640
64 | Malancha, Ctg. EPZ (United) | 29 | 33 | 33 | 35 | 36 | 36 | 31 | 8 | 2 | 2 | 2 | 2 | 7 | 14 | 2 | 2 | 16 | 17 |  | 25 | 30 | 30 | 17 | 27 | 26 | 26 | 452640
65 | Feni 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 0 | [5 empty] | 7 | 16 | 16 | 16 | 17 | 17 | 17 |  |  |  |  | 8 | 8 | 16 | 18 | 259092
66 | Feni 11 MW PP (Doreen) | 10 | 10 | 10 | 10 | 10 | 10 |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  |  | 11 | 11 | 11 | 11 | 194040
67 | Jangalia 33 MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 25 | 32 | 31 | 31 | 30 | 30 | 30 |  | 33 | 30 |  | 31 | 32 | 32 | 32 | 742200
68 | Cumilla 25 MW PP (Summit) | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 12 | 12 |  | 17 | 17 |  |  |  | 17 | 17 | 355990
69 | Summit Ashulia | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 456000
70 | Summit Madhabdi | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 10 | 12 | 19 | 19 | 12 | 14 | 14 | 14 | 14 | 14 |  | 22 | 22 | 22 | 22 | 14 | 19 | 14 | 395280
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 17 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 664200
72 | Rupganj 33 MW PP(Summit) | 23 | 23 | 23 | 23 | 23 | 23 | 16 | 24 | 10 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 16 | 16 | 23 | 25 | 16 | 432500
73 | Ghorashal 108 MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 301090
| Feni Lanka Power | 17 | 17 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 352260
| Chowmuhani 113 MW | 9 | 9 | 9 | 9 | 7 | 9 | 8 | 9 | 9 | 9 | 9 | 27 | 27 | 12 | 9 | 9 | 9 | 9 |  | 26 | 56 | 56 | 57 | 58 | 28 | 12 | 438480
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 90 | 90 |  | 90 | 162 | 162 | 162 | 162 | 162 | 17 | 1556640
77 | Siddhirganj 100 PP(Dutch Bangla) | 33 | 33 | 33 | 33 | 33 | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 42 | 50 | 50 | 50 | 62 |  | 65 | 65 | 65 | 65 | 56 | 56 | 41 | 1104960
78 | Gazipur 52 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 |  | 2 | 8 | 238522
79 | Kodda 150 MW PP | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 1782720
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 36 | 37 | 43 | 43 | 43 | 32 | 37 | 37 | 38 |  | 38 | 38 | 39 | 40 | 43 | 43 | 43 | 971309
| Gazipur 100 MW PP | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 88 | 88 | 88 | 105 | 105 | 105 | 35 | 1142400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 2 | 2 | 6 | 5 | 6 | 4 | 4 | 3 | 0 | [9 empty] | 30121
| Jodiac Power | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 617466
| Karnaphuli Power Ltd. | 74 | 74 | 74 | 65 | 74 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1432680
82 | Madanganj 102 PP(Summit) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 75 | 34 | 34 | 34 |  | 38 | 51 | 51 | 51 | 96 | 40 | 17 | 1676676
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit)
87 | Meghnaghat 100 MW(IEL) | 42 | 42 | 43 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 49 | 50 | 51 | 50 | 50 | 51 | 49 | 55 |  | 58 | 59 | 59 | 59 | 58 | 59 | 45 | 1210560
| Meghnaghat 104 MW PP (OPCL) | 40 | 36 | 35 | 35 | 47 | 52 | 53 | 46 | 35 | 35 | 35 | 50 | 54 | 54 | 54 | 53 | 53 | 54 |  | 72 | 72 | 72 | 72 | 72 | 72 | 54 | 1235520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 46 | 46 | 46 | 46 | 46 | 58 | 58 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 46 | 1172040
92 | Fenchuganj 44 MW (Energyprima) | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 43 | 43 | 39 | 39 | 41 | 38 | 39 | 44 |  | 44 | 45 | 42 | 45 | 46 | 46 | 46 | 1075968
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 939968
94 | Gagnagar 102 MW PP (Digital Power) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 50 | 50 | 50 | 50 | 50 | 50 | 74 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1203696
95 | Patenga 50MW PP (Baraka) | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 37 | 45 |  | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 444480
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 4 | 5 | 5 | 22 | 24 |  | 24 | 24 | 24 | 24 | 24 |  |  | 159360
97 | katpotti 52 MW
98 | Bosila 108 MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 380041
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 6 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 532617
101 | Kushiara 163 MW CCPP (KP) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 80 |  |  | 112 | [14 empty] | 1132854
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | [8 empty] | 15450
103 | Kamalaghat 54 MW PP(Banco Energy) | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 387360
104 | Keranigonj 300 MW PP (APR) | 300 | 300 | 299 | 300 | 180 | [5 empty] | 100 | 63 | 300 | 20 | 250 | 26 | 0 |  |  | 226 | 53 | 53 | 250 | 12 | 77 | 150 | 3000687
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 77 | 67 | 66 | 66 | 65 | 68 | 68 | 68 |  | 86 | 86 | 87 | 86 | 87 | 68 | 68 | 1718400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 36 | 68 | 71 | 71 | 71 | 71 | 68 | 62 | 68 | 72 | 83 |  | 135 | 135 | 135 | 144 | 149 | 88 | 47 | 1699488
115 | Juldah 100 MW PP Unit-3 (Acorn) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 37 | 37 | 37 | 25 | 37 | 36 | 36 | 48 |  | 100 | 100 | 100 | 100 | 100 | 100 | 25 | 1046400
116 | Chandpur 200 MW (Desh energy) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 35 | 44 | 68 | 71 | 69 | 68 | 68 | 68 | 70 | 90 |  | 100 | 120 | 135 | 156 | 156 | 156 | 115 | 1764950
117 | Ashuganj 150 MW PP (Midland) | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 6 | 5 | 6 | 5 | 6 | 5 | 5 | 6 | 5 |  | 11 | 25 | 26 | 48 | 60 | 65 | 25 | 344581
118 | Bibiyana-III 400 MW CCPP | 382 | 390 | 367 | 397 | 400 | 387 | 371 | 367 | 343 | 403 | 368 | 386 | 370 | 370 | 380 | 393 | 370 | 370 |  | 398 | 368 | 375 | 367 | 367 | 404 | 367 | 9153000
| Jamalpur 115 MW PP (United) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 21 | 24 | 24 | 19 | 24 | 19 | 19 | 19 |  | 90 | 93 | 84 | 84 | 84 | 19 | 18 | 752400
| Anwara 300 MW PP (United) | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 121 | 121 | 123 | 124 | 124 | 124 | 124 | 124 |  | 257 | 257 | 264 | 265 | 265 | 267 | 267 | 3377236
| Juldah unit-2 (Acorn) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 |  | 88 | 88 | 88 | 88 | 88 | 88 | 50 | 1170240
| Anlima Energy Ltd. | 40 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 37 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1062600
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 650880
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 18 | 19 | 29 | 27 | 34 | 34 | 32 | 9 | 1 | 1 | 1 | [8 empty] | 218086
| Chandpur 115(Doreen) | 22 | 18 | 17 | 17 | 18 | 18 | 17 | 18 | 18 | 28 | 60 | 59 | 72 | 72 | 72 | 72 | 72 | 72 |  | 95 | 97 | 96 | 109 | 115 | 115 | 93 | 1373760
| Kanchan Purbachal Power Generation Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | [5 empty] | 12 | 17 | 17 | 17 | 17 | [5 empty] | 13 | 17 | 17 | 296280
| Mirsharai 150 MW (Oil) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 17 | 17 |  | 70 | 110 | 142 | 142 | 142 | 142 | 17 | 935054
Mirsharai 150 MW (Gas)
| Cox's Bazar Wind | 0 |  | 4 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 14 | 9 |  | 3 | 5 | 3 | 0 | 0 | 0 | 5 | 45600
| Matarbari 2*600 MW (CPGCL) | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 145 | 150 | 150 | 150 |  | 150 | 150 | 150 | 110 | 150 | 150 | 150 | 3003636
120 | Eastern Zone Total | 7535 | 7507 | 7468 | 7519 | 7418 | 7222 | 7158 | 7119 | 6924 | 7148 | 7368 | 7551 | 7805 | 7329 | 7594 | 7373 | 7639 | 7666 |  | 8726 | 8669 | 8630 | 8917 | 8675 | 8728 | 8113 | 184936156
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
| Khulna 115 PP MW (KPCL-2) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 379200
125 | Khulna 330 MW CCPP (GAS)
126 | Khulna 330 MW CCPP (OIL) | [9 empty] | 15 | 125 | 226 | 225 | 225 | 222 | 75 | 75 | 75 |  | 234 | 234 | 234 | 234 | 100 | 100 | 220 | 2187676
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 14 |  | 27 | 40 | 25 | 22 | 22 | 11 | 11 | 282240
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 180 | 180 | 120 | 120 | 3115227
Kulna 225 MW CCPP (GAS)
129 | Rupsha 105 MW PP (Orion rupsha) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 838560
130 | Mongla Orion 100 MW Solar PP | [5 empty] | 2 | 8 | 28 | 36 | 59 | 65 | 63 | 101 | 82 | 14 | 18 | 2 | 2 | [8 empty] | 496800
131 | Rampal 1320 MW (BIFPCL)
132 | United Payra Power Ltd. | 150 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 72 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1418400
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 222 | 221 | 222 | 222 | 222 | 225 | 224 | 225 | 220 | 220 | 218 | 217 | 217 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 222 | 222 | 5286655
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 40 |  | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 711552
Barisal GT PP Unit-1& 2
136 | Barisal 307 MW | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 250 | 250 | 150 | 150 | 150 | 150 | 5695000
137 | Bhola 95 MW PP (Aggreko)
| Bhola 225 MW CCPP | 130 | 132 | 132 | 132 | 134 | 134 | 132 | 131 | 132 | 130 | 120 | 130 | 122 | 130 | 124 | 130 | 62 | 62 |  | 66 | 62 | 66 | 65 | 63 | 132 | 124 | 2699000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 35 | 34 | 31 | 25 | 24 | 21 | 21 | 23 | 23 | 25 | 25 | 28 | 29 | 24 | 12 | 20 |  | 29 | 29 | 33 | 34 | 35 | 25 | 28 | 651551
141 | Noapara 100 MW PP (Bangla Trac)
142 | Noapara 40 MW PP (Khanjahan Ali) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 191625
143 | Gopalganj 100 MW Peaking PP | 48 | 48 | 48 | 48 | 43 | 43 | 34 | 30 | 20 | 20 | 19 | 22 | 35 | 21 | 21 | 21 | 21 | 35 |  | 50 | 55 | 61 | 56 | 51 |  |  | 787200
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 32 | 32 | 50 | 50 | 32 | 32 | 32 | 90 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 15 | 2011680
146 | Bheramara HVDC | 913 | 912 | 913 | 913 | 912 | 913 | 913 | 913 | 912 | 913 | 913 | 913 | 913 | 912 | 912 | 913 | 907 | 908 |  | 908 | 908 | 814 | 814 | 814 | 777 | 777 | 21894545
147 | Bheramara 410 MW CCPP | 130 | 140 | 150 | 160 | 170 | 175 | 165 | 160 | 145 | 140 | 140 | 130 | 125 | 120 | 115 | 115 | 120 | 120 |  | 125 | 130 | 135 | 135 | 140 | 150 | 150 | 3559104
148 | Payra 1320 MW | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1220 | 1210 | 1244 | 1244 | 1244 | 1244 | 1244 | 1200 | 1200 |  | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 1244 | 31481000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 181 | 230 | 240 | 240 | 240 | 230 | 230 | 180 | 180 |  | 230 | 210 | 220 | 220 | 220 | 210 | 210 | 4962000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 35 | 35 | 35 | 35 | 35 | 35 |  | 159259
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 3 | 3 | 4 | 5 | 5 | 5 | 3 | 4 | 0 | 1 | 0 | [8 empty] | 38280
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
| Sirajgonj 225 MW CCPP Unit-2 (Oil) | 210 | 199 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 163 | 163 | 180 | 197 |  | 210 | 214 | 214 | 213 | 140 | 140 | 182 | 4370091
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 151 | 150 | 153 | 154 | 156 | 157 | 157 | 154 | 149 | 146 | 144 | 143 | 140 | 139 | 139 | 140 | 142 | 144 |  | 144 | 146 | 147 | 147 | 152 | 151 | 151 | 3806709
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 403 | 377 | 355 | 348 | 336 | 319 | 302 | 285 | 334 | 334 | 341 |  | 346 | 362 | 358 | 344 | 381 | 388 | 388 | 8848727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [12 empty] | 5 | 5 | 25 | 25 | 25 | 25 |  | 20 | 20 | 20 | 25 | 20 | 20 | 20 | 208335
162 | Bogra 22 MW PP (GBB)
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 |  | 8 | 8 | 8 | 8 |  |  | 8 | 173520
165 | Amnura 50 MW PP(Sinha) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 493220
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 8 | 25 | 42 | 25 | 34 | 34 | 126188
167 | Katakhali 50 MW Peaking PP | 22 | [9 empty] | 15 | 38 | 29 | 29 | 29 |  |  |  |  | 26 | 30 | 38 | 35 | 35 | 36 | 29 | 312516
168 | Santahar 50 MW Peaking PP | 31 | [18 empty] | 24 | 24 | 24 | 24 | 24 | 24 |  | 137385
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | 8 | 1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 17 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 199421
170 | Chapainawabganj 100 MW Peaking PP | [10 empty] | 20 | 48 | 48 | 48 | 48 |  |  |  |  | 90 | 90 | 90 | 90 | 90 | 90 | 12 | 662384
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 90 | 95 | 95 | 75 | 75 | 70 | 70 | 1340640
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 94 | 95 | 1135392
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 13 | 10 | 10 | 0 | 43000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 10 | 8 | 0 | 21000
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 34 | 62 | 76 |  | 77 | 77 | 97 | 98 | 98 | 98 | 98 | 1205817
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 4 |  | 7 | 7 | 7 | 7 | 6 | 5 | 3 | 1 | [8 empty] | 50432
178 | Energypac Power Venture Thakurgaon Ltd. | 17 | [10 empty] | 35 | 36 | 36 | 36 | 36 | 36 | 36 |  | 72 | 114 | 114 | 114 | 114 | 114 | 35 | 876038
| Intraco Solar 30 MW | [5 empty] | 1 | 7 | 15 | 22 | 24 | 17 | 20 | 18 | 22 | 12 | 8 | 10 | 3 |  | 0 | [6 empty] | 210442
| Adani Power Jharkhanda Ltd | 766 | 771 | 777 | 764 | 771 | 772 | 772 | 768 | 759 | 760 | 770 | 765 | 763 | 770 | 769 | 768 | 771 | 760 |  | 771 | 769 | 762 | 774 | 775 | 772 | 771 | 18418910
178 | Teesta Solar Limited | [5 empty] | 10 | 27 | 92 | 133 | 182 | 198 | 201 | 200 | 126 | 156 | 132 | 52 | 12 | [8 empty] | 1538750