## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-03 | Sunday
|  | Date (day): | 2018-06-03 |  | Sunday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10676 | MW |  |  | (b) At Evening Peak Hour : |  | 11990 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-02 | 2018-06-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | # 1 under maint.
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 190 | 120 | 190 | 0
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 349 | 350 | 350 |  |  | On test
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 50 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 24 | 107 | 100 | 100 | 8 |  | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Gas shortage
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 370 | 315 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 84 | 84 | 84 |  | 26 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 348 | 292 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 450 | 430 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 100 | 100 | 100 |  | 10
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 200 | 200 | 305 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 14 | 96 | 100 | 100
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 99 | 103 | 100 | 100 | 110 |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 100 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 87 | 87 |  | 13 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 120 | 185 | 170 | 170 |  |  | On test
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 10 | 21 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 94 | 94 | 94
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 49 | 49 | 49 |  | 2
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 65 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 91 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 32 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 8 | 50 | 51 | 51
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 15 | 291 | 100 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 MW | 0 | 0 | 0 | 21 | 0 | 0 |  |  | On test
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2513 | 3869 | 4011 | 4281 | 273 | 576
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 26 | 25 | 25 |  | 9 | Engine problem
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 31 | 45 | 45 | 45 |  | 5 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 115 | 114 | 115 | 119 |  | 50 | #4,5 Under maint.
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 202 | 189 | 203 | 206
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 70 | 135 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 8 | 51 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 82 | 85 | 85
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 14 | 49 | 51 | 51
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 102 | 90 | 102 |  | 10
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 29 | 6 | 20
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 91 | 98 | 98 | 98 |  | 10 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 679 | 874 | 924 | 957 | 360 | 124
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 |  | 135 | Under maint.
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 150 | 150 | 150
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 80 | 80 |  | 134
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 195 | 226 | 225 | 225
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 300 | 360 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 316 | 300 | 360 | 360
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 40 | 40 | 42 | 42
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | 132 kV Cable fault
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 5 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 176 | 68 | 68 | 68 | 127 |  | Gas shortage
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 86 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 30 | 0 | 50
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 153 | 153 | 153 | 153
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 128 | 180 | 143 | 186
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 15 | 25 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 34 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 21 | 20 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 82 | 0 | 200 |  |  | On test
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1604 | 1781 | 1862 | 2157 | 170 | 324
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 135 | 65 | 100 | 135 | 67 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 95 | 95 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.4 | 0 | 2 | 0
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 252.4 | 182 | 219 | 252 | 67 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 25 | 54 | 60 | 60
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 75 | 74 | 76 | 76
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 140 | 130 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 307 | 291 | 330 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 22 | 53 | 50 | 50
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 17 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 45 | 66 | 66
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 86 | 86 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 49 | 49 | 49
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 0 | 127 | 100 | 100 |  | 142
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 30 | 42 | 44 | 44
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 23 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 260 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 9 | 9
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1168 | 1301 | 1458 | 1458 | 0 | 162
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 33 | 0 | 33
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 478 | 460 | 475 | 475
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 110 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 83 | 115 | 115
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 48 | 0 | 50
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 200 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 6 | 75 | 50 | 75
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 0 | 80 | 300
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 40 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 50 | 0 | 55
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 0 | 100
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 958 | 1197 | 1095 | 1578 | 0 | 0
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 7 | 35 | 30 | 30
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 197 | 184 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 37 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 230 | 366 | 429 | 459 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 48 | 0 | 48
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 50 | 50 | 50 | 50 |  | 10
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 8 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 46 | 45 | 45
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Fuel shortage
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 |  | 225 | Under maint.
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 0 | 44
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 0 | 18 | 18
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 10 | 10 | 10
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 0 | 102 | 100 | 100
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 99 | 436 | 320 | 455 | 281 | 351
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 77 | 78 | 78
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 280 | 264 | 280 | 280 |  |  | on test
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 358 | 358 | 358 | 393 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 7861.4 | 10364 | 10676 | 11990 | 1151 | 1622
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7416.1432 | 9777 | 10071.3288 | 11310.906
A. |  | 2018-06-02 | (Yesterday) |  |  |  |  | Saturday
1 | Highest Generation : |  |  | 10397 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6506.1 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10364 | MW
3 | Day peak Generation : |  |  | 7861.4 | MW at | 11:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9777 | MW
4 | Evening peak Generation : |  |  | 10364 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 200.623 | MKWHr | By Solar | 0.015601 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 127.4826 | MKWHr |  | By Oil: | 48.3081 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 8.5436 | MKWHr |  | By Hydro: | 2.6188 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1151 | MW | Dhaka | 3733 | 3733 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1622 | MW | Chittagong | 1096 | 1096 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2773 | MW | Khulna | 1103 | 1103 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1064.33 | MMCFD |  |  | Rajshahi | 1040 | 1040 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 98342317.712 | ii) Oil : | Taka | 492701322.4 | Comilla | 948 | 948 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 11270332.89 | Total | Taka | 602313973.002 | Mymensingh | 632 | 632 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.3655 | MKWHr. | Sylhet | 432 | 432 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -860 | MW at | 21:00 | hrs | Barisal | 255 | 255 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -1000 | MW at | 20:00 | hrs | Rangpur | 538 | 538 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 9777 | 9777 |  | 0
B. |  | 2018-06-03 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.6° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 11990 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
4 | Reserve(Generation end) |  |  |  | 990 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 212.2586 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7592.1 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.3135 | MKWHr. | ii) HVDC Flow at Peak Time |  | 460 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3408 | MKWHr. | iii) Maximum HVDC Flow : |  | 478 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 81.19 |  | (b) Today: | 81.19 |  | (c) Rule Curve: |  | 76.26
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-06-02
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 0 | 0 | 120 | 300 | 82 | 76 | 345 | 311 | 0 | 0 | 360 | 200 | 50 | 14 | 30 | 120 | 0 | 102 | 0 | 0 | 7 | 62 | 10 | 51 | 10 | 0 | 36 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 22 | 0 | 89 | 32 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 51 | 85 | 31 | 90 | 97 | 44 | 19 | 38 | 0 | 100 | 0 | 260 | 250 | 185 | 65 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 140 | 104 | 72 | 22 | 0 | 58 | 76 | 50 | 50 | 130 | 276 | 65 | 87 | 48 | 0 | 0 | 43 | 9 | 285 | 23 | 8 | 0 | 15 | 0 | 0 |  | 476 | 0 | 305 | 10 | 16 | 120 | 0 | 0 | 50 | 59 | 8 | 200 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 43 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 0 |  | 6209 | 1869 | 8078 | 3403 | 476 | 1886 | 1001 | 358 | 121 | 693 | 140 | 0 | 0 | 81.34
2:00 | 37 | 0 | 0 | 120 | 300 | 82 | 76 | 350 | 311 | 0 | 0 | 360 | 200 | 10 | 14 | 30 | 120 | 0 | 102 | 0 | 0 | 7 | 30 | 10 | 25 | 11 | 0 | 36 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 51 | 0 | 89 | 33 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 51 | 43 | 31 | 90 | 97 | 44 | 19 | 40 | 0 | 100 | 0 | 265 | 257 | 187 | 65 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 144 | 103 | 72 | 22 | 0 | 60 | 76 | 50 | 50 | 130 | 276 | 64 | 87 | 48 | 0 | 0 | 43 | 9 | 290 | 23 | 8 | 0 | 15 | 0 | 0 |  | 475 | 0 | 305 | 10 | 16 | 120 | 0 | 0 | 25 | 30 | 8 | 202 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 43 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 79 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 |  | 6130 | 1806 | 7936 | 3424 | 475 | 1891 | 965 | 359 | 122 | 556 | 144 | 0 | 0 | 81.31
3:00 | 37 | 0 | 0 | 120 | 365 | 82 | 76 | 365 | 352 | 0 | 0 | 420 | 200 | 7 | 14 | 30 | 120 | 0 | 102 | 0 | 0 | 7 | 30 | 10 | 25 | 10 | 0 | 36 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 51 | 0 | 86 | 33 | 0 | 0 | 16 | 0 | 203 | 0 | 50 | 0 | 51 | 43 | 31 | 90 | 97 | 44 | 19 | 41 | 0 | 100 | 0 | 270 | 261 | 192 | 65 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 144 | 111 | 72 | 22 | 0 | 58 | 76 | 50 | 50 | 163 | 271 | 60 | 87 | 48 | 0 | 0 | 43 | 9 | 305 | 23 | 8 | 0 | 15 | 0 | 0 |  | 476 | 0 | 340 | 10 | 16 | 120 | 0 | 0 | 25 | 30 | 8 | 197 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 43 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 |  | 6365 | 1836 | 8201 | 3545 | 476 | 2041 | 961 | 358 | 119 | 557 | 144 | 0 | 0 | 81.28
4:00 | 37 | 0 | 0 | 120 | 365 | 82 | 60 | 345 | 331 | 0 | 0 | 380 | 200 | 7 | 14 | 15 | 170 | 0 | 102 | 0 | 0 | 7 | 15 | 0 | 8 | 11 | 0 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 8 | 0 | 86 | 31 | 0 | 0 | 16 | 0 | 203 | 0 | 50 | 0 | 8 | 0 | 15 | 90 | 97 | 44 | 19 | 40 | 0 | 100 | 0 | 260 | 250 | 183 | 65 | 153 | 42 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 22 | 126 | 140 | 24 | 22 | 0 | 56 | 76 | 50 | 50 | 163 | 267 | 64 | 87 | 48 | 0 | 0 | 43 | 9 | 275 | 23 | 8 | 0 | 15 | 0 | 0 |  | 475 | 0 | 360 | 5 | 0 | 120 | 0 | 0 | 5 | 10 | 8 | 197 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 43 | 0 | 8 | 0 | 18 | 10 | 9 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 |  | 5997 | 1741 | 7738 | 3596 | 475 | 1928 | 721 | 357 | 117 | 418 | 126 | 0 | 0 | 81.25
5:00 | 37 | 0 | 0 | 120 | 300 | 24 | 40 | 345 | 311 | 0 | 0 | 380 | 200 | 7 | 14 | 15 | 170 | 0 | 65 | 0 | 0 | 7 | 15 | 0 | 8 | 0 | 0 | 18 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 8 | 0 | 83 | 31 | 0 | 0 | 16 | 0 | 182 | 0 | 51 | 0 | 8 | 0 | 15 | 60 | 44 | 28 | 19 | 40 | 0 | 100 | 0 | 265 | 250 | 183 | 65 | 153 | 40 | 0 | 5 | 45 | 20 | 0 | 0 | 19 | 11 | 8 | 16 | 110 | 156 | 8 | 22 | 0 | 20 | 76 | 22 | 20 | 100 | 276 | 64 | 10 | 20 | 0 | 0 | 41 | 7 | 290 | 23 | 8 | 0 | 15 | 0 | 0 |  | 476 | 0 | 300 | 5 | 0 | 120 | 0 | 0 | 0 | 10 | 0 | 197 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 16 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 78 | 279 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 |  | 5307 | 1599 | 6906 | 3391 | 476 | 1505 | 560 | 357 | 114 | 393 | 110 | 0 | 0 | 81.22
6:00 | 37 | 0 | 0 | 120 | 270 | 24 | 40 | 345 | 291 | 0 | 0 | 330 | 200 | 7 | 14 | 15 | 170 | 0 | 38 | 0 | 0 | 7 | 15 | 0 | 8 | 0 | 0 | 0 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 8 | 0 | 81 | 30 | 0 | 0 | 16 | 0 | 182 | 0 | 51 | 0 | 8 | 0 | 15 | 30 | 32 | 18 | 19 | 40 | 0 | 100 | 0 | 275 | 264 | 193 | 65 | 153 | 40 | 0 | 5 | 6 | 5 | 0 | 0 | 19 | 11 | 8 | 16 | 102 | 156 | 8 | 22 | 0.1 | 20 | 76 | 5 | 5 | 100 | 278 | 64 | 10 | 5 | 0 | 0 | 7 | 7 | 290 | 23 | 8 | 0 | 15 | 0 | 0 |  | 475 | 0 | 230 | 5 | 0 | 120 | 0 | 0 | 0 | 10 | 0 | 197 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 |  | 5000.1 | 1506 | 6506.1 | 3300 | 475 | 1297 | 470 | 358 | 111 | 393 | 102 | 0.1 | 0 | 81.19
7:00 | 37 | 0 | 0 | 120 | 270 | 24 | 40 | 365 | 321 | 0 | 0 | 430 | 200 | 7 | 14 | 15 | 120 | 0 | 39 | 0 | 0 | 7 | 15 | 0 | 8 | 0 | 0 | 0 | 18 | 17 | 22 | 25 | 32 | 33 | 31 | 8 | 0 | 82 | 30 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 8 | 0 | 14 | 30 | 32 | 0 | 19 | 4 | 0 | 100 | 0 | 305 | 290 | 206 | 65 | 153 | 40 | 0 | 5 | 6 | 5 | 0 | 0 | 19 | 11 | 8 | 16 | 102 | 139 | 8 | 22 | 0.3 | 20 | 76 | 5 | 5 | 100 | 294 | 62 | 10 | 5 | 0 | 0 | 5 | 9 | 310 | 23 | 8 | 0 | 15 | 0 | 0 |  | 478 | 0 | 260 | 5 | 0 | 120 | 0 | 0 | 0 | 10 | 0 | 193 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 |  | 5151.3 | 1534 | 6685.3 | 3363 | 478 | 1411 | 452 | 357 | 112 | 410 | 102 | 0.3 | 0 | 81.16
8:00 | 37 | 0 | 0 | 120 | 320 | 24 | 40 | 360 | 353 | 0 | 0 | 430 | 200 | 7 | 15 | 15 | 120 | 0 | 104 | 0 | 0 | 7 | 32 | 10 | 8 | 11 | 0 | 0 | 36 | 17 | 22 | 0 | 32 | 33 | 31 | 8 | 0 | 84 | 31 | 0 | 0 | 16 | 0 | 184 | 0 | 50 | 0 | 8 | 0 | 14 | 68 | 96 | 4 | 19 | 2 | 0 | 100 | 0 | 260 | 250 | 183 | 65 | 153 | 35 | 0 | 5 | 6 | 41 | 0 | 0 | 19 | 11 | 8 | 16 | 114 | 145 | 32 | 22 | 0.8 | 20 | 76 | 5 | 5 | 100 | 263 | 64 | 84 | 30 | 0 | 0 | 5 | 9 | 290 | 23 | 8 | 0 | 15 | 0 | 0 |  | 478 | 0 | 320 | 5 | 0 | 120 | 0 | 0 | 0 | 10 | 8 | 191 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 5430.8 | 1590 | 7020.8 | 3370 | 478 | 1547 | 630 | 356 | 115 | 410 | 114 | 0.8 | 0 | 81.13
9:00 | 37 | 0 | 0 | 120 | 320 | 24 | 40 | 350 | 350 | 0 | 0 | 400 | 200 | 7 | 14 | 15 | 120 | 0 | 101 | 0 | 0 | 7 | 65 | 10 | 8 | 11 | 0 | 18 | 40 | 17 | 22 | 0 | 32 | 33 | 31 | 8 | 0 | 86 | 32 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 8 | 0 | 14 | 90 | 97 | 30 | 19 | 2 | 0 | 100 | 0 | 300 | 327 | 200 | 65 | 153 | 37 | 0 | 5 | 35 | 42 | 0 | 0 | 19 | 11 | 8 | 16 | 116 | 143 | 90 | 22 | 2 | 25 | 76 | 5 | 5 | 100 | 282 | 62 | 84 | 47 | 0 | 0 | 5 | 7 | 280 | 8 | 8 | 0 | 15 | 0 | 0 |  | 478 | 0 | 320 | 10 | 16 | 120 | 0 | 0 | 0 | 5 | 8 | 200 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 5745 | 1652 | 7397 | 3507 | 478 | 1547 | 817 | 357 | 118 | 455 | 116 | 2 | 0 | 81.11
10:00 | 37 | 0 | 0 | 120 | 320 | 24 | 40 | 370 | 350 | 0 | 0 | 400 | 200 | 7 | 14 | 15 | 120 | 0 | 100 | 0 | 0 | 7 | 65 | 10 | 8 | 11 | 0 | 18 | 54 | 17 | 22 | 0 | 32 | 33 | 33 | 8 | 0 | 86 | 31 | 0 | 0 | 16 | 0 | 198 | 0 | 50 | 0 | 8 | 0 | 14 | 90 | 92 | 31 | 19 | 2 | 0 | 100 | 0 | 335 | 334 | 206 | 70 | 153 | 37 | 0 | 5 | 51 | 43 | 0 | 0 | 19 | 11 | 8 | 0 | 128 | 141 | 95 | 20 | 0.9 | 25 | 75 | 5 | 5 | 100 | 285 | 61 | 86 | 47 | 0 | 0 | 5 | 7 | 320 | 23 | 8 | 0 | 15 | 0 | 0 |  | 478 | 0 | 330 | 10 | 16 | 120 | 0 | 0 | 0 | 5 | 8 | 197 | 6 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 5895.9 | 1651 | 7546.9 | 3579 | 478 | 1604 | 832 | 356 | 117 | 452 | 128 | 0.9 | 0 | 81.09
11:00 | 37 | 0 | 0 | 120 | 365 | 24 | 40 | 370 | 348 | 0 | 0 | 450 | 200 | 7 | 14 | 15 | 120 | 0 | 99 | 0 | 0 | 7 | 65 | 10 | 8 | 10 | 0 | 18 | 56 | 17 | 0 | 0 | 32 | 33 | 25 | 8 | 0 | 85 | 30 | 0 | 0 | 16 | 0 | 202 | 0 | 100 | 0 | 8 | 0 | 14 | 80 | 91 | 31 | 19 | 3 | 0 | 100 | 0 | 310 | 316 | 195 | 176 | 153 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 15 | 0 | 128 | 135 | 95 | 20 | 2.4 | 25 | 75 | 22 | 17 | 140 | 307 | 61 | 86 | 47 | 0 | 0 | 30 | 7 | 320 | 23 | 8 | 0 | 15 | 0 | 0 |  | 478 | 0 | 320 | 10 | 16 | 120 | 0 | 0 | 0 | 6 | 8 | 197 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 6216.4 | 1645 | 7861.4 | 3555 | 478 | 1896 | 822 | 358 | 115 | 507 | 128 | 2.4 | 0 | 81.07
12:00 | 37 | 0 | 0 | 120 | 365 | 55 | 60 | 355 | 350 | 0 | 0 | 450 | 305 | 11 | 14 | 15 | 170 | 0 | 100 | 0 | 0 | 7 | 65 | 39 | 8 | 48 | 0 | 18 | 56 | 17 | 22 | 0 | 32 | 33 | 25 | 8 | 0 | 86 | 30 | 0 | 0 | 16 | 0 | 204 | 0 | 116 | 0 | 26 | 0 | 0 | 80 | 90 | 30 | 16 | 2 | 0 | 150 | 0 | 290 | 300 | 139 | 194 | 153 | 40 | 0 | 53 | 6 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 126 | 124 | 95 | 20 | 2.6 | 25 | 75 | 22 | 41 | 163 | 284 | 62 | 86 | 46 | 0 | 0 | 43 | 7 | 300 | 23 | 8 | 0 | 15 | 0 | 0 |  | 0 | 0 | 290 | 57 | 16 | 145 | 0 | 0 | 0 | 3 | 32 | 187 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 15 | 0 | 18 | 10 | 5 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 9 | 0 | 0 |  | 6536.6 | 1281 | 7817.6 | 3528 | 0 | 2055 | 1101 | 356 | 116 | 533 | 126 | 2.6 | 0 | 81.05
13:00 | 37 | 0 | 0 | 120 | 365 | 83 | 71 | 352 | 350 | 0 | 0 | 450 | 200 | 35 | 14 | 43 | 170 | 0 | 100 | 0 | 0 | 7 | 65 | 10 | 8 | 46 | 0 | 54 | 56 | 30 | 22 | 0 | 32 | 33 | 33 | 10 | 0 | 86 | 31 | 0 | 0 | 16 | 0 | 201 | 0 | 125 | 0 | 44 | 0 | 0 | 90 | 97 | 32 | 16 | 2 | 0 | 120 | 0 | 330 | 334 | 206 | 78 | 153 | 40 | 0 | 5 | 6 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 130 | 124 | 95 | 20 | 2.3 | 25 | 74 | 50 | 50 | 130 | 304 | 62 | 85 | 48 | 0 | 0 | 40 | 7 | 280 | 23 | 8 | 0 | 15 | 0 | 0 |  | 0 | 0 | 290 | 96 | 49 | 180 | 0 | 0 | 0 | 8 | 40 | 194 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 24 | 0 | 43 | 0 | 18 | 10 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 40 | 0 | 0 |  | 6549.3 | 1502 | 8051.3 | 3676 | 0 | 1915 | 1242 | 358 | 117 | 611 | 130 | 2.3 | 0 | 81.03
14:00 | 37 | 0 | 0 | 120 | 365 | 83 | 71 | 355 | 350 | 0 | 0 | 450 | 200 | 16 | 14 | 55 | 170 | 0 | 100 | 0 | 0 | 7 | 65 | 10 | 8 | 50 | 0 | 54 | 56 | 36 | 22 | 0 | 32 | 33 | 33 | 32 | 0 | 86 | 32 | 0 | 0 | 25 | 0 | 196 | 0 | 116 | 0 | 41 | 0 | 17 | 90 | 97 | 31 | 19 | 2 | 0 | 120 | 0 | 300 | 300 | 183 | 68 | 153 | 40 | 0 | 5 | 11 | 85 | 0 | 0 | 19 | 11 | 0 | 21 | 130 | 118 | 95 | 22 | 2 | 25 | 73 | 50 | 50 | 130 | 293 | 59 | 86 | 48 | 45 | 0 | 40 | 7 | 300 | 23 | 8 | 0 | 32 | 0 | 0 |  | 470 | 0 | 290 | 103 | 49 | 190 | 0 | 0 | 0 | 12 | 40 | 192 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 24 | 24 | 0 | 43 | 0 | 18 | 10 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 40 | 0 | 0 |  | 6528 | 2016 | 8544 | 3586 | 470 | 1931 | 1320 | 357 | 118 | 630 | 130 | 2 | 0 | 81.01
15:00 | 37 | 0 | 0 | 120 | 365 | 82 | 71 | 358 | 344 | 0 | 0 | 450 | 200 | 22 | 14 | 55 | 170 | 0 | 98 | 0 | 0 | 7 | 98 | 10 | 8 | 20 | 0 | 54 | 37 | 36 | 22 | 0 | 32 | 33 | 33 | 35 | 0 | 87 | 31 | 0 | 0 | 25 | 0 | 212 | 0 | 115 | 0 | 42 | 0 | 10 | 90 | 97 | 31 | 19 | 2 | 0 | 120 | 0 | 330 | 327 | 203 | 68 | 154 | 40 | 0 | 5 | 42 | 85 | 0 | 0 | 19 | 11 | 26 | 21 | 146 | 115 | 95 | 22 | 1.7 | 25 | 72 | 50 | 50 | 130 | 304 | 61 | 86 | 48 | 80 | 0 | 39 | 7 | 300 | 23 | 8 | 0 | 47 | 0 | 0 |  | 470 | 0 | 293 | 97 | 49 | 150 | 0 | 0 | 0 | 13 | 40 | 192 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 24 | 0 | 43 | 0 | 18 | 10 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 40 | 0 | 0 |  | 6732.7 | 1999 | 8731.7 | 3738 | 470 | 1953 | 1316 | 357 | 118 | 632 | 146 | 1.7 | 0 | 80.99
16:00 | 37 | 0 | 0 | 160 | 365 | 0 | 71 | 350 | 332 | 0 | 0 | 450 | 200 | 22 | 14 | 55 | 170 | 0 | 98 | 0 | 0 | 24 | 98 | 10 | 40 | 21 | 0 | 54 | 37 | 36 | 22 | 0 | 32 | 0 | 33 | 47 | 0 | 87 | 30 | 0 | 0 | 25 | 0 | 202 | 0 | 115 | 0 | 42 | 0 | 17 | 90 | 97 | 31 | 19 | 2 | 0 | 120 | 0 | 310 | 309 | 192 | 68 | 154 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 25 | 21 | 136 | 95 | 95 | 22 | 1.7 | 30 | 71 | 49 | 47 | 130 | 300 | 60 | 86 | 48 | 80 | 0 | 39 | 0 | 320 | 8 | 8 | 0 | 50 | 0 | 0 |  | 469 | 0 | 320 | 103 | 49 | 120 | 0 | 0 | 0 | 14 | 40 | 192 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 34 | 50 | 24 | 0 | 43 | 0 | 18 | 10 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 40 | 0 | 0 |  | 6620.7 | 2005 | 8625.7 | 3678 | 469 | 1880 | 1387 | 357 | 117 | 600 | 136 | 1.7 | 0 | 80.97
17:00 | 37 | 0 | 0 | 190 | 365 | 0 | 71 | 336 | 306 | 13 | 0 | 450 | 200 | 22 | 14 | 55 | 170 | 0 | 98 | 5 | 0 | 24 | 98 | 10 | 40 | 10 | 0 | 54 | 37 | 36 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 82 | 28 | 0 | 0 | 25 | 0 | 202 | 0 | 114 | 0 | 51 | 0 | 17 | 90 | 97 | 40 | 19 | 7 | 0 | 120 | 0 | 300 | 300 | 188 | 68 | 154 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 21 | 140 | 0 | 0 | 22 | 1 | 30 | 71 | 53 | 50 | 130 | 288 | 59 | 50 | 48 | 80 | 0 | 39 | 9 | 310 | 23 | 8 | 0 | 47 | 0 | 0 |  | 470 | 0 | 320 | 51 | 49 | 120 | 0 | 0 | 0 | 27 | 40 | 191 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 43 | 50 | 24 | 0 | 25 | 0 | 18 | 10 | 5 | 0 | 77 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 40 | 0 | 0 |  | 6461 | 1958 | 8419 | 3643 | 470 | 1830 | 1247 | 357 | 110 | 621 | 140 | 1 | 0 | 80.95
18:00 | 37 | 0 | 0 | 190 | 365 | 0 | 71 | 327 | 300 | 13 | 0 | 430 | 200 | 40 | 15 | 55 | 170 | 0 | 98 | 20 | 0 | 24 | 98 | 10 | 52 | 11 | 0 | 54 | 37 | 36 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 83 | 28 | 0 | 0 | 26 | 0 | 204 | 0 | 115 | 0 | 51 | 48 | 20 | 90 | 97 | 45 | 19 | 10 | 0 | 120 | 0 | 250 | 250 | 190 | 68 | 153 | 40 | 0 | 5 | 51 | 50 | 0 | 1 | 19 | 11 | 30 | 21 | 144 | 66 | 95 | 22 | 0 | 56 | 71 | 22 | 20 | 100 | 288 | 60 | 50 | 20 | 80 | 0 | 39 | 9 | 320 | 23 | 8 | 0 | 62 | 0 | 0 |  | 459 | 0 | 280 | 33 | 49 | 130 | 0 | 0 | 12 | 45 | 24 | 192 | 22 | 80 | 0 | 0 | 0 | 12 | 15 | 43 | 50 | 24 | 0 | 8 | 3 | 18 | 10 | 5 | 0 | 76 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 0 |  | 6498 | 1930 | 8428 | 3586 | 459 | 1665 | 1362 | 356 | 111 | 745 | 144 | 0 | 0 | 80.93
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51.57
19:00 | 37 | 0 | 0 | 190 | 365 | 70 | 40 | 319 | 304 | 84 | 0 | 430 | 200 | 55 | 54 | 55 | 110 | 0 | 101 | 50 | 0 | 64 | 149 | 60 | 91 | 11 | 13 | 54 | 56 | 36 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 83 | 28 | 0 | 0 | 25 | 0 | 202 | 0 | 80 | 0 | 42 | 82 | 49 | 102 | 97 | 44 | 19 | 23 | 0 | 120 | 0 | 288 | 309 | 190 | 68 | 153 | 40 | 0 | 5 | 51 | 55 | 0 | 20 | 19 | 11 | 33 | 21 | 170 | 35 | 95 | 22 | 0 | 54 | 74 | 22 | 25 | 100 | 297 | 64 | 86 | 20 | 100 | 0 | 17 | 9 | 270 | 23 | 8 | 10 | 148 | 0 | 11 |  | 459 | 0 | 300 | 33 | 49 | 170 | 0 | 13 | 47 | 60 | 40 | 191 | 29 | 80 | 0 | 0 | 0 | 43 | 48 | 76 | 50 | 24 | 47 | 9 | 35 | 18 | 10 | 11 | 0 | 76 | 280 | 17 | 0 | 0 | 0 | 0 | 0 | 51 | 10 | 0 | 0 |  | 7112 | 2276 | 9388 | 3649 | 459 | 1703 | 1835 | 356 | 111 | 1105 | 170 | 0 | 0 | 80.91
19:30 | 37 | 0 | 0 | 190 | 365 | 97 | 60 | 316 | 311 | 84 | 0 | 430 | 305 | 100 | 58 | 55 | 125 | 0 | 101 | 50 | 0 | 80 | 149 | 80 | 91 | 30 | 20 | 54 | 56 | 36 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 83 | 29 | 0 | 0 | 25 | 0 | 202 | 0 | 130 | 0 | 42 | 82 | 49 | 102 | 92 | 44 | 19 | 23 | 0 | 120 | 0 | 300 | 300 | 184 | 68 | 153 | 40 | 0 | 5 | 51 | 86 | 0 | 25 | 19 | 11 | 33 | 21 | 172 | 35 | 95 | 22 | 0 | 54 | 74 | 53 | 50 | 163 | 291 | 63 | 86 | 48 | 130 | 0 | 40 | 9 | 310 | 23 | 8 | 62 | 285 | 0 | 15 |  | 381 | 0 | 0 | 108 | 83 | 170 | 0 | 11 | 48 | 0 | 40 | 195 | 26 | 110 | 0 | 0 | 0 | 43 | 49 | 102 | 50 | 24 | 47 | 43 | 44 | 0 | 10 | 11 | 0 | 75 | 255 | 17 | 0 | 0 | 0 | 0 | 0 | 51 | 55 | 0 | 0 |  | 7901 | 2048 | 9949 | 3385 | 381 | 1977 | 2460 | 330 | 112 | 1132 | 172 | 0 | 0 | 0
20:00 | 37 | 0 | 0 | 190 | 365 | 107 | 50 | 316 | 306 | 84 | 0 | 430 | 270 | 91 | 60 | 55 | 125 | 0 | 104 | 70 | 0 | 84 | 149 | 88 | 91 | 51 | 31 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 84 | 29 | 0 | 0 | 25 | 0 | 202 | 0 | 100 | 0 | 42 | 82 | 49 | 102 | 91 | 44 | 19 | 25 | 0 | 150 | 0 | 300 | 301 | 183 | 68 | 153 | 40 | 0 | 5 | 51 | 86 | 0 | 30 | 19 | 11 | 33 | 21 | 164 | 50 | 95 | 22 | 0 | 54 | 74 | 53 | 50 | 163 | 290 | 49 | 86 | 49 | 128 | 0 | 41 | 9 | 270 | 23 | 8 | 85 | 218 | 0 | 50 |  | 381 | 33 | 0 | 105 | 83 | 180 | 0 | 13 | 48 | 30 | 40 | 175 | 31 | 110 | 0 | 0 | 0 | 43 | 48 | 102 | 50 | 43 | 47 | 43 | 44 | 0 | 10 | 8 | 0 | 74 | 240 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 98 | 0 | 0 |  | 7890 | 2145 | 10035 | 3393 | 381 | 1940 | 2557 | 314 | 113 | 1173 | 164 | 0 | 0 | 80.89
21:00 | 37 | 0 | 0 | 190 | 349 | 107 | 50 | 315 | 292 | 84 | 0 | 430 | 200 | 100 | 96 | 55 | 185 | 0 | 103 | 100 | 0 | 94 | 149 | 100 | 91 | 21 | 49 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 84 | 30 | 0 | 0 | 26 | 0 | 189 | 0 | 70 | 0 | 51 | 82 | 49 | 102 | 98 | 45 | 19 | 29 | 0 | 150 | 0 | 300 | 300 | 226 | 68 | 153 | 40 | 0 | 5 | 51 | 86 | 30 | 34 | 19 | 11 | 25 | 21 | 180 | 65 | 95 | 22 | 0 | 54 | 74 | 53 | 50 | 130 | 291 | 45 | 86 | 49 | 127 | 0 | 42 | 9 | 260 | 23 | 8 | 82 | 291 | 0 | 21 |  | 460 | 33 | 0 | 110 | 83 | 200 | 0 | 50 | 48 | 75 | 40 | 184 | 35 | 110 | 0 | 0 | 0 | 43 | 48 | 102 | 50 | 43 | 46 | 43 | 43 | 0 | 10 | 8 | 0 | 77 | 264 | 17 | 0 | 0 | 0 | 0 | 0 | 37 | 98 | 0 | 0 |  | 8007 | 2357 | 10364 | 3489 | 460 | 1879 | 2677 | 341 | 114 | 1224 | 180 | 0 | 0 | 80.87
22:00 | 37 | 0 | 0 | 190 | 350 | 104 | 50 | 290 | 292 | 84 | 0 | 430 | 200 | 100 | 100 | 55 | 170 | 0 | 100 | 100 | 0 | 94 | 149 | 100 | 91 | 10 | 49 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 84 | 30 | 0 | 0 | 26 | 0 | 189 | 0 | 70 | 0 | 51 | 82 | 49 | 102 | 98 | 45 | 19 | 27 | 0 | 150 | 0 | 300 | 300 | 225 | 68 | 153 | 40 | 0 | 5 | 51 | 85 | 50 | 25 | 19 | 11 | 32 | 21 | 172 | 80 | 95 | 20 | 0 | 54 | 74 | 53 | 50 | 100 | 292 | 43 | 86 | 49 | 122 | 0 | 43 | 9 | 270 | 23 | 8 | 11 | 301 | 0 | 11 |  | 460 | 33 | 130 | 110 | 83 | 214 | 0 | 53 | 48 | 70 | 40 | 185 | 36 | 110 | 12 | 0 | 0 | 43 | 48 | 102 | 50 | 43 | 46 | 43 | 43 | 0 | 10 | 11 | 0 | 75 | 254 | 17 | 0 | 0 | 0 | 0 | 0 | 49 | 100 | 0 | 0 |  | 7879 | 2518 | 10397 | 3594 | 460 | 1867 | 2596 | 329 | 114 | 1265 | 172 | 0 | 0 | 80.85
23:00 | 37 | 0 | 0 | 190 | 300 | 106 | 50 | 290 | 272 | 55 | 0 | 400 | 200 | 100 | 98 | 30 | 170 | 0 | 100 | 17 | 0 | 94 | 149 | 70 | 91 | 10 | 49 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 51 | 0 | 86 | 31 | 0 | 0 | 26 | 0 | 189 | 0 | 70 | 0 | 51 | 82 | 49 | 90 | 98 | 45 | 19 | 30 | 0 | 130 | 25 | 315 | 320 | 220 | 68 | 153 | 40 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 32 | 21 | 174 | 79 | 95 | 20 | 0 | 53 | 75 | 53 | 50 | 100 | 307 | 60 | 86 | 49 | 98 | 0 | 44 | 9 | 260 | 23 | 8 | 11 | 300 | 0 | 11 |  | 460 | 33 | 283 | 109 | 83 | 213 | 0 | 53 | 48 | 67 | 33 | 193 | 31 | 110 | 12 | 0 | 0 | 43 | 48 | 102 | 50 | 43 | 45 | 26 | 42 | 10 | 10 | 11 | 0 | 75 | 255 | 17 | 0 | 0 | 0 | 0 | 0 | 93 | 100 | 0 | 0 |  | 7590 | 2698 | 10288 | 3747 | 460 | 1862 | 2389 | 330 | 117 | 1209 | 174 | 0 | 0 | 80.83
24:00 | 37 | 0 | 0 | 190 | 300 | 106 | 50 | 285 | 270 | 13 | 0 | 380 | 200 | 100 | 80 | 30 | 170 | 0 | 100 | 17 | 0 | 94 | 149 | 70 | 91 | 10 | 46 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 52 | 0 | 86 | 31 | 0 | 0 | 26 | 0 | 188 | 0 | 135 | 0 | 51 | 82 | 49 | 78 | 98 | 44 | 19 | 30 | 0 | 130 | 60 | 300 | 300 | 222 | 68 | 153 | 40 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 32 | 22 | 172 | 51 | 95 | 20 | 0 | 54 | 75 | 53 | 50 | 100 | 297 | 64 | 86 | 49 | 98 | 0 | 42 | 9 | 310 | 23 | 8 | 11 | 220 | 0 | 11 |  | 459 | 17 | 287 | 109 | 83 | 215 | 0 | 53 | 48 | 57 | 33 | 194 | 31 | 110 | 0 | 0 | 0 | 0 | 48 | 102 | 50 | 43 | 45 | 26 | 42 | 18 | 10 | 11 | 0 | 75 | 255 | 16 | 0 | 0 | 0 | 0 | 0 | 98 | 70 | 0 | 0 |  | 7488 | 2605 | 10093 | 3717 | 459 | 1901 | 2204 | 330 | 117 | 1193 | 172 | 0 | 0 | 80.81
KWH | 780000 | 0 | 0 | 3276000 | 7940672 | 1304727 | 1462944 | 8210430 | 7679000 | 421800 | 0 | 9475226 | 5232291 | 878400 | 793320 | 865427 | 3843093 | 0 | 2329000 | 425280 | 0 | 709632 | 1877280 | 699904 | 844800 | 362000 | 239856 | 867960 | 960158 | 720000 | 448632 | 350000 | 729000 | 792800 | 803100 | 760128 | 0 | 1890487 | 728300 | 0 | 0 | 488700 | 0 | 4683387 | 0 | 1886318 | 0 | 816960 | 676024 | 576323 | 1972080 | 2120640 | 867360 | 447940 | 437760 | 0 | 2780495 | 60108 | 7419500 | 7096250 | 4802000 | 1906909 | 3638610 | 921960 | 0 | 168000 | 891906 | 793320 | 73832 | 182010 | 446148 | 252180 | 564400 | 463580 | 3340800 | 2422450 | 1780555 | 504072 | 15601 | 952000 | 1788000 | 873600 | 845000 | 3093709 | 6551103 | 1395000 | 1744320 | 969840 | 992180 | 0 | 769860 | 184860 | 7539880 | 527496 | 192384 | 186240 | 1957090 | 0 | 121160 |  | 10313455 | 126300 | 6645312 | 1155960 | 895680 | 3599040 | 0 | 201290 | 388800 | 606464 | 520875 | 4698325 | 539140 | 1106880 | 26780 | 0 | 0 | 187553 | 270818 | 846922 | 958490 | 605104 | 232397 | 497280 | 254300 | 365760 | 236268 | 157896 | 0 | 1856727 | 6686900 | 91000 | 0 | 0 | 0 | 0 | 0 | 978429 | 689280 | 0 | 0 |  | 154883547 | 45739425 | 200622972 | 85222116 | 10313455 | 42260458 | 31904590 | 8543627 | 2618787 | 16403538 | 3340800 | 15601 | 0
Fuel Cost | 670800 | 0 | 0 | 2817360 | 6828977.92 | 1056828.87 | 1375167.36 | 5008362.3 | 4684190 | 4053498 | 0 | 6348401.42 | 79478500.29 | 5516352 | 5299377.6 | 5287758.97 | 2498010.45 | 0 | 2585190 | 6617356.8 | 0 | 4676474.88 | 18153297.6 | 4458388.48 | 5060352 | 5788380 | 1599839.52 | 6188554.8 | 6000987.5 | 4514400 | 336474 | 262500 | 0 | 0 | 0 | 7190810.88 | 0 | 0 | 0 | 0 | 0 | 4627989 | 0 | 63928232.55 | 0 | 41329227.38 | 0 | 7181078.4 | 7280778.48 | 5607622.79 | 12207175.2 | 13699334.4 | 5672534.4 | 380749 | 0 | 0 | 2530250.45 | 54698.28 | 6751745 | 4896412.5 | 3361400 | 1315767.21 | 3493065.6 | 617713.2 | 0 | 154560 | 731362.92 | 745720.8 | 800338.88 | 1350514.2 | 343533.96 | 189135 | 434588 | 347685 | 22851072 | 1816837.5 | 16363300.45 | 388135.44 | 0 | 990080 | 1859520 | 838656 | 760500 | 3990884.61 | 4585772.1 | 1590300 | 1866422.4 | 1066824 | 1131085.2 | 0 | 715969.8 | 171919.8 | 4825523.2 | 395622 | 146211.84 | 3227539.2 | 0 | 0 | 0 |  | 52598620.5 | 3681645 | 4452359.04 | 7629336 | 6001056 | 57872563.2 | 0 | 3212588.4 | 4377888 | 7144145.92 | 3317973.75 | 4651341.75 | 533748.6 | 6840518.4 | 901950.4 | 0 | 0 | 2147481.85 | 2903168.96 | 7588421.12 | 8290938.5 | 5385425.6 | 2475028.05 | 4933017.6 | 2738811 | 402336 | 222091.92 | 119527.272 | 0 | 11270332.89 | 0 | 2099370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 463971979.78 | 213791685.722 | 677763665.502 | 66535442.802 | 52598620.5 | 31806874.91 | 261671351.22 | 11270332.89 | 0 | 231029971.18 | 22851072 | 0 | 0
Yesterday Day Peak | 37 | 0 | 0 | 120 | 365 | 24 | 40 | 370 | 348 | 0 | 0 | 450 | 200 | 7 | 14 | 15 | 120 | 0 | 99 | 0 | 0 | 7 | 65 | 10 | 8 | 10 | 0 | 18 | 56 | 17 | 0 | 0 | 32 | 33 | 25 | 8 | 0 | 85 | 30 | 0 | 0 | 16 | 0 | 202 | 0 | 100 | 0 | 8 | 0 | 14 | 80 | 91 | 31 | 19 | 3 | 0 | 100 | 0 | 310 | 316 | 195 | 176 | 153 | 40 | 0 | 5 | 51 | 85 | 0 | 0 | 19 | 11 | 15 | 0 | 128 | 135 | 95 | 20 | 2.4 | 25 | 75 | 22 | 17 | 140 | 307 | 61 | 86 | 47 | 0 | 0 | 30 | 7 | 320 | 23 | 8 | 0 | 15 | 0 | 0 |  | 478 | 0 | 320 | 10 | 16 | 120 | 0 | 0 | 0 | 6 | 8 | 197 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 78 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 |  | 7861.4 | DayPeak
Yesterday Evening Peak | 37 | 0 | 0 | 190 | 349 | 107 | 50 | 315 | 292 | 84 | 0 | 430 | 200 | 100 | 96 | 55 | 185 | 0 | 103 | 100 | 0 | 94 | 149 | 100 | 91 | 21 | 49 | 54 | 56 | 55 | 22 | 25 | 32 | 33 | 33 | 50 | 0 | 84 | 30 | 0 | 0 | 26 | 0 | 189 | 0 | 70 | 0 | 51 | 82 | 49 | 102 | 98 | 45 | 19 | 29 | 0 | 150 | 0 | 300 | 300 | 226 | 68 | 153 | 40 | 0 | 5 | 51 | 86 | 30 | 34 | 19 | 11 | 25 | 21 | 180 | 65 | 95 | 22 | 0 | 54 | 74 | 53 | 50 | 130 | 291 | 45 | 86 | 49 | 127 | 0 | 42 | 9 | 260 | 23 | 8 | 82 | 291 | 0 | 21 |  | 460 | 33 | 0 | 110 | 83 | 200 | 0 | 50 | 48 | 75 | 40 | 184 | 35 | 110 | 0 | 0 | 0 | 43 | 48 | 102 | 50 | 43 | 46 | 43 | 43 | 0 | 10 | 8 | 0 | 77 | 264 | 17 | 0 | 0 | 0 | 0 | 0 | 37 | 98 | 0 | 0 |  | 10364 | EvPeak
Forecast for Evening | 37 | 0 | 0 | 190 | 350 | 100 | 78 | 412 | 360 | 84 | 0 | 450 | 305 | 100 | 100 | 55 | 170 | 0 | 100 | 100 | 87 | 94 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 87 | 32 | 0 | 0 | 25 | 0 | 206 | 0 | 135 | 0 | 51 | 85 | 51 | 102 | 98 | 45 | 20 | 20 | 0 | 150 | 80 | 360 | 360 | 225 | 68 | 153 | 42 | 0 | 10 | 51 | 85 | 50 | 52 | 19 | 11 | 33 | 22 | 186 | 135 | 95 | 22 | 0 | 60 | 76 | 50 | 50 | 163 | 330 | 66 | 86 | 49 | 100 | 0 | 44 | 9 | 341 | 23 | 11 | 200 | 300 | 0 | 0 |  | 475 | 33 | 300 | 110 | 115 | 225 | 0 | 55 | 50 | 75 | 40 | 194 | 30 | 110 | 30 | 0 | 0 | 43 | 48 | 100 | 50 | 43 | 45 | 43 | 44 | 18 | 10 | 11 | 0 | 78 | 280 | 17 | 18 | 0 | 0 | 0 | 0 | 95 | 100
Forecast for Day | 37 | 0 | 0 | 120 | 350 | 100 | 78 | 412 | 360 | 84 | 0 | 450 | 305 | 100 | 100 | 55 | 170 | 0 | 100 | 100 | 87 | 94 | 149 | 100 | 100 | 50 | 49 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 51 | 0 | 85 | 30 | 0 | 0 | 25 | 0 | 203 | 0 | 135 | 0 | 51 | 85 | 51 | 90 | 98 | 45 | 20 | 6 | 0 | 150 | 80 | 360 | 360 | 225 | 68 | 153 | 42 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 11 | 33 | 20 | 143 | 100 | 95 | 22 | 2 | 60 | 76 | 50 | 50 | 163 | 330 | 66 | 86 | 49 | 100 | 0 | 44 | 9 | 341 | 23 | 11 | 0 | 100 | 0 | 0 |  | 475 | 0 | 80 | 110 | 115 | 225 | 0 | 0 | 0 | 50 | 40 | 194 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 50 | 43 | 45 | 43 | 0 | 18 | 10 | 11 | 0 | 78 | 280 |  | 0 | 0 | 0 | 0 | 0 | 95
Generation at 08:00(Today) | 37 | 0 | 0 | 190 | 250 | 0 | 0 | 385 | 348 | 13 | 0 | 430 | 200 | 29 | 48 | 35 | 170 | 0 | 0 | 0 | 0 | 24 | 98 | 30 | 8 | 11 | 6 | 36 | 50 | 36 | 22 | 25 | 32 | 33 | 33 | 10 | 0 | 82 | 30 | 0 | 0 | 25 | 0 | 203 | 0 | 60 | 0 | 0 | 16 | 16 | 90 | 59 | 17 | 19 | 2 | 0 | 100 | 80 | 325 | 276 | 194 | 68 | 153 | 37 | 0 | 5 | 51 | 51 | 0 | 0 | 19 | 11 | 8 | 22 | 118 | 99 | 95 | 20 | 0.8 | 50 | 75 | 53 | 50 | 130 | 307 | 62 | 20 | 49 | 78 | 0 | 43 | 9 | 320 | 22 | 8 | 0 | 100 | 0 | 0 | 0 | 460 | 0 | 0 | 10 | 16 | 120 | 0 | 0 | 0 | 8 | 33 | 193 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 8 | 0 | 8 | 0 | 18 | 10 | 5 | 0 | 75 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6506.1 | 6:00
| Highest Generation |  | 10397 | 22:00
| Day Peak Generation |  | 7861.4 | 11:00
| Evening Peak Generation |  | 10364 | 21:00
| HVDC Max Flow |  | 478 | 7:00
| HVDC EvPeak Flow |  | 460 | 21:00
| Load factor L.F |  | 80.4%

## P1
z |  |  | POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-03
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7861.4 | MW Hour : | 11:00 | Min. Gen. at | 7:00 | 7592.1 | MW
Evening Peak Generation : |  | 10364 | MW Hour : | 21:00 | Available Max Generation : |  | 11990 | MW
E.P. Demand (at gen end) : |  | 10364 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10397 | MW Hour : | 22:00 | Reserve(Generation end) |  | 990 | MW
Total Gen. (MKWH) : |  | 200.623 | System Load Factor : | 80.4% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -1000 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-03
Actual : | 81.19 | Ft.(MSL) , | Rule curve : | 76.26 | Ft.( MSL )
Gas Consumed : | Total = | 1064.33 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 98342317.712
|  | Coal : | 11270332.89 | Oil : | 492701322.4 | Total : | 602313973.002
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3865.854 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1314.0092 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1177.2026 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1063.6642 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 961.2387 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 775.6841 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 434.4903 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 199.7381 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 598.2424 |  |  | 0 | 0%
Total | 0 |  | 10390.1235 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj ST: Unit- 5
| Nil |  |  | 2) Sylhet 20 MW |  | 11) Haripur GT-1,2
|  |  |  | 3) Khulna ST 110 MW | (04/11/14) | 12) Sirajgonj Unit-1 & 2
|  |  |  | 4) Ghorasal Unit-2,3,4 |  | 13) Ashuganj 55 MW
|  |  |  | 5) Baghabari 100 MW |  | 14) Sylhet-150 MW
6) Tongi GT
7) Chittagong Unit-1,2
8) Baghabari-71 MW
9) Siddhirganj 210 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Aminbazar-Savar 132 kV Ckt-1 was under shut down from 08:40 to 14:37 for C/M.
b) Ishurdi 230 kV bus-2 was under shut down from was shut down at 09:35 for C/M.
c) Ishurdi-Ghorasal 230 kV Ckt-2 was under shut down from 10:59 to 15:39 for C/M.
d) Comilla(N) 132/33 kV T3 transformer was under shut down from 09:10 to 10:50 due to red
hot at 33 kV PBS feeder.
e) Ishurdi-Baghabari 230 kV Ckt-2 was shut down at 09:35 for C/M.
f) Khulna-Satkhira 132 kV Ckt-1 was under shut down from 12:43 to 13:35 for Tree trimming.
g) BSRM 230/132 kV TR transformer tripped at 09:19 showing PRD and was switched on at 11:57.
h) Ishurdi-Ghorasal 230 kV Ckt-1 tripped at 11:40 from both end showing PD3,PTAW,RST,D2,D2H,Z2
at Ishurdi end & DTS,PD3,PTAW at Ghorasal end and was switched on at 12:34. Again tripped at 13:23
from both end showing same signal and was switched on at 13:27.
i) Amnura 132/33 kV T1 transformer tripped at 12:35 due to O/V and was switched on at 12:40.
j) Bheramara HVDC pole-1 tripped at 11:23 due to all 400 kV filter & reactor tripped and was switched on at 13:10.
k) Bogra 230/132 kV T1 transformer was under shut down from 10:21 to 11:06 for red hot at DS.
l) Tongi 132/33 kV T1 ,T2 & T3 transformer tripped at 13:28 due to 33 kV saver PBS feeder fault and |  |  |  | About 98MW & 38MW power interruption occurred under Tongi S/S
were switched on at 13:38,13:38 & 18:03 respectively. |  |  |  | area from 13:28 to 13:38 & 13:38 to 18:03 respectively.
m) Tangail-Mymensingh 132 kV Ckt-1 was under shut down from 13:11 to 16:16 for red hot maintenance.
n) Tongi(New) 132/33 kV T2 transformer was under shut down 15:30 to due to top-up oil and was switched |  |  |  | About 14MW power interruption occurred under Tongi(New) S/S
on at 16:32 |  |  |  | area from 15:30 to 16:32.
o) Fenchuganj S/S-Fenchuganj P/S 132 kV Ckt-2 tripped at 16:58 from Fenchuganj S/S and was switched on at 17:37.
p) Bheramara 410 MW CCPP tripped at 19:09 due to GBC problem and was synchronized at 21:15.
q) Ashuganj-Kishoreganj 132 kV Ckt-1 tripped at 16:46 from Kishoreganj end showing dist AC and was |  |  |  | About 292 MW power interruption occurred under Kishoreganj
switched on at 17:26. |  |  |  | Jamalpur,Sherpur,Mymensing & Netrokona S/S area
r) After maintenance Ashuganj-Kishorganj 132 kV Ckt-2 was switched on at 16:55. |  |  |  | from 16:46 to 17:26.
s) Bagherhat 132/33 kV T3 transformer tripped at 21:37 due to 33 kV Rampal feeder fault and was |  |  |  | About 55 MW power interruption occurred under Bagherhat S/S
switched on at 21:43. |  |  |  | area from 21:37 to 21:43.
t) Mymensingh RPCL tripped at 16:46 due to tripping of system disturbance at Mymensingh zone.
u) Ashuganj-Bhulta 400 kV Ckt-1 tripped at 15:45 showing SOTF.
v) Bakulia-Sikalbaha 132 kV Ckt-1 was under shut down from 23:59 to due to red hot at Y-phase isolator.
w) Bheramara CCPP GT was shut down at 05:46 for synchronizing ST.
x) Ashuganj-Kishoreganj 132 kV Ckt-2 was shut down at 07:06 (03/06/2018) for C/M.
y) Pabna-shajadpur 132 kV Ckt was shut down at 23:02 due to Pabna-Ishurdi line O/L and was
switched on at 04:10(03/06/2018).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 37 | 780000 | #1 Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 190 | 3276000
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 349 | 7940672 | On test.
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 50 | 1462944 | Gas shortage
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 107 | 1304727
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 315 | 8210430 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 84 | 421800 | Engine problem
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 292 | 7679000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 430 | 9475226 | frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 878400
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 200 | 5232291 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 96 | 793320 | Engine problem
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 865427
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 699904
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 448632
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 103 | 2329000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 100 | 425280
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | 132 kV Line fault.
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 185 | 3843093 | On test.
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 21 | 362000 | Low demand
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 94 | 709632 | Engine problem
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 49 | 239856
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 867960
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1877280
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 960158
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 720000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 91 | 844800 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1079000 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 792800
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 803100
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 760128
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 291 | 1957090 | On test.
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 MW | 0 | 21 | 121160 | On test.
| Dhaka area Total |  |  |  | 5199 | 3869 | 68161110
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 26 | 488700
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 45 | 867360 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 114 | 2618787
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 189 | 4683387
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 70 | 1886318 | FGMO
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 816960
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 82 | 676024
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 49 | 576323
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 102 | 1972080
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 447940 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 437760
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 2120640 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 874 | 17592279
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Under maint.
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 2780495 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 60108 | Under maint.
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 226 | 4802000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7419500 | FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7096250 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 40 | 921960
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 168000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 68 | 1906909 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 891906
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 86 | 793320
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 30 | 73832
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 153 | 3638610
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 446148
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252180
** | Tripura |  | Imported power | 0 | 160 | 180 | 3340800
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 25 | 564400 | Engine problem
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 34 | 182010 | Low demand
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 463580
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 82 | 186240 | On test.
| Comilla Area Total |  |  |  | 2541 | 1781 | 35988248
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 65 | 2422450 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 22 | 504072
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1780555
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 15601
| Mymensingh Area Total |  |  |  | 322 | 182 | 4722678
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 54 | 952000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 74 | 1788000
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 130 | 3093709
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 291 | 6551103 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 873600
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 845000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 8 | 192384
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 45 | 1395000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1744320
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 49 | 969840
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 127 | 992180
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 42 | 769860
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 527496
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 260 | 7539880 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 184860
| Sylhet Area Total |  |  |  | 1549 | 1301 | 28419232
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 33 | 126300
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 460 | 10313455
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 110 | 1155960
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 895680 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 48 | 388800
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 200 | 3599040 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 75 | 606464
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 0 | 6645312 | Gas shortage
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 520875
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 50 | 201290
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 98 | 689280 | On test.
| Khulna Area Total |  |  |  | 1769 | 1197 | 25142456
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 110 | 1106880
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 26780 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 35 | 539140
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 184 | 4698325
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 37 | 978429
| Barisal Area Total |  |  |  | 462 | 366 | 7349554
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 187553
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 48 | 270818
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 50 | 958490
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 605104 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 46 | 232397
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Under maint.
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 43 | 254300
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 0 | 365760 | Engine problem
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 10 | 236268
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 157896
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 497280 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 846922
| Rajshahi Area Total |  |  |  | 1123 | 436 | 4612788
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 77 | 1856727
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 264 | 6686900
117 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 91000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 0 | 0
| Rangpur Area Total |  |  |  | 484 | 358 | 8634627
| Total |  |  |  | 15010 | 10364 | 200622972
| Eastern Grid Total |  |  |  | 11172 | 8007 | 154883547
| Western Grid Total |  |  |  | 3838 | 2357 | 45739425
| National Grid Total |  |  |  | 15010 | 10364 | 200622972
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-02 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6841 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2936 | MW
i) Dhaka area |  |  | 3733 | MW | i) Khulna area |  |  | 1103 | MW
ii) Chittagong area |  |  | 1096 | MW | ii) Rajshahi area |  |  | 1040 | MW
iii) Comilla area |  |  | 948 | MW | iii) Barisal area |  |  | 255 | MW
iv) Mymensingh area |  |  | 632 | MW | iv) Rangpur area |  |  | 538 | MW
v) Sylhet area |  |  | 432 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9777 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 1200 | Kishorganj | 87 | 2200 | Central s/s | 70 | 2200
Munsiganj | 112 | 2100 | Netrokona | 76 | 2100 | Noapara | 92 | 2000
Megnaghat | 45 | 2200 | Jamalpur | 85 | 2000 | Jessore | 133 | 2300
Shyampur | 160 | 1300 | Sherpur | 62 | 2200 | Jhenida | 89 | 2300
Bhulta | 187 | 2300 | Srimongal | 33 | 1900 | Bottail | 98 | 2300
Madanganj | 52 | 1930 | Shahjibazar | 105 | 2100 | G.K Project | 54 | 2100
Shitalakhya | 105 | 1100 | Fenchuganj | 52 | 1930 | Faridpur | 140 | 2300
Rahim steel | 8 | 900 | Kulawara | 40 | 2100 | Madaripur | 109 | 2300
Matuail | 92 | 1500 | Sylhet | 154 | 2100 | Gopalganj | 85 | 2200
Ghorasal | 72 | 2000 | Chatak | 28 | 1900 | Bagerhat | 86 | 1930
Narsingdi | 122 | 2100 | Sunamganj | 28 | 1900 | Mongla | 36 | 900
Haripur (SBU) | 86 | 900 | Comilla (S) | 180 | 2100 | Satkhira | 91 | 2100
Ullon | 90 | 2000 | Comilla(N) | 101 | 1900 | Gallamari | 50 | 1900
Hasnabad | 192 | 2000 | Chandpur | 115 | 1930 | Magura | 46 | 1930
Magbazar | 115 | 1300 | Feni | 110 | 2200 | Chuadanga | 66 | 2300
Maniknagar | 80 | 2100 | Chowmuhani | 180 | 2300 | Barisal | 106 | 2200
Bangabhaban | 20 | 1300 | Ashuganj | 57 | 2100 | Patuakhali | 88 | 2100
Narinda | 84 | 1400 | Daudkandi | 104 | 2200 | Bhandaria | 46 | 2200
Dhanmondi | 106 | 1300 | B.Baria | 126 | 2100 | Ishurdi | 48 | 2100
Lalbag | 83 | 1300 | Madunaghat | 52 | 2100 | Ruppur Paromanobik | 1 | 100
Madartek | 49 | 2000 | Hathazari | 92 | 2100 | Natore | 107 | 2100
Mirpur | 101 | 2100 | Khulshi | 192 | 1400 | Bogra | 196 | 2100
Kalyanpur | 120 | 2100 | Halishahar | 134 | 2000 | Noagaon | 92 | 2100
Gulshan | 108 | 1300 | Baraulia | 129 | 400 | Rajshahi | 134 | 2000
Uttara | 83 | 2000 | Sikalbaha | 44 | 1900 | C.Nawabganj | 63 | 2100
Kamrangirchar | 81 | 1500 | Dohazari | 82 | 2100 | Amnura | 33 | 2100
Savar | 148 | 1930 | Cox'sbazar | 87 | 2100 | Pabna | 110 | 2000
Bhasantec | 146 | 2100 | Chandraghona | 34 | 2100 | Shahjadpur | 88 | 2100
Agargaon | 43 | 1930 | Kaptai | 5 | 1900 | Serajganj | 87 | 2000
Satmosjid | 96 | 2000 | A. Khaer Stl. | 8 | 400 | Niyamatpur | 48 | 2100
Tongi | 112 | 800 | Bakulia | 107 | 2100 | Joypurhat | 44 | 2000
Kabirpur | 175 | 1700 | Julda | 22 | 1500 | Rangpur | 112 | 1900
Basundhara | 119 | 2100 | TK chemical | 6 | 1300 | Lalmonirhat | 84 | 1930
Manikganj | 65 | 1200 | Modern Steel | 14 | 900 | Saidpur | 106 | 1930
Joydevpur | 217 | 2100 | Shahmirpur | 27 | 2100 | Purbasadipur | 80 | 1930
New Tongi | 109 | 1400 | Abul Khair 230 | 201 | 1600 | Thakurgaon | 64 | 2100
Korda | 212 | 1200 | BSRM | 110 | 400 | Palashbari | 84 | 2100
Tangail | 156 | 2000 | Khagrachhari | 15 | 1930 | Barapukuria | 42 | 2000
Mymensing | 194 | 1930 | Goalpara | 47 | 2200 | Panchagar | 38 | 2000
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC
Planning Commission. |  |  | (17) C.E. System Operation,PGCB |  |  |  | Page 4 of 7

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-02
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 393 | 4:00 | 381 | 17:00 | Kaliakoir | 374 | 5:00 | 358 | 15:00
Bheramara | 414 | 5:00 | 396 | 15:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 226 | 10:00 | Tongi | 224 | 5:00 | 212 | 11:00
Ishurdi | 235 | 12:00 | 212 | 21:00 | Comilla (N) | 230 | 4:00 | 221 | 14:00
Ashuganj | 235 | 1:00 | 228 | 21:00 | Hathazari | 220 | 18:00 | 210 | 15:00
Serajganj | 229 | 6:00 | 202 | 19:30 | Megnaghat | 229 | 1:00 | 221 | 10:00
Baghabari | 224 | 9:00 | 208 | 19:30 | Fenchuganj | 235 | 3:00 | 230 | 13:00
Barapukuria | 237 | 6:00 | 225 | 19:30 | Siddhirganj | 225 | 1:00 | 218 | 15:00
Bogra | 225 | 5:00 | 200 | 20:00 | Maniknagar | 225 | 6:00 | 217 | 11:00
Khulna South | 236 | 12:00 | 222 | 20:00 | Old Airport | 224 | 5:00 | 213 | 15:00
Rampura | 225 | 5:00 | 218 | 15:00 | Barisal | 237 | 20:00 | 227 | 4:00
Haripur | 224 | 1:00 | 217 | 14:00 | AKSML | 219 | 1:00 | 207 | 4:00
Hasnabad | 226 | 5:00 | 215 | 11:00 | BSRM | 221 | 18:30 | 209 | 13:00
Aminbazar | 225 | 1:00 | 215 | 16:00 | Bibiyana | 232 | 2:00 | 227 | 15:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1830 | 130 | 1100 | Madanhat | 132 | 1830 | 126 | 1500
Munsiganj | 136 | 1830 | 129 | 1100 | Hathazari | 128 | 2100 | 126 | 1800
Megnaghat | 134 | 2000 | 128 | 900 | Khulshi | 128 | 100 | 122 | 1500
Shyampur | 131 | 2100 | 124 | 1000 | Halishahar | 130 | 1830 | 124 | 700
Bhulta | 138 | 1830 | 130 | 1000 | Baraulia | 128 | 1830 | 124 | 1500
Madanganj | 133 | 100 | 126 | 1100 | Sikalbaha | 131 | 500 | 124 | 700
Shitalakhya | 137 | 1830 | 125 | 1100 | Dohazari | 128 | 1930 | 124 | 1500
Rahim steal | 135 | 1800 | 130 | 1100 | Cox'sbazar | 126 | 2100 | 118 | 1930
Matuail | 135 | 1830 | 128 | 1100 | Chandraghona | 130 | 2100 | 127 | 1500
Ghorasal | 137 | 100 | 133 | 1000 | Kaptai | 130 | 2100 | 127 | 1500
Narsinghdi | 133 | 1900 | 123 | 1100 | A. Khaer Stl. | 128 | 2000 | 125 | 1100
Haripur (SBU) | 136 | 200 | 130 | 1600 | Bakulia | 127 | 1830 | 123 | 1100
Ullon | 138 | 600 | 131 | 1300 | Julda | 130 | 100 | 125 | 1400
Hasnabad | 135 | 600 | 127 | 1100 | TK Chemical | 132 | 1900 | 129 | 1700
Magbazar | 138 | 600 | 130 | 1300 | Modern Steel | 128 | 1900 | 124 | 1400
Maniknagar | 137 | 600 | 131 | 1200 | Shahmirpur | 130 | 1830 | 125 | 1100
Bangabhaban | 132 | 1900 | 131 | 1000 | Khagrachhari | 131 | 300 | 126 | 1400
Narinda | 137 | 600 | 131 | 1300 | Goalpara | 137 | 2200 | 130 | 1100
Dhanmondi | 138 | 600 | 131 | 1300 | Central s/s | 137 | 1200 | 130 | 1100
Lalbag | 132 | 1900 | 122 | 1000 | Noapara | 135 | 2200 | 128 | 300
Madartek | 137 | 600 | 130 | 1300 | Jessore | 130 | 600 | 120 | 1900
Mirpur | 135 | 100 | 127 | 1300 | Jhenida | 130 | 700 | 118 | 2000
Kalyanpur | 136 | 400 | 127 | 1500 | Bottail | 137 | 1000 | 121 | 1930
Gulshan | 138 | 500 | 130 | 1500 | G.K.Project | 141 | 500 | 127 | 2000
Uttara | 133 | 600 | 122 | 1300 | Faridpur | 132 | 100 | 125 | 1100
Kamrangirchar | 133 | 400 | 123 | 1500 | Madaripur | 133 | 1830 | 125 | 300
Savar | 133 | 600 | 123 | 1500 | Gopalganj | 135 | 1830 | 124 | 1500
Bhasantec | 130 | 600 | 121 | 1500 | Bagerhat | 138 | 1200 | 126 | 400
Agargaon | 130 | 400 | 122 | 1500 | Mongla | 133 | 1200 | 123 | 400
Satmosjid | 130 | 600 | 122 | 1300 | Satkhira | 137 | 1200 | 128 | 1100
Tongi | 136 | 2100 | 126 | 1100 | Gallamari | 137 | 1200 | 131 | 100
Kabirpur | 134 | 400 | 118 | 1200 | Magura | 131 | 600 | 117 | 1930
Basundhara | 131 | 100 | 123 | 1200 | Chuadanga | 127 | 600 | 112 | 1900
Manikganj | 140 | 500 | 130 | 1200 | Barisal | 138 | 1200 | 131 | 1100
Joydevpur | 138 | 300 | 129 | 1200 | Patuakhali | 138 | 1200 | 131 | 1100
New Tongi | 135 | 1900 | 125 | 1100 | Bhandaria | 135 | 1200 | 126 | 300
Kodda | 135 | 1800 | 125 | 1100 | Ishurdi | 142 | 1200 | 126 | 2000
Tangail | 135 | 1100 | 123 | 2200 | Ruppur Paromanobik | 140 | 1100 | 128 | 2000
Mymensing | 131 | 800 | 108 | 2100 | Natore | 137 | 1200 | 121 | 2000
Kishorganj | 132 | 800 | 117 | 2000 | Bogra | 135 | 700 | 118 | 2000
Netrokona | 138 | 1700 | 110 | 2100 | Noagaon | 130 | 500 | 114 | 2000
Jamalpur | 132 | 900 | 113 | 1930 | Rajshahi | 135 | 1830 | 124 | 2000
Sherpur | 133 | 900 | 108 | 2100 | C.Nawabganj | 133 | 1830 | 123 | 2000
Srimongal | 135 | 1830 | 130 | 1100 | Amnura | 137 | 1800 | 124 | 1300
Shahjibazar | 136 | 1830 | 129 | 1100 | Pabna | 132 | 800 | 120 | 2000
Fenchuganj | 134 | 2000 | 128 | 900 | Shahjadpur | 140 | 500 | 130 | 1930
Khulawara | 131 | 2100 | 124 | 1000 | Serajganj | 133 | 100 | 120 | 2000
Sylhet | 138 | 1830 | 130 | 1000 | Niyamatpur | 133 | 1400 | 110 | 2000
Chatak | 133 | 100 | 126 | 1100 | Joypurhat | 132 | 600 | 111 | 2000
Sunamganj | 137 | 1830 | 125 | 1100 | Rangpur | 129 | 700 | 108 | 1930
Comilla(s) | 131 | 600 | 121 | 1900 | Lalmonirhat | 128 | 700 | 100 | 2000
Comilla(n) | 135 | 700 | 127 | 1400 | Saidpur | 129 | 500 | 106 | 1930
Chandpur | 131 | 900 | 123 | 2300 | Purbasadipur | 136 | 500 | 117 | 1930
Feni | 121 | 700 | 115 | 2300 | Thakurgaon | 130 | 600 | 110 | 1930
Chowmuhani | 126 | 700 | 119 | 2300 | Palashbari | 130 | 600 | 110 | 2000
Ashuganj | 137 | 700 | 131 | 2100 | Barapukuria | 137 | 600 | 125 | 1930
Daudkandi | 135 | 1930 | 128 | 1300 | Panchagar | 125 | 500 | 102 | 1930
B.Baria | 136 | 1000 | 129 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-06-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 640 | 7488 | 2605 | 10093 |  |  |  | QF-LDC-12
0:30 | 535 | 6848.5 | 2237 | 9085.5 | Date: | 2018-06-02
1:00 | 430 | 6209 | 1869 | 8078
1:30 | 515 | 6169.5 | 1837.5 | 8007
2:00 | 600 | 6130 | 1806 | 7936
2:30 | 615 | 6247.5 | 1821 | 8068.5 | [5 empty] | Gen. at Eve. Peak | 10364 | 10364 MW (21:00 )
3:00 | 630 | 6365 | 1836 | 8201 | [6 empty] | 21:00
3:30 | 585 | 6181 | 1788.5 | 7969.5 | [5 empty] | Gen. at Day Peak | 7861.4 | 7861.4 MW (11:00 )
4:00 | 540 | 5997 | 1741 | 7738 | [6 empty] | 11:00
4:30 | 465 | 5652 | 1670 | 7322 | [5 empty] | Highest Generation | 10397
5:00 | 390 | 5307 | 1599 | 6906 | [6 empty] | 22:00
5:30 | 365 | 5153.55 | 1552.5 | 6706.05
6:00 | 340 | 5000.1 | 1506 | 6506.1
6:30 | 325 | 5075.7 | 1520 | 6595.7
7:00 | 310 | 5151.3 | 1534 | 6685.3
7:30 | 300 | 5291.05 | 1562 | 6853.05
8:00 | 290 | 5430.8 | 1590 | 7020.8
8:30 | 300 | 5587.9 | 1621 | 7208.9
9:00 | 310 | 5745 | 1652 | 7397
9:30 | 345 | 5820.45 | 1651.5 | 7471.95
10:00 | 380 | 5895.9 | 1651 | 7546.9
10:30 | 380 | 6056.15 | 1648 | 7704.15
11:00 | 380 | 6216.4 | 1645 | 7861.4
11:30 | 475 | 6376.5 | 1463 | 7839.5
12:00 | 570 | 6536.6 | 1281 | 7817.6
12:30 | 580 | 6542.95 | 1391.5 | 7934.45
13:00 | 590 | 6549.3 | 1502 | 8051.3
13:30 | 475 | 6538.65 | 1759 | 8297.65
14:00 | 360 | 6528 | 2016 | 8544
14:30 | 380 | 6630.35 | 2007.5 | 8637.85
15:00 | 400 | 6732.7 | 1999 | 8731.7
15:30 | 420 | 6676.7 | 2002 | 8678.7
16:00 | 440 | 6620.7 | 2005 | 8625.7
16:30 | 445 | 6540.85 | 1981.5 | 8522.35
17:00 | 450 | 6461 | 1958 | 8419
17:30 | 495 | 6479.5 | 1944 | 8423.5
18:00 | 540 | 6498 | 1930 | 8428
18:30 | 630 | 6805 | 2103 | 8908
19:00 | 720 | 7112 | 2276 | 9388
19:30 | 980 | 7901 | 2048 | 9949
20:00 | 1000 | 7890 | 2145 | 10035 |  |  |  | Executive Engineer
20:30 | 930 | 7948.5 | 2251 | 10199.5 |  |  |  | Network Operation Division
21:00 | 860 | 8007 | 2357 | 10364
21:30 | 815 | 7943 | 2437.5 | 10380.5
22:00 | 770 | 7879 | 2518 | 10397 |  |  |  |  | Page 6 of 7
22:30 | 700 | 7734.5 | 2608 | 10342.5
23:00 | 630 | 7590 | 2698 | 10288
23:30 | 635 | 7539 | 2651.5 | 10190.5
24:00 | 640 | 7488 | 2605 | 10093
10364 MW (21:00 )
7861.4 MW (11:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-02 |  | Energy | 200622972
[10 empty] | 2018-06-02 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3717 | 459 | 1901 | 2204 | 330 | 117 | 1193 | 0 | 172
0:30 | 3560 | 467.5 | 1893.5 | 1602.5 | 344 | 119 | 943 | 0 | 156 | Date: | 2018-06-02
1:00 | 3403 | 476 | 1886 | 1001 | 358 | 121 | 693 | 0 | 140
1:30 | 3413.5 | 475.5 | 1888.5 | 983 | 358.5 | 121.5 | 624.5 | 0 | 142 | [7 empty] | Total Energy | 200.623 | Total Energy Gen 200.623 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 200.623 MKWHr
2:00 | 3424 | 475 | 1891 | 965 | 359 | 122 | 556 | 0 | 144 | [7 empty] | Energy not Served | 0
2:30 | 3484.5 | 475.5 | 1966 | 963 | 358.5 | 120.5 | 556.5 | 0 | 144 | [7 empty] | Energy Requirement | 200.623
3:00 | 3545 | 476 | 2041 | 961 | 358 | 119 | 557 | 0 | 144
3:30 | 3570.5 | 475.5 | 1984.5 | 841 | 357.5 | 118 | 487.5 | 0 | 135 | [6 empty] | Shortage
4:00 | 3596 | 475 | 1928 | 721 | 357 | 117 | 418 | 0 | 126
4:30 | 3493.5 | 475.5 | 1716.5 | 640.5 | 357 | 115.5 | 405.5 | 0 | 118
5:00 | 3391 | 476 | 1505 | 560 | 357 | 114 | 393 | 0 | 110
5:30 | 3345.5 | 475.5 | 1401 | 515 | 357.5 | 112.5 | 393 | 0 | 106
6:00 | 3300 | 475 | 1297 | 470 | 358 | 111 | 393 | 0 | 102
6:30 | 3331.5 | 476.5 | 1354 | 461 | 357.5 | 111.5 | 401.5 | 0 | 102 |  |  |  |  | Coal
7:00 | 3363 | 478 | 1411 | 452 | 357 | 112 | 410 | 0 | 102
7:30 | 3366.5 | 478 | 1479 | 541 | 356.5 | 113.5 | 410 | 0 | 108 |  |  |  | Oil |  |  |  | ,
8:00 | 3370 | 478 | 1547 | 630 | 356 | 115 | 410 | 0 | 114
8:30 | 3438.5 | 478 | 1547 | 723.5 | 356.5 | 116.5 | 432.5 | 0 | 115
9:00 | 3507 | 478 | 1547 | 817 | 357 | 118 | 455 | 0 | 116
9:30 | 3543 | 478 | 1575.5 | 824.5 | 356.5 | 117.5 | 453.5 | 0 | 122
10:00 | 3579 | 478 | 1604 | 832 | 356 | 117 | 452 | 0 | 128
10:30 | 3567 | 478 | 1750 | 827 | 357 | 116 | 479.5 | 0 | 128
11:00 | 3555 | 478 | 1896 | 822 | 358 | 115 | 507 | 0 | 128
11:30 | 3541.5 | 239 | 1975.5 | 961.5 | 357 | 115.5 | 520 | 0 | 127
12:00 | 3528 | 0 | 2055 | 1101 | 356 | 116 | 533 | 0 | 126
12:30 | 3602 | 0 | 1985 | 1171.5 | 357 | 116.5 | 572 | 0 | 128
13:00 | 3676 | 0 | 1915 | 1242 | 358 | 117 | 611 | 0 | 130
13:30 | 3676 | 0 | 1915 | 1242 | 358 | 117 | 611 | 0 | 130
14:00 | 3676 | 0 | 1915 | 1242 | 358 | 117 | 611 | 0 | 130
14:30 | 3707 | 235 | 1934 | 1279 | 357.5 | 117.5 | 621.5 | 0 | 138
15:00 | 3738 | 470 | 1953 | 1316 | 357 | 118 | 632 | 0 | 146
15:30 | 3708 | 469.5 | 1916.5 | 1351.5 | 357 | 117.5 | 616 | 0 | 141
16:00 | 3678 | 469 | 1880 | 1387 | 357 | 117 | 600 | 0 | 136
16:30 | 3660.5 | 469.5 | 1855 | 1317 | 357 | 113.5 | 610.5 | 0 | 138
17:00 | 3643 | 470 | 1830 | 1247 | 357 | 110 | 621 | 0 | 140
17:30 | 3614.5 | 464.5 | 1747.5 | 1304.5 | 356.5 | 110.5 | 683 | 0 | 142
18:00 | 3586 | 459 | 1665 | 1362 | 356 | 111 | 745 | 0 | 144
18:30 | 3617.5 | 459 | 1684 | 1598.5 | 356 | 111 | 925 | 0 | 157
19:00 | 3649 | 459 | 1703 | 1835 | 356 | 111 | 1105 | 0 | 170
19:30 | 3385 | 381 | 1977 | 2460 | 330 | 112 | 1132 | 0 | 172
20:00 | 3393 | 381 | 1940 | 2557 | 314 | 113 | 1173 | 0 | 164
20:30 | 3441 | 420.5 | 1909.5 | 2617 | 327.5 | 113.5 | 1198.5 | 0 | 172
21:00 | 3489 | 460 | 1879 | 2677 | 341 | 114 | 1224 | 0 | 180
21:30 | 3541.5 | 460 | 1873 | 2636.5 | 335 | 114 | 1244.5 | 0 | 176
22:00 | 3594 | 460 | 1867 | 2596 | 329 | 114 | 1265 | 0 | 172
22:30 | 3670.5 | 460 | 1864.5 | 2492.5 | 329.5 | 115.5 | 1237 | 0 | 173
23:00 | 3747 | 460 | 1862 | 2389 | 330 | 117 | 1209 | 0 | 174
23:30 | 3732 | 459.5 | 1881.5 | 2296.5 | 330 | 117 | 1201 | 0 | 173 | Max Temp. in Dhaka |  | 33.2° C
24:00 | 3717 | 459 | 1901 | 2204 | 330 | 117 | 1193 | 0 | 172
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 200.623 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 200.623 MKWHr
Note on W13: Author:

## Generation
2018-06-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 89 | 89 | 86 | 86 | 83 | 81 | 82 | 84 | 86 | 86 | 85 | 86 | 86 | 86 | 87 | 87 | 82 | 83 |  | 83 | 83 | 84 | 84 | 84 | 86 | 86 | 1890487
2 | Kaptai Unit-4 & 5 | 32 | 33 | 33 | 31 | 31 | 30 | 30 | 31 | 32 | 31 | 30 | 30 | 31 | 32 | 31 | 30 | 28 | 28 |  | 28 | 29 | 29 | 30 | 30 | 31 | 31 | 728300
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 25 | 25 | 25 | 26 |  | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 488700
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 202 | 202 | 203 | 203 | 182 | 182 | 201 | 184 | 201 | 198 | 202 | 204 | 201 | 196 | 212 | 202 | 202 | 204 |  | 202 | 202 | 202 | 189 | 189 | 189 | 188 | 4683387
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 50 | 50 | 50 | 50 | 51 | 51 | 50 | 50 | 50 | 50 | 100 | 116 | 125 | 116 | 115 | 115 | 114 | 115 |  | 80 | 130 | 100 | 70 | 70 | 70 | 135 | 1886318
| Dohazari Peaking | 31 | 31 | 31 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 0 |  | 17 | 10 | 17 | 17 | 20 |  | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 576323
12 | Hathazari peaking | 85 | 43 | 43 | 0 | [13 empty] | 48 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 676024
| Daudkandi bangla trak | [17 empty] | 0 |  | 10 | 62 | 85 | 82 | 11 | 11 | 11 | 186240
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 0 |  | 0 | 30 | 50 | 0 |  | 73832
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 102 | 102 | 102 | 102 | 65 | 38 | 39 | 104 | 101 | 100 | 99 | 100 | 100 | 100 | 98 | 98 | 98 | 98 |  | 101 | 101 | 104 | 103 | 100 | 100 | 100 | 2329000
17 | Siddhirganj CCPP-335 MW | 120 | 120 | 120 | 170 | 170 | 170 | 120 | 120 | 120 | 120 | 120 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 110 | 125 | 125 | 185 | 170 | 170 | 170 | 3843093
18 | Summit Gazipur | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 32 | 47 | 50 | 47 | 62 |  | 148 | 285 | 218 | 291 | 301 | 300 | 220 | 1957090
19 | Ashuganj 195MW Modular | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 70 | 176 | 194 | 78 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1906909
20 | Ghorasal ST: Unit-1,2 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 780000
21 | Ghorasal ST: Unit-3
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 3276000
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 365 | 365 | 300 | 270 | 270 | 320 | 320 | 320 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 |  | 365 | 365 | 365 | 349 | 350 | 300 | 300 | 7940672
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 150 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 150 | 150 | 150 | 130 | 130 | 2780495
30 | Ashuganj ST: Unit- 5 | [23 empty] | 0 | 25 | 60 | 60108
32 | Ashuganj Engines TSK | 42 | 42 | 42 | 42 | 40 | 40 | 40 | 35 | 37 | 37 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 921960
33 | Ashuganj CCPP 225 MW | 185 | 187 | 192 | 183 | 183 | 193 | 206 | 183 | 200 | 206 | 195 | 139 | 206 | 183 | 203 | 192 | 188 | 190 |  | 190 | 184 | 183 | 226 | 225 | 220 | 222 | 4802000
34 | Ashuganj CCPP(South) | 250 | 257 | 261 | 250 | 250 | 264 | 290 | 250 | 327 | 334 | 316 | 300 | 334 | 300 | 327 | 309 | 300 | 250 |  | 309 | 300 | 301 | 300 | 300 | 320 | 300 | 7096250
| Ashuganj CCPP(North) | 260 | 265 | 270 | 260 | 265 | 275 | 305 | 260 | 300 | 335 | 310 | 290 | 330 | 300 | 330 | 310 | 300 | 250 |  | 288 | 300 | 300 | 300 | 300 | 315 | 300 | 7419500
35 | Ashuganj (Precision) 55MW | [17 empty] | 0
36 | Chandpur CCPP | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 154 | 154 | 154 | 153 |  | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 3638610
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 345 | 350 | 365 | 345 | 345 | 345 | 365 | 360 | 350 | 370 | 370 | 355 | 352 | 355 | 358 | 350 | 336 | 327 |  | 319 | 316 | 316 | 315 | 290 | 290 | 285 | 8210430
40 | Meghnaghat CCPP 450MW | 360 | 360 | 420 | 380 | 380 | 330 | 430 | 430 | 400 | 400 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 430 |  | 430 | 430 | 430 | 430 | 430 | 400 | 380 | 9475226
41 | Haripur Power CCPP 360MW | 311 | 311 | 352 | 331 | 311 | 291 | 321 | 353 | 350 | 350 | 348 | 350 | 350 | 350 | 344 | 332 | 306 | 300 |  | 304 | 311 | 306 | 292 | 292 | 272 | 270 | 7679000
42 | Mymensingh RPCL 210MW | 104 | 103 | 111 | 140 | 156 | 156 | 139 | 145 | 143 | 141 | 135 | 124 | 124 | 118 | 115 | 95 | 0 | 66 |  | 35 | 35 | 50 | 65 | 80 | 79 | 51 | 2422450
43 | Haripur NEPC 110MW | [16 empty] | 13 | 13 |  | 84 | 84 | 84 | 84 | 84 | 55 | 13 | 421800
44 | Fenchugonj CCPP-1 | 58 | 60 | 58 | 56 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 | 30 | 56 |  | 54 | 54 | 54 | 54 | 54 | 53 | 54 | 952000
45 | Fenchugonj CCPP-2 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 75 | 75 | 75 | 74 | 73 | 72 | 71 | 71 | 71 |  | 74 | 74 | 74 | 74 | 74 | 75 | 75 | 1788000
46 | Shajibazar 330 MW | 276 | 276 | 271 | 267 | 276 | 278 | 294 | 263 | 282 | 285 | 307 | 284 | 304 | 293 | 304 | 300 | 288 | 288 |  | 297 | 291 | 290 | 291 | 292 | 307 | 297 | 6551103
47 | Shahjibazar GT: Unit- 8, 9 | 65 | 64 | 60 | 64 | 64 | 64 | 62 | 64 | 62 | 61 | 61 | 62 | 62 | 59 | 61 | 60 | 59 | 60 |  | 64 | 63 | 49 | 45 | 43 | 60 | 64 | 1395000
48 | Shahjibazar 86MW | 87 | 87 | 87 | 87 | 10 | 10 | 10 | 84 | 84 | 86 | 86 | 86 | 85 | 86 | 86 | 86 | 50 | 50 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1744320
49 | Shahjibazar (EPL) 50MW | 48 | 48 | 48 | 48 | 20 | 5 | 5 | 30 | 47 | 47 | 47 | 46 | 48 | 48 | 48 | 48 | 48 | 20 |  | 20 | 48 | 49 | 49 | 49 | 49 | 49 | 969840
50 | Sylhet GT 150 MW | [13 empty] | 45 | 80 | 80 | 80 | 80 |  | 100 | 130 | 128 | 127 | 122 | 98 | 98 | 992180
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 43 | 43 | 43 | 43 | 41 | 7 | 5 | 5 | 5 | 5 | 30 | 43 | 40 | 40 | 39 | 39 | 39 | 39 |  | 17 | 40 | 41 | 42 | 43 | 44 | 42 | 769860
53 | Sylhet (Desh) 10MW | 9 | 9 | 9 | 9 | 7 | 7 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 0 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 184860
54 | Hobiganj 11MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192384
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 22 | 5 | 5 | 5 | 5 | 5 | 22 | 22 | 50 | 50 | 50 | 49 | 53 | 22 |  | 22 | 53 | 53 | 53 | 53 | 53 | 53 | 873600
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 8 | 23 | 23 | 23 | 23 | 23 | 23 | 8 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 527496
57 | Summit Bibiana- 2 | 285 | 290 | 305 | 275 | 290 | 290 | 310 | 290 | 280 | 320 | 320 | 300 | 280 | 300 | 300 | 320 | 310 | 320 |  | 270 | 310 | 270 | 260 | 270 | 260 | 310 | 7539880
58 | Southern 55MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 30 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 55 | 55 | 55 | 55 | 55 | 720000
59 | Sikalbaha (Energis) | 51 | 51 | 51 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 44 | 41 | 42 | 42 | 51 | 51 |  | 42 | 42 | 42 | 51 | 51 | 51 | 51 | 816960
60 | Barabkunda (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 447940
61 | Narshingdi (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 448632
62 | Tangail (Doreen) 22MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 504072
63 | Tripura | 140 | 144 | 144 | 126 | 110 | 102 | 102 | 114 | 116 | 128 | 128 | 126 | 130 | 130 | 146 | 136 | 140 | 144 |  | 170 | 172 | 164 | 180 | 172 | 174 | 172 | 3340800
64 | Malancha, Ctg. EPZ (United) | 38 | 40 | 41 | 40 | 40 | 40 | 4 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 7 | 10 |  | 23 | 23 | 25 | 29 | 27 | 30 | 30 | 437760
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 446148
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252180
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 33 | 33 | 0 | 26 | 25 | 33 | 30 |  | 33 | 33 | 33 | 25 | 32 | 32 | 32 | 564400
68 | Summit Comilla 25MW | 22 | 22 | 22 | 22 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 15 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 463580
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 350000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 729000
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 792800
72 | Summit Rupganj | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803100
73 | Ghorashal (Regent) | 82 | 82 | 82 | 82 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 55 | 83 | 83 | 82 | 0 | 0 |  |  | 70 | 97 | 107 | 107 | 104 | 106 | 106 | 1304727
76 | Siddhirganj (Desh) | [16 empty] | 5 | 20 |  | 50 | 50 | 70 | 100 | 100 | 17 | 17 | 425280
77 | Siddhirganj (Dutch Bangla)
78 | Gazipur (RPCL) | 22 | 51 | 51 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 32 | 35 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 51 | 51 | 52 | 760128
79 | Kodda 150MW | 62 | 30 | 30 | 15 | 15 | 15 | 15 | 32 | 65 | 65 | 65 | 65 | 65 | 65 | 98 | 98 | 98 | 98 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 1877280
80 | Jamalpur 95MW | 72 | 72 | 72 | 24 | 8 | 8 | 8 | 32 | 90 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 1780555
81 | Lakdhanvi 52 MW | [17 empty] | 1 |  | 20 | 25 | 30 | 34 | 25 | 25 | 25 | 182010
82 | Madanganj 102MW | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 15 |  | 54 | 58 | 60 | 96 | 100 | 98 | 80 | 793320
83 | Pagla (DPA ) | 10 | 11 | 10 | 11 | 0 |  |  | 11 | 11 | 11 | 10 | 48 | 46 | 50 | 20 | 21 | 10 | 11 |  | 11 | 30 | 51 | 21 | 10 | 10 | 10 | 362000
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 20 | 5 | 5 | 41 | 42 | 43 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 50 |  | 55 | 86 | 86 | 86 | 85 | 85 | 85 | 793320
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 0 |  |  |  | 10 | 10 | 10 | 10 | 39 | 10 | 10 | 10 | 10 | 10 | 10 |  | 60 | 80 | 88 | 100 | 100 | 70 | 70 | 699904
86 | Meghnaghat CCPP(Summit) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 305 | 200 | 200 | 200 | 200 | 200 | 200 |  | 200 | 305 | 270 | 200 | 200 | 200 | 200 | 5232291
87 | Meghnaghat (IEL) | 50 | 10 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 11 | 35 | 16 | 22 | 22 | 22 | 40 |  | 55 | 100 | 91 | 100 | 100 | 100 | 100 | 878400
88 | Ghorashal 78MW (MAX) | 76 | 76 | 76 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 71 | 71 | 71 | 71 | 71 | 71 |  | 40 | 60 | 50 | 50 | 50 | 50 | 50 | 1462944
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 53 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 168000
91 | Juldah (Acorn) | 90 | 90 | 90 | 90 | 60 | 30 | 30 | 68 | 90 | 90 | 80 | 80 | 90 | 90 | 90 | 90 | 90 | 90 |  | 102 | 102 | 102 | 102 | 102 | 90 | 78 | 1972080
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 20 | 5 | 5 | 5 | 5 | 5 | 17 | 41 | 50 | 50 | 50 | 47 | 50 | 20 |  | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 845000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 45 | 6 | 6 | 6 | 35 | 51 | 51 | 6 | 6 | 11 | 42 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 891906
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 | 24 | 24 |  | 64 | 80 | 84 | 94 | 94 | 94 | 94 | 709632
95 | Patenga 50MW | 44 | 44 | 44 | 44 | 28 | 18 | 0 | 4 | 30 | 31 | 31 | 30 | 32 | 31 | 31 | 31 | 40 | 45 |  | 44 | 44 | 44 | 45 | 45 | 45 | 44 | 867360
96 | Chittagong ECPV 108 MW | 97 | 97 | 97 | 97 | 44 | 32 | 32 | 96 | 97 | 92 | 91 | 90 | 97 | 97 | 97 | 97 | 97 | 97 |  | 97 | 92 | 91 | 98 | 98 | 98 | 98 | 2120640
97 | Katpotti 51 MW | [17 empty] | 0 |  | 13 | 20 | 31 | 49 | 49 | 49 | 46 | 239856
98 | Bosila 108MW | 51 | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 | 40 | 52 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 844800
99 | Madanganj-55 MW | 30 | 30 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 43 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 865427
100 | Northern 55 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 40 | 54 | 56 | 56 | 56 | 56 | 37 | 37 | 37 | 37 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 960158
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 163 | 130 | 130 | 130 | 130 | 130 | 100 |  | 100 | 163 | 163 | 130 | 100 | 100 | 100 | 3093709
102 | Sarishabari (Solar) |  |  |  |  | 0 | 0.1 | 0.3 | 0.8 | 2 | 0.9 | 2.4 | 2.6 | 2.3 | 2 | 1.7 | 1.7 | 1 | 0 |  | 0 | 0 | 0 | 0 |  |  |  | 15601
103 | Banco Energy 54MW | 36 | 36 | 36 | 18 | 18 | 0 |  | 0 | 18 | 18 | 18 | 18 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 867960
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko) | [19 empty] | 11 | 15 | 50 | 21 | 11 | 11 | 11 | 121160
106
112
113
114
115
116
117
118 | Eastern Zone Total | 6209 | 6130 | 6365 | 5997 | 5307 | 5000.1 | 5151.3 | 5430.8 | 5745 | 5895.9 | 6216.4 | 6536.6 | 6549.3 | 6528 | 6732.7 | 6620.7 | 6461 | 6498 | 0 | 7112 | 7901 | 7890 | 8007 | 7879 | 7590 | 7488 | 154883547
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 57 | 96 | 103 | 97 | 103 | 51 | 33 |  | 33 | 108 | 105 | 110 | 110 | 109 | 109 | 1155960
124 | Khulna (KPCL-2) | 16 | 16 | 16 | 0 |  |  |  |  | 16 | 16 | 16 | 16 | 49 | 49 | 49 | 49 | 49 | 49 |  | 49 | 83 | 83 | 83 | 83 | 83 | 83 | 895680
125
126 | Khulna (Aggreko) 55MW | [19 empty] | 13 | 11 | 13 | 50 | 53 | 53 | 53 | 201290
127 | Faridpur Peaking | 50 | 25 | 25 | 5 | 0 | [12 empty] | 12 |  | 47 | 48 | 48 | 48 | 48 | 48 | 48 | 388800
128 | Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 | 180 | 190 | 150 | 120 | 120 | 130 |  | 170 | 170 | 180 | 200 | 214 | 213 | 215 | 3599040
129
130
131
132
133
| Summit Barisal 110 MW | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 80 |  | 80 | 110 | 110 | 110 | 110 | 110 | 110 | 1106880
| Barisal GT: Unit-1, 2 | [21 empty] | 0 | 0 | 12 | 12 | 0 | 26780
136 | Bhola Aggreko 95MW | 55 | 53 | 53 | 50 | 15 | 16 | 13 | 10 | 10 | 10 | 10 | 44 | 45 | 46 | 46 | 46 | 48 | 50 |  | 51 | 51 | 50 | 37 | 49 | 93 | 98 | 978429
137 | Bhola CCPP 194MW | 200 | 202 | 197 | 197 | 197 | 197 | 193 | 191 | 200 | 197 | 197 | 187 | 194 | 192 | 192 | 192 | 191 | 192 |  | 191 | 195 | 175 | 184 | 185 | 193 | 194 | 4698325
| Bhola (Venture) 33MW | 28 | 28 | 28 | 26 | 22 | 18 | 21 | 15 | 13 | 6 | 7 | 20 | 22 | 21 | 20 | 23 | 22 | 22 |  | 29 | 26 | 31 | 35 | 36 | 31 | 31 | 539140
140 | Bangla Trak Noapara | [11 empty] | 9 | 40 | 40 | 40 | 40 | 40 | 10 |  | 10 | 55 | 98 | 98 | 100 | 100 | 70 | 689280
141 | Noapara (KZA) 40MW | 8 | 8 | 8 | 8 | 0 |  |  | 8 | 8 | 8 | 8 | 32 | 40 | 40 | 40 | 40 | 40 | 24 |  | 40 | 40 | 40 | 40 | 40 | 33 | 33 | 520875
142 | Gopalganj Peaking | 59 | 30 | 30 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 6 | 3 | 8 | 12 | 13 | 14 | 27 | 45 |  | 60 | 0 | 30 | 75 | 70 | 67 | 57 | 606464
143 | Bheramara GT-1,2,3 | [20 empty] | 0 | 33 | 33 | 33 | 33 | 17 | 126300
144
145 |  | 476 | 475 | 476 | 475 | 476 | 475 | 478 | 478 | 478 | 478 | 478 |  |  | 470 | 470 | 469 | 470 | 459 |  | 459 | 381 | 381 | 460 | 460 | 460 | 459 | 10313455
146 | Bheramara 360 MW | 305 | 305 | 340 | 360 | 300 | 230 | 260 | 320 | 320 | 330 | 320 | 290 | 290 | 290 | 293 | 320 | 320 | 280 |  | 300 | 0 |  |  | 130 | 283 | 287 | 6645312
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 78 | 79 | 78 | 77 | 78 | 78 | 77 | 76 | 77 | 76 | 78 | 76 | 78 | 77 | 77 | 77 | 77 | 76 |  | 76 | 75 | 74 | 77 | 75 | 75 | 75 | 1856727
151 | Barapukuria Unit-3 | 280 | 280 | 280 | 280 | 279 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 255 | 240 | 264 | 254 | 255 | 255 | 6686900
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | [17 empty] | 12 |  | 43 | 43 | 43 | 43 | 43 | 43 | 0 | 187553
Sirajgonj Unit-1 225MW (Gas)
157 | Sirajgonj Unit-1 225MW (Oil)
158 | Sirajgonj Unit-2 225MW (Gas)
Sirajgonj Unit-2 225MW (Oil)
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | [17 empty] | 15 |  | 48 | 49 | 48 | 48 | 48 | 48 | 48 | 270818
161 | Bogra (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 0 | 0 |  |  | 10 | 18 | 365760
162 | Bogra (EPL) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 236268
163 | Ullapara (Summit) | 5 | 5 | 5 | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 157896
164 | Amnura 50MW | 50 | 50 | 50 | 24 | 24 | 12 | 12 | 12 | 50 | 50 | 50 | 50 | 0 | 24 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 958490
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 43 | 43 | 43 | 43 | 43 | 605104
166 | Katakhali Peaking | [17 empty] | 0 |  | 47 | 47 | 47 | 46 | 46 | 45 | 45 | 232397
167 | Santahar Peaking | [17 empty] | 3 |  | 35 | 44 | 44 | 43 | 43 | 42 | 42 | 254300
168 | Rajlanka 52 MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 43 | 43 | 43 | 43 | 25 | 8 |  | 9 | 43 | 43 | 43 | 43 | 26 | 26 | 497280
169 | Chapainawabganj-100 MW | 34 | 25 | 25 | 0 | [8 empty] | 32 | 34 | 34 | 34 | 43 | 43 |  | 76 | 102 | 102 | 102 | 102 | 102 | 102 | 846922
170
171
172 | Rangpur GT | [17 empty] | 0 |  | 17 | 17 | 16 | 17 | 17 | 17 | 16 | 91000
173 | Saidpur GT | [17 empty] | 0 |  | 0
175
176
177
178 | Western Zone Total | 1869 | 1806 | 1836 | 1741 | 1599 | 1506 | 1534 | 1590 | 1652 | 1651 | 1645 | 1281 | 1502 | 2016 | 1999 | 2005 | 1958 | 1930 | 0 | 2276 | 2048 | 2145 | 2357 | 2518 | 2698 | 2605 | 45739425
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953