## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-30 | Saturday
|  | Date (day): | 2018-06-30 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 10341 | MW |  |  | (b) At Evening Peak Hour : |  | 12206 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-29 | 2018-06-30 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | # 2 under maint
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 350 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 60 | 76 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 85 | 100 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 340 | 360 | 0 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 98 | 98 |  | 12 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 345 | 350 | 360 | 300
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 65 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 100 | 100 | 150 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 15 | 100 | 102 | 102
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 20 | 0 | 0 |  |  | 132 kV line S/D.
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 19 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 |  |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 7 | 60 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 150 | 164 | 200 | 200
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 10 | 0 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 32 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 12 | 39 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 18 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 100 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 18 | 55 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 8 | 64 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 56 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 24 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 50 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 48 | 278 | 150 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 0 | 100 | 100
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2319 | 3281 | 3409 | 4126 | 205 | 575
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 16 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 33 | 44 | 44 | 44
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 160 | 170 | 169 | 169 |  | 61 | # 2 under maint
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 213 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 80 | 50 | 60 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 27 | 32 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 72 | 68 | 68
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 32 | 74 | 74
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 90 | 80 | 80 |  | 20 | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 18 | 18 |  | 4
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 8 | 42 | 5 | 15
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 80 | 99 | 103 | 103 |  | 5 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 696 | 878 | 922 | 1007 | 360 | 130
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Under maint.
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 150 | 150 | 150 |  | 129
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 130 | 130 | 130 | 4 |  | Gas shortage
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 206 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 0 | 210 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 301 | 342 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 39 | 39
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 5 | 24 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 125 | 78 | 195 | 0
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 12 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 10 | 86 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 48
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 100 | 100 | 100 | 100 |  |  | ST under maint.
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 110 | 156 | 124 | 164
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 8 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 0 | 21 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1373 | 1490 | 1696 | 2254 | 182 | 184
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 43 | 46 | 97 | 100 | 102 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 32 | 95 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 0.7 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 80 | 102 | 150 | 185
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 175.7 | 263 | 366 | 402 | 102 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 59 | 58 | 58
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 62 | 62 | 62
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 193 | 217 | 220 | 220 |  |  | ST under maint.
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 10 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60 |  | 6
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 86 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 10 | 47 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 78 | 78 | 80 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 11 | 45 | 45 | 45
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 21 | 22 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 260 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 973 | 1220 | 1310 | 1330 | 0 | 26
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 461 | 457 | 470 | 470
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 10 | 89 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 117 | 115 | 115
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 48 | 36 | 47
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 78 | 78
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 50 | 270 | 330 | 330 | 80
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 33 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 54
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 80 | 80
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 665 | 1194 | 1484 | 1581 | 80 | 0
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 96 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 33 | 30 | 30
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 191 | 192 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 54 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 275 | 418 | 429 | 459 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 51 | 0 | 50
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 37 | 0 | 38
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 40 | 43 | 43 |  | 7 | Engine problem
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 24 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 46 | 46
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 135 | 0 | 0 | 214
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 178 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 40 | 40 | 42 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 0 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 12 | 12
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 24 | 59 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 457 | 557 | 582 | 887 | 71 | 123
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  |  | Under maint.
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 118 | 120 | 125 | 125
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 118 | 155 | 143 | 160 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 7051.7 | 9456 | 10341 | 12206 | 1000 | 1123
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6772.0482 | 9081 | 9930.9032 | 11721.9423
A. |  | 2018-06-29 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 9574 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6526.4 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9456 | MW
3 | Day peak Generation : |  |  | 7051.7 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9081 | MW
4 | Evening peak Generation : |  |  | 9456 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 191.9186 | MKWHr | By Solar | 0.0144 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 121.1613 | MKWHr |  | By Oil: | 50.5629 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 2.9604 | MKWHr |  | By Hydro: | 3.8504 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1000 | MW | Dhaka | 3267 | 3267 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1123 | MW | Chittagong | 940 | 940 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2123 | MW | Khulna | 1157 | 1157 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1042.95 | MMCFD |  |  | Rajshahi | 959 | 959 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 90746729.384 | ii) Oil : | Taka | 418955590.74 | Comilla | 874 | 874 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 0 | Total | Taka | 509702320.124 | Mymensingh | 723 | 723 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 9.1315 | MKWHr. | Sylhet | 354 | 354 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -760 | MW at | 21:00 | hrs | Barisal | 250 | 250 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -810 | MW at | 22:00 | hrs | Rangpur | 557 | 557 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 9081 | 9081 |  | 0
B. |  | 2018-06-30 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 33.9° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12206 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8600 | MW
4 | Reserve(Generation end) |  |  |  | 1306 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 218.4993 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6748.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 10.3615 | MKWHr. | ii) HVDC Flow at Peak Time |  | 457 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0077 | MKWHr. | iii) Maximum HVDC Flow : |  | 474 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.49 |  | (b) Today: | 102.25 |  | (c) Rule Curve: |  | 83.73
.

## YesterdayGen
2018-06-29
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 120 | 0 | 0 | 350 | 89 | 70 | 373 | 290 | 0 | 0 | 400 | 130 | 60 | 48 | 55 | 155 | 0 | 0 | 0 | 60 | 7 | 149 | 50 | 74 | 11 | 39 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 113 | 0 | 42 | 55 | 0 | 80 | 99 | 44 | 18 | 30 | 0 | 100 | 0 | 300 | 301 | 189 | 78 | 100 | 39 | 0 | 5 | 51 | 86 | 0 | 8 | 19 | 11 | 33 | 20 | 154 | 48 | 95 | 20 | 0 | 55 | 62 | 50 | 50 | 130 | 200 | 50 | 86 | 47 | 78 | 0 | 44 | 10 | 270 | 23 | 11 | 0 | 301 | 0 | 0 | 173 | 0 |  | 474 | 0 | 160 | 71 | 115 | 165 | 0 | 0 | 49 | 45 | 40 | 193 | 30 | 98 | 0 | 0 | 0 | 43 | 37 | 100 | 40 | 43 | 0 | 43 | 42 | 22 | 11 | 11 | 0 | 0 | 121 | 16 | 17 | 135 | 0 | 0 | 171 | 97 | 0 | 0 | 0 |  | 7081 | 2389 | 9470 | 3353 | 474 | 1946 | 2057 | 121 | 168 | 1197 | 154 | 0 | 0 | 102.54
2:00 | 37 | 120 | 0 | 0 | 350 | 89 | 70 | 384 | 317 | 0 | 0 | 400 | 100 | 65 | 48 | 55 | 145 | 0 | 0 | 0 | 60 | 7 | 120 | 50 | 74 | 11 | 39 | 54 | 36 | 55 | 19 | 25 | 32 | 33 | 33 | 0 | 0 | 80 | 80 | 0 | 0 | 17 | 0 | 195 | 0 | 110 | 0 | 42 | 55 | 0 | 80 | 99 | 44 | 18 | 39 | 0 | 100 | 0 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 86 | 0 | 8 | 19 | 11 | 33 | 20 | 148 | 49 | 95 | 20 | 0 | 55 | 62 | 50 | 50 | 130 | 200 | 63 | 86 | 48 | 78 | 0 | 44 | 10 | 280 | 23 | 11 | 0 | 301 | 0 | 0 | 163 | 0 |  | 464 | 0 | 160 | 77 | 115 | 135 | 0 | 0 | 49 | 45 | 40 | 180 | 27 | 96 | 0 | 0 | 0 | 43 | 37 | 100 | 40 | 43 | 0 | 43 | 42 | 22 | 11 | 11 | 0 | 0 | 121 | 16 | 17 | 135 | 0 | 0 | 173 | 97 | 0 | 0 | 0 |  | 6987 | 2339 | 9326 | 3349 | 464 | 1990 | 1957 | 121 | 160 | 1137 | 148 | 0 | 0 | 102.53
3:00 | 37 | 120 | 0 | 0 | 349 | 89 | 70 | 400 | 325 | 0 | 0 | 400 | 100 | 30 | 15 | 30 | 145 | 0 | 0 | 0 | 7 | 7 | 105 | 10 | 74 | 0 | 39 | 54 | 18 | 36 | 19 | 25 | 32 | 33 | 33 | 23 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 195 | 0 | 90 | 0 | 42 | 55 | 0 | 80 | 72 | 44 | 18 | 37 | 0 | 100 | 0 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 86 | 0 | 8 | 19 | 11 | 33 | 20 | 146 | 58 | 80 | 20 | 0 | 58 | 62 | 50 | 50 | 130 | 192 | 52 | 86 | 48 | 77 | 0 | 44 | 10 | 270 | 23 | 11 | 0 | 301 | 0 | 0 | 163 | 0 |  | 464 | 0 | 160 | 64 | 115 | 120 | 0 | 0 | 42 | 45 | 40 | 191 | 30 | 96 | 0 | 0 | 0 | 34 | 0 | 100 | 40 | 43 | 0 | 43 | 42 | 18 | 11 | 11 | 0 | 0 | 121 | 16 | 17 | 135 | 0 | 0 | 169 | 97 | 0 | 0 | 0 |  | 6691 | 2264 | 8955 | 3367 | 464 | 1985 | 1682 | 121 | 160 | 1030 | 146 | 0 | 0 | 102.52
4:00 | 37 | 120 | 0 | 0 | 349 | 89 | 70 | 410 | 350 | 0 | 0 | 430 | 100 | 7 | 15 | 15 | 140 | 0 | 0 | 0 | 7 | 7 | 76 | 10 | 60 | 0 | 39 | 36 | 18 | 36 | 19 | 25 | 32 | 33 | 33 | 34 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 195 | 0 | 70 | 0 | 32 | 24 | 0 | 80 | 72 | 30 | 18 | 40 | 0 | 130 | 15 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 86 | 0 | 8 | 19 | 11 | 33 | 20 | 142 | 78 | 48 | 20 | 0 | 58 | 62 | 50 | 50 | 163 | 200 | 53 | 86 | 48 | 78 | 0 | 45 | 10 | 280 | 23 | 11 | 0 | 219 | 0 | 0 | 150 | 0 |  | 464 | 0 | 95 | 51 | 115 | 120 | 0 | 0 | 43 | 20 | 40 | 193 | 29 | 80 | 0 | 0 | 0 | 16 | 0 | 24 | 40 | 43 | 0 | 43 | 42 | 22 | 11 | 11 | 0 | 0 | 121 | 16 | 17 | 135 | 0 | 0 | 171 | 94 | 0 | 0 | 0 |  | 6579 | 2056 | 8635 | 3384 | 464 | 2087 | 1443 | 121 | 160 | 834 | 142 | 0 | 0 | 102.51
5:00 | 37 | 120 | 0 | 0 | 328 | 89 | 70 | 410 | 352 | 0 | 0 | 430 | 100 | 7 | 15 | 15 | 130 | 0 | 0 | 0 | 7 | 7 | 44 | 10 | 47 | 0 | 30 | 36 | 18 | 17 | 16 | 25 | 32 | 33 | 33 | 16 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 195 | 0 | 50 | 0 | 32 | 24 | 0 | 80 | 52 | 30 | 18 | 41 | 0 | 130 | 60 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 86 | 0 | 8 | 19 | 11 | 33 | 20 | 132 | 66 | 8 | 20 | 0 | 58 | 62 | 50 | 50 | 163 | 194 | 50 | 86 | 48 | 78 | 0 | 44 | 10 | 260 | 23 | 11 | 0 | 200 | 0 | 0 | 130 | 0 |  | 464 | 0 | 95 | 10 | 92 | 120 | 0 | 0 | 43 | 20 | 16 | 191 | 28 | 80 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 43 | 42 | 22 | 11 | 11 | 0 | 0 | 121 | 0 | 0 | 135 | 0 | 0 | 171 | 98 | 0 | 0 | 0 |  | 6331 | 1920 | 8251 | 3372 | 464 | 2072 | 1197 | 121 | 160 | 733 | 132 | 0 | 0 | 102.5
6:00 | 37 | 120 | 0 | 0 | 310 | 24 | 40 | 330 | 321 | 0 | 0 | 350 | 100 | 7 | 15 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 30 | 10 | 19 | 0 | 12 | 18 | 18 | 17 | 16 | 25 | 32 | 33 | 33 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 191 | 0 | 50 | 0 | 16 | 0 | 0 | 50 | 12 | 18 | 18 | 16 | 0 | 130 | 85 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 20 | 0 | 0 | 19 | 11 | 8 | 20 | 110 | 66 | 8 | 20 | 0 | 58 | 62 | 11 | 10 | 100 | 194 | 50 | 20 | 10 | 78 | 0 | 11 | 10 | 260 | 23 | 11 | 0 | 92 | 0 | 0 | 65 | 0 |  | 464 | 0 | 95 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 173 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 8 | 42 | 22 | 11 | 10 | 0 | 0 | 121 | 0 | 0 | 135 | 0 | 0 | 168 | 75 | 0 | 0 | 0 |  | 5214 | 1625 | 6839 | 3235 | 464 | 1469 | 655 | 121 | 160 | 625 | 110 | 0 | 0 | 102.49
7:00 | 37 | 120 | 0 | 0 | 280 | 24 | 40 | 300 | 301 | 0 | 0 | 320 | 100 | 7 | 15 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 16 | 25 | 32 | 33 | 33 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 206 | 0 | 50 | 0 | 8 | 0 | 0 | 15 | 12 | 18 | 17 | 17 | 0 | 100 | 100 | 327 | 327 | 199 | 78 | 100 | 39 | 0 | 5 | 12 | 11 | 0 | 0 | 19 | 11 | 8 | 15 | 104 | 64 | 8 | 20 | 0.4 | 58 | 62 | 11 | 10 | 100 | 202 | 50 | 10 | 10 | 78 | 0 | 11 | 10 | 270 | 23 | 11 | 0 | 48 | 0 | 0 | 50 | 0 |  | 464 | 0 | 96 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 154 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 8 | 42 | 22 | 11 | 10 | 0 | 0 | 123 | 0 | 0 | 135 | 0 | 0 | 173 | 11 | 0 | 0 | 0 |  | 4977.4 | 1549 | 6526.4 | 3211 | 464 | 1307 | 542 | 123 | 160 | 615 | 104 | 0.4 | 0 | 102.48
8:00 | 37 | 120 | 0 | 0 | 280 | 25 | 40 | 300 | 301 | 0 | 0 | 320 | 100 | 7 | 16 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 216 | 0 | 50 | 0 | 8 | 0 | 0 | 15 | 12 | 18 | 17 | 16 | 0 | 100 | 100 | 337 | 334 | 204 | 78 | 100 | 39 | 0 | 5 | 12 | 11 | 0 | 0 | 19 | 11 | 8 | 12 | 104 | 63 | 8 | 20 | 1.5 | 58 | 62 | 11 | 10 | 100 | 208 | 50 | 10 | 10 | 78 | 0 | 13 | 10 | 320 | 23 | 5 | 0 | 48 | 0 | 0 | 55 | 0 |  | 463 | 0 | 95 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 154 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 8 | 42 | 18 | 11 | 10 | 0 | 0 | 119 | 0 | 0 | 135 | 0 | 0 | 184 | 12 | 0 | 0 | 0 |  | 5048.5 | 1549 | 6597.5 | 3212 | 463 | 1354 | 548 | 119 | 160 | 636 | 104 | 1.5 | 0 | 102.47
9:00 | 37 | 120 | 0 | 0 | 320 | 64 | 40 | 330 | 301 | 0 | 0 | 350 | 100 | 7 | 15 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 82 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 49 | 0 | 8 | 0 | 0 | 50 | 12 | 18 | 17 | 16 | 0 | 100 | 100 | 315 | 316 | 184 | 78 | 100 | 39 | 0 | 5 | 12 | 12 | 0 | 0 | 19 | 8 | 8 | 12 | 96 | 45 | 8 | 20 | 1.9 | 58 | 60 | 11 | 10 | 130 | 201 | 60 | 10 | 10 | 78 | 0 | 11 | 10 | 310 | 23 | 5 | 0 | 48 | 0 | 0 | 50 | 0 |  | 460 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 154 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 8 | 41 | 16 | 11 | 10 | 0 | 0 | 120 | 0 | 0 | 135 | 0 | 0 | 180 | 12 | 0 | 0 | 0 |  | 5133.9 | 1496 | 6629.9 | 3155 | 460 | 1441 | 577 | 120 | 162 | 617 | 96 | 1.9 | 0 | 102.48
10:00 | 37 | 120 | 0 | 0 | 320 | 83 | 40 | 300 | 303 | 0 | 0 | 350 | 100 | 7 | 15 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 16 | 25 | 30 | 33 | 26 | 0 | 0 | 82 | 80 | 0 | 0 | 8 | 0 | 207 | 0 | 50 | 0 | 22 | 0 | 0 | 56 | 12 | 18 | 17 | 16 | 0 | 100 | 100 | 325 | 323 | 194 | 78 | 100 | 39 | 0 | 5 | 12 | 10 | 0 | 0 | 19 | 8 | 8 | 12 | 102 | 49 | 32 | 20 | 2.3 | 58 | 60 | 11 | 10 | 100 | 204 | 59 | 10 | 10 | 78 | 0 | 11 | 10 | 270 | 8 | 5 | 0 | 48 | 0 | 0 | 80 | 0 |  | 460 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 154 | 9 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 8 | 41 | 14 | 11 | 10 | 0 | 0 | 115 | 0 | 0 | 135 | 0 | 0 | 175 | 12 | 0 | 0 | 0 |  | 5165.3 | 1471 | 6636.3 | 3152 | 460 | 1375 | 651 | 115 | 162 | 617 | 102 | 2.3 | 0 | 102.45
11:00 | 37 | 120 | 0 | 0 | 320 | 86 | 40 | 300 | 332 | 0 | 0 | 350 | 100 | 7 | 15 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 12 | 18 | 18 | 17 | 16 | 25 | 26 | 33 | 17 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 225 | 0 | 49 | 0 | 30 | 0 | 0 | 80 | 50 | 19 | 17 | 8 | 0 | 100 | 100 | 330 | 331 | 178 | 78 | 100 | 36 | 0 | 5 | 12 | 10 | 0 | 0 | 19 | 5 | 8 | 0 | 104 | 46 | 32 | 20 | 2.7 | 58 | 60 | 11 | 10 | 100 | 202 | 59 | 10 | 10 | 78 | 0 | 11 | 10 | 320 | 12 | 11 | 0 | 48 | 0 | 0 | 80 | 0 |  | 459 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 154 | 13 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 24 | 0 | 8 | 41 | 14 | 11 | 10 | 0 | 0 | 120 | 0 | 0 | 135 | 0 | 0 | 186 | 12 | 0 | 0 | 0 |  | 5308.7 | 1443 | 6751.7 | 3123 | 459 | 1453 | 685 | 120 | 160 | 645 | 104 | 2.7 | 0 | 102.44
12:00 | 37 | 120 | 0 | 0 | 350 | 88 | 60 | 340 | 345 | 0 | 0 | 420 | 100 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 12 | 18 | 18 | 17 | 16 | 25 | 26 | 33 | 17 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 80 | 0 | 27 | 0 | 0 | 80 | 80 | 33 | 17 | 8 | 0 | 100 | 100 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 12 | 10 | 0 | 0 | 19 | 8 | 8 | 0 | 110 | 43 | 32 | 20 | 0.7 | 58 | 60 | 11 | 10 | 130 | 193 | 60 | 10 | 10 | 78 | 0 | 11 | 10 | 300 | 21 | 11 | 0 | 48 | 0 | 0 | 80 | 0 |  | 461 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 24 | 0 | 8 | 40 | 18 | 11 | 10 | 0 | 0 | 118 | 0 | 0 | 135 | 0 | 0 | 175 | 54 | 0 | 0 | 0 |  | 5536.7 | 1515 | 7051.7 | 3219 | 461 | 1615 | 726 | 118 | 160 | 642 | 110 | 0.7 | 0 | 102.43
13:00 | 37 | 120 | 0 | 0 | 365 | 88 | 72 | 367 | 342 | 0 | 0 | 420 | 100 | 7 | 15 | 19 | 165 | 0 | 0 | 0 | 7 | 24 | 0 | 20 | 8 | 10 | 12 | 18 | 18 | 17 | 16 | 25 | 24 | 33 | 17 | 3 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 131 | 0 | 24 | 0 | 0 | 80 | 84 | 37 | 17 | 8 | 0 | 100 | 100 | 300 | 301 | 162 | 78 | 100 | 39 | 0 | 5 | 12 | 70 | 0 | 0 | 18 | 8 | 20 | 0 | 106 | 44 | 40 | 20 | 0.8 | 58 | 60 | 35 | 29 | 163 | 189 | 62 | 70 | 10 | 78 | 0 | 44 | 10 | 295 | 23 | 11 | 0 | 48 | 0 | 0 | 80 | 0 |  | 452 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 181 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 24 | 0 | 16 | 40 | 20 | 11 | 10 | 0 | 0 | 119 | 0 | 0 | 135 | 0 | 0 | 183 | 54 | 0 | 0 | 0 |  | 5907.8 | 1545 | 7452.8 | 3255 | 452 | 1851 | 809 | 119 | 160 | 700 | 106 | 0.8 | 0 | 102.42
14:00 | 37 | 120 | 0 | 0 | 295 | 88 | 73 | 345 | 323 | 0 | 0 | 370 | 100 | 7 | 15 | 30 | 165 | 0 | 0 | 0 | 7 | 24 | 3 | 20 | 16 | 10 | 34 | 18 | 18 | 17 | 16 | 25 | 20 | 33 | 17 | 33 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 210 | 0 | 100 | 0 | 30 | 0 | 0 | 80 | 85 | 38 | 17 | 20 | 0 | 120 | 103 | 0 | 316 | 198 | 78 | 100 | 38 | 0 | 5 | 20 | 87 | 0 | 0 | 18 | 8 | 33 | 21 | 100 | 44 | 40 | 20 | 2.2 | 58 | 60 | 44 | 50 | 163 | 200 | 54 | 84 | 45 | 78 | 0 | 44 | 10 | 265 | 23 | 11 | 0 | 48 | 0 | 0 | 100 | 0 |  | 462 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 24 | 0 | 16 | 40 | 21 | 11 | 10 | 0 | 0 | 116 | 0 | 0 | 135 | 0 | 0 | 171 | 20 | 0 | 0 | 0 |  | 5715.2 | 1520 | 7235.2 | 2979 | 462 | 1839 | 908 | 116 | 160 | 669 | 100 | 2.2 | 0 | 102.56
15:00 | 37 | 120 | 0 | 0 | 365 | 88 | 73 | 355 | 346 | 0 | 0 | 420 | 120 | 7 | 15 | 30 | 170 | 0 | 0 | 0 | 7 | 24 | 48 | 87 | 60 | 0 | 39 | 36 | 18 | 17 | 16 | 25 | 20 | 33 | 17 | 43 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 130 | 0 | 32 | 0 | 0 | 80 | 85 | 45 | 17 | 17 | 0 | 150 | 130 | 0 | 290 | 182 | 78 | 100 | 38 | 0 | 5 | 42 | 85 | 0 | 0 | 18 | 8 | 33 | 21 | 108 | 46 | 45 | 20 | 2.8 | 58 | 59 | 50 | 50 | 163 | 190 | 56 | 86 | 40 | 80 | 0 | 44 | 10 | 300 | 23 | 11 | 0 | 57 | 0 | 0 | 101 | 0 |  | 0 | 0 | 50 | 15 | 32 | 130 | 0 | 51 | 0 | 0 | 33 | 187 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 24 | 0 | 16 | 41 | 3 | 11 | 10 | 0 | 0 | 120 | 0 | 0 | 135 | 0 | 0 | 180 | 40 | 35 | 0 | 0 |  | 6191.8 | 1187 | 7378.8 | 3070 | 0 | 1968 | 1194 | 120 | 160 | 756 | 108 | 2.8 | 0 | 102.56
16:00 | 37 | 120 | 0 | 0 | 365 | 88 | 74 | 345 | 333 | 0 | 0 | 400 | 100 | 7 | 15 | 46 | 170 | 0 | 0 | 0 | 7 | 24 | 48 | 100 | 60 | 0 | 39 | 54 | 18 | 17 | 16 | 25 | 20 | 33 | 24 | 49 | 0 | 85 | 80 | 0 | 0 | 8 | 0 | 202 | 0 | 60 | 0 | 32 | 0 | 0 | 80 | 90 | 44 | 17 | 13 | 0 | 150 | 130 | 0 | 301 | 182 | 78 | 100 | 38 | 0 | 5 | 45 | 85 | 0 | 0 | 18 | 8 | 33 | 21 | 106 | 46 | 90 | 20 | 0.9 | 58 | 59 | 50 | 50 | 130 | 190 | 48 | 86 | 46 | 79 | 0 | 44 | 10 | 275 | 22 | 11 | 0 | 98 | 0 | 0 | 102 | 0 |  | 0 | 0 | 80 | 46 | 66 | 160 | 0 | 12 | 0 | 13 | 32 | 182 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 25 | 25 | 43 | 0 | 25 | 41 | 10 | 11 | 10 | 0 | 0 | 120 | 0 | 0 | 135 | 0 | 0 | 168 | 89 | 10 | 0 | 0 |  | 6159.9 | 1353 | 7512.9 | 3093 | 0 | 1940 | 1371 | 120 | 165 | 717 | 106 | 0.9 | 0 | 102.56
17:00 | 37 | 120 | 0 | 0 | 300 | 64 | 50 | 345 | 333 | 0 | 0 | 400 | 100 | 7 | 15 | 30 | 170 | 0 | 0 | 0 | 7 | 16 | 48 | 10 | 31 | 0 | 24 | 36 | 18 | 17 | 16 | 25 | 20 | 33 | 24 | 25 | 0 | 85 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 60 | 0 | 32 | 0 | 0 | 80 | 45 | 44 | 17 | 17 | 0 | 150 | 130 | 0 | 301 | 183 | 78 | 100 | 35 | 0 | 5 | 51 | 21 | 0 | 0 | 19 | 8 | 33 | 0 | 94 | 46 | 24 | 20 | 0.2 | 58 | 59 | 11 | 10 | 100 | 188 | 60 | 50 | 10 | 79 | 0 | 12 | 10 | 275 | 23 | 11 | 0 | 48 | 0 | 0 | 103 | 0 |  | 459 | 0 | 80 | 10 | 16 | 120 | 0 | 0 | 0 | 28 | 8 | 181 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 43 | 0 | 8 | 41 | 10 | 11 | 8 | 0 | 0 | 122 | 0 | 0 | 91 | 0 | 0 | 169 | 58 | 0 | 0 | 0 |  | 5395.2 | 1544 | 6939.2 | 2970 | 459 | 1592 | 845 | 122 | 165 | 692 | 94 | 0.2 | 0 | 102.56
18:00 | 37 | 120 | 0 | 0 | 270 | 46 | 40 | 345 | 282 | 0 | 0 | 370 | 100 | 7 | 15 | 30 | 170 | 0 | 0 | 0 | 7 | 16 | 48 | 10 | 31 | 0 | 24 | 36 | 17 | 17 | 16 | 0 | 20 | 33 | 24 | 25 | 0 | 88 | 80 | 0 | 0 | 8 | 0 | 201 | 0 | 50 | 0 | 32 | 0 | 0 | 80 | 45 | 45 | 18 | 33 | 0 | 150 | 130 | 0 | 301 | 182 | 78 | 100 | 35 | 0 | 5 | 45 | 20 | 0 | 0 | 19 | 8 | 33 | 0 | 100 | 46 | 24 | 20 | 0 | 30 | 36 | 11 | 10 | 100 | 189 | 60 | 20 | 10 | 79 | 0 | 12 | 10 | 295 | 23 | 11 | 0 | 48 | 0 | 0 | 103 | 0 |  | 463 | 0 | 105 | 10 | 16 | 120 | 0 | 0 | 14 | 41 | 8 | 186 | 16 | 16 | 0 | 0 | 0 | 0 | 10 | 25 | 24 | 43 | 0 | 8 | 40 | 18 | 11 | 10 | 0 | 0 | 119 | 0 | 0 | 0 | 0 | 0 | 169 | 35 | 0 | 0 | 0 |  | 5179 | 1507 | 6686 | 2806 | 463 | 1467 | 845 | 119 | 168 | 718 | 100 | 0 | 0 | 102.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.55
19:00 | 37 | 120 | 0 | 0 | 300 | 85 | 40 | 364 | 330 | 16 | 0 | 400 | 100 | 12 | 15 | 30 | 170 | 0 | 0 | 3 | 8 | 50 | 55 | 90 | 63 | 0 | 24 | 54 | 30 | 50 | 19 | 25 | 20 | 33 | 24 | 26 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 216 | 0 | 50 | 0 | 32 | 72 | 0 | 90 | 78 | 44 | 18 | 32 | 0 | 150 | 130 | 0 | 334 | 204 | 125 | 100 | 35 | 0 | 5 | 45 | 50 | 41 | 0 | 19 | 8 | 33 | 19 | 134 | 46 | 43 | 20 | 0 | 60 | 63 | 17 | 21 | 100 | 207 | 60 | 50 | 10 | 80 | 0 | 45 | 10 | 310 | 22 | 11 | 0 | 50 | 0 | 0 | 112 | 0 |  | 463 | 0 | 165 | 62 | 71 | 120 | 0 | 50 | 47 | 37 | 33 | 192 | 22 | 60 | 0 | 0 | 0 | 40 | 38 | 25 | 35 | 43 | 45 | 8 | 40 | 18 | 11 | 11 | 0 | 0 | 119 | 15 | 18 | 0 | 0 | 0 | 183 | 85 | 10 | 0 | 0 |  | 6180 | 2066 | 8246 | 3099 | 463 | 1811 | 1408 | 119 | 170 | 1042 | 134 | 0 | 0 | 102.55
19:30 | 37 | 120 | 0 | 0 | 365 | 85 | 76 | 347 | 350 | 50 | 0 | 420 | 140 | 93 | 30 | 35 | 168 | 0 | 0 | 8 | 8 | 66 | 100 | 88 | 64 | 0 | 40 | 54 | 30 | 55 | 19 | 25 | 20 | 33 | 24 | 38 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 32 | 64 | 24 | 90 | 98 | 44 | 18 | 41 | 0 | 150 | 130 | 0 | 301 | 182 | 125 | 100 | 39 | 0 | 5 | 45 | 85 | 41 | 0 | 19 | 8 | 33 | 19 | 132 | 48 | 95 | 20 | 0 | 57 | 62 | 47 | 50 | 163 | 190 | 60 | 86 | 45 | 80 | 0 | 45 | 10 | 300 | 22 | 11 | 0 | 50 | 0 | 0 | 112 | 0 |  | 463 | 0 | 230 | 83 | 115 | 145 | 0 | 27 | 49 | 38 | 24 | 192 | 23 | 96 | 0 | 0 | 0 | 51 | 38 | 85 | 40 | 43 | 45 | 30 | 40 | 18 | 11 | 11 | 0 | 0 | 120 | 15 | 18 | 0 | 0 | 0 | 179 | 93 | 10 | 0 | 0 |  | 6803 | 2332 | 9135 | 3140 | 463 | 2123 | 1804 | 120 | 170 | 1183 | 132 | 0 | 0 | 102.55
20:00 | 37 | 120 | 0 | 0 | 365 | 85 | 60 | 360 | 353 | 55 | 0 | 420 | 100 | 85 | 60 | 55 | 168 | 0 | 0 | 17 | 75 | 50 | 149 | 100 | 64 | 0 | 38 | 54 | 56 | 55 | 19 | 25 | 20 | 33 | 24 | 45 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 50 | 0 | 32 | 64 | 32 | 90 | 98 | 45 | 17 | 41 | 0 | 150 | 130 | 0 | 301 | 183 | 125 | 100 | 39 | 0 | 24 | 45 | 86 | 41 | 0 | 19 | 8 | 33 | 21 | 152 | 48 | 95 | 20 | 0 | 57 | 62 | 48 | 50 | 130 | 190 | 48 | 86 | 47 | 78 | 0 | 45 | 10 | 265 | 23 | 11 | 0 | 102 | 0 | 0 | 112 | 0 |  | 463 | 0 | 246 | 86 | 115 | 160 | 0 | 0 | 49 | 48 | 33 | 177 | 30 | 96 | 0 | 0 | 0 | 51 | 37 | 102 | 40 | 43 | 47 | 43 | 40 | 18 | 11 | 11 | 0 | 0 | 123 | 15 | 18 | 0 | 0 | 0 | 173 | 97 | 0 | 0 | 0 |  | 6987 | 2372 | 9359 | 3143 | 463 | 2076 | 1955 | 123 | 170 | 1277 | 152 | 0 | 0 | 102.55
21:00 | 37 | 120 | 0 | 0 | 365 | 85 | 76 | 360 | 350 | 0 | 0 | 450 | 100 | 65 | 100 | 55 | 164 | 0 | 0 | 0 | 60 | 32 | 115 | 20 | 64 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 24 | 50 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 213 | 0 | 50 | 0 | 32 | 72 | 32 | 90 | 99 | 44 | 18 | 42 | 0 | 150 | 130 | 0 | 342 | 206 | 125 | 100 | 39 | 0 | 24 | 51 | 86 | 0 | 0 | 19 | 8 | 33 | 21 | 156 | 46 | 95 | 20 | 0 | 59 | 62 | 50 | 50 | 163 | 217 | 60 | 86 | 47 | 78 | 0 | 45 | 10 | 260 | 22 | 11 | 0 | 278 | 0 | 0 | 102 | 0 |  | 457 | 0 | 270 | 89 | 117 | 120 | 0 | 0 | 48 | 60 | 33 | 192 | 33 | 96 | 0 | 0 | 0 | 51 | 37 | 59 | 40 | 43 | 45 | 43 | 40 | 0 | 11 | 10 | 0 | 0 | 120 | 17 | 18 | 0 | 0 | 0 | 178 | 97 | 0 | 0 | 0 |  | 7132 | 2324 | 9456 | 3291 | 457 | 2141 | 1966 | 120 | 170 | 1155 | 156 | 0 | 0 | 102.55
22:00 | 37 | 120 | 0 | 0 | 365 | 85 | 75 | 375 | 350 | 0 | 0 | 450 | 135 | 65 | 100 | 55 | 165 | 0 | 0 | 0 | 60 | 32 | 115 | 20 | 64 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 24 | 50 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 214 | 0 | 50 | 0 | 32 | 72 | 31 | 90 | 99 | 44 | 18 | 42 | 0 | 150 | 130 | 0 | 342 | 210 | 125 | 100 | 39 | 0 | 24 | 51 | 85 | 0 | 0 | 19 | 8 | 33 | 21 | 160 | 47 | 95 | 20 | 0 | 59 | 62 | 50 | 50 | 163 | 218 | 60 | 86 | 47 | 78 | 0 | 43 | 10 | 325 | 22 | 11 | 0 | 298 | 0 | 0 | 102 | 0 |  | 464 | 0 | 270 | 46 | 115 | 120 | 0 | 0 | 48 | 58 | 34 | 193 | 33 | 96 | 0 | 0 | 0 | 51 | 37 | 59 | 40 | 43 | 45 | 43 | 41 | 14 | 11 | 10 | 0 | 0 | 114 | 16 | 18 | 0 | 0 | 0 | 183 | 97 | 0 | 0 | 0 |  | 7275 | 2299 | 9574 | 3315 | 464 | 2216 | 1977 | 114 | 170 | 1158 | 160 | 0 | 0 | 102.55
23:00 | 37 | 120 | 0 | 0 | 365 | 86 | 76 | 384 | 351 | 0 | 0 | 450 | 100 | 65 | 98 | 55 | 165 | 0 | 0 | 0 | 60 | 32 | 115 | 20 | 65 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 24 | 50 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 205 | 0 | 100 | 0 | 32 | 72 | 31 | 80 | 99 | 44 | 18 | 42 | 0 | 150 | 130 | 0 | 331 | 203 | 125 | 100 | 39 | 0 | 24 | 51 | 86 | 0 | 0 | 19 | 8 | 33 | 21 | 156 | 47 | 95 | 20 | 0 | 58 | 61 | 50 | 50 | 163 | 204 | 60 | 86 | 47 | 80 | 0 | 44 | 10 | 330 | 23 | 11 | 0 | 301 | 0 | 0 | 102 | 0 |  | 464 | 0 | 269 | 46 | 115 | 120 | 0 | 0 | 41 | 57 | 33 | 193 | 32 | 96 | 0 | 0 | 0 | 51 | 37 | 59 | 40 | 43 | 44 | 43 | 41 | 18 | 11 | 10 | 0 | 0 | 125 | 16 | 18 | 0 | 0 | 0 | 186 | 97 | 0 | 0 | 0 |  | 7257 | 2305 | 9562 | 3292 | 464 | 2229 | 1933 | 125 | 170 | 1193 | 156 | 0 | 0 | 102.55
24:00 | 37 | 120 | 0 | 0 | 365 | 86 | 76 | 377 | 352 | 0 | 0 | 450 | 100 | 30 | 98 | 55 | 150 | 0 | 0 | 0 | 60 | 7 | 115 | 0 | 65 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 24 | 50 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 205 | 0 | 60 | 0 | 32 | 72 | 29 | 80 | 99 | 44 | 18 | 42 | 0 | 150 | 130 | 0 | 331 | 204 | 125 | 100 | 39 | 0 | 24 | 51 | 85 | 0 | 0 | 19 | 8 | 33 | 22 | 152 | 51 | 95 | 20 | 0 | 58 | 61 | 50 | 50 | 163 | 204 | 60 | 86 | 47 | 80 | 0 | 44 | 10 | 320 | 23 | 11 | 0 | 301 | 0 | 0 | 102 | 0 |  | 464 | 0 | 285 | 46 | 115 | 120 | 0 | 0 | 41 | 58 | 40 | 193 | 30 | 96 | 0 | 0 | 0 | 43 | 37 | 59 | 40 | 43 | 44 | 43 | 42 | 21 | 11 | 10 | 0 | 0 | 122 | 16 | 18 | 0 | 0 | 0 | 187 | 98 | 0 | 0 | 0 |  | 7105 | 2322 | 9427 | 3292 | 464 | 2221 | 1860 | 122 | 170 | 1146 | 152 | 0 | 0 | 102.55
KWH | 866000 | 2876265 | 0 | 0 | 8102854 | 1804977 | 1640128 | 8706080 | 7771000 | 61400 | 0 | 9284376 | 2757324 | 646080 | 858816 | 807084 | 3840731 | 0 | 0 | 22080 | 646080 | 486864 | 1364160 | 717406 | 970560 | 83160 | 698880 | 872280 | 677337 | 734000 | 373860 | 575000 | 653220 | 800148 | 708500 | 651156 | 0 | 1956120 | 1894300 | 0 | 0 | 261000 | 0 | 4793602 | 0 | 1699118 | 0 | 706432 | 579056 | 141706 | 1708920 | 882240 | 896640 | 421968 | 590400 | 0 | 2928920 | 2314158 | 4457000 | 7553000 | 4564000 | 2141090 | 2378050 | 893232 | 0 | 215000 | 823806 | 858816 | 59688 | 54960 | 433548 | 201600 | 609900 | 378200 | 3007680 | 1204520 | 1270347 | 446508 | 14400 | 1309000 | 1416843 | 833400 | 790000 | 3323290 | 4485195 | 1354000 | 1408320 | 765360 | 1926170 | 0 | 783940 | 253440 | 7527600 | 525672 | 241872 | 0 | 3507708 | 0 | 0 | 2544000 | 0 |  | 10361454 | 0 | 3075268 | 771840 | 1448640 | 3212160 | 0 | 92490 | 480480 | 531072 | 500250 | 4365801 | 471709 | 1220160 | 0 | 0 | 0 | 409528 | 300261 | 983108 | 878120 | 914592 | 253120 | 617760 | 994270 | 408240 | 268704 | 247032 | 0 | 0 | 2960400 | 148000 | 179000 | 2439264 | 0 | 0 | 4422827 | 1524374 | 45120 | 0 | 0 |  | 147393541 | 44525044 | 191918585 | 77673379 | 10361454 | 43487970 | 30011726 | 2960400 | 3850420 | 20551156 | 3007680 | 14400 | 0
Fuel Cost | 744760 | 2473587.9 | 0 | 0 | 6968454.44 | 1462031.37 | 1541720.32 | 5310708.8 | 4740310 | 590054 | 0 | 6220531.92 | 41883751.56 | 4057382.4 | 5736890.88 | 4931283.24 | 2496475.15 | 0 | 0 | 343564.8 | 4038000 | 3208433.76 | 13191427.2 | 4569876.22 | 5813654.4 | 1329728.4 | 4661529.6 | 6219356.4 | 4233356.25 | 4602180 | 280395 | 431250 | 0 | 0 | 0 | 6159935.76 | 0 | 0 | 0 | 0 | 0 | 2471670 | 0 | 65432667.3 | 0 | 37227675.38 | 0 | 6209537.28 | 6236433.12 | 1378799.38 | 10578214.8 | 5699270.4 | 5864025.6 | 358672.8 | 0 | 0 | 2665317.2 | 2105883.78 | 4055870 | 5211570 | 3194800 | 1477352.1 | 2282928 | 598465.44 | 0 | 197800 | 675520.92 | 807287.04 | 647017.92 | 407803.2 | 333831.96 | 151200 | 469623 | 283650 | 20572531.2 | 903390 | 11674488.93 | 343811.16 | 0 | 1361360 | 1473516.72 | 800064 | 711000 | 4287044.1 | 3139636.5 | 1543560 | 1506902.4 | 841896 | 2195833.8 | 0 | 729064.2 | 235699.2 | 4817664 | 394254 | 183822.72 | 0 | 0 | 0 | 0 | 0 | 0 |  | 52843415.4 | 0 | 2060429.56 | 5094144 | 9705888 | 51651532.8 | 0 | 1476140.4 | 5410204.8 | 6256028.16 | 3186592.5 | 4322142.99 | 466991.91 | 7540588.8 | 0 | 0 | 0 | 4689095.6 | 3218797.92 | 8808647.68 | 7595738 | 8139868.8 | 2695728 | 6128179.2 | 10708287.9 | 449064 | 252581.76 | 187003.224 | 0 | 0 | 0 | 3414360 | 3837760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 372979055.32 | 210139211.404 | 583118266.724 | 58526204.144 | 52843415.4 | 32220525.24 | 194151127.58 | 0 | 0 | 224804463.16 | 20572531.2 | 0 | 0
Yesterday Day Peak | 37 | 120 | 0 | 0 | 350 | 88 | 60 | 340 | 345 | 0 | 0 | 420 | 100 | 7 | 15 | 15 | 150 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 10 | 12 | 18 | 18 | 17 | 16 | 25 | 26 | 33 | 17 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 203 | 0 | 80 | 0 | 27 | 0 | 0 | 80 | 80 | 33 | 17 | 8 | 0 | 100 | 100 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 12 | 10 | 0 | 0 | 19 | 8 | 8 | 0 | 110 | 43 | 32 | 20 | 0.7 | 58 | 60 | 11 | 10 | 130 | 193 | 60 | 10 | 10 | 78 | 0 | 11 | 10 | 300 | 21 | 11 | 0 | 48 | 0 | 0 | 80 | 0 |  | 461 | 0 | 50 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 14 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 12 | 24 | 0 | 8 | 40 | 18 | 11 | 10 | 0 | 0 | 118 | 0 | 0 | 135 | 0 | 0 | 175 | 54 | 0 | 0 | 0 |  | 7051.7 | DayPeak
Yesterday Evening Peak | 37 | 120 | 0 | 0 | 365 | 85 | 76 | 360 | 350 | 0 | 0 | 450 | 100 | 65 | 100 | 55 | 164 | 0 | 0 | 0 | 60 | 32 | 115 | 20 | 64 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 24 | 50 | 0 | 90 | 80 | 0 | 0 | 16 | 0 | 213 | 0 | 50 | 0 | 32 | 72 | 32 | 90 | 99 | 44 | 18 | 42 | 0 | 150 | 130 | 0 | 342 | 206 | 125 | 100 | 39 | 0 | 24 | 51 | 86 | 0 | 0 | 19 | 8 | 33 | 21 | 156 | 46 | 95 | 20 | 0 | 59 | 62 | 50 | 50 | 163 | 217 | 60 | 86 | 47 | 78 | 0 | 45 | 10 | 260 | 22 | 11 | 0 | 278 | 0 | 0 | 102 | 0 |  | 457 | 0 | 270 | 89 | 117 | 120 | 0 | 0 | 48 | 60 | 33 | 192 | 33 | 96 | 0 | 0 | 0 | 51 | 37 | 59 | 40 | 43 | 45 | 43 | 40 | 0 | 11 | 10 | 0 | 0 | 120 | 17 | 18 | 0 | 0 | 0 | 178 | 97 | 0 | 0 | 0 |  | 9456 | EvPeak
Forecast for Evening | 37 | 120 | 0 | 0 | 365 | 108 | 78 | 412 | 300 | 98 | 0 | 450 | 305 | 100 | 102 | 55 | 200 | 0 | 0 | 100 | 93 | 102 | 149 | 0 | 100 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 89 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 135 | 0 | 51 | 68 | 74 | 80 | 103 | 44 | 18 | 15 | 0 | 150 | 130 | 360 | 360 | 225 | 195 | 100 | 39 | 0 | 10 | 51 | 85 | 48 | 52 | 19 | 11 | 33 | 22 | 164 | 100 | 95 | 22 | 0 | 58 | 62 | 51 | 50 | 163 | 220 | 60 | 86 | 50 | 100 | 0 | 45 | 10 | 341 | 23 | 11 | 200 | 300 | 0 | 0 | 185 | 100 |  | 470 | 32 | 330 | 110 | 115 | 225 | 0 | 54 | 47 | 78 | 40 | 194 | 30 | 110 | 30 | 0 | 0 | 50 | 38 | 102 | 43 | 43 | 46 | 43 | 43 | 22 | 12 | 11 | 0 | 0 | 125 | 17 | 18 | 0 | 214 | 0 | 220 | 95 | 80
Forecast for Day | 37 | 120 | 0 | 0 | 365 | 100 | 78 | 0 | 360 | 98 | 0 | 450 | 150 | 100 | 102 | 55 | 200 | 0 | 0 | 100 | 93 | 102 | 100 | 0 | 100 | 50 | 40 | 54 | 55 | 55 | 19 | 25 | 33 | 33 | 33 | 52 | 0 | 89 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 60 | 0 | 51 | 68 | 74 | 80 | 103 | 44 | 18 | 5 | 0 | 150 | 130 | 210 | 360 | 225 | 78 | 100 | 39 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 8 | 33 | 22 | 124 | 97 | 95 | 22 | 2 | 58 | 62 | 51 | 50 | 163 | 220 | 60 | 86 | 50 | 80 | 0 | 45 | 10 | 341 | 23 | 11 | 0 | 150 | 0 | 0 | 150 | 100 |  | 470 | 0 | 330 | 110 | 115 | 225 | 0 | 0 | 36 | 78 | 40 | 194 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 43 | 43 | 46 | 43 | 42 | 22 | 12 | 11 | 0 | 0 | 125 |  | 18 | 0 |  | 0 | 220 | 95 | 80
Generation at 08:00(Today) | 37 | 120 | 0 | 0 | 365 | 86 | 40 | 0 | 352 | 0 | 0 | 450 | 100 | 7 | 15 | 15 | 142 | 0 | 0 | 0 | 7 | 7 | 16 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 19 | 25 | 22 | 33 | 33 | 16 | 0 | 90 | 80 | 0 | 0 | 8 | 0 | 208 | 0 | 60 | 0 | 8 | 0 | 0 | 20 | 12 | 18 | 18 | 6 | 0 | 150 | 130 | 210 | 342 | 216 | 77 | 100 | 39 | 0 | 5 | 5 | 11 | 0 | 0 | 19 | 5 | 33 | 12 | 116 | 83 | 8 | 20 | 1 | 58 | 61 | 5 | 50 | 163 | 218 | 59 | 10 | 5 | 80 | 0 | 43 | 10 | 320 | 23 | 11 | 0 | 48 | 0 | 0 | 52 | 0 | 0 | 464 | 0 | 328 | 10 | 112 | 120 | 0 | 0 | 0 | 0 | 41 | 193 | 15 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 12 | 8 | 0 | 8 | 0 | 21 | 11 | 10 | 0 | 0 | 124 | 0 | 0 | 0 | 0 | 0 | 187 | 98 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6526.4 | 7:00
| Highest Generation |  | 9574 | 22:00
| Day Peak Generation |  | 7051.7 | 12:00
| Evening Peak Generation |  | 9456 | 21:00
| HVDC Max Flow |  | 474 | 1:00
| HVDC EvPeak Flow |  | 457 | 21:00
| Load factor L.F |  | 83.52%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-30
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-29 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7051.7 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6748.4 | MW
Evening Peak Generation : |  | 9456 | MW Hour : | 21:00 | Available Max Generation : |  | 12206 | MW
E.P. Demand (at gen end) : |  | 9456 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10900 | MW
Maximum Generation : |  | 9574 | MW Hour : | 22:00 | Reserve(Generation end) |  | 1306 | MW
Total Gen. (MKWH) : |  | 191.9186 | System Load Factor : | 83.52% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -810 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-30
Actual : | 102.25 | Ft.(MSL) , | Rule curve : | 83.73 | Ft.( MSL )
Gas Consumed : | Total = | 1042.95 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 90746729.384
|  | Coal : | 0 | Oil : | 418955590.74 | Total : | 509702320.124
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3897.6383 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1325.048 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1187.1341 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1072.6527 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 969.3535 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 782.233 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 437.8556 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 201.4164 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 603.2947 |  |  | 0 | 0%
Total | 0 |  | 10476.6263 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
3) Ghorasal Unit-2,4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Haripur-Shyampur 132 kV Ckt tripped at 09:21 from Haripur end showing Z1,CN relay and was switched on at 09:33. |  |  |  | About 76 MW Power interruption occurred under Shyampur S/S
area from 09:21 to 09:33.
b) Bogra-Polashbari 132 kV Ckt-1 was under shut down from 09:15 to 10:20 for 132 kV bus coupler maint at Bogra end. |  |  |  | About 60 MW Power interruption occurred under Polashbari S/S
area from 09:15 to 10:20.
c) Bogra-Bogra(new) 132 kV Ckt-2 was under shut down from 10:40 to 12:30 for C/M. |  |  |  | About 56 MW Power interruption occurred under Bogra S/S
area from 10:40 to 12:30.
d) Bogra-Naogaon 132 kV Ckt-2 was under shut down from 09:52 to 10:32 for C/M.
e) Sayedpur 132/33 kV T4 transformer was under shut down from 11:20 to 11:35 for oil leakage maintenance. |  |  |  | About 9 MW Power interruption occurred under Sayedpur S/S
area from 11:20 to 11:35.
f) Polashbari 132/33 kV T2 transformer was under shut down from 10:38 to 11:18 for red hot maint at R phase LT bushing.
g) Ashuganj(N) tripped at 13:50 due to Nitrogen compressor trip and was synchronized at 01:57(30/06/2018).
h) Tongi-Kabirpur 132 kV Ckt-1,2 tripped at 14:34 from Tongi end showing Z1,dist CSW,CAR,CDC relay and were switched on at
14:56,14:58 respectively.
i) HVDC Bheramara P1 & P2 tripped at 14:40 due to DC system problem and was switched on P1 at 16:00.
j) Sirajganj # 1 GT & ST were under shut down at 16:46,17:07 due to gas pressure low.
k) After maint Bheramara 360 MW ST was synchronized at 18:30.
l) Bakulia 132/33 kV T3 transformer is under shut down since 06:16(30/6/2018) for C/M.
m) Gopalganj 132/33 kV T1 transformer is under shut down since 07:20(30/6/2018) for D/W.
n) Hasnabad-Kamrangirchar 132 kV Ckt is under shut down since 07:27(30/6/18) for C/M.
o) Lalmonirhat 132/33 kV T4 transformer is under shut down since 08:05(30/6/2018) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-29 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 37 | 866000 | # 2 Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2876265 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 8102854
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 76 | 1640128
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 85 | 1804977 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 360 | 8706080 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 61400 | Low demand
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 350 | 7771000
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 9284376
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 65 | 646080 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 100 | 2757324 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 100 | 858816
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 807084
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 20 | 717406 | Low demand
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 373860 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 22080 | Low demand
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 60 | 646080 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 164 | 3840731 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 83160 | Reserve
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 32 | 486864 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 39 | 698880 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 872280
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 1364160
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 55 | 677337
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 734000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 64 | 970560 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1228220 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 800148
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 24 | 708500
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 651156
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 278 | 3507708 | Engine problem
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 0 | 0 | On test.
| Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | On test.
| Dhaka area Total |  |  |  | 5199 | 3281 | 64565514
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 261000 | Engine problem
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 44 | 896640 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 170 | 3850420 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 213 | 4793602 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 50 | 1699118
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 32 | 706432 | Engine problem
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 72 | 579056
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 32 | 141706
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1708920 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 421968
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 590400
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 99 | 882240 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 878 | 16531502
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 150 | 2928920
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 130 | 2314158
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 206 | 4564000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 4457000 | tripped at 13:50
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 342 | 7553000 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 39 | 893232 | Engine problem
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 24 | 215000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 125 | 2141090 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 823806
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 86 | 858816
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 59688
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 2378050
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 433548
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 201600
** | Tripura |  | Imported power | 0 | 160 | 156 | 3007680
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 609900
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 0 | 54960 | Low demand
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 378200 | Engine problem
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 0 | 0 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1490 | 33872648
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 46 | 1204520 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 446508
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 1270347
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 14400
| United Mymensingh PPL |  | IPP | 200 | 0 | 102 | 2544000 | On test.
| Mymensingh Area Total |  |  |  | 322 | 263 | 5479775
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 59 | 1309000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1416843
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3323290
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 217 | 4485195 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 833400
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 790000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 241872
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 60 | 1354000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1408320
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 765360
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1926170
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 45 | 783940 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 22 | 525672
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 260 | 7527600 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 10 | 253440
| Sylhet Area Total |  |  |  | 1549 | 1220 | 26944102
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 457 | 10361454
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 89 | 771840 | Engine problem
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 117 | 1448640
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 48 | 480480
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3212160 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 531072
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 270 | 3075268 | Gas shortage
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 33 | 500250
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 0 | 92490 | Low demand
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 0 | 45120 | Low demand
| Khulna Area Total |  |  |  | 1769 | 1194 | 20518774
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 96 | 1220160
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 33 | 471709
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 192 | 4365801
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1524374
| Barisal Area Total |  |  |  | 462 | 418 | 7582044
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 51 | 409528
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 37 | 300261
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 878120 | Engine problem
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 914592 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 253120
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Reserve
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 40 | 994270
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 0 | 408240 | tripped
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 268704
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 10 | 247032
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 617760 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 59 | 983108 | Low demand
| Rajshahi Area Total |  |  |  | 1123 | 557 | 6274735
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 120 | 2960400
117 | Rangpur GT |  | PDB | 1*20 | 20 | 17 | 148000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 179000
| Rangpur Area Total |  |  |  | 484 | 155 | 3287400
| Total |  |  |  | 15010 | 9456 | 185056494
| Eastern Grid Total |  |  |  | 11172 | 7132 | 147393541
| Western Grid Total |  |  |  | 3838 | 2324 | 37662953
| National Grid Total |  |  |  | 15010 | 9456 | 185056494
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-29 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6158 | MW | (b) ENTIRE WESTERN GRID : |  |  | 2923 | MW
i) Dhaka area |  |  | 3267 | MW | i) Khulna area |  |  | 1157 | MW
ii) Chittagong area |  |  | 940 | MW | ii) Rajshahi area |  |  | 959 | MW
iii) Comilla area |  |  | 874 | MW | iii) Barisal area |  |  | 250 | MW
iv) Mymensingh area |  |  | 723 | MW | iv) Rangpur area |  |  | 557 | MW
v) Sylhet area |  |  | 354 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9081 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 100 | Kishorganj | 94 | 2200 | Goalpara | 34 | 100
Munsiganj | 104 | 2100 | Netrokona | 88 | 2100 | Central s/s | 56 | 100
Sonargaon | 37 | 1930 | Jamalpur | 108 | 2300 | Noapara | 70 | 1930
Shyampur | 138 | 100 | Sherpur | 80 | 100 | Jessore | 136 | 2100
Bhulta | 170 | 100 | Srimongal | 34 | 2100 | Jhenida | 94 | 1930
Madanganj | 41 | 2100 | Shahjibazar | 96 | 2200 | Bottail | 110 | 2100
Shitalakhya | 91 | 300 | Fenchuganj | 47 | 1900 | G.K Project | 52 | 2000
Rahim steel | 2 | 100 | Kulawara | 36 | 2000 | Faridpur | 140 | 2100
Matuail | 72 | 200 | Sylhet | 116 | 2200 | Madaripur | 116 | 2100
Ghorasal | 71 | 100 | Chatak | 26 | 2200 | Gopalganj | 71 | 2100
Narsingdi | 106 | 100 | Sunamganj | 31 | 2100 | Bagerhat | 71 | 0
Haripur (SBU) | 72 | 900 | Biani Bazar | 33 | 100 | Mongla | 22 | 200
Ullon | 87 | 2000 | Comilla (S) | 156 | 2100 | Satkhira | 70 | 200
Hasnabad | 181 | 2000 | Comilla(N) | 89 | 2000 | Gallamari | 46 | 2100
Magbazar | 99 | 2000 | Chandpur | 109 | 1930 | Magura | 46 | 1930
Maniknagar | 66 | 1200 | Feni | 107 | 2100 | Chuadanga | 70 | 2300
Bangabhaban | 16 | 1700 | Chowmuhani | 172 | 2200 | Barisal | 108 | 2300
Narinda | 62 | 1600 | Ashuganj | 57 | 2300 | Patuakhali | 82 | 2200
Dhanmondi | 81 | 1900 | Daudkandi | 82 | 2200 | Bhandaria | 46 | 2100
Lalbag | 59 | 2000 | B.Baria | 128 | 2000 | Ishurdi | 50 | 2000
Madartek | 47 | 1930 | Ramganj | 28 | 1930 | Ruppur Paromanobik | 1 | 100
Mirpur | 95 | 2100 | Madunaghat | 62 | 1930 | Natore | 104 | 200
Kalyanpur | 111 | 1500 | Hathazari | 70 | 2100 | Bogra | 206 | 100
Gulshan | 102 | 2000 | Khulshi | 164 | 1500 | Noagaon | 108 | 2000
Uttara | 79 | 2100 | Halishahar | 117 | 2000 | Rajshahi | 135 | 2000
Kamrangirchar | 57 | 2100 | Baraulia | 138 | 300 | C.Nawabganj | 60 | 2000
Savar | 114 | 2000 | Sikalbaha | 37 | 1930 | Amnura | 32 | 100
Bhasantec | 133 | 2000 | Dohazari | 72 | 1900 | Pabna | 104 | 2000
Agargaon | 40 | 2000 | Cox'sbazar | 78 | 2100 | Shahjadpur | 70 | 2000
Satmosjid | 89 | 1100 | Chandraghona | 30 | 1900 | Serajganj | 70 | 100
Tongi | 116 | 1000 | Kaptai | 4 | 1900 | Niyamatpur | 44 | 100
Kabirpur | 141 | 2000 | A. Khaer Stl. | 17 | 1700 | Joypurhat | 42 | 2000
Basundhara | 115 | 2100 | Bakulia | 86 | 2000 | Rangpur | 114 | 100
Manikganj | 111 | 2100 | Julda | 14 | 100 | Lalmonirhat | 85 | 2000
Joydevpur | 203 | 1500 | TK chemical | 6 | 1700 | Saidpur | 99 | 2000
New Tongi | 87 | 1600 | Modern Steel | 8 | 300 | Purbasadipur | 89 | 1930
Korda | 197 | 2200 | Shahmirpur | 25 | 100 | Thakurgaon | 60 | 100
Dhamrai | 19 | 2000 | Abul Khair 230 | 191 | 900 | Palashbari | 97 | 2000
Tangail | 169 | 2200 | BSRM | 108 | 1000 | Barapukuria | 46 | 2000
Mymensing | 217 | 2200 | Khagrachhari | 18 | 2000 | Panchagar | 32 | 100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-29
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 395 | 5:00 | 387 | 13:00 | Kaliakoir | 375 | 3:00 | 367 | 21:00
Bheramara | 407 | 5:00 | 384 | 20:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 224 | 4:00 | 217 | 12:00
Ishurdi | 235 | 6:00 | 222 | 21:00 | Comilla (N) | 233 | 7:00 | 230 | 1:00
Ashuganj | 237 | 5:00 | 231 | 23:00 | Hathazari | 222 | 19:30 | 214 | 7:00
Serajganj | 225 | 7:00 | 212 | 21:00 | Megnaghat | 228 | 5:00 | 223 | 14:00
Baghabari | 225 | 7:00 | 216 | 23:00 | Fenchuganj | 237 | 5:00 | 233 | 11:00
Barapukuria | 234 | 6:00 | 220 | 22:00 | Siddhirganj | 226 | 2:00 | 222 | 10:00
Bogra | 226 | 9:00 | 208 | 22:00 | Maniknagar | 224 | 2:00 | 220 | 11:00
Khulna South | 241 | 16:00 | 226 | 22:00 | Old Airport | 226 | 2:00 | 219 | 11:00
Rampura | 222 | 2:00 | 200 | 19:00 | Barisal | 235 | 16:00 | 222 | 14:00
Haripur | 222 | 1:00 | 220 | 16:00 | AKSML | 220 | 20:00 | 210 | 14:00
Hasnabad | 226 | 4:00 | 221 | 11:00 | BSRM | 221 | 5:00 | 213 | 10:00
Aminbazar | 226 | 3:00 | 219 | 12:00 | Bibiyana | 233 | 5:00 | 229 | 21:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 1930 | 133 | 1000 | B.Baria | 137 | 1500 | 132 | 2100
Munsiganj | 136 | 1930 | 132 | 1300 | Ramganj | 130 | 1100 | 122 | 1930
Megnaghat | 135 | 2000 | 131 | 700 | Madanhat | 133 | 1800 | 128 | 1000
Shyampur | 131 | 1930 | 127 | 1000 | Hathazari | 130 | 1800 | 125 | 700
Bhulta | 129 | 1300 | 126 | 100 | Khulshi | 127 | 1800 | 123 | 900
Madanganj | 138 | 2000 | 130 | 400 | Halishahar | 132 | 2000 | 126 | 1600
Shitalakhya | 139 | 1930 | 132 | 1100 | Baraulia | 128 | 1800 | 126 | 900
Rahim steal | 135 | 1900 | 133 | 1000 | Sikalbaha | 131 | 2000 | 126 | 1000
Matuail | 134 | 1800 | 132 | 1100 | Dohazari | 130 | 600 | 126 | 900
Ghorasal | 135 | 100 | 135 | 200 | Cox'sbazar | 123 | 1400 | 116 | 100
Narsinghdi | 134 | 1800 | 128 | 100 | Chandraghona | 131 | 600 | 128 | 100
Haripur (SBU) | 136 | 1600 | 133 | 1000 | Kaptai | 132 | 2000 | 130 | 1300
Ullon | 135 | 600 | 132 | 1200 | A. Khaer Stl. | 129 | 2000 | 125 | 100
Hasnabad | 135 | 600 | 132 | 1300 | Bakulia | 129 | 1930 | 125 | 900
Magbazar | 136 | 600 | 131 | 1400 | Julda | 130 | 1800 | 127 | 500
Maniknagar | 136 | 600 | 134 | 1600 | TK Chemical | 133 | 2000 | 129 | 100
Bangabhaban | 136 | 600 | 134 | 1600 | Modern Steel | 129 | 2000 | 125 | 100
Narinda | 136 | 600 | 134 | 1600 | Shahmirpur | 130 | 1930 | 126 | 100
Dhanmondi | 136 | 600 | 134 | 1600 | Khagrachhari | 130 | 2000 | 127 | 900
Lalbag | 134 | 600 | 130 | 1100 | Goalpara | 138 | 1500 | 130 | 2200
Madartek | 135 | 600 | 131 | 1900 | Central s/s | 138 | 1600 | 131 | 2200
Mirpur | 138 | 100 | 130 | 1200 | Noapara | 136 | 1500 | 125 | 2200
Kalyanpur | 137 | 300 | 131 | 1300 | Jessore | 135 | 1500 | 120 | 2200
Gulshan | 135 | 600 | 131 | 1200 | Jhenida | 132 | 1500 | 118 | 2200
Uttara | 133 | 300 | 127 | 1200 | Bottail | 138 | 1500 | 127 | 2200
Kamrangirchar | 136 | 300 | 131 | 1200 | G.K.Project | 141 | 600 | 135 | 2100
Savar | 135 | 200 | 120 | 1200 | Faridpur | 134 | 500 | 125 | 2100
Bhasantec | 133 | 200 | 129 | 1200 | Madaripur | 134 | 500 | 125 | 1930
Agargaon | 135 | 200 | 130 | 1200 | Gopalganj | 137 | 600 | 122 | 1400
Satmosjid | 134 | 200 | 129 | 1200 | Bagerhat | 136 | 1500 | 130 | 1800
Tongi | 134 | 800 | 131 | 1300 | Mongla | 136 | 1500 | 125 | 2200
Kabirpur | 134 | 500 | 127 | 2200 | Satkhira | 137 | 1500 | 126 | 2200
Basundhara | 132 | 600 | 128 | 1900 | Gallamari | 138 | 1500 | 130 | 2200
Manikganj | 138 | 400 | 132 | 2100 | Magura | 131 | 1500 | 115 | 200
Joydevpur | 137 | 400 | 131 | 1900 | Chuadanga | 128 | 600 | 112 | 2200
New Tongi | 135 | 400 | 130 | 2000 | Barisal | 139 | 400 | 133 | 1300
Kodda | 137 | 100 | 130 | 1700 | Patuakhali | 135 | 300 | 125 | 2200
Dhamrai | 133 | 500 | 127 | 2100 | Bhandaria | 136 | 600 | 128 | 2200
Tangail | 134 | 600 | 123 | 2200 | Ishurdi | 142 | 600 | 135 | 1930
Mymensing | 129 | 600 | 115 | 2100 | Ruppur Paromanobik | 140 | 700 | 134 | 1930
Kishorganj | 128 | 500 | 120 | 2200 | Natore | 139 | 1000 | 131 | 1930
Netrokona | 130 | 500 | 115 | 2100 | Bogra | 135 | 900 | 122 | 1930
Jamalpur | 135 | 1500 | 122 | 2100 | Noagaon | 132 | 900 | 119 | 2000
Sherpur | 134 | 1830 | 122 | 2100 | Rajshahi | 136 | 1000 | 128 | 1500
Srimongal | 138 | 1500 | 135 | 100 | C.Nawabganj | 135 | 1800 | 127 | 1930
Shahjibazar | 137 | 1600 | 132 | 2100 | Amnura | 138 | 1400 | 130 | 1200
Fenchuganj | 136 | 400 | 134 | 1830 | Pabna | 135 | 900 | 125 | 1930
Khulawara | 135 | 400 | 133 | 2100 | Shahjadpur | 141 | 500 | 135 | 2000
Sylhet | 134 | 300 | 133 | 2200 | Serajganj | 135 | 600 | 126 | 2000
Chatak | 135 | 500 | 132 | 2100 | Niyamatpur | 132 | 900 | 115 | 1930
Sunamganj | 134 | 1500 | 132 | 900 | Joypurhat | 132 | 700 | 115 | 1930
Biani Bazar | 135 | 500 | 131 | 2300 | Rangpur | 124 | 600 | 108 | 100
Comilla(s) | 125 | 700 | 121 | 1900 | Lalmonirhat | 120 | 600 | 99 | 1930
Comilla(n) | 137 | 1500 | 134 | 1300 | Saidpur | 122 | 900 | 104 | 100
Chandpur | 127 | 700 | 125 | 2000 | Purbasadipur | 132 | 600 | 120 | 1930
Feni | 122 | 1200 | 117 | 2200 | Thakurgaon | 126 | 600 | 108 | 100
Chowmuhani | 125 | 600 | 116 | 100 | Palashbari | 125 | 600 | 110 | 2000
Ashuganj | 137 | 700 | 135 | 200 | Barapukuria | 134 | 600 | 122 | 1930
Daudkandi | 133 | 1930 | 127 | 2400 | Panchagar | 119 | 800 | 103 | 1930

## L-Curve
Date | 2018-06-29
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 740 | 7105 | 2322 | 9427 |  |  |  | QF-LDC-12
0:30 | 720 | 7093 | 2355.5 | 9448.5 | Date: | 2018-06-29
1:00 | 700 | 7081 | 2389 | 9470
1:30 | 690 | 7034 | 2364 | 9398
2:00 | 680 | 6987 | 2339 | 9326
2:30 | 675 | 6839 | 2301.5 | 9140.5 | [5 empty] | Gen. at Eve. Peak | 9456 | 9456 MW (21:00 )
3:00 | 670 | 6691 | 2264 | 8955 | [6 empty] | 21:00
3:30 | 670 | 6635 | 2160 | 8795 | [5 empty] | Gen. at Day Peak | 7051.7 | 7051.7 MW (12:00 )
4:00 | 670 | 6579 | 2056 | 8635 | [6 empty] | 12:00
4:30 | 665 | 6455 | 1988 | 8443 | [5 empty] | Highest Generation | 9574
5:00 | 660 | 6331 | 1920 | 8251 | [6 empty] | 22:00
5:30 | 620 | 5772.5 | 1772.5 | 7545
6:00 | 580 | 5214 | 1625 | 6839
6:30 | 525 | 5095.7 | 1587 | 6682.7
7:00 | 470 | 4977.4 | 1549 | 6526.4
7:30 | 465 | 5012.95 | 1549 | 6561.95
8:00 | 460 | 5048.5 | 1549 | 6597.5
8:30 | 420 | 5091.2 | 1522.5 | 6613.7
9:00 | 380 | 5133.9 | 1496 | 6629.9
9:30 | 360 | 5149.6 | 1483.5 | 6633.1
10:00 | 340 | 5165.3 | 1471 | 6636.3
10:30 | 395 | 5237 | 1457 | 6694
11:00 | 450 | 5308.7 | 1443 | 6751.7
11:30 | 465 | 5422.7 | 1479 | 6901.7
12:00 | 480 | 5536.7 | 1515 | 7051.7
12:30 | 570 | 5722.25 | 1530 | 7252.25
13:00 | 660 | 5907.8 | 1545 | 7452.8
13:30 | 645 | 5811.5 | 1532.5 | 7344
14:00 | 630 | 5715.2 | 1520 | 7235.2
14:30 | 705 | 5953.5 | 1353.5 | 7307
15:00 | 780 | 6191.8 | 1187 | 7378.8
15:30 | 740 | 6175.85 | 1270 | 7445.85
16:00 | 700 | 6159.9 | 1353 | 7512.9
16:30 | 560 | 5777.55 | 1448.5 | 7226.05
17:00 | 420 | 5395.2 | 1544 | 6939.2
17:30 | 430 | 5287.1 | 1525.5 | 6812.6
18:00 | 440 | 5179 | 1507 | 6686
18:30 | 430 | 5679.5 | 1786.5 | 7466
19:00 | 420 | 6180 | 2066 | 8246
19:30 | 740 | 6803 | 2332 | 9135
20:00 | 710 | 6987 | 2372 | 9359 |  |  |  | Executive Engineer
20:30 | 735 | 7059.5 | 2348 | 9407.5 |  |  |  | Network Operation Division
21:00 | 760 | 7132 | 2324 | 9456
21:30 | 785 | 7203.5 | 2311.5 | 9515
22:00 | 810 | 7275 | 2299 | 9574 |  |  |  |  | Page 6 of 7
22:30 | 785 | 7266 | 2302 | 9568
23:00 | 760 | 7257 | 2305 | 9562
23:30 | 750 | 7181 | 2313.5 | 9494.5
24:00 | 740 | 7105 | 2322 | 9427
9456 MW (21:00 )
7051.7 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-29 |  | Energy | 191918585
[10 empty] | 2018-06-29 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3292 | 464 | 2221 | 1860 | 122 | 170 | 1146 | 0 | 152
0:30 | 3322.5 | 469 | 2083.5 | 1958.5 | 121.5 | 169 | 1171.5 | 0 | 153 | Date: | 2018-06-29
1:00 | 3353 | 474 | 1946 | 2057 | 121 | 168 | 1197 | 0 | 154
1:30 | 3351 | 469 | 1968 | 2007 | 121 | 164 | 1167 | 0 | 151 | [7 empty] | Total Energy | 191.9186 | Total Energy Gen 191.919 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 191.919 MKWHr
2:00 | 3349 | 464 | 1990 | 1957 | 121 | 160 | 1137 | 0 | 148 | [7 empty] | Energy not Served | 0
2:30 | 3358 | 464 | 1987.5 | 1819.5 | 121 | 160 | 1083.5 | 0 | 147 | [7 empty] | Energy Requirement | 191.9186
3:00 | 3367 | 464 | 1985 | 1682 | 121 | 160 | 1030 | 0 | 146
3:30 | 3375.5 | 464 | 2036 | 1562.5 | 121 | 160 | 932 | 0 | 144 | [6 empty] | Shortage
4:00 | 3384 | 464 | 2087 | 1443 | 121 | 160 | 834 | 0 | 142
4:30 | 3378 | 464 | 2079.5 | 1320 | 121 | 160 | 783.5 | 0 | 137
5:00 | 3372 | 464 | 2072 | 1197 | 121 | 160 | 733 | 0 | 132
5:30 | 3303.5 | 464 | 1770.5 | 926 | 121 | 160 | 679 | 0 | 121
6:00 | 3235 | 464 | 1469 | 655 | 121 | 160 | 625 | 0 | 110
6:30 | 3223 | 464 | 1388 | 598.5 | 122 | 160 | 620 | 0 | 107 |  |  |  |  | Coal
7:00 | 3211 | 464 | 1307 | 542 | 123 | 160 | 615 | 0 | 104
7:30 | 3211.5 | 463.5 | 1330.5 | 545 | 121 | 160 | 625.5 | 0 | 104 |  |  |  | Oil |  |  |  | ,
8:00 | 3212 | 463 | 1354 | 548 | 119 | 160 | 636 | 0 | 104
8:30 | 3183.5 | 461.5 | 1397.5 | 562.5 | 119.5 | 161 | 626.5 | 0 | 100
9:00 | 3155 | 460 | 1441 | 577 | 120 | 162 | 617 | 0 | 96
9:30 | 3153.5 | 460 | 1408 | 614 | 117.5 | 162 | 617 | 0 | 99
10:00 | 3152 | 460 | 1375 | 651 | 115 | 162 | 617 | 0 | 102
10:30 | 3137.5 | 459.5 | 1414 | 668 | 117.5 | 161 | 631 | 0 | 103
11:00 | 3123 | 459 | 1453 | 685 | 120 | 160 | 645 | 0 | 104
11:30 | 3171 | 460 | 1534 | 705.5 | 119 | 160 | 643.5 | 0 | 107
12:00 | 3219 | 461 | 1615 | 726 | 118 | 160 | 642 | 0 | 110
12:30 | 3237 | 456.5 | 1733 | 767.5 | 118.5 | 160 | 671 | 0 | 108
13:00 | 3255 | 452 | 1851 | 809 | 119 | 160 | 700 | 0 | 106
13:30 | 3255 | 452 | 1851 | 809 | 119 | 160 | 700 | 0 | 106
14:00 | 3255 | 452 | 1851 | 809 | 119 | 160 | 700 | 0 | 106
14:30 | 3162.5 | 226 | 1909.5 | 1001.5 | 119.5 | 160 | 728 | 0 | 107
15:00 | 3070 | 0 | 1968 | 1194 | 120 | 160 | 756 | 0 | 108
15:30 | 3081.5 | 0 | 1954 | 1282.5 | 120 | 162.5 | 736.5 | 0 | 107
16:00 | 3093 | 0 | 1940 | 1371 | 120 | 165 | 717 | 0 | 106
16:30 | 3031.5 | 229.5 | 1766 | 1108 | 121 | 165 | 704.5 | 0 | 100
17:00 | 2970 | 459 | 1592 | 845 | 122 | 165 | 692 | 0 | 94
17:30 | 2888 | 461 | 1529.5 | 845 | 120.5 | 166.5 | 705 | 0 | 97
18:00 | 2806 | 463 | 1467 | 845 | 119 | 168 | 718 | 0 | 100
18:30 | 2952.5 | 463 | 1639 | 1126.5 | 119 | 169 | 880 | 0 | 117
19:00 | 3099 | 463 | 1811 | 1408 | 119 | 170 | 1042 | 0 | 134
19:30 | 3140 | 463 | 2123 | 1804 | 120 | 170 | 1183 | 0 | 132
20:00 | 3143 | 463 | 2076 | 1955 | 123 | 170 | 1277 | 0 | 152
20:30 | 3217 | 460 | 2108.5 | 1960.5 | 121.5 | 170 | 1216 | 0 | 154
21:00 | 3291 | 457 | 2141 | 1966 | 120 | 170 | 1155 | 0 | 156
21:30 | 3303 | 460.5 | 2178.5 | 1971.5 | 117 | 170 | 1156.5 | 0 | 158
22:00 | 3315 | 464 | 2216 | 1977 | 114 | 170 | 1158 | 0 | 160
22:30 | 3303.5 | 464 | 2222.5 | 1955 | 119.5 | 170 | 1175.5 | 0 | 158
23:00 | 3292 | 464 | 2229 | 1933 | 125 | 170 | 1193 | 0 | 156
23:30 | 3292 | 464 | 2225 | 1896.5 | 123.5 | 170 | 1169.5 | 0 | 154 | Max Temp. in Dhaka |  | 33.8° C
24:00 | 3292 | 464 | 2221 | 1860 | 122 | 170 | 1146 | 0 | 152
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 191.919 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 191.919 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-29
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 88 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 82 | 82 | 80 | 80 | 80 | 80 | 80 | 85 | 85 | 88 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1956120
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1894300
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 261000
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 195 | 195 | 195 | 195 | 195 | 191 | 206 | 216 | 203 | 207 | 225 | 203 | 201 | 210 | 202 | 202 | 201 | 201 |  | 216 | 201 | 201 | 213 | 214 | 205 | 205 | 4793602
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 113 | 110 | 90 | 70 | 50 | 50 | 50 | 50 | 49 | 50 | 49 | 80 | 131 | 100 | 130 | 60 | 60 | 50 |  | 50 | 50 | 50 | 50 | 50 | 100 | 60 | 1699118
| Dohazari Peaking | [19 empty] | 0 | 24 | 32 | 32 | 31 | 31 | 29 | 141706
12 | Hathazari peaking | 55 | 55 | 55 | 24 | 24 | 0 | [13 empty] | 72 | 64 | 64 | 72 | 72 | 72 | 72 | 579056
| Daudkandi bangla trak | 0
14 | Daudkandi Peaking 52MW | [19 empty] | 41 | 41 | 41 | 0 |  |  |  | 59688
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2
17 | Siddhirganj CCPP-335 MW | 155 | 145 | 145 | 140 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 150 | 165 | 165 | 170 | 170 | 170 | 170 |  | 170 | 168 | 168 | 164 | 165 | 165 | 150 | 3840731
18 | Summit Gazipur | 301 | 301 | 301 | 219 | 200 | 92 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 57 | 98 | 48 | 48 |  | 50 | 50 | 102 | 278 | 298 | 301 | 301 | 3507708
19 | Ashuganj 195MW Modular | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2141090
20 | Ghorasal ST: Unit-1,2 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 866000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2876265
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 350 | 350 | 349 | 349 | 328 | 310 | 280 | 280 | 320 | 320 | 320 | 350 | 365 | 295 | 365 | 365 | 300 | 270 |  | 300 | 365 | 365 | 365 | 365 | 365 | 365 | 8102854
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2928920
30 | Ashuganj ST: Unit- 5 | 0 |  | 0 | 15 | 60 | 85 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 103 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2314158
32 | Ashuganj Engines TSK | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 39 | 39 | 38 | 38 | 38 | 35 | 35 |  | 35 | 39 | 39 | 39 | 39 | 39 | 39 | 893232
33 | Ashuganj CCPP 225 MW | 189 | 183 | 183 | 183 | 183 | 183 | 199 | 204 | 184 | 194 | 178 | 183 | 162 | 198 | 182 | 182 | 183 | 182 |  | 204 | 182 | 183 | 206 | 210 | 203 | 204 | 4564000
34 | Ashuganj CCPP(South) | 301 | 301 | 301 | 301 | 301 | 301 | 327 | 334 | 316 | 323 | 331 | 301 | 301 | 316 | 290 | 301 | 301 | 301 |  | 334 | 301 | 301 | 342 | 342 | 331 | 331 | 7553000
| Ashuganj CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 327 | 337 | 315 | 325 | 330 | 300 | 300 | 0 | [12 empty] | 4457000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2378050
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 373 | 384 | 400 | 410 | 410 | 330 | 300 | 300 | 330 | 300 | 300 | 340 | 367 | 345 | 355 | 345 | 345 | 345 |  | 364 | 347 | 360 | 360 | 375 | 384 | 377 | 8706080
40 | Meghnaghat CCPP 450MW | 400 | 400 | 400 | 430 | 430 | 350 | 320 | 320 | 350 | 350 | 350 | 420 | 420 | 370 | 420 | 400 | 400 | 370 |  | 400 | 420 | 420 | 450 | 450 | 450 | 450 | 9284376
41 | Haripur Power CCPP 360MW | 290 | 317 | 325 | 350 | 352 | 321 | 301 | 301 | 301 | 303 | 332 | 345 | 342 | 323 | 346 | 333 | 333 | 282 |  | 330 | 350 | 353 | 350 | 350 | 351 | 352 | 7771000
42 | Mymensingh RPCL 210MW | 48 | 49 | 58 | 78 | 66 | 66 | 64 | 63 | 45 | 49 | 46 | 43 | 44 | 44 | 46 | 46 | 46 | 46 |  | 46 | 48 | 48 | 46 | 47 | 47 | 51 | 1204520
43 | Haripur NEPC 110MW | [17 empty] | 0 |  | 16 | 50 | 55 | 0 |  |  |  | 61400
44 | Fenchugonj CCPP-1 | 55 | 55 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 30 |  | 60 | 57 | 57 | 59 | 59 | 58 | 58 | 1309000
45 | Fenchugonj CCPP-2 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 36 |  | 63 | 62 | 62 | 62 | 62 | 61 | 61 | 1416843
46 | Shajibazar 330 MW | 200 | 200 | 192 | 200 | 194 | 194 | 202 | 208 | 201 | 204 | 202 | 193 | 189 | 200 | 190 | 190 | 188 | 189 |  | 207 | 190 | 190 | 217 | 218 | 204 | 204 | 4485195
47 | Shahjibazar GT: Unit- 8, 9 | 50 | 63 | 52 | 53 | 50 | 50 | 50 | 50 | 60 | 59 | 59 | 60 | 62 | 54 | 56 | 48 | 60 | 60 |  | 60 | 60 | 48 | 60 | 60 | 60 | 60 | 1354000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 86 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 84 | 86 | 86 | 50 | 20 |  | 50 | 86 | 86 | 86 | 86 | 86 | 86 | 1408320
49 | Shahjibazar (EPL) 50MW | 47 | 48 | 48 | 48 | 48 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 45 | 40 | 46 | 10 | 10 |  | 10 | 45 | 47 | 47 | 47 | 47 | 47 | 765360
50 | Sylhet GT 150 MW | 78 | 78 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 80 | 79 | 79 | 79 |  | 80 | 80 | 78 | 78 | 78 | 80 | 80 | 1926170
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 44 | 44 | 44 | 45 | 44 | 11 | 11 | 13 | 11 | 11 | 11 | 11 | 44 | 44 | 44 | 44 | 12 | 12 |  | 45 | 45 | 45 | 45 | 43 | 44 | 44 | 783940
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 253440
54 | Hobiganj 11MW | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 241872
55 | Fenchugonj (Barakatullah) 51MW | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 35 | 44 | 50 | 50 | 11 | 11 |  | 17 | 47 | 48 | 50 | 50 | 50 | 50 | 833400
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 8 | 12 | 21 | 23 | 23 | 23 | 22 | 23 | 23 |  | 22 | 22 | 23 | 22 | 22 | 23 | 23 | 525672
57 | Summit Bibiana- 2 | 270 | 280 | 270 | 280 | 260 | 260 | 270 | 320 | 310 | 270 | 320 | 300 | 295 | 265 | 300 | 275 | 275 | 295 |  | 310 | 300 | 265 | 260 | 325 | 330 | 320 | 7527600
58 | Southern 55MW | 55 | 55 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 734000
59 | Sikalbaha (Energis) | 42 | 42 | 42 | 32 | 32 | 16 | 8 | 8 | 8 | 22 | 30 | 27 | 24 | 30 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 706432
60 | Barabkunda (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 |  | 18 | 18 | 17 | 18 | 18 | 18 | 18 | 421968
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 373860
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 446508
63 | Tripura | 154 | 148 | 146 | 142 | 132 | 110 | 104 | 104 | 96 | 102 | 104 | 110 | 106 | 100 | 108 | 106 | 94 | 100 |  | 134 | 132 | 152 | 156 | 160 | 156 | 152 | 3007680
64 | Malancha, Ctg. EPZ (United) | 30 | 39 | 37 | 40 | 41 | 16 | 17 | 16 | 16 | 16 | 8 | 8 | 8 | 20 | 17 | 13 | 17 | 33 |  | 32 | 41 | 41 | 42 | 42 | 42 | 42 | 590400
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 433548
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 201600
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 20 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 609900
68 | Summit Comilla 25MW | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 12 | 12 | 12 | 0 | 0 | 0 | 21 | 21 | 21 | 0 | 0 |  | 19 | 19 | 21 | 21 | 21 | 21 | 22 | 378200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 30 | 26 | 26 | 24 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 31 | 32 | 32 | 32 | 653220
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 800148
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 17 | 17 | 17 | 17 | 17 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 708500
73 | Ghorashal (Regent) | 89 | 89 | 89 | 89 | 89 | 24 | 24 | 25 | 64 | 83 | 86 | 88 | 88 | 88 | 88 | 88 | 64 | 46 |  | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 1804977
76 | Siddhirganj (Desh) | [19 empty] | 3 | 8 | 17 | 0 |  |  |  | 22080
77 | Siddhirganj (Dutch Bangla) | 60 | 60 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 8 | 8 | 75 | 60 | 60 | 60 | 60 | 646080
78 | Gazipur (RPCL) | 50 | 0 | 23 | 34 | 16 | 0 | 0 | [5 empty] | 3 | 33 | 43 | 49 | 25 | 25 |  | 26 | 38 | 45 | 50 | 50 | 50 | 50 | 651156
79 | Kodda 150MW | 149 | 120 | 105 | 76 | 44 | 30 | 0 | [6 empty] | 3 | 48 | 48 | 48 | 48 |  | 55 | 100 | 149 | 115 | 115 | 115 | 115 | 1364160
80 | Jamalpur 95MW | 95 | 95 | 80 | 48 | 8 | 8 | 8 | 8 | 8 | 32 | 32 | 32 | 40 | 40 | 45 | 90 | 24 | 24 |  | 43 | 95 | 95 | 95 | 95 | 95 | 95 | 1270347
81 | Lakdhanvi 52 MW | 8 | 8 | 8 | 8 | 8 | 0 | [20 empty] | 54960
82 | Madanganj 102MW | 48 | 48 | 15 | 15 | 15 | 15 | 15 | 16 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 30 | 60 | 100 | 100 | 98 | 98 | 858816
83 | Pagla (DPA ) | 11 | 11 | 0 | [7 empty] | 10 | 10 | 10 | 10 | 0 | [11 empty] | 83160
84 | B.Baria (Aggreko) 85MW | 86 | 86 | 86 | 86 | 86 | 20 | 11 | 11 | 12 | 10 | 10 | 10 | 70 | 87 | 85 | 85 | 21 | 20 |  | 50 | 85 | 86 | 86 | 85 | 86 | 85 | 858816
85 | Keraniganj (Powerpac) 100MW | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 20 | 87 | 100 | 10 | 10 |  | 90 | 88 | 100 | 20 | 20 | 20 | 0 | 717406
86 | Meghnaghat CCPP(Summit) | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 100 | 100 | 100 |  | 100 | 140 | 100 | 100 | 135 | 100 | 100 | 2757324
87 | Meghnaghat (IEL) | 60 | 65 | 30 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 12 | 93 | 85 | 65 | 65 | 65 | 30 | 646080
88 | Ghorashal 78MW (MAX) | 70 | 70 | 70 | 70 | 70 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 72 | 73 | 73 | 74 | 50 | 40 |  | 40 | 76 | 60 | 76 | 75 | 76 | 76 | 1640128
90 | Ashuganj (United) 53MW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 24 | 24 | 24 | 24 | 24 | 215000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 50 | 15 | 15 | 50 | 56 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 1708920
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 29 | 50 | 50 | 50 | 10 | 10 |  | 21 | 50 | 50 | 50 | 50 | 50 | 50 | 790000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 51 | 51 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 20 | 42 | 45 | 51 | 45 |  | 45 | 45 | 45 | 51 | 51 | 51 | 51 | 823806
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 24 | 24 | 24 | 24 | 16 | 16 |  | 50 | 66 | 50 | 32 | 32 | 32 | 7 | 486864
95 | Patenga 50MW | 44 | 44 | 44 | 30 | 30 | 18 | 18 | 18 | 18 | 18 | 19 | 33 | 37 | 38 | 45 | 44 | 44 | 45 |  | 44 | 44 | 45 | 44 | 44 | 44 | 44 | 896640
96 | Chittagong ECPV 108 MW | 99 | 99 | 72 | 72 | 52 | 12 | 12 | 12 | 12 | 12 | 50 | 80 | 84 | 85 | 85 | 90 | 45 | 45 |  | 78 | 98 | 98 | 99 | 99 | 99 | 99 | 882240
97 | Katpotti 51 MW | 39 | 39 | 39 | 39 | 30 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 34 | 39 | 39 | 24 | 24 |  | 24 | 40 | 38 | 39 | 39 | 39 | 39 | 698880
98 | Bosila 108MW | 74 | 74 | 74 | 60 | 47 | 19 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 60 | 60 | 31 | 31 |  | 63 | 64 | 64 | 64 | 64 | 65 | 65 | 970560
99 | Madanganj-55 MW | 55 | 55 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 19 | 30 | 30 | 46 | 30 | 30 |  | 30 | 35 | 55 | 55 | 55 | 55 | 55 | 807084
100 | Northern 55 MW | 56 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 |  | 30 | 30 | 56 | 55 | 55 | 55 | 55 | 677337
101 | Kushiara 163 MW CCPP GT | 130 | 130 | 130 | 163 | 163 | 100 | 100 | 100 | 130 | 100 | 100 | 130 | 163 | 163 | 163 | 130 | 100 | 100 |  | 100 | 163 | 130 | 163 | 163 | 163 | 163 | 3323290
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.4 | 1.5 | 1.9 | 2.3 | 2.7 | 0.7 | 0.8 | 2.2 | 2.8 | 0.9 | 0.2 | 0 | [8 empty] | 14400
103 | Banco Energy 54MW | 54 | 54 | 54 | 36 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 54 | 36 | 36 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 872280
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 173 | 163 | 163 | 150 | 130 | 65 | 50 | 55 | 50 | 80 | 80 | 80 | 80 | 100 | 101 | 102 | 103 | 103 |  | 112 | 112 | 112 | 102 | 102 | 102 | 102 | 2544000
112 | Aggreko Aurahati 100MW
113
114
115
116
117
118 | Eastern Zone Total | 7081 | 6987 | 6691 | 6579 | 6331 | 5214 | 4977.4 | 5048.5 | 5133.9 | 5165.3 | 5308.7 | 5536.7 | 5907.8 | 5715.2 | 6191.8 | 6159.9 | 5395.2 | 5179 |  | 6180 | 6803 | 6987 | 7132 | 7275 | 7257 | 7105 | 147393541
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 71 | 77 | 64 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 46 | 10 | 10 |  | 62 | 83 | 86 | 89 | 46 | 46 | 46 | 771840
124 | Khulna (KPCL-2) | 115 | 115 | 115 | 115 | 92 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 66 | 16 | 16 |  | 71 | 115 | 115 | 117 | 115 | 115 | 115 | 1448640
125
126 | Khulna (Aggreko) 55MW | [14 empty] | 51 | 12 | 0 |  |  | 50 | 27 | 0 |  |  |  |  | 92490
127 | Faridpur Peaking | 49 | 49 | 42 | 43 | 43 | [12 empty] | 14 |  | 47 | 49 | 49 | 48 | 48 | 41 | 41 | 480480
128 | Khulna CCPP 225MW | 165 | 135 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 160 | 120 | 120 |  | 120 | 145 | 160 | 120 | 120 | 120 | 120 | 3212160
129
130
131
132
133
| Summit Barisal 110 MW | 98 | 96 | 96 | 80 | 80 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 32 | 32 | 16 | 16 |  | 60 | 96 | 96 | 96 | 96 | 96 | 96 | 1220160
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 97 | 97 | 97 | 94 | 98 | 75 | 11 | 12 | 12 | 12 | 12 | 54 | 54 | 20 | 40 | 89 | 58 | 35 |  | 85 | 93 | 97 | 97 | 97 | 97 | 98 | 1524374
137 | Bhola CCPP 194MW | 193 | 180 | 191 | 193 | 191 | 173 | 154 | 154 | 154 | 154 | 154 | 191 | 181 | 191 | 187 | 182 | 181 | 186 |  | 192 | 192 | 177 | 192 | 193 | 193 | 193 | 4365801
| Bhola (Venture) 33MW | 30 | 27 | 30 | 29 | 28 | 24 | 23 | 21 | 22 | 9 | 13 | 14 | 15 | 18 | 17 | 18 | 16 | 16 |  | 22 | 23 | 30 | 33 | 33 | 32 | 30 | 471709
140 | Bangla Trak Noapara | [14 empty] | 35 | 10 | 0 |  |  | 10 | 10 | 0 |  |  |  |  | 45120
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 32 | 8 | 8 |  | 33 | 24 | 33 | 33 | 34 | 33 | 40 | 500250
142 | Gopalganj Peaking | 45 | 45 | 45 | 20 | 20 | [10 empty] | 13 | 28 | 41 |  | 37 | 38 | 48 | 60 | 58 | 57 | 58 | 531072
143 | Bheramara GT-1,2,3
144
145 | Bheramara HVDC | 474 | 464 | 464 | 464 | 464 | 464 | 464 | 463 | 460 | 460 | 459 | 461 | 452 | 462 | 0 |  | 459 | 463 |  | 463 | 463 | 463 | 457 | 464 | 464 | 464 | 10361454
146 | Bheramara 360 MW | 160 | 160 | 160 | 95 | 95 | 95 | 96 | 95 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 80 | 105 |  | 165 | 230 | 246 | 270 | 270 | 269 | 285 | 3075268
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2
151 | Barapukuria Unit-3 | 121 | 121 | 121 | 121 | 121 | 121 | 123 | 119 | 120 | 115 | 120 | 118 | 119 | 116 | 120 | 120 | 122 | 119 |  | 119 | 120 | 123 | 120 | 114 | 125 | 122 | 2960400
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | 43 | 43 | 34 | 16 | 0 | 0 | [13 empty] | 40 | 51 | 51 | 51 | 51 | 51 | 43 | 409528
| Sirajgonj Unit-1 225MW (Gas) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 91 | 0 | [8 empty] | 2439264
157 | Sirajgonj Unit-1 225MW (Oil)
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 171 | 173 | 169 | 171 | 171 | 168 | 173 | 184 | 180 | 175 | 186 | 175 | 183 | 171 | 180 | 168 | 169 | 169 |  | 183 | 179 | 173 | 178 | 183 | 186 | 187 | 4422827
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | 37 | 37 | 0 | 0 | 0 | 0 | [11 empty] | 10 |  | 38 | 38 | 37 | 37 | 37 | 37 | 37 | 300261
161 | Bogra (GBB) | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 18 | 16 | 14 | 14 | 18 | 20 | 21 | 3 | 10 | 10 | 18 |  | 18 | 18 | 18 | 0 | 14 | 18 | 21 | 408240
162 | Bogra (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 268704
163 | Ullapara (Summit) | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8 | 10 |  | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 247032
164 | Amnura 50MW | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 12 | 40 | 40 | 0 | 25 | 24 | 24 |  | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 878120
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 24 | 24 | 24 | 24 | 24 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 914592
166 | Katakhali Peaking | [19 empty] | 45 | 45 | 47 | 45 | 45 | 44 | 44 | 253120
167 | Santahar Peaking | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 40 | 40 | 40 | 41 | 41 | 41 | 40 |  | 40 | 40 | 40 | 40 | 41 | 41 | 42 | 994270
168 | Rajlanka 52 MW | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 25 | 8 | 8 |  | 8 | 30 | 43 | 43 | 43 | 43 | 43 | 617760
169 | Chapainawabganj-100 MW | 100 | 100 | 100 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 85 | 102 | 59 | 59 | 59 | 59 | 983108
170
171
172 | Rangpur GT | 16 | 16 | 16 | 16 | 0 | 0 | [13 empty] | 15 | 15 | 15 | 17 | 16 | 16 | 16 | 148000
173 | Saidpur GT | 17 | 17 | 17 | 17 | 0 | 0 | [13 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 179000
175
176
177
178 | Western Zone Total | 2389 | 2339 | 2264 | 2056 | 1920 | 1625 | 1549 | 1549 | 1496 | 1471 | 1443 | 1515 | 1545 | 1520 | 1187 | 1353 | 1544 | 1507 | 0 | 2066 | 2332 | 2372 | 2324 | 2299 | 2305 | 2322 | 44525044
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953