## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month: July 2016
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | July 2016 |  | June 2016 |  | July 2015
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 8795 | 01/07/16 | 9036 | 30/06/16 | 8122 | 06/07/15 | 9036 | 30/06/16
|  |  | 1:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 4303 | 06/07/16 | 4767 | 12/06/16 | 3544 | 19/07/15 | - | -
|  |  | 7:00 |  | 6:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 8616 | 28/07/16 | 9036 | 30/06/16 | 8122 | 06/07/15 | 9036 | 30/06/16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 7443 | 28/07/16 | 7889 | 26/06/16 | 6986 | 14/07/15 | 7889 | 26/06/16
|  |  | 21:00 |  | 11:00 |  | 12:00 |  | 11:00
5 | Maximum Evening Peak Demand (MW) Estimated | 8650 | 20/07/16 | 9036 | 30/06/16 | 8122 | 06/07/15 | 9036 | 30/06/16
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 8093.6774 |  | 8503.2 |  | 7192 |  | 8503.2 | June-16
7 | Average Generation (MW) at Day Peak | 6395.3871 |  | 7050.4333 |  | 5558.7419 |  | 7050.43 | June-16
8 | Maximum Power Import from India (MW) | 470 | 03/07/16 | 460 | 09/06/16 | 458 | 23/07/15 | 481 | 01/01/14
|  |  | 21:00 |  | 3:00 |  | 24:00 |  | 14:00
9 | Maximum Power Import from Tripura, India (MW) | 99 | 29/07/16 | 112 | 17/06/16 | - | - | 114 | 03/05/16
|  |  | 18:00 |  | 22:00 |  | - |  | 23:00
10 | Maximum Load Shed (MW) at Evening Peak | 265 | 31/07/16 | 292 | 04/06/16 | - | - | 1459 | 2010-05-04
|  |  | 21:00 |  | 21:00 |  | - |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 8156 | 31/07/16 | 8076 | 04/06/16 | - | - | 3707.5 | 05/04/10
|  |  | 21:00 |  | 21:00 |  | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 126 | 26/07/16 | 106 | 18/06/16 | - | -
|  |  | 21:00 |  | 21:00 |  | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 8260 | 26/07/16 | 8582 | 18/06/16 | - | -
|  |  | 21:00 |  | 21:00 |  | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | 203 | 27/06/16 | - | -
|  |  | - |  | 12:00 |  | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | 7674 | 27/06/16 | - | -
|  |  | - |  | 12:00 |  | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | 203 | 27/06/16 | - | -
|  |  | - |  | 12:00 |  | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | 7674 | 27/06/16 | - | -
|  |  | - |  | 12:00 |  | -
18 | Nos. of Days Load Shed at Evening Peak | 4 |  | 13 |  | - |  | 30 | April 10
19 | Nos. of Days Load Shed at Day Peak | - |  | 1 |  | - |  | 30 | Mar 10
20 | Gross Generation of BPDB (Mkwh) | 2349.6056 |  | 2318.2408 |  | 1971.2106
21 | Station Use of BPDB (Mkwh) | 116.8243 |  | 115.9768 |  | 97.4294
22 | Net Generation of BPDB (Mkwh) | 2232.7813 |  | 2202.264 |  | 1873.7812
23 | Net Generation of IPP & RPCL (Mkwh) | 1165.6143 |  | 1293.5381 |  | 652.8773
24 | Net Generation of REB (Mkwh) | 116.3535 |  | 118.84 |  | 111.0275
24 | Net Generation of Rental Power Plant (MKWh) | 1068.7343 |  | 1241.2901 |  | 1365.771
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 4583.4834 |  | 4855.9333 |  | 4003.4571 |  | 4864.06 | June-16
26 | Energy Generation by Gas (MKWh) | 3350.4514 |  | 3287.1737 |  | 3148.2934 |  | 3350.45 | July-16
27 | Energy Generation by Diesel (MKWh) | 195.8322 |  | 351.5153 |  | 122.8929 |  | 351.5153 | June-16
28 | Energy Generation by Furnace Oil (MKWh) | 925.1981 |  | 1176.4451 |  | 654.4237 |  | 1176.4451 | June-16
29 | Energy Generation by Hydro (MKWh) | 109.96 |  | 52.2675 |  | 81.7377 |  | 168.2059 | Aug-15
30 | Energy Generation by Coal (MKWh) | 118.866 |  | 104.5085 |  | 93.5389 |  | 123.5872 | April-14
31 | Enegry Import from India (HVDC & AC) (MKWh) | 367.3173 |  | 376.2972 |  | 310.7982 |  | 376.3 | June-16
32 | Monthly Load Factor (%) | 77.45% |  | 82.21% |  | 73.01%

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month: July 2016
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 8795 | 28/07/16 | 21:00
Generation Period
| Dhaka | MW | 3050
| Chittagong | MW | 947
| Comilla | MW | 741
| Mymensingh | MW | 441
| Sylhet | MW | 334
a) | Total supply in East zone | MW | 5513
| Khulna | MW | 975
| Barisal | MW | 183
| Rajshahi | MW | 884
| Rangpur | MW | 389
b) | Total supply in West zone | MW | 2431
c) | Total supply in both zone ( a+b) | MW | 7944
Ref: | PGCB/IMD/4.01/2016/50 | Date: 16/08/2016
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month: July 2016
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 860 | 07/07/16 | 5:00
| b) Ishurdi end | MW | - | - | -
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | - | - | -
| b) Ishurdi end | MW | 380 | 07/07/16 | 5:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 3.7785 | 08/07/16
| b) Ishurdi end | MKWH | 0.40145 | 04/07/16
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.38941 | 04/07/16
| b) Ishurdi end | MKWH | 3.7135 | 10/07/16
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 91.8619
| b) Ishurdi end | MKWH | 0.40145
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.38941
| b) Ishurdi end | MKWH | 89.3978
23 | Transmission loss of EWI/ NO-1 | % | 2.6824
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 500 | 07/07/16 | 5:00
| b)Serajganj end | MW | - | - | -
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | - | - | -
| b)Sirajganj end | MW | 480 | 07/07/16 | 1:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 9.068 | 07/07/16
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 8.85 | 07/07/16
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 221.622
| b)Sirajganj end | MKWH | -
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | -
| b)Sirajganj end | MKWH | 218.276
30 | Transmission loss of EWI /NO-2 | % | 1.5098
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishurdi, Pabna.
* The energy metre of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2016
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Jamalpur | 132/33 kV Trnasformer -T2 | 2016-07-04 13:20 | 2016-07-04 15:22 | 2:02 | E/O | Due to red hot maintenance work | 0 | 0 | No interruption
Agargaon | 132/33 kV Trnasformer -T2 | 2016-07-04 16:03 | 2016-07-05 12:06 | 20:03 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Sherpur | 132/33 kV Trnasformer -T1 | 2016-07-06 07:25 | 2016-07-06 07:36 | 0:11 | T | Tripped showing differential relay | 0 | 0 | No interruption
Mymensingh | 132/33 kV Trnasformer -T3 | 2016-07-06 15:48 | 2016-07-06 16:47 | 0:59 | T | Tripped showing PRD relay | 30 | 29.5 | Power interruption
Aminbazar | 230/132 kV Trnasformer- T03 | 2016-07-09 09:04 | 2016-07-09 12:56 | 3:52 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 230/132 kV Trnasformer -T02 | 2016-07-09 15:35 | 2016-07-09 16:30 | 0:55 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Trnasformer -T1 | 2016-07-19 11:50 | 2016-07-19 12:20 | 0:30 | E/O | Due to red hot maintenance | 4 | 2 | Power interruption
Tongi | 230/132 kV Trnasformer -T01 | 2016-07-23 16:50 | 2016-07-23 17:57 | 1:07 | E/O | Due to OLTC problem | 0 | 0 | No interruption
Jamalpur | 132/33 kV Trnasformer -T1 | 2016-07-26 02:55 | 2016-07-26 10:13 | 7:18 | T | Tripped showing dist.relay | 0 | 0 | No interruption
Mymensingh | 132/33 kV Trnasformer -T1 | 2016-07-27 09:45 | 2016-07-27 10:41 | 0:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 37:53 |  | Unserved Energy: |  | 31.5
Dhaka (South) Grid Circle :
Haripur | 230/132 kV Trnasformer -T01 | 2016-07-01 15:32 | 2016-07-01 16:55 | 1:23 | T | Tripped showing Oil temperature high | 0 | 0 | No interruption
Shyampur | 132/33 kV Trnasformer GT3 | 2016-07-04 09:18 | 2016-07-04 13:55 | 4:37 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Trnasformer- T2 | 2016-07-13 11:32 | 2016-07-13 17:58 | 6:26 | T | Tripped showing E/F realy | 0 | 0 | No interruption
| 230/132 kV Trnasformer -T02 | 2016-07-17 10:24 | 2016-07-17 18:25 | 8:01 | T | Tripped showing differential relay | 0 | 0 | No interruption
Munshiganj | 132/33 kV Trnasformer- T2 | 2016-07-23 16:55 | 2016-07-23 23:12 | 6:17 | T | Tripped showing differential relay | 56 | 351.8667 | Power interruption
Maniknagar | 132/33 kV Trnasformer -T1 | 2016-07-29 23:12 | 2016-07-30 06:39 | 7:27 | T | Tripped showing O/C & E/F realy | 0 | 0 | No interruption
Haripur | 230/132 kV Trnasformer -T01 | 2016-07-31 03:48 | 2016-07-31 07:55 | 4:07 | T | Due to kill the fire of TR2 Transformer | 0 | 0 | No interruption
|  |  | Total : | 38:18 |  | Unserved Energy: |  | 351.8667
Chittagong Grid Circle :
Hathazari | 230/132 kV Trnasformer -MT2 | 2016-07-09 07:46 | 2016-07-09 16:38 | 8:52 | T | Tripped showing PRD relay | 0 | 0 | No interruption
|  |  | Total : | 8:52 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Kulaura | 132/33 kV Trnasformer -T2 | 2016-07-09 15:01 | 2016-07-09 16:27 | 1:26 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Comiila (S) | 132/33 kV Trnasformer -T3 | 2016-07-08 15:04 | 2016-07-09 15:01 | 23:57 | T | Tripped showing PRD relay | 0 | 0 | No interruption
| 132/33 kV Trnasformer -T3 | 2016-07-09 20:46 | 2016-07-10 13:29 | 16:43 | T |  | 0 | 0 | No interruption
Feni | 132/33 kV Trnasformer -T1 | 2016-07-16 04:44 | 2016-07-16 05:03 | 0:19 | T | Tripped showing inst. E/F relay | 0 | 0 | No interruption
| 132/33 kV Trnasformer- T2 | 2016-07-16 04:44 | 2016-07-16 05:02 | 0:18 | T |  | 0 | 0 | No interruption
Chhatak | 132/33 kV Trnasformer -T1 | 2016-07-28 15:33 | 2016-07-28 16:01 | 0:28 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 43:11 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Madaripur | 132/33 kV Trnasformer -T1 | 2016-07-08 08:53 | 2016-07-08 10:04 | 1:11 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| 132/33 kV Trnasformer -T3 | 2016-07-13 12:52 | 2016-07-13 14:31 | 1:39 | T | Tripped showing O/C & E/F relay | 15 | 24.75 | Power interruption
Barisal | 132/33 kV Trnasformers -T1 | 2016-07-21 11:42 | 2016-07-21 12:14 | 0:32 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Trnasformers -T2 | 2016-07-21 11:42 | 2016-07-21 18:40 | 6:58 | T |  | 65 | 34.6667 | Power interruption
Bagerhat | 132/33 kV Trnasformers -T1 | 2016-07-26 07:50 | 2016-07-26 09:11 | 1:21 | E/O | Due to red hot maintenance | 30 | 40.5 | Power interruption
Madaripur | 132/33 kV Trnasformers -T1 & T2 | 2016-07-29 09:47 | 2016-07-29 11:29 | 1:42 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 13:23 |  | Unserved Energy: |  | 99.9167
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: July 2016
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | 132/33 kV Trnasformer -T1 | 2016-07-06 10:13 | 2016-07-06 11:11 | 0:58 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bottail | 132/33 kV Trnasformers -T1 & T2 | 2016-07-23 13:30 | 2016-07-23 13:33 | 0:03 | T | Tripped showing E/F relay | 68 | 3.4 | Power interruption
|  |  | Total : | 1:01 |  | Unserved Energy: |  | 3.4
Bogra Grid Circle:
Naogaon | 132/33 kV Trnasformer -T1 | 2016-07-03 14:35 | 2016-07-03 16:13 | 1:38 | T | Tripped showing E/F relay | 25 | 40.8333 | Power interruption
| 132/33 kV Trnasformer -T3 | 2016-07-04 12:27 | 2016-07-04 12:37 | 0:10 | T | Tripped showing O/C & E/F relay | 0 | 0 | No interruption
Bogra | 132/33 kV Trnasformer -T2 | 2016-07-12 10:24 | 2016-07-12 14:16 | 3:52 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Naogaon | 132/33 kV Trnasformer -T3 | 2016-07-25 06:55 | 2016-07-25 07:55 | 1:00 | T | Tripped showing E/F relay | 15 | 15 | Power interruption
Saidpur | 132/33 kV Trnasformer -T2 | 2016-07-31 06:30 | 2016-07-31 06:58 | 0:28 | E/O | Due to red hot maintenance | 7 | 3.2667 | Power interruption
|  |  | Total : | 7:08 |  | Unserved Energy: |  | 59.1
Others :
Kamrangirchar | 132/33 kV Trnasformer T-1 | 2016-07-08 09:20 | 2016-07-08 12:10 | 2:50 | T | Tripped showing PRD relay | 0 | 0 | No interruption
Ghorasal | 132/33 kV Trnasformer -T1 | 2016-07-14 09:42 | 2016-07-14 10:40 | 0:58 | T | Tripped showing O/C & E/F realy | 35 | 33.8333 | Power interruption
Ashuganj | 230/132 kV Trnasformer -T1 | 2016-07-30 10:05 | 2016-07-30 12:42 | 2:37 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 6:25 |  | Unserved Energy: |  | 33.8333
Total outage period of Sub-station Equipment : |  |  |  | 156:11 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2016
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
| Tongi-Bashundhara 132 kV line-1 | 2016-07-02 09:32 | 2016-07-02 09:48 | 0:16 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 KV line-2 | 2016-07-13 14:52 | 2016-07-13 14:58 | 0:06 | T | Tripped showing E/F relay | 0 | 0 | No interruption
| Tongi-Kabirpur 132 KV line-1 | 2016-07-19 11:28 | 2016-07-19 11:35 | 0:07 | T | Tripped showing dist. relay | 100 | 11.6667 | Power interruption
| Tongi-Kabirpur 132 KV line-2 | 2016-07-19 11:28 | 2016-07-19 11:36 | 0:08 | T
Aminbazar | Aminbazar-Savar 132 kV line-2 | 2016-07-23 15:56 | 2016-07-23 16:16 | 0:20 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Basundhara | Basundhara -Tongi 132 kV line-1 | 2016-07-27 12:17 | 2016-07-27 12:37 | 0:20 | T | Tripped showing dist.(B-phase)relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 KV line-2 | 2016-07-27 13:12 | 2016-07-27 13:21 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 1:26 |  | Unserved Energy: |  | 11.6667
Dhaka (South) Grid Circle :
Rampura | Rampura-Madertek 132 kV line-1 & 2 | 2016-07-13 06:20 | 2016-07-13 07:28 | 1:08 | T | Tripped showing E/F & O/C relay | 30 | 34 | Power interruption
Haripur | Haripur-Rahim steel 132 kV line | 2016-07-16 14:45 | 2016-07-18 13:17 | 46:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Haripur-Rampura 230 kV line-2 | 2016-07-16 14:45 | 2016-07-16 14:53 | 0:08 | T | Tripped showing differential & E/F relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV line-1 | 2016-07-18 00:12 | 2016-07-18 00:30 | 0:18 | T | Tripped showing PD-3,DT dist. PD3,& DT signal | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-2 | 2016-07-20 05:34 | 2016-07-20 06:09 | 0:35 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Moghbazar | Moghbazar-Rampura 132 kV line-1 | 2016-07-22 05:24 | 2016-07-22 16:40 | 11:16 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Rampura-Basundhara 132 kV line-1 | 2016-07-23 12:00 | 2016-07-23 12:24 | 0:24 | T | Tripped showing main protcetion relay | 0 | 0 | No interruption
Rampura | Rampura-Basundhara 132 kV line-1 | 2016-07-31 19:42 | 2016-07-31 19:58 | 0:16 | T | Tripped showing high impedance relay | 90 | 24 | Power interruption
| Rampura-Basundhara 132 kV line-2 | 2016-07-31 19:42 | 2016-07-31 23:18 | 3:36 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 64:13 |  | Unserved Energy: |  | 58
Chittagong Grid Circle :
Madunaghat | Madunaghat-Kaptai 132 kV line | 2016-07-04 12:33 | 2016-07-04 15:11 | 2:38 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-1 | 2016-07-17 09:35 | 2016-07-25 22:33 | 204:58 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
| Sikalbaha-Gaganagar 132 kV line | 2016-07-18 00:18 | 2016-07-18 09:30 | 9:12 | T | Tripped showing differential relay | 0 | 0 | No interruption
Madunaghat | Madunaghat-Khulshi 132 kV line-2 | 2016-07-19 15:53 | 2016-07-19 17:15 | 1:22 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shyampur 132 kV line-1 | 2016-07-25 10:37 | 2016-07-25 12:33 | 1:56 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madunaghat | Madunaghat-Kaptai 132 kV line-1 | 2016-07-28 09:45 | 2016-07-28 10:39 | 0:54 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2016-07-30 10:58 | 2016-07-30 17:21 | 6:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Cox's Bazar | Cox's Bazar-Dohazari 132 kV line-1 | 2016-07-31 13:02 | 2016-07-31 13:16 | 0:14 | T | Tripped showing E/F relay | 21 | 4.9 | Power interruption
| Cox's Bazar-Dohazari 132 kV line-2 | 2016-07-31 13:02 | 2016-07-31 14:13 | 1:11 | T |  | 0 | 0 | No interruption
|  |  | Total : | 228:48 |  | Unserved Energy: |  | 4.9
Comilla Grid Circle :
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-1 & 2 | 2016-07-08 19:50 | 2016-07-08 20:33 | 0:43 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tripura | Tripura-Comilla (S) 132 kV line-1 & 2 | 2016-07-09 13:55 | 2016-07-09 14:43 | 0:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-1 | 2016-07-14 10:54 | 2016-07-14 11:41 | 0:47 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2016-07-16 05:01 | 2016-07-16 05:09 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Ashuganj-Ghorasal 230 kV line-2 | 2016-07-17 16:48 | 2016-07-17 17:21 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-Sreemongal 132 kV line-2 | 2016-07-31 09:52 | 2016-07-31 09:58 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 3:05 |  | Unserved Energy: |  | 0
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division, LDC, Dhaka.
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: July 2016
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Khulna Grid Circle :
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2016-07-16 13:17 | 2016-07-17 14:36 | 25:19 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barisal (S) | Barisal (S)-Patuakhali 132 kV line | 2016-07-17 18:38 | 2016-07-17 19:18 | 0:40 | T | Tripped showing inst.E/F relay | 22 | 14.6667 | Power interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2016-07-24 13:01 | 2016-07-24 13:09 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2016-07-27 09:03 | 2016-07-27 09:17 | 0:14 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Khulna (S) | Khulna (S)-Satkhira 132 kV line | 2016-07-30 21:07 | 2016-07-30 21:40 | 0:33 | T | Tripped showing dist. & E/F relay | 65 | 35.75 | Power interruption
Khulna (C) | Khulna ( C )-KPCL 132 kV line | 2016-07-31 08:08 | 2016-07-31 16:38 | 8:30 | E/O | Due to torn loop at KPCL-2 | 0 | 0 | No interruption
|  |  | Total : | 35:24 |  | Unserved Energy: |  | 50.4167
HVDC Grid Circle :
Bheramara | Bheramara-Bahrampur 400 kV line-2 | 2016-07-04 19:44 | 2016-07-04 20:07 | 0:23 | T | Tripped showing signal-Direct trip signal | 0 | 0 | No interruption
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2016-07-14 11:40 | 2016-07-14 12:10 | 0:30 | T | Tripped showing DT,PD3 & PTAW signal | 0 | 0 | No interruption
|  |  | Total : | 0:53 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
| Rajshahi-Natore 132 kVline-2 | 2016-07-09 20:30 | 2016-07-09 20:44 | 0:14 | T | Tripped showing dist. relay | 0 | 0
Rajshahi | Rajshahi-Natore 132 kVline-2 | 2016-07-09 20:44 | 2016-07-09 21:03 | 0:19 | T |  | 0 | 0
| Rajshahi-Natore 132 kVline-1 | 2016-07-09 20:30 | 2016-07-09 20:58 | 0:28 | T | Tripped showing O/C. relay | 180 | 84 | Power interruption
| Rajshahi-Natore 132 kVline-1 | 2016-07-15 20:35 | 2016-07-15 22:55 | 2:20 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Palashbari | Palashbari-Rangpur 132 kV line-2 | 2016-07-18 14:48 | 2016-07-18 17:20 | 2:32 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Bogra | Bogra -Palashabari 132 kV line-2 | 2016-07-31 14:14 | 2016-07-31 14:26 | 0:12 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:05 |  | Unserved Energy: |  | 84
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 339:54 | Hours
T = Tripping
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/1 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: July 2016
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Meghnaghat | 230 kV Bus-1 | 2016-07-03 11:20 | 2016-07-03 18:02 | 6:42 | S/O | Due to isolator maintenance | 0 | 0 | No interruption
Hasnabad | 132/33 kV Transformer T1 | 2016-07-20 15:40 | 2016-07-20 17:33 | 1:53 | S/O | Due to grounding maintenance work | 0 | 0 | No interruption
Munshiganj | 132/33 kV Transformer T1 | 2016-07-29 11:47 | 2016-07-29 15:23 | 3:36 | S/O | Due to cable connection | 0 | 0 | No interruption
|  |  | Total : | 12:11 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
Sikalbaha | 132/33 kV Trnasformer GT-3 | 2016-07-19 11:30 | 2016-07-19 13:03 | 1:33 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer T2 | 2016-07-24 16:42 | 2016-07-24 18:32 | 1:50 | S/O | Due to cable fault | 0 | 0 | No interruption
|  |  | Total : | 3:23 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Fenchuganj | 132/33 kV Trnasformer T-1 | 2016-07-19 16:45 | 2016-07-19 21:05 | 4:20 | S/O | Due to installation of new transformer | 0 | 0 | No interruption
| 132/33 kV Transformer T2 | 2016-07-20 08:46 | 2016-07-20 15:53 | 7:07 | S/O | Due to installation work | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer T1 | 2016-07-28 22:08 | 2016-07-30 13:30 | 39:22 | S/O | Due to development work | 0 | 0 | No interruption
|  |  | Total | 50:49 |  | Unserved Energy : |  | 0
Khulna Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy : |  | 0
HVDC Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogra Grid Circle:
Ishurdi | 132/33 kV Trnasformer T-1 | 2016-07-18 11:45 | 2016-07-18 13:13 | 1:28 | S/O | Due to attend 132 kV isolator B-phase | 0 | 0 | No interruption
Natore | 132 kV main bus | 2016-07-22 06:45 | 2016-07-22 09:20 | 2:35 | S/O | Due to hook up at new Transformer-T4 | 51 | 131.75 | Power interruption
|  |  | Total | 4:03 |  | Unserved Energy : |  | 131.75
Others :
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule
maintenance: |  |  |  | 70:26 | Hours
S/O=Schedule Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/1 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: July 2016
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-07-01 06:02 | 2016-07-01 10:34 | 4:32 | S/O | Due to painting work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Hasnabad 230 kV line-1 | 2016-07-03 11:38 | 2016-07-03 19:36 | 7:58 | S/O | Due to isolator finger aligment work | 0 | 0 | No interruption
| Hasnabad-Shyampur 132 kV line | 2016-07-19 08:10 | 2016-07-19 16:48 | 8:38 | S/O | Due to loop maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Shyampur 132 kV line | 2016-07-20 08:05 | 2016-07-20 16:47 | 8:42 | S/O | Due to changing work | 0 | 0 | No interruption
| Hasnabad-Shitalakyha 132 kV line | 2016-07-27 07:19 | 2016-07-27 17:01 | 9:42 | S/O | Due to changing work | 0 | 0 | No interruption
| Hasnabad-Shitalakyha 132 kV line | 2016-07-28 07:24 | 2016-07-28 16:54 | 9:30 | S/O | Due to development work | 0 | 0 | No interruption
Haripur | Haripur S/S-Haripur P/S 132 kV line | 2016-07-31 03:58 | 2016-07-31 03:58 | 0:00 | S/O | Due to development work | 0 | 0 | No interruption
|  |  | Total : | 49:02 |  | Unserved Energy: |  | 0
Chittagong Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Comilla Grid Circle :
Chandpur | Chandpur-Chowmuhani 132 kV line-1 | 2016-07-23 10:02 | 2016-07-23 13:52 | 3:50 | S/O | Due to loop maintenance | 0 | 0 | No interruption
| Chandpur-Chowmuhani 132 kV line-2 | 2016-07-23 10:02 | 2016-07-23 11:52 | 1:50 | S/O
Feni | Feni-Hathazari 132 kV line-1 | 2016-07-27 12:36 | 2016-07-27 22:52 | 10:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ashuganj-Kishoreganj 132 kV line-2 | 2016-07-29 06:30 | 2016-07-29 16:28 | 9:58 | S/O | Due to maintenance work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghoashsal 132 kV line-1 | 2016-07-29 07:04 | 2016-07-29 16:20 | 9:16 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ashuganj-Ghoashsal 132 kV line-2 | 2016-07-29 07:04 | 2016-07-29 16:33 | 9:29 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Ashuganj-Sirajganj 230 kV line-2 | 2016-07-30 10:07 | 2016-07-30 21:40 | 11:33 | S/O | Due to loop maintenance | 0 | 0 | No interruption
|  |  | Total : | 56:12 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Jessore | Jessore-Jhenaidah 132 kV line-2 | 2016-07-16 08:50 | 2016-07-16 10:47 | 1:57 | S/O | Due to armoring at tower no-322 | 0 | 0 | No interruption
|  |  | Total : | 1:57 |  | Unserved Energy: |  | 0
Bogra Grid Circle :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Transmissiom Lines due to schedule
maintenance: |  |  |  | 107:11 | Hours
S/O=Schedule Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month: July 2016
| Area | Previous Month (June 2016) |  |  |  | Current Month (July 2016)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 14 | 8 | 8 | 30 | 11 | 6 | - | 17
2 | Dhaka (South) Grid Circle. | 16 | 4 | 8 | 28 | 13 | 3 | 10 | 26
3 | Chittagong Grid Circle. | 9 | 2 | 3 | 14 | 5 | 5 | 2 | 12
4 | Comilla Grid Circle. | 8 | 5 | 9 | 22 | 12 | - | 10 | 22
5 | Khulna Grid Circle. | 23 | 1 | 7 | 31 | 8 | 4 | - | 12
6 | HVDC Grid Circle | 8 | 3 | 2 | 13 | 3 | 1 | 1 | 5
7 | Bogra Grid Circle. | 6 | 6 | 2 | 14 | 7 | 4 | 2 | 13
8 | Others . | 1 | 2 | - | 3 | 2 | 1 | - | 3
9 | Total | 85 | 31 | 39 | 155 | 61 | 24 | 25 | 110
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month: July 2016
| Area | Previous Month (June 2016) |  |  |  | Current Month (July 2016)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) grid circle. | 499.53 | 158 | 604.92 | 1262.45 | 41.1667 | 2 | - | 43.1667
2 | Dhaka ( South) grid circle | 604.58 | - | 491.33 | 1095.91 | 409.8667 | - | - | 409.8667
3 | Chittagong grid circle. | 274.1 | 67.75 | 40 | 381.85 | 4.9 | - | - | 4.9
4 | Comilla grid circle. | 22.35 | 35.33 | - | 57.68 | - | - | - | 0
5 | Khulna grid circle. | 35.2 | - | 2.5 | 37.7 | 109.8333 | 40.5 | - | 150.3333
6 | HVDC grid circle | 13 | - | - | 13 | 3.4 | - | - | 3.4
7 | Bogra grid circle. | 16 | 44 | - | 60 | 139.8333 | 3.2667 | 131.75 | 274.85
8 | Others | - | 90.33 | - | 90.33 | 33.8333 | - | - | 33.8333
9 | Total | 1464.76 | 395.41 | 1138.75 | 2998.92 | 742.8333 | 45.7667 | 131.75 | 920.35
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month: July 2016
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 5308 | 3 | - | 3 | 1 | 2 | - | 65.3333
2 | Dhaka (South) | 5031.6 | 1 | - | 1 | - | - | 1 | 351.8667
3 | Chittagong | 2042 | - | - | 0 | - | - | - | -
4 | Khulna | 2434 | 3 | - | 3 | - | - | 3 | 99.9167
5 | Bheramara (HVDC) | 2423.3 | 1 | - | 1 | 1 | - | - | 3.4
6 | Bogra | 3145.6 | 3 | 1 | 4 | 1 | 1 | 2 | 190.85
7 | Comilla | 2981 | - | - | 0 | - | - | - | -
| Total | 23365.5 | [6 empty] | 711.3667
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.89%
2 | Dhaka (South) | 99.86%
3 | Chittagong | 99.91%
4 | Khulna | 99.96%
5 | Bheramara (HVDC) | 100% | [6 empty] | Executive Engineer
6 | Bogra | 99.98% | [6 empty] | Information Management Division
7 | Comilla | 99.92% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month: July 2016
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 1666.28 | 54+15(Partial) | 1 | - | 1 | 1 | - | - | 11.6667
2 | Dhaka (South) | 965.69 |  | 2 | - | 2 | 1 | - | 1 | 58
3 | Chittagong | 917 | 20+9(Partial) | 1 | - | 1 | 1 | - | - | 4.9
4 | Khulna | 1238.4 | 21 | 2 | - | 2 | - | 2 | - | 50.4167
5 | Bheramara (HVDC) | 598.7 |  | - | - | 0 | - | - | - | 0
6 | Bogra | 1803.3 | 38 | 1 | - | 1 | 1 | - | - | 84
7 | Comilla | 1648.16 | 17 | - | - | 0 | - | - | - | 0
| Total | 8837.53 | 150+24(Partial) | [6 empty] | 208.9833
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 100%
2 | Dhaka (South) | 99.96%
3 | Chittagong | 99.61%
4 | Khulna | 99.88%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogra | 99.98% | [7 empty] | Information Management Division
7 | Comilla | 99.98% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month: July 2016
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2016-07-01 | 8 | 0/50 | - | - | - | - | - | - | - | - | - | -
Note:-If U/F operates due to tripping of a generator is accounted in the category "Trouble in Generation System ".
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the System
Month: July 2016
| Total Nos.of | Total | Unserved | Total
Sub-station | Interruption | Duration of | Load | Unserved | Remarks
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 1 | 0:59 | 30 | 29.5 | Due to tripping of 132/33 kV Transformer-T3
Kishoreganj | 1 | 0:30 | 4 | 2 | Due to emergency outage of 132/33 kV Transformer-T1
Tongi | 1 | 0:07 | 100 | 11.6667 | Due to tripping of Tongi-Kabirpur 132 kV line-1
Munshiganj | 1 | 6:17 | 56 | 351.8667 | Due to tripping of 132/33 kV Transformer-T2
Rampura | 2 | 1:08 | 30 | 34 | Due to tripping of Rampura-Madartek 132 kV line-1&2
|  | 0:16 | 90 | 24 | Due to tripping of Rampura-Bashundhara 132 kV line-1
Cox's Bazar | 1 | 0:14 | 21 | 4.9 | Due to tripping of Cox's Bazar-Dohazari 132 kV line-1
Madaripur | 1 | 1:39 | 15 | 24.75 | Due to tripping of 132/33 kV Transformer-T3
Barisal | 1 | 0:32 | 65 | 34.6667 | Due to tripping of 132/33 kV Transformer-T2
Barisal (S) | 1 | 0:40 | 22 | 14.6667 | Due to tripping of Barisal (S)-Patuakhali 132 kV line
Bagerhat | 1 | 1:21 | 30 | 40.5 | Due to emergency outage of 132/33 kV Transformer-T1
Khulna (S) | 1 | 0:33 | 65 | 35.75 | Due to tripping of Khulna (S)-Satkhira 132 kV line
Bottail | 1 | 0:03 | 68 | 3.4 | Due to tripping of 132/33 kV Transformer-T1 &T2
Naogaon | 2 | 1:38 | 25 | 40.8333 | Due to tripping of 132/33 kV Transformer-T1 &T2
|  | 1:00 | 15 | 15 | Due to tripping of 132/33 kV Transformer-T3
Saidpur | 1 | 0:28 | 7 | 3.2667 | Due to emergency outage of 132/33 kV Transformer-T2
Natore | 1 | 2:35 | 51 | 131.75 | Due to schedule outage of 132 kV main bus
Rajshahi | 1 | 0:28 | 180 | 84 | Due to tripping of Rajshahi-Natore 132 kV line-1
Ghorasal | 1 | 0:58 | 35 | 33.8333 | Due to tripping of 132/33 kV Transformer-T1
| Total unserved energy : |  |  | 920.35 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July 2016
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 122 | 27 | 2016-07-01 | 15:00
2 | Munsiganj | 108 | 15 | 2016-07-01 | 21:00
3 | Megnaghat | 58 | 29 | 2016-07-01 | 21:00
4 | Shyampur | 158 | 26 | 2016-07-01 | 13:00
5 | Bhulta | 138 | 1 | 2016-07-01 | 01:00
6 | Madanganj | 50 | 20 | 2016-07-01 | 20:00
7 | Shitalakhya | 95 | 27 | 2016-07-01 | 19:00
8 | Rahim steel | 12 | 2 | 2016-07-01 | 9:00
9 | Matuail | 68 | 27 | 2016-07-01 | 13:00
10 | Ghorasal | 96 | 30 | 2016-07-01 | 20:00
11 | Narsingdi | 85 | 12 | 2016-07-01 | 22:00
12 | Haripur (SBU) | 78 | 30 | 2016-07-01 | 12:00
13 | Ullon | 89 | 2 | 2016-07-01 | 20:00
14 | Hasnabad | 137 | 1 | 2016-07-01 | 1:00
15 | Magbazar | 130 | 27 | 2016-07-01 | 12:00
16 | Maniknagar | 82 | 1 | 2016-07-01 | 1:00
17 | Bangabhaban | 40 | 12 | 2016-07-01 | 11:00
18 | Narinda | 82 | 1 | 2016-07-01 | 22:00
19 | Dhanmondi | 158 | 25 | 2016-07-01 | 15:00
20 | Lalbag | 79 | 28 | 2016-07-01 | 14:00
21 | Madartek | 61 | 30 | 2016-07-01 | 21:00
22 | Mirpur | 97 | 27 | 2016-07-01 | 19:00
23 | Kalyanpur | 111 | 1 | 2016-07-01 | 23:00
24 | Gulshan | 135 | 14 | 2016-07-01 | 15:00
25 | Uttara | 98 | 31 | 2016-07-01 | 19:00
26 | Kamrangirchar | 80 | 23 | 2016-07-01 | 13:00
27 | Savar | 104 | 18 | 2016-07-01 | 19:30
28 | Bhasantec | 108 | 1 | 2016-07-01 | 22:00
29 | Agargaon | 52 | 31 | 2016-07-01 | 13:00
30 | Satmosjid | 68 | 31 | 2016-07-01 | 19:00
31 | Tongi | 109 | 17 | 2016-07-01 | 11:00
32 | Kabirpur | 199 | 13 | 2016-07-01 | 20:00
33 | Basundhara | 120 | 31 | 2016-07-01 | 14:00
34 | Manikganj | 84 | 21 | 2016-07-01 | 20:00
35 | Joydevpur | 257 | 29 | 2016-07-01 | 1:00
36 | New Tongi | 117 | 21 | 2016-07-01 | 15:00
37 | Tangail | 139 | 4 | 2016-07-01 | 21:00
38 | Mymensing | 180 | 15 | 2016-07-01 | 21:00
39 | Kishorganj | 70 | 4 | 2016-07-01 | 20:00
40 | Netrokona | 61 | 6 | 2016-07-01 | 19:30
41 | Jamalpur | 84 | 8 | 2016-07-01 | 24:00
42 | Sherpur | 55 | 29 | 2016-07-01 | 19:30
43 | Srimongal | 34 | 19 | 2016-07-01 | 19:00
44 | Shahjibazar | 68 | 15 | 2016-07-01 | 21:00
45 | Fenchuganj | 40 | 28 | 2016-07-01 | 19:30
46 | Khulawara | 39 | 14 | 2016-07-01 | 21:00
47 | Sylhet | 150 | 31 | 2016-07-01 | 20:00
48 | Chatak | 53 | 29 | 2016-07-01 | 20:00
49 | Comilla (S) | 100 | 27 | 2016-07-01 | 20:00
50 | Comilla(N) | 142 | 2 | 2016-07-01 | 22:00
51 | Chandpur | 90 | 27 | 2016-07-01 | 21:00
52 | Feni | 103 | 1 | 2016-07-01 | 20:00
53 | Chowmuhani | 168 | 1 | 2016-07-01 | 19:00
54 | Ashuganj | 62 | 14 | 2016-07-01 | 22:00
55 | Daudkandi | 74 | 3 | 2016-07-01 | 20:00
56 | B.Baria | 87 | 1 | 2016-07-01 | 21:00
57 | Madanhat | 59.2 | 30 | 2016-07-01 | 13:00
58 | Hathazari | 98 | 30 | 2016-07-01 | 20:00
59 | Khulshi | 176 | 1 | 2016-07-01 | 01:00
60 | Halishahar | 129 | 20 | 2016-07-01 | 15:00
61 | Baraulia | 140 | 24 | 2016-07-01 | 03:00
62 | Sikalbaha | 38 | 30 | 2016-07-01 | 20:00
Page: 2/2 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: July 2016
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
63 | Dohazari | 88 | 16 | 2016-07-01 | 22:00
64 | Cox'sbazar | 58 | 13 | 2016-07-01 | 19:30
65 | Chandraghona | 30 | 27 | 2016-07-01 | 19:00
66 | Kaptai | 4.1 | 30 | 2016-07-01 | 19:30
67 | A. Khaer Stl. | 20 | 17 | 2016-07-01 | 14:00
68 | Bakulia | 109 | 31 | 2016-07-01 | 19:00
69 | Julda | 20 | 28 | 2016-07-01 | 24:00
70 | TK chemical | 14.4 | 5 | 2016-07-01 | 2:00
71 | Modern Steel | 18 | 14 | 2016-07-01 | 14:00
72 | Shahmirpur | 26 | 28 | 2016-07-01 | 14:00
73 | Abul Khair 230 | 190 | 11 | 2016-07-01 | 17:00
74 | BSRM | 105 | 23 | 2016-07-01 | 16:00
75 | Goalpara | 34 | 19 | 2016-07-01 | 20:00
76 | Central s/s | 90 | 28 | 2016-07-01 | 22:00
77 | Noapara | 75 | 9 | 2016-07-01 | 19:30
78 | Jessore | 126 | 14 | 2016-07-01 | 22:00
79 | Jhenida | 74 | 11 | 2016-07-01 | 19:30
80 | Bottail | 96 | 17 | 2016-07-01 | 20:00
81 | G.K Project | 44 | 1 | 2016-07-01 | 21:00
82 | Faridpur | 124 | 2 | 2016-07-01 | 20:00
83 | Madaripur | 106 | 12 | 2016-07-01 | 21:00
84 | Gopalganj | 53 | 17 | 2016-07-01 | 21:00
85 | Bagerhat | 72 | 15 | 2016-07-01 | 19:30
86 | Mongla | 32 | 2 | 2016-07-01 | 12:00
87 | Satkhira | 74 | 18 | 2016-07-01 | 20:00
88 | Gallamari | 48 | 31 | 2016-07-01 | 13:00
89 | Magura | 37 | 12 | 2016-07-01 | 19:30
90 | Chuadanga | 51 | 2 | 2016-07-01 | 21:00
91 | Barisal | 106 | 24 | 2016-07-01 | 21:00
92 | Patuakhali | 41.5 | 10 | 2016-07-01 | 21:00
93 | Bhandaria | 38 | 7 | 2016-07-01 | 21:00
94 | Ishurdi | 46 | 1 | 2016-07-01 | 21:00
95 | Natore | 88 | 28 | 2016-07-01 | 21:00
96 | Bogra | 211 | 31 | 2016-07-01 | 20:00
97 | Noagaon | 99 | 14 | 2016-07-01 | 21:00
98 | Rajshahi | 123 | 12 | 2016-07-01 | 21:00
99 | C.Nawabganj | 60 | 15 | 2016-07-01 | 20:00
100 | Amnura | 34 | 12 | 2016-07-01 | 21:00
101 | Pabna | 91 | 19 | 2016-07-01 | 20:00
102 | Shahjadpur | 80 | 3 | 2016-07-01 | 20:00
103 | Serajganj | 70 | 27 | 2016-07-01 | 20:00
104 | Niyamatpur | 49 | 13 | 2016-07-01 | 21:00
105 | Joypurhat | 32 | 22 | 2016-07-01 | 21:00
106 | Rangpur | 101 | 11 | 2016-07-01 | 21:00
107 | Lalmonirhat | 73 | 14 | 2016-07-01 | 20:00
108 | Saidpur | 84 | 23 | 2016-07-01 | 19:30
109 | Purbasadipur | 71 | 22 | 2016-07-01 | 20:00
110 | Thakurgaon | 60 | 1 | 2016-07-01 | 21:00
111 | Palashbari | 81 | 11 | 2016-07-01 | 21:00
112 | Barapukuria | 41 | 24 | 2016-07-01 | 21:00
113 | Panchagar | 27 | 21 | 2016-07-01 | 19:30
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month: July 2016
Area | MW | Date | Hour | Remarks
Dhaka | 3178 | 01.07.16 | 1:00
Chittagong | 1055 | 01.07.16 | 1:00
Khulna | 1002 | 18.07.16 | 19:30
Rajshahi | 929 | 01.07.16 | 22:00
Comilla | 787 | 01.07.16 | 3:00
Mymensingh | 536 | 06.07.16 | 19:30
Sylhet | 361 | 01.07.16 | 21:00
Barisal | 190 | 28.07.16 | 23:00
Rangpur | 504 | 11.07.16 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July 2016
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 230 | 5 | 2016-07-01 | 10:00 | 210 | 28 | 2016-07-01 | 18:30
2 | Ishurdi | 230 | 236 | 12 | 2016-07-01 | 10:00 | 220 | 4 | 2016-07-01 | 23:00
3 | Ashuganj | 230 | 239 | 7 | 2016-07-01 | 6:00 | 224 | 31 | 2016-07-01 | 13:00
4 | Serajganj | 230 | 226 | 6 | 2016-07-01 | 9:00 | 212 | 27 | 2016-07-01 | 21:00
5 | Baghabari | 230 | 226 | 9 | 2016-07-01 | 7:00 | 212 | 27 | 2016-07-01 | 21:00
6 | Barapukuria | 230 | 230 | 2 | 2016-07-01 | 22:00 | 214 | 28 | 2016-07-01 | 19:30
7 | Bogra | 230 | 227 | 4 | 2016-07-01 | 7:00 | 205 | 27 | 2016-07-01 | 21:00
8 | Khulna South | 230 | 239 | 1 | 2016-07-01 | 15:00 | 216 | 30 | 2016-07-01 | 7:00
9 | Rampura | 230 | 221 | 7 | 2016-07-01 | 8:00 | 202 | 31 | 2016-07-01 | 12:00
10 | Haripur | 230 | 220 | 5 | 2016-07-01 | 19:00 | 200 | 31 | 2016-07-01 | 12:00
11 | Hasnabad | 230 | 222 | 7 | 2016-07-01 | 7:00 | 200 | 31 | 2016-07-01 | 17:00
12 | Aminbazar | 230 | 221 | 7 | 2016-07-01 | 5:00 | 196 | 31 | 2016-07-01 | 12:00
13 | Tongi | 230 | 222 | 7 | 2016-07-01 | 7:00 | 199 | 28 | 2016-07-01 | 21:00
14 | Comilla (N) | 230 | 232 | 8 | 2016-07-01 | 16:00 | 203 | 12 | 2016-07-01 | 23:00
15 | Hathazari | 230 | 221 | 24 | 2016-07-01 | 7:00 | 200 | 26 | 2016-07-01 | 9:00
16 | Megnaghat | 230 | 224 | 7 | 2016-07-01 | 7:00 | 200 | 31 | 2016-07-01 | 17:00
17 | Fenchuganj | 230 | 236 | 5 | 2016-07-01 | 8:00 | 224 | 14 | 2016-07-01 | 19:00
18 | Siddhirganj | 230 | 235 | 5 | 2016-07-01 | 7:00 | 213 | 2 | 2016-07-01 | 10:00
19 | Maniknagar | 230 | 235 | 5 | 2016-07-01 | 7:00 | 211 | 31 | 2016-07-01 | 13:00
20 | Old Airport | 230 | 224 | 9 | 2016-07-01 | 16:00 | 194 | 31 | 2016-07-01 | 17:00
21 | Barisal | 230 | 244 | 17 | 2016-07-01 | 6:00 | 222 | 4 | 2016-07-01 | 14:00
22 | AKSML | 230 | 222 | 5 | 2016-07-01 | 20:00 | 203 | 26 | 2016-07-01 | 11:00
23 | BSRM | 230 | 224 | 10 | 2016-07-01 | 18:30 | 206 | 26 | 2016-07-01 | 9:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 23 | 2016-07-01 | 22:00 | 127 | 2 | 2016-07-01 | 10:00
2 | Munsiganj | 132 | 139 | 23 | 2016-07-01 | 23:00 | 129 | 3 | 2016-07-01 | 11:00
3 | Megnaghat | 132 | 136 | 16 | 2016-07-01 | 19:30 | 126 | 2 | 2016-07-01 | 9:00
4 | Shyampur | 132 | 134 | 6 | 2016-07-01 | 7:00 | 120 | 2 | 2016-07-01 | 10:00
5 | Bhulta | 132 | 134 | 7 | 2016-07-01 | 7:00 | 118 | 30 | 2016-07-01 | 12:00
6 | Madanganj | 132 | 137 | 5 | 2016-07-01 | 5:00 | 126 | 2 | 2016-07-01 | 10:00
7 | Shitalakhya | 132 | 140 | 5 | 2016-07-01 | 7:00 | 121 | 2 | 2016-07-01 | 11:00
8 | Rahim Steal | 132 | 137 | 14 | 2016-07-01 | 1:00 | 125 | 20 | 2016-07-01 | 12:00
9 | Matuail | 132 | 137 | 5 | 2016-07-01 | 7:00 | 126 | 31 | 2016-07-01 | 13:00
10 | Ghorasal | 132 | 140 | 9 | 2016-07-01 | 19:00 | 126 | 30 | 2016-07-01 | 15:00
11 | Narsinghdi | 132 | 139 | 7 | 2016-07-01 | 8:00 | 127 | 27 | 2016-07-01 | 19:30
12 | Haripur (SBU) | 132 | 137 | 13 | 2016-07-01 | 5:00 | 128 | 26 | 2016-07-01 | 11:00
13 | Ullon | 132 | 136 | 5 | 2016-07-01 | 5:00 | 124 | 31 | 2016-07-01 | 13:00
14 | Hasnabad | 132 | 138 | 5 | 2016-07-01 | 5:00 | 124 | 2 | 2016-07-01 | 12:00
15 | Magbazar | 132 | 138 | 5 | 2016-07-01 | 6:00 | 120 | 31 | 2016-07-01 | 13:00
16 | Maniknagar | 132 | 137 | 5 | 2016-07-01 | 5:00 | 125 | 31 | 2016-07-01 | 13:00
17 | Bangabhaban | 132 | 137 | 5 | 2016-07-01 | 5:00 | 122 | 17 | 2016-07-01 | 11:00
18 | Narinda | 132 | 137 | 5 | 2016-07-01 | 5:00 | 124 | 14 | 2016-07-01 | 14:00
19 | Dhanmondi | 132 | 138 | 5 | 2016-07-01 | 6:00 | 120 | 31 | 2016-07-01 | 13:00
20 | Lalbag | 132 | 139 | 5 | 2016-07-01 | 7:00 | 118 | 31 | 2016-07-01 | 13:00
21 | Madartek | 132 | 136 | 5 | 2016-07-01 | 7:00 | 122 | 28 | 2016-07-01 | 15:00
22 | Mirpur | 132 | 136 | 5 | 2016-07-01 | 5:00 | 117 | 28 | 2016-07-01 | 17:00
23 | Kalyanpur | 132 | 138 | 6 | 2016-07-01 | 6:00 | 120 | 29 | 2016-07-01 | 21:00
24 | Gulshan | 132 | 137 | 5 | 2016-07-01 | 7:00 | 120 | 3 | 2016-07-01 | 11:00
25 | Uttara | 132 | 134 | 5 | 2016-07-01 | 7:00 | 117 | 31 | 2016-07-01 | 12:00
26 | Kamrangirchar | 132 | 137 | 7 | 2016-07-01 | 8:00 | 119 | 2 | 2016-07-01 | 11:00
27 | Savar | 132 | 135 | 5 | 2016-07-01 | 6:00 | 119 | 31 | 2016-07-01 | 17:00
28 | Bhasantec | 132 | 136 | 7 | 2016-07-01 | 6:00 | 119 | 31 | 2016-07-01 | 17:00
29 | Agargaon | 132 | 136 | 3 | 2016-07-01 | 5:00 | 121 | 26 | 2016-07-01 | 11:00
30 | Satmosjid | 132 | 136 | 25 | 2016-07-01 | 1:00 | 121 | 26 | 2016-07-01 | 12:00
31 | Tongi | 132 | 139 | 5 | 2016-07-01 | 8:00 | 124 | 11 | 2016-07-01 | 19:30
32 | Kabirpur | 132 | 136 | 8 | 2016-07-01 | 18:00 | 120 | 10 | 2016-07-01 | 13:00
33 | Basundhara | 132 | 132 | 22 | 2016-07-01 | 4:00 | 117 | 31 | 2016-07-01 | 15:00
34 | Manikganj | 132 | 139 | 5 | 2016-07-01 | 8:00 | 115 | 11 | 2016-07-01 | 19:30
35 | Joydevpur | 132 | 137 | 8 | 2016-07-01 | 18:30 | 123 | 30 | 2016-07-01 | 15:00
36 | New Tongi | 132 | 136 | 5 | 2016-07-01 | 8:00 | 112 | 4 | 2016-07-01 | 21:00
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July 2016
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
37 | Tangail | 132 | 135 | 5 | 2016-07-01 | 8:00 | 114 | 24 | 2016-07-01 | 20:00
38 | Mymensing | 132 | 132 | 17 | 2016-07-01 | 14:00 | 110 | 1 | 2016-07-01 | 5:00
39 | Kishorganj | 132 | 132 | 18 | 2016-07-01 | 5:00 | 116 | 15 | 2016-07-01 | 18:00
40 | Netrokona | 132 | 132 | 5 | 2016-07-01 | 9:00 | 111 | 1 | 2016-07-01 | 6:00
41 | Jamalpur | 132 | 128 | 5 | 2016-07-01 | 9:00 | 103 | 6 | 2016-07-01 | 19:30
42 | Sherpur | 132 | 129 | 17 | 2016-07-01 | 18:00 | 102 | 3 | 2016-07-01 | 1:00
43 | Srimongal | 132 | 140 | 6 | 2016-07-01 | 16:00 | 131 | 29 | 2016-07-01 | 14:00
44 | Shahjibazar | 132 | 140 | 7 | 2016-07-01 | 5:00 | 130 | 29 | 2016-07-01 | 9:00
45 | Fenchuganj | 132 | 140 | 7 | 2016-07-01 | 6:00 | 134 | 15 | 2016-07-01 | 19:00
46 | Khulawara | 132 | 139 | 7 | 2016-07-01 | 7:00 | 133 | 15 | 2016-07-01 | 19:00
47 | Sylhet | 132 | 138 | 3 | 2016-07-01 | 10:00 | 130 | 1 | 2016-07-01 | 24:00
48 | Chattak | 132 | 138 | 16 | 2016-07-01 | 10:00 | 128 | 15 | 2016-07-01 | 19:30
49 | Comilla(South) | 132 | 135 | 7 | 2016-07-01 | 18:00 | 122 | 30 | 2016-07-01 | 19:00
50 | Comilla (North) | 132 | 136 | 16 | 2016-07-01 | 7:00 | 129 | 28 | 2016-07-01 | 10:00
51 | Chandpur | 132 | 134 | 29 | 2016-07-01 | 11:00 | 121 | 14 | 2016-07-01 | 21:00
52 | Feni | 132 | 134 | 22 | 2016-07-01 | 20:00 | 115 | 14 | 2016-07-01 | 16:00
53 | Chowmuhani | 132 | 128 | 3 | 2016-07-01 | 12:00 | 119 | 2 | 2016-07-01 | 20:00
54 | Ashuganj | 132 | 140 | 7 | 2016-07-01 | 7:00 | 130 | 29 | 2016-07-01 | 12:00
55 | Daudkandi | 132 | 135 | 5 | 2016-07-01 | 7:00 | 126 | 27 | 2016-07-01 | 16:00
56 | Brahminbaria | 132 | 137 | 7 | 2016-07-01 | 15:00 | 126 | 29 | 2016-07-01 | 7:00
57 | Madanhat | 132 | 139 | 3 | 2016-07-01 | 2:00 | 125 | 26 | 2016-07-01 | 9:00
58 | Hathazari | 132 | 133 | 4 | 2016-07-01 | 20:00 | 120 | 26 | 2016-07-01 | 9:00
59 | Khulshi | 132 | 138 | 3 | 2016-07-01 | 3:00 | 126 | 26 | 2016-07-01 | 9:00
60 | Halishahar | 132 | 135 | 2 | 2016-07-01 | 20:00 | 121 | 26 | 2016-07-01 | 10:00
61 | Baraulia | 132 | 133 | 17 | 2016-07-01 | 23:00 | 120 | 26 | 2016-07-01 | 9:00
62 | Sikalbaha | 132 | 134 | 3 | 2016-07-01 | 2:00 | 122 | 26 | 2016-07-01 | 10:00
63 | Dohazari | 132 | 133 | 1 | 2016-07-01 | 18:00 | 121 | 26 | 2016-07-01 | 10:00
64 | Cox'sbazar | 132 | 133 | 4 | 2016-07-01 | 14:00 | 118 | 30 | 2016-07-01 | 13:00
65 | Chandraghona | 132 | 135 | 17 | 2016-07-01 | 20:00 | 125 | 26 | 2016-07-01 | 9:00
66 | Kaptai | 132 | 135 | 5 | 2016-07-01 | 20:00 | 125 | 26 | 2016-07-01 | 10:00
67 | A. Khaer Stl. | 132 | 136 | 4 | 2016-07-01 | 18:00 | 123 | 14 | 2016-07-01 | 15:00
68 | Bakulia | 132 | 132 | 5 | 2016-07-01 | 21:00 | 119 | 26 | 2016-07-01 | 9:00
69 | Julda | 132 | 136 | 4 | 2016-07-01 | 19:30 | 119 | 26 | 2016-07-01 | 9:00
70 | TK Chemical | 132 | 136 | 3 | 2016-07-01 | 1:00 | 124 | 26 | 2016-07-01 | 15:00
71 | Modern Steel | 132 | 133 | 5 | 2016-07-01 | 20:00 | 119 | 26 | 2016-07-01 | 9:00
72 | Shahmirpur | 132 | 133 | 3 | 2016-07-01 | 2:00 | 119 | 26 | 2016-07-01 | 9:00
73 | Goalpara | 132 | 139 | 1 | 2016-07-01 | 15:00 | 124 | 30 | 2016-07-01 | 7:00
74 | Khulna Central | 132 | 139 | 14 | 2016-07-01 | 17:00 | 125 | 30 | 2016-07-01 | 7:00
75 | Noapara | 132 | 137 | 22 | 2016-07-01 | 15:00 | 123 | 30 | 2016-07-01 | 8:00
76 | Jessore | 132 | 131 | 30 | 2016-07-01 | 18:00 | 115 | 30 | 2016-07-01 | 22:00
77 | Jhenida | 132 | 134 | 22 | 2016-07-01 | 16:00 | 110 | 30 | 2016-07-01 | 22:00
78 | Bottail | 132 | 135 | 2 | 2016-07-01 | 18:00 | 120 | 27 | 2016-07-01 | 21:00
79 | G.K.Project | 132 | 139 | 10 | 2016-07-01 | 18:30 | 124 | 4 | 2016-07-01 | 23:00
80 | Faridpur | 132 | 135 | 10 | 2016-07-01 | 18:30 | 121 | 28 | 2016-07-01 | 21:00
81 | Madaripur | 132 | 136 | 16 | 2016-07-01 | 6:00 | 122 | 28 | 2016-07-01 | 21:00
82 | Gopalganj | 132 | 142 | 13 | 2016-07-01 | 18:30 | 123 | 4 | 2016-07-01 | 13:00
83 | Bagerhat | 132 | 140 | 31 | 2016-07-01 | 5:00 | 125 | 11 | 2016-07-01 | 14:00
84 | Mongla | 132 | 135 | 1 | 2016-07-01 | 15:00 | 122 | 11 | 2016-07-01 | 12:00
85 | Satkhira | 132 | 139 | 25 | 2016-07-01 | 14:00 | 116 | 2 | 2016-07-01 | 21:00
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July 2016
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
86 | Gallamari | 132 | 140 | 27 | 2016-07-01 | 6:00 | 126 | 11 | 2016-07-01 | 12:00
87 | Magura | 132 | 134 | 22 | 2016-07-01 | 15:00 | 110 | 4 | 2016-07-01 | 23:00
88 | Chuadanga | 132 | 131 | 6 | 2016-07-01 | 6:00 | 105 | 30 | 2016-07-01 | 23:00
89 | Barisal | 132 | 140 | 1 | 2016-07-01 | 16:00 | 126 | 10 | 2016-07-01 | 21:00
90 | Patuakhali | 132 | 138 | 4 | 2016-07-01 | 6:00 | 116 | 9 | 2016-07-01 | 22:00
91 | Bhandaria | 132 | 140 | 16 | 2016-07-01 | 16:00 | 125 | 21 | 2016-07-01 | 21:00
92 | Ishurdi | 132 | 136 | 6 | 2016-07-01 | 7:00 | 125 | 27 | 2016-07-01 | 19:30
93 | Natore | 132 | 136 | 8 | 2016-07-01 | 18:30 | 124 | 22 | 2016-07-01 | 14:00
94 | Bogra | 132 | 135 | 4 | 2016-07-01 | 7:00 | 118 | 27 | 2016-07-01 | 19:30
95 | Noagaon | 132 | 132 | 6 | 2016-07-01 | 8:00 | 116 | 15 | 2016-07-01 | 20:00
96 | Rajshahi | 132 | 136 | 21 | 2016-07-01 | 18:00 | 120 | 27 | 2016-07-01 | 21:00
97 | C.Nawabganj | 132 | 135 | 10 | 2016-07-01 | 18:30 | 119 | 6 | 2016-07-01 | 19:30
98 | Amnura | 132 | 140 | 21 | 2016-07-01 | 16:00 | 121 | 27 | 2016-07-01 | 21:00
99 | Pabna | 132 | 131 | 21 | 2016-07-01 | 18:30 | 122 | 27 | 2016-07-01 | 19:30
100 | Shahjadpur | 132 | 138 | 8 | 2016-07-01 | 18:00 | 128 | 27 | 2016-07-01 | 12:00
101 | Serajganj | 132 | 139 | 12 | 2016-07-01 | 21:00 | 122 | 27 | 2016-07-01 | 21:00
102 | Niyamatpur | 132 | 133 | 10 | 2016-07-01 | 18:30 | 113 | 15 | 2016-07-01 | 20:00
103 | Joypurhat | 132 | 135 | 7 | 2016-07-01 | 18:00 | 115 | 15 | 2016-07-01 | 20:00
104 | Rangpur | 132 | 129 | 3 | 2016-07-01 | 9:00 | 109 | 14 | 2016-07-01 | 21:00
105 | Lalmonirhat | 132 | 135 | 7 | 2016-07-01 | 18:00 | 104 | 10 | 2016-07-01 | 21:00
106 | Saidpur | 132 | 129 | 3 | 2016-07-01 | 9:00 | 108 | 15 | 2016-07-01 | 20:00
107 | Purbasadipur | 132 | 129 | 3 | 2016-07-01 | 7:00 | 108 | 14 | 2016-07-01 | 21:00
108 | Thakurgaon | 132 | 128 | 3 | 2016-07-01 | 8:00 | 106 | 14 | 2016-07-01 | 21:00
109 | Palashbari | 132 | 132 | 4 | 2016-07-01 | 7:00 | 113 | 14 | 2016-07-01 | 21:00
110 | Barapukuria | 132 | 136 | 26 | 2016-07-01 | 6:00 | 114 | 28 | 2016-07-01 | 19:30
111 | Panchagar | 132 | 127 | 4 | 2016-07-01 | 7:00 | 90 | 2 | 2016-07-01 | 1:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
| Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month: July 2016
| Name of the | Auto transofrmer |  | Recorded maximum load
| sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kv side ) | Date | Time | Remarks
|  | TR1 | 225 | 120 | 430
IP-299421 | Hasnabad | TR2 | 225 | 102 | 425 | 02.07.16 | 11:00
|  | TR3 | 225 | 100 | 385
|  | TR1 | 225 | 140 | 460
IP-299866 | Tongi | TR2 | 225 | 140 | 460 | 12.07.16 | 21:00
|  | TR3 | 225 | 140 | 460
|  | TR1 | 225 | 180 | 525
IP-299427 | Haripur | TR2 | 225 | 180 | 525 | 31.07.16 | 22:00
|  | TR1 | 225 | 150 | 460
| Rampura | TR2 | 225 | 150 | 460 | 28.07.16 | 15:00
IP-299728 |  | TR3 | 225 | 150 | 460
|  | TR1 | 225 | 134 | 396
| Aminbazar | TR2 | 225 | 134 | 396 | 01.07.16 | 23:00
IP-299264 |  | TR3 | 225 | 138 | 410
| Maniknagar | TR1 | 300 | 105 | 330 | 28.07.16 | 13:00
|  | TR2 | 300 | 105 | 330
| Comilla (N) | TR1 | 225 | 125 | 380 | 03.07.16 | 23:00
IP-399266 |  | TR2 | 225 | 128 | 432
| Fenchuganj | TR1 | 300 | 171 | 448 | 26.07.16 | 10:00
|  | TR1 | 150 | 110 | 300
| Hathazari | TR2 | 150 | 110 | 300 | 09.07.16 | 9:00
|  | TR3 | 150 | 110 | 300
IP-399428 |  | TR4 | 150 | 110 | 300
|  | TR1 | 225 | 170 | 450
| Ishurdi | TR2 | 225 | 170 | 450 | 16.07.16 | 23:00
|  | TR3 | 225 | 170 | 450
IP-499474 | Khulna(S) | TR1 | 225 | 151 | 380
|  | TR2 | 225 | 151 | 380 | 29.07.16 | 6:00
IP-58001/58002 | Bogra | TR1 | 225 | 165 | 511 | 15.07.16 | 21:00
|  | TR2 | 225 | 165 | 511
IP-43002/499264 | Baghabari | TR1 | 225 | 120 | 355 | 15.07.16 | 2:00
IP-499224 | Barapukuria | TR1 | 225 | 180 | 900 | 11.07.16 | 21:00
|  | TR2 | 225 | 180 | 900
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: July 2016 | [6 empty] | (For Evening Peak) | [7 empty] | Month: July 2016 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-07-16 | 8588 | 8588 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 01-07-16 | 7155 | 7155 | 0 | 10:00 | - | - | - | - | - | - | - | - | - | -
02-07-16 | 8367 | 8367 | 0 | 22:00 | - | - | - | - | - | - | - | - | - | - | 02-07-16 | 6946 | 6946 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
03-07-16 | 8066 | 8066 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 03-07-16 | 6253 | 6253 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
04-07-16 | 7643 | 7643 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 04-07-16 | 5560 | 5560 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
05-07-16 | 7265 | 7265 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 05-07-16 | 4701 | 4701 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
06-07-16 | 7241 | 7241 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 06-07-16 | 4632 | 4632 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
07-07-16 | 7162 | 7162 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 07-07-16 | 5351 | 5351 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
08-07-16 | 7339 | 7339 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 08-07-16 | 5164 | 5164 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
09-07-16 | 7361 | 7361 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 09-07-16 | 5271 | 5271 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
10-07-16 | 7767 | 7767 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 10-07-16 | 5653 | 5653 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
11-07-16 | 8120 | 8120 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 11-07-16 | 6213 | 6213 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
12-07-16 | 8197 | 8197 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 12-07-16 | 6476 | 6476 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
13-07-16 | 8366 | 8366 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 13-07-16 | 6861 | 6861 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
14-07-16 | 8528 | 8528 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 14-07-16 | 7276 | 7276 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
15-07-16 | 8319 | 8319 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 15-07-16 | 6405 | 6405 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
16-07-16 | 7990 | 7990 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 16-07-16 | 6621 | 6621 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
17-07-16 | 8207 | 8207 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 17-07-16 | 6712 | 6712 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
18-07-16 | 8479 | 8479 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 18-07-16 | 6547 | 6547 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
19-07-16 | 8615 | 8615 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 19-07-16 | 6778 | 6778 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
20-07-16 | 8477 | 8650 | 156 | 21:00 | - | 31 | 37 | 26 | 23 | 16 | - | 5 | 18 | Due to generation shortage & gas restriction | 20-07-16 | 7103 | 7103 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
21-07-16 | 8371 | 8371 | 0 | 20:00 | - | - | - | - | - | - | - | - | - | - | 21-07-16 | 7094 | 7094 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
22-07-16 | 7939 | 7939 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 22-07-16 | 5816 | 5816 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
23-07-16 | 8259 | 8259 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 23-07-16 | 6585 | 6585 | 0 | 11:00 | - | - | - | - | - | - | - | - | - | -
24-07-16 | 8375 | 8375 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 24-07-16 | 6829 | 6829 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
25-07-16 | 8216 | 8216 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 25-07-16 | 6877 | 6877 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
26-07-16 | 8260 | 8400 | 126 | 21:00 | - | 22 | 27 | 26 | 20 | 14 | - | 4 | 13 | Due to generation shortage & gas restriction | 26-07-16 | 6779 | 6779 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
27-07-16 | 8354 | 8354 | 0 | 19:30 | - | - | - | - | - | - | - | - | - | - | 27-07-16 | 6881 | 6881 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
28-07-16 | 8616 | 8616 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 28-07-16 | 7443 | 7443 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
29-07-16 | 8277 | 8277 | 0 | 21:00 | - | - | - | - | - | - | - | - | - | - | 29-07-16 | 6101 | 6101 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
30-07-16 | 7984 | 8300 | 216 | 21:00 | - | - | 112 | 104 | - | - | - | - | - | Due to generation shortage & gas restriction | 30-07-16 | 7080 | 7080 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -
31-07-16 | 8156 | 8450 | 0 | 21:00 | 62 | 37 | 37 | 35 | 27 | 20 | 17 | 10 | 20 | Do | 31-07-16 | 7094 | 7094 | 0 | 12:00 | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month: July 2016
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 8795 | 01/07/16 | 1:00
2 | Maximum day peak Genaration | MW | 7443 | 28/07/16 | 21:00
3 | Evening Peak Demand | MW | 8650 | 20/07/16 | 21:00
4 | Minimum Generation | MW | 4303 | 06/07/16 | 7:00
5 | Average of the daily evening peak Genaration | MW | 8093.6774
6 | Average of the daily day peak Genaration | MW | 6395.3871
7 | Maximum load shed | MW | 265 | 31/07/16 | 21:00
8 | Minimum load shed | MW | 126 | 26/07/16 | 21:00
9 | Total nos. of load shed days | Day | 4
10 | Average load shed ( Avg. of the 31 days in the month) | MW | 24.6129
11 | Total Generation | MKWH | 5067.625
12 | Total Generation by IPP | MKWH | 938.764 | % of total Gen. | 18.5247
13 | Total Generation by BPDB | MKWH | 2349.6056 | " | 46.365
14 | A) Total Generation by RPCL | MKWH | 226.8503 |  | 4.4765
| B) Total Generation by REB | MKWH | 116.3535 | " | 2.296
| C) Total Generation by RENTAL | MKWH | 1068.7343 | " | 21.0895
| D) Total Imported from India (HVDC) | MKWH | 313.6946 | " | 6.1902
| E) Total Imported from Tripura, India (A.C) | MKWH | 53.6227 | " | 1.0581
15 | Fuel wise Generation.
| A) Gas | MKWH | 3350.4514 | % of total Gen. | 66.11%
| B) Oil | MKWH | 1121.0303 | '' | 22.12%
| C) Hydro | MKWH | 109.96 | '' | 2.17%
| D) Coal | MKWH | 118.866 | '' | 2.346%
| E) HVDC (Import from India) | MKWH | 313.6946 | '' | 6.19%
| F) A.C (Import from Tripura, India) | MKWH | 53.6227 | '' | 1.058%
16 | Maximun of the daily total Generation . | MKWH | 182.5605 | 01/07/16
17 | Monthly Load factor | % | 77.4454
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 14345.6275
| A) Gas | M.Taka | 2157.7979
| B) Liquid fuel | M.Taka | 11725.2033
| C) Coal | M.Taka | 462.6263
| D) HVDC (Import from India) | M.Taka | 909.7144
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 624.7176 | 01/07/16
| A) Gas | M.Taka | 84.984 | 30/07/16
| B) Liquid fuel | M.Taka | 539.536 | 01/07/16
| C) Coal | M.Taka | 46.4495 | 22/07/16
| D) HVDC (Import from India) | M.Taka | 32.0687 | 04/07/16
20 | Fuel cost of per unit Generation
| A) Including Hydro (Excluding Tripura, (India) | Taka/KWHR | 3.4715
| B) Excluding Hydro & Tripura, India | Taka/KWHR | 3.5494
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 89 | 31/07/16 | 06:00
b) | Actual | FT (MSL) | 95 | 31/07/16 | 06:00
22 | Peak Genaration of July 2015 | MW | 7802 | 06/07/15 | 21:00
23 | Peak Demand of July 2015 | MW | 7802 | 06/07/15 | 21:00
24 | Maximum peak Generation recorded upto 31/07/16 | MW | 9036 | 13/08/15 | 21:00
25 | Maximum peak Demand recorded upto 31/07/16 | MW | 9036 | 13/08/15 | 21:00
26 | Maximum load shed recorded upto 31/07/16 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.