## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-28 | Thursday
|  | Date (day): | 2018-06-28 |  | Thursday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11329 | MW |  |  | (b) At Evening Peak Hour : |  | 12584 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-27 | 2018-06-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | # 2 under maint
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 365 | 365 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 40 | 50 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 88 | 83 | 100 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 368 | 365 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 98 | 98 |  | 12 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 217 | 242 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 380 | 450 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 10 | 100 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 180 | 100 | 150 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 40 | 100 | 102 | 102
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 30 | 40 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 38 | 64 | 99 | 99
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 15 | 91 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 170 | 175 | 200 | 200
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 10 | 0 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 24 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 40 | 40 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 36 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 149 | 149 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 56 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 50 | 90 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 57 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 50 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 149 | 300 | 150 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 104 | 104 | 106 | 106
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2873 | 3501 | 4078 | 4391 | 205 | 575
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 45 | 44 | 44
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 163 | 161 | 169 | 169 |  | 61 | # 2 under maint
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 200 | 195 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 60 | 80 | 60 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 42 | 43 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 65 | 68 | 68
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 80 | 74 | 74
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 68 | 90 | 80 | 80 |  | 20 | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 19 | 15 | 23
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 85 | 98 | 103 | 103 |  | 5 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 690 | 908 | 930 | 1013 | 360 | 132
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Under maint.
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 120 | 100 | 150 | 150 |  | 129
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 100 | 100 | 100 | 34 |  | Gas shortage
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 195 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 327 | 310 | 360 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 327 | 320 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 39 | 39
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 10 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 76 | 78 | 195 | 0
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 34 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 11 | 86 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 48
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 100 | 0 | 0 |  | 163
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 8 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 116 | 164 | 124 | 164
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 10 | 20 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 10 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1424 | 1660 | 1716 | 2124 | 212 | 347
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 81 | 91 | 97 | 100 | 102 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 64 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 1.9 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 150 | 185 | 150 | 185
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 260.9 | 360 | 366 | 402 | 102 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 55 | 56 | 58 | 58
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 50 | 60 | 62 | 62
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 120 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 266 | 266 | 330 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 8 | 8
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 29 | 62 | 50 | 60 |  | 6
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 20 | 86 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 47 | 47 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 78 | 80 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 11 | 46 | 45 | 45
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 320 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1095 | 1284 | 1407 | 1437 | 0 | 26
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 461 | 461 | 480 | 480
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 15 | 97 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 49 | 36 | 47
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 120 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 78 | 78
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 0 | 365 | 250 | 365 | 45 |  | Gas shortage
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 33 | 40 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 0 | 0 | 54
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 80 | 80
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 712 | 1341 | 1398 | 1610 | 45 | 0
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 64 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 29 | 30 | 30
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 192 | 193 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 95 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 324 | 381 | 429 | 459 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 38 | 0 | 38
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 40 | 43 | 43 |  | 7 | Engine problem
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 45 | 46 | 46
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 192 | 140 | 215 | 215
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 185 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 43 | 0 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 11 | 11 | 12 | 12
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 25 | 102 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 532 | 766 | 755 | 881 | 71 | 123
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 71 | 72 | 72
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 125 | 120 | 160 | 160
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 197 | 225 | 250 | 267 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 8107.9 | 10426 | 11329 | 12584 | 995 | 1288
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7686.4074 | 9884 | 10740.0572 | 11929.8155
A. |  | 2018-06-27 | (Yesterday) |  |  |  |  | Wednesday
1 | Highest Generation : |  |  | 10426 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6928.3 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10426 | MW
3 | Day peak Generation : |  |  | 8107.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9884 | MW
4 | Evening peak Generation : |  |  | 10426 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 201.704 | MKWHr | By Solar | 0.012972 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 124.298 | MKWHr |  | By Oil: | 54.4014 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.9677 | MKWHr |  | By Hydro: | 3.4759 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 995 | MW | Dhaka | 3582 | 3582 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1288 | MW | Chittagong | 1047 | 1047 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2283 | MW | Khulna | 1268 | 1268 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1072.01 | MMCFD |  |  | Rajshahi | 1091 | 1091 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 92093514.256 | ii) Oil : | Taka | 441130673.65 | Comilla | 932 | 932 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 10295600.15 | Total | Taka | 543519788.056 | Mymensingh | 724 | 724 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.6205 | MKWHr. | Sylhet | 408 | 408 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -760 | MW at | 21:00 | hrs | Barisal | 255 | 255 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -760 | MW at | 21:00 | hrs | Rangpur | 577 | 577 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 32.2° C |  |  | Total | 9884 | 9884 |  | 0
B. |  | 2018-06-28 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12584 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 8400 | MW
4 | Reserve(Generation end) |  |  |  | 1884 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 207.0048 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6763.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.3455 | MKWHr. | ii) HVDC Flow at Peak Time |  | 461 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2026 | MKWHr. | iii) Maximum HVDC Flow : |  | 479 | MW at | 9:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.48 |  | (b) Today: | 102.48 |  | (c) Rule Curve: |  | 82.92
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-06-27
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 120 | 0 | 0 | 300 | 88 | 74 | 350 | 252 | 55 | 0 | 350 | 100 | 7 | 0 | 55 | 170 | 0 | 102 | 0 | 50 | 7 | 98 | 10 | 90 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 87 | 80 | 0 | 0 | 25 | 0 | 204 | 0 | 80 | 0 | 51 | 64 | 74 | 80 | 105 | 43 | 16 | 31 | 0 | 120 | 100 | 300 | 305 | 183 | 86 | 0 | 32 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 0 | 18 | 148 | 85 | 32 | 20 | 0 | 60 | 62 | 53 | 50 | 163 | 283 | 31 | 86 | 47 | 80 | 0 | 45 | 10 | 300 | 23 | 8 | 0 | 303 | 0 | 0 | 189 | 105 |  | 475 | 16 | 157 | 46 | 99 | 150 | 0 | 0 | 0 | 52 | 40 | 186 | 33 | 81 | 0 | 0 | 0 | 43 | 38 | 100 | 40 | 43 | 45 | 25 | 41 | 22 | 12 | 10 | 0 | 70 | 160 | 15 | 18 | 178 | 0 | 0 | 173 | 96 | 0 | 0 | 0 |  | 7153 | 2464 | 9617 | 3508 | 475 | 1944 | 1934 | 230 | 167 | 1211 | 148 | 0 | 0 | 102.39
2:00 | 37 | 120 | 0 | 0 | 300 | 88 | 73 | 350 | 257 | 0 | 0 | 350 | 100 | 7 | 10 | 15 | 170 | 0 | 102 | 0 | 7 | 7 | 64 | 10 | 90 | 0 | 39 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 85 | 50 | 0 | 0 | 25 | 0 | 202 | 0 | 80 | 0 | 51 | 64 | 74 | 80 | 105 | 43 | 16 | 29 | 0 | 120 | 100 | 300 | 305 | 184 | 86 | 0 | 32 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 0 | 18 | 146 | 99 | 32 | 20 | 0 | 60 | 63 | 53 | 50 | 130 | 285 | 20 | 86 | 47 | 80 | 0 | 45 | 10 | 290 | 20 | 8 | 0 | 303 | 0 | 0 | 189 | 105 |  | 475 | 0 | 157 | 32 | 100 | 150 | 0 | 0 | 0 | 47 | 40 | 187 | 33 | 48 | 0 | 0 | 0 | 0 | 25 | 90 | 40 | 43 | 45 | 25 | 42 | 22 | 12 | 10 | 0 | 71 | 158 | 15 | 18 | 174 | 0 | 0 | 170 | 97 | 0 | 0 | 0 |  | 6918 | 2326 | 9244 | 3509 | 475 | 1904 | 1760 | 229 | 135 | 1086 | 146 | 0 | 0 | 102.41
3:00 | 37 | 120 | 0 | 0 | 280 | 88 | 74 | 350 | 261 | 0 | 0 | 380 | 100 | 7 | 16 | 15 | 170 | 0 | 101 | 0 | 7 | 7 | 34 | 10 | 90 | 0 | 39 | 36 | 18 | 36 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 85 | 50 | 0 | 0 | 25 | 0 | 201 | 0 | 80 | 0 | 51 | 64 | 76 | 80 | 105 | 43 | 16 | 38 | 0 | 120 | 100 | 300 | 305 | 183 | 78 | 0 | 32 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 0 | 18 | 140 | 100 | 8 | 20 | 0 | 60 | 63 | 53 | 50 | 100 | 281 | 31 | 40 | 47 | 80 | 0 | 45 | 10 | 280 | 20 | 8 | 0 | 303 | 0 | 0 | 189 | 105 |  | 475 | 0 | 0 | 5 | 85 | 150 | 0 | 0 | 0 | 30 | 40 | 186 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 45 | 8 | 26 | 22 | 12 | 10 | 0 | 71 | 160 | 15 | 18 | 171 | 0 | 0 | 168 | 97 | 0 | 0 | 0 |  | 6727 | 1980 | 8707 | 3334 | 475 | 1851 | 1609 | 231 | 135 | 932 | 140 | 0 | 0 | 102.43
4:00 | 37 | 120 | 0 | 0 | 280 | 88 | 74 | 350 | 281 | 0 | 0 | 380 | 100 | 7 | 16 | 15 | 170 | 0 | 102 | 0 | 7 | 7 | 15 | 10 | 90 | 0 | 39 | 18 | 18 | 36 | 19 | 25 | 32 | 33 | 33 | 24 | 0 | 85 | 50 | 0 | 0 | 8 | 0 | 201 | 0 | 80 | 0 | 51 | 32 | 31 | 80 | 60 | 44 | 16 | 37 | 0 | 120 | 100 | 300 | 305 | 183 | 78 | 0 | 32 | 0 | 10 | 51 | 51 | 0 | 0 | 19 | 3 | 0 | 18 | 130 | 99 | 8 | 20 | 0 | 60 | 63 | 53 | 50 | 100 | 284 | 20 | 40 | 45 | 80 | 0 | 45 | 10 | 280 | 23 | 8 | 0 | 303 | 0 | 0 | 189 | 105 |  | 475 | 0 | 0 | 5 | 68 | 150 | 0 | 0 | 0 | 14 | 40 | 189 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 43 | 45 | 8 | 0 | 22 | 12 | 10 | 0 | 71 | 159 | 0 | 18 | 173 | 0 | 0 | 169 | 96 | 0 | 0 | 0 |  | 6486 | 1884 | 8370 | 3326 | 475 | 1832 | 1487 | 230 | 135 | 755 | 130 | 0 | 0 | 102.45
5:00 | 37 | 120 | 0 | 0 | 280 | 88 | 74 | 350 | 311 | 0 | 0 | 380 | 100 | 7 | 16 | 15 | 170 | 0 | 103 | 0 | 7 | 7 | 15 | 10 | 30 | 0 | 39 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 24 | 0 | 85 | 50 | 0 | 0 | 8 | 0 | 201 | 0 | 60 | 0 | 51 | 32 | 31 | 80 | 52 | 44 | 16 | 41 | 0 | 120 | 100 | 300 | 305 | 183 | 78 | 0 | 32 | 0 | 10 | 40 | 51 | 0 | 0 | 19 | 8 | 0 | 18 | 120 | 99 | 8 | 20 | 0 | 60 | 63 | 53 | 50 | 100 | 289 | 20 | 40 | 45 | 80 | 0 | 45 | 10 | 300 | 23 | 8 | 0 | 150 | 0 | 0 | 170 | 105 |  | 475 | 0 | 0 | 5 | 66 | 150 | 0 | 0 | 0 | 0 | 40 | 180 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 43 | 45 | 8 | 0 | 22 | 12 | 10 | 0 | 71 | 159 | 0 | 0 | 178 | 0 | 0 | 173 | 95 | 0 | 0 | 0 |  | 6251 | 1849 | 8100 | 3333 | 475 | 1874 | 1226 | 230 | 135 | 707 | 120 | 0 | 0 | 102.47
6:00 | 37 | 120 | 0 | 0 | 280 | 56 | 50 | 350 | 311 | 0 | 0 | 380 | 100 | 7 | 16 | 15 | 170 | 0 | 100 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 8 | 0 | 85 | 50 | 0 | 0 | 8 | 0 | 201 | 0 | 60 | 0 | 8 | 0 | 0 | 80 | 12 | 35 | 16 | 39 | 0 | 120 | 100 | 300 | 301 | 183 | 78 | 0 | 32 | 0 | 10 | 6 | 11 | 0 | 0 | 19 | 11 | 0 | 18 | 118 | 99 | 0 | 20 | 0 | 60 | 60 | 11 | 10 | 100 | 267 | 20 | 10 | 10 | 80 | 0 | 45 | 10 | 280 | 23 | 8 | 0 | 48 | 0 | 0 | 72 | 105 |  | 475 | 0 | 0 | 5 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 194 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 43 | 0 | 8 | 0 | 22 | 12 | 10 | 0 | 71 | 159 | 0 | 0 | 171 | 0 | 0 | 168 | 61 | 0 | 0 | 0 |  | 5477 | 1615 | 7092 | 3311 | 475 | 1535 | 724 | 230 | 135 | 564 | 118 | 0 | 0 | 102.48
7:00 | 37 | 120 | 0 | 0 | 280 | 54 | 50 | 350 | 280 | 0 | 0 | 380 | 100 | 7 | 15 | 15 | 170 | 0 | 100 | 0 | 7 | 7 | 15 | 0 | 8 | 0 | 6 | 18 | 0 | 17 | 19 | 25 | 32 | 33 | 33 | 8 | 0 | 88 | 50 | 0 | 0 | 0 | 0 | 207 | 0 | 60 | 0 | 8 | 0 | 0 | 20 | 12 | 8 | 16 | 34 | 0 | 120 | 100 | 325 | 325 | 200 | 78 | 0 | 32 | 0 | 10 | 6 | 11 | 0 | 0 | 19 | 8 | 0 | 18 | 112 | 97 | 0 | 20 | 0.3 | 60 | 60 | 11 | 10 | 100 | 275 | 20 | 10 | 10 | 80 | 0 | 45 | 0 | 310 | 15 | 8 | 0 | 47 | 0 | 0 | 32 | 105 |  | 475 | 0 | 0 | 5 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 196 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 43 | 0 | 8 | 0 | 21 | 12 | 10 | 0 | 72 | 143 | 0 | 0 | 179 | 0 | 0 | 175 | 11 | 0 | 0 | 0 |  | 5368.3 | 1560 | 6928.3 | 3382 | 475 | 1460 | 569 | 215 | 138 | 577 | 112 | 0.3 | 0 | 102.49
8:00 | 37 | 120 | 0 | 0 | 320 | 54 | 50 | 370 | 281 | 0 | 0 | 380 | 140 | 7 | 15 | 15 | 170 | 0 | 99 | 0 | 7 | 7 | 32 | 0 | 8 | 0 | 6 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 14 | 0 | 89 | 45 | 0 | 0 | 0 | 0 | 219 | 0 | 60 | 0 | 8 | 0 | 0 | 24 | 12 | 6 | 16 | 11 | 0 | 120 | 100 | 342 | 342 | 208 | 78 | 0 | 32 | 0 | 10 | 6 | 11 | 0 | 0 | 19 | 8 | 0 | 0 | 114 | 97 | 0 | 20 | 0.9 | 58 | 60 | 11 | 10 | 100 | 285 | 30 | 10 | 10 | 78 | 0 | 45 | 0 | 320 | 23 | 8 | 0 | 48 | 0 | 0 | 32 | 106 |  | 475 | 0 | 0 | 5 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 191 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 43 | 0 | 8 | 0 | 20 | 12 | 10 | 0 | 72 | 125 | 0 | 0 | 189 | 0 | 0 | 184 | 12 | 0 | 0 | 0 |  | 5558.9 | 1555 | 7113.9 | 3494 | 475 | 1447 | 637 | 197 | 134 | 615 | 114 | 0.9 | 0 | 102.5
9:00 | 37 | 120 | 0 | 0 | 365 | 88 | 60 | 375 | 255 | 0 | 0 | 380 | 140 | 7 | 15 | 15 | 170 | 0 | 99 | 0 | 7 | 7 | 64 | 0 | 30 | 0 | 6 | 18 | 43 | 17 | 19 | 25 | 32 | 33 | 33 | 34 | 0 | 87 | 50 | 0 | 0 | 16 | 0 | 203 | 0 | 135 | 0 | 26 | 0 | 0 | 80 | 12 | 12 | 16 | 5 | 0 | 120 | 100 | 300 | 301 | 183 | 78 | 0 | 32 | 0 | 10 | 10 | 80 | 0 | 0 | 19 | 5 | 0 | 10 | 108 | 97 | 0 | 0 | 0 | 52 | 60 | 27 | 47 | 163 | 271 | 30 | 84 | 40 | 80 | 0 | 42 | 0 | 290 | 23 | 8 | 0 | 48 | 0 | 0 | 50 | 105 |  | 479 | 0 | 0 | 39 | 17 | 120 | 0 | 0 | 0 | 0 | 33 | 190 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 43 | 0 | 8 | 0 | 20 | 12 | 10 | 0 | 72 | 122 | 0 | 0 | 190 | 0 | 0 | 179 | 93 | 0 | 0 | 0 |  | 6009 | 1699 | 7708 | 3405 | 479 | 1800 | 884 | 194 | 137 | 701 | 108 | 0 | 0 | 102.51
10:00 | 37 | 120 | 0 | 0 | 365 | 87 | 60 | 365 | 245 | 0 | 0 | 380 | 100 | 11 | 15 | 15 | 170 | 0 | 37 | 0 | 9 | 7 | 64 | 30 | 91 | 21 | 33 | 36 | 56 | 36 | 19 | 25 | 32 | 33 | 33 | 38 | 0 | 87 | 50 | 0 | 0 | 16 | 0 | 195 | 0 | 100 | 0 | 33 | 0 | 0 | 80 | 73 | 36 | 16 | 3 | 0 | 120 | 100 | 300 | 301 | 183 | 78 | 0 | 32 | 0 | 10 | 25 | 11 | 0 | 0 | 18 | 11 | 0 | 15 | 108 | 98 | 0 | 20 | 0.7 | 56 | 60 | 47 | 50 | 163 | 266 | 20 | 50 | 45 | 80 | 0 | 10 | 0 | 270 | 23 | 8 | 0 | 145 | 0 | 0 | 150 | 104 |  | 461 | 0 | 0 | 45 | 80 | 145 | 0 | 0 | 0 | 0 | 33 | 176 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 43 | 0 | 8 | 0 | 17 | 12 | 11 | 0 | 72 | 123 | 0 | 0 | 174 | 0 | 0 | 171 | 98 | 0 | 0 | 0 |  | 6236.7 | 1745 | 7981.7 | 3324 | 461 | 1681 | 1400 | 195 | 137 | 675 | 108 | 0.7 | 0 | 102.52
11:00 | 37 | 120 | 0 | 0 | 365 | 87 | 40 | 365 | 234 | 0 | 0 | 301 | 110 | 35 | 24 | 49 | 170 | 0 | 38 | 0 | 15 | 7 | 64 | 30 | 50 | 10 | 41 | 54 | 56 | 55 | 19 | 25 | 32 | 0 | 33 | 41 | 0 | 87 | 50 | 0 | 0 | 16 | 0 | 193 | 0 | 60 | 0 | 33 | 0 | 0 | 80 | 85 | 38 | 16 | 2 | 0 | 120 | 100 | 301 | 301 | 185 | 78 | 0 | 36 | 0 | 10 | 30 | 11 | 0 | 0 | 18 | 11 | 12 | 10 | 106 | 82 | 8 | 20 | 0.8 | 54 | 60 | 50 | 50 | 100 | 263 | 30 | 20 | 46 | 80 | 0 | 10 | 7 | 270 | 15 | 8 | 0 | 148 | 0 | 0 | 150 | 106 |  | 461 | 0 | 0 | 40 | 83 | 130 | 0 | 0 | 0 | 0 | 33 | 190 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 8 | 0 | 21 | 12 | 11 | 0 | 72 | 129 | 0 | 0 | 172 | 0 | 0 | 168 | 96 | 0 | 0 | 0 |  | 6073.8 | 1770 | 7843.8 | 3299 | 461 | 1495 | 1504 | 201 | 137 | 640 | 106 | 0.8 | 0 | 102.53
12:00 | 37 | 120 | 0 | 0 | 365 | 88 | 40 | 368 | 217 | 0 | 0 | 380 | 180 | 10 | 40 | 55 | 170 | 0 | 38 | 0 | 15 | 7 | 64 | 30 | 50 | 10 | 40 | 36 | 56 | 55 | 19 | 25 | 30 | 0 | 33 | 42 | 0 | 83 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 60 | 0 | 42 | 0 | 0 | 68 | 85 | 38 | 16 | 2 | 0 | 120 | 100 | 327 | 327 | 201 | 78 | 0 | 39 | 0 | 10 | 34 | 11 | 0 | 0 | 18 | 0 | 33 | 10 | 116 | 81 | 8 | 20 | 1.9 | 55 | 50 | 50 | 50 | 100 | 266 | 29 | 20 | 47 | 80 | 0 | 11 | 7 | 300 | 22 | 8 | 0 | 149 | 0 | 0 | 150 | 104 |  | 461 | 0 | 0 | 15 | 83 | 120 | 0 | 0 | 0 | 0 | 33 | 192 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 8 | 0 | 21 | 11 | 11 | 0 | 72 | 125 | 0 | 0 | 192 | 0 | 0 | 181 | 96 | 0 | 0 | 0 |  | 6342.9 | 1765 | 8107.9 | 3402 | 461 | 1593 | 1524 | 197 | 163 | 650 | 116 | 1.9 | 0 | 102.53
13:00 | 37 | 120 | 0 | 0 | 365 | 87 | 40 | 370 | 218 | 0 | 0 | 380 | 200 | 7 | 15 | 55 | 170 | 0 | 38 | 0 | 15 | 7 | 64 | 30 | 37 | 10 | 40 | 36 | 56 | 55 | 19 | 25 | 31 | 0 | 33 | 42 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 60 | 0 | 42 | 0 | 0 | 80 | 92 | 35 | 16 | 2 | 0 | 120 | 100 | 305 | 312 | 193 | 78 | 0 | 39 | 0 | 10 | 34 | 11 | 0 | 0 | 18 | 11 | 33 | 10 | 120 | 77 | 8 | 20 | 0 | 53 | 50 | 53 | 50 | 100 | 270 | 29 | 20 | 47 | 80 | 0 | 10 | 7 | 310 | 22 | 8 | 0 | 99 | 0 | 0 | 100 | 105 |  | 461 | 0 | 0 | 45 | 83 | 120 | 0 | 0 | 0 | 0 | 24 | 189 | 17 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 33 | 43 | 0 | 8 | 0 | 22 | 11 | 11 | 0 | 70 | 122 | 0 | 0 | 188 | 0 | 0 | 182 | 95 | 0 | 0 | 0 |  | 6218 | 1765 | 7983 | 3362 | 461 | 1602 | 1434 | 192 | 161 | 651 | 120 | 0 | 0 | 102.54
14:00 | 37 | 120 | 0 | 0 | 365 | 88 | 60 | 371 | 211 | 0 | 0 | 380 | 135 | 7 | 15 | 55 | 170 | 0 | 98 | 0 | 15 | 16 | 64 | 87 | 16 | 11 | 12 | 36 | 56 | 55 | 19 | 0 | 31 | 33 | 33 | 46 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 100 | 0 | 42 | 0 | 0 | 80 | 92 | 36 | 16 | 2 | 0 | 120 | 100 | 320 | 320 | 197 | 78 | 0 | 39 | 0 | 10 | 34 | 85 | 0 | 0 | 18 | 11 | 33 | 10 | 128 | 67 | 8 | 0 | 0.9 | 58 | 50 | 53 | 50 | 163 | 269 | 29 | 50 | 46 | 80 | 0 | 44 | 7 | 290 | 22 | 8 | 0 | 48 | 0 | 0 | 100 | 104 |  | 461 | 0 | 49 | 39 | 49 | 120 | 0 | 0 | 0 | 0 | 8 | 188 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 69 | 125 | 0 | 0 | 184 | 0 | 0 | 180 | 95 | 0 | 0 | 0 |  | 6430.9 | 1758 | 8188.9 | 3473 | 461 | 1797 | 1291 | 194 | 160 | 684 | 128 | 0.9 | 0 | 102.54
15:00 | 37 | 120 | 0 | 0 | 365 | 88 | 70 | 375 | 221 | 0 | 0 | 380 | 140 | 12 | 15 | 55 | 170 | 0 | 98 | 0 | 16 | 40 | 64 | 100 | 48 | 10 | 14 | 36 | 56 | 55 | 19 | 25 | 29 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 193 | 0 | 135 | 0 | 42 | 0 | 0 | 80 | 92 | 36 | 16 | 2 | 0 | 120 | 100 | 303 | 315 | 180 | 78 | 20 | 39 | 0 | 10 | 34 | 85 | 0 | 0 | 18 | 11 | 33 | 0 | 130 | 68 | 8 | 0 | 1.9 | 56 | 60 | 50 | 50 | 163 | 264 | 54 | 84 | 46 | 80 | 0 | 43 | 7 | 320 | 23 | 8 | 0 | 50 | 0 | 0 | 100 | 103 |  | 461 | 0 | 30 | 46 | 49 | 120 | 0 | 0 | 0 | 0 | 24 | 189 | 23 | 28 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 8 | 0 | 20 | 11 | 8 | 0 | 68 | 122 | 0 | 0 | 191 | 0 | 0 | 187 | 95 | 0 | 0 | 0 |  | 6660.9 | 1788 | 8448.9 | 3490 | 461 | 1880 | 1412 | 190 | 160 | 724 | 130 | 1.9 | 0 | 102.55
16:00 | 37 | 120 | 0 | 0 | 365 | 85 | 50 | 385 | 227 | 0 | 0 | 400 | 100 | 42 | 26 | 30 | 150 | 0 | 37 | 0 | 40 | 24 | 98 | 30 | 51 | 10 | 39 | 36 | 56 | 55 | 16 | 25 | 30 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 196 | 0 | 80 | 0 | 42 | 8 | 0 | 80 | 92 | 37 | 16 | 3 | 0 | 120 | 100 | 295 | 300 | 183 | 78 | 30 | 39 | 0 | 10 | 34 | 85 | 0 | 13 | 18 | 11 | 33 | 0 | 128 | 83 | 8 | 20 | 1.6 | 56 | 60 | 50 | 50 | 100 | 262 | 50 | 84 | 47 | 80 | 0 | 44 | 7 | 270 | 23 | 8 | 0 | 98 | 0 | 0 | 125 | 105 |  | 461 | 0 | 35 | 46 | 49 | 120 | 0 | 0 | 0 | 9 | 33 | 188 | 15 | 32 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 16 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 67 | 120 | 0 | 0 | 174 | 0 | 0 | 170 | 96 | 0 | 0 | 0 |  | 6518.6 | 1745 | 8263.6 | 3423 | 461 | 1768 | 1429 | 187 | 160 | 706 | 128 | 1.6 | 0 | 102.55
17:00 | 37 | 120 | 0 | 0 | 320 | 56 | 40 | 408 | 237 | 0 | 0 | 400 | 100 | 40 | 30 | 30 | 150 | 0 | 37 | 0 | 30 | 24 | 98 | 10 | 51 | 10 | 40 | 36 | 56 | 55 | 16 | 25 | 30 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 194 | 0 | 60 | 0 | 42 | 33 | 16 | 80 | 92 | 37 | 16 | 2 | 0 | 120 | 100 | 252 | 257 | 183 | 78 | 30 | 39 | 0 | 10 | 34 | 42 | 0 | 16 | 18 | 11 | 8 | 0 | 122 | 94 | 8 | 20 | 0.8 | 56 | 60 | 22 | 20 | 100 | 263 | 51 | 40 | 20 | 80 | 0 | 22 | 10 | 270 | 23 | 8 | 0 | 100 | 0 | 0 | 125 | 105 |  | 461 | 0 | 120 | 27 | 49 | 120 | 0 | 0 | 0 | 10 | 8 | 189 | 19 | 32 | 0 | 0 | 0 | 0 | 5 | 25 | 25 | 16 | 0 | 8 | 0 | 20 | 11 | 8 | 0 | 66 | 117 | 0 | 0 | 172 | 0 | 0 | 169 | 98 | 0 | 0 | 0 |  | 6167.8 | 1775 | 7942.8 | 3387 | 461 | 1551 | 1348 | 183 | 160 | 730 | 122 | 0.8 | 0 | 102.55
18:00 | 37 | 120 | 0 | 0 | 270 | 31 | 40 | 300 | 251 | 0 | 0 | 350 | 100 | 35 | 31 | 30 | 110 | 0 | 36 | 0 | 30 | 7 | 98 | 10 | 51 | 11 | 40 | 36 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 194 | 0 | 50 | 0 | 42 | 33 | 16 | 80 | 70 | 43 | 16 | 5 | 0 | 120 | 100 | 250 | 250 | 182 | 78 | 30 | 39 | 0 | 10 | 34 | 21 | 0 | 16 | 18 | 11 | 8 | 17 | 126 | 99 | 8 | 20 | 0.2 | 56 | 59 | 22 | 20 | 100 | 260 | 52 | 40 | 20 | 80 | 0 | 12 | 6 | 265 | 23 | 8 | 0 | 100 | 0 | 0 | 125 | 105 |  | 460 | 0 | 330 | 10 | 49 | 120 | 0 | 0 | 17 | 18 | 8 | 154 | 17 | 32 | 0 | 0 | 0 | 0 | 13 | 25 | 25 | 16 | 0 | 8 | 0 | 10 | 11 | 11 | 0 | 67 | 117 | 0 | 0 | 159 | 0 | 0 | 151 | 98 | 0 | 0 | 0 |  | 5842.2 | 1926 | 7768.2 | 3367 | 460 | 1441 | 1295 | 184 | 160 | 735 | 126 | 0.2 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.55
19:00 | 37 | 120 | 0 | 0 | 300 | 37 | 40 | 300 | 261 | 26 | 0 | 450 | 100 | 25 | 30 | 30 | 110 | 0 | 65 | 10 | 30 | 7 | 80 | 10 | 63 | 10 | 40 | 36 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 208 | 0 | 80 | 0 | 42 | 65 | 82 | 90 | 78 | 44 | 16 | 5 | 0 | 100 | 100 | 257 | 255 | 207 | 78 | 75 | 39 | 0 | 10 | 51 | 86 | 26 | 16 | 18 | 11 | 8 | 20 | 156 | 95 | 8 | 20 | 0 | 56 | 59 | 13 | 28 | 130 | 276 | 62 | 75 | 10 | 80 | 0 | 43 | 6 | 260 | 23 | 3 | 0 | 100 | 0 | 0 | 125 | 106 |  | 461 | 0 | 360 | 10 | 49 | 120 | 0 | 0 | 50 | 58 | 16 | 188 | 27 | 25 | 0 | 0 | 0 | 0 | 38 | 90 | 35 | 16 | 47 | 8 | 41 | 10 | 11 | 11 | 0 | 70 | 120 | 17 | 18 | 137 | 0 | 0 | 153 | 70 | 0 | 0 | 0 |  | 6497 | 2256 | 8753 | 3550 | 461 | 1701 | 1362 | 190 | 160 | 1173 | 156 | 0 | 0 | 102.55
19:30 | 37 | 120 | 0 | 0 | 330 | 81 | 73 | 384 | 262 | 40 | 0 | 450 | 100 | 75 | 50 | 50 | 140 | 0 | 62 | 17 | 50 | 24 | 149 | 10 | 90 | 11 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 193 | 0 | 60 | 0 | 42 | 65 | 82 | 90 | 90 | 44 | 16 | 8 | 0 | 100 | 100 | 280 | 301 | 183 | 78 | 70 | 39 | 0 | 10 | 51 | 85 | 49 | 16 | 19 | 11 | 33 | 20 | 166 | 100 | 32 | 20 | 0 | 56 | 59 | 53 | 50 | 163 | 260 | 40 | 86 | 47 | 80 | 0 | 43 | 6 | 265 | 23 | 8 | 10 | 140 | 0 | 0 | 175 | 104 |  | 465 | 0 | 355 | 57 | 85 | 120 | 0 | 12 | 50 | 58 | 40 | 170 | 29 | 64 | 0 | 0 | 0 | 0 | 38 | 102 | 40 | 25 | 47 | 25 | 42 | 22 | 11 | 11 | 0 | 69 | 117 | 17 | 18 | 143 | 0 | 0 | 178 | 96 | 30 | 0 | 0 |  | 7299 | 2536 | 9835 | 3712 | 465 | 1969 | 1909 | 186 | 160 | 1268 | 166 | 0 | 0 | 102.56
20:00 | 37 | 120 | 0 | 0 | 318 | 83 | 50 | 370 | 247 | 0 | 0 | 450 | 100 | 70 | 64 | 50 | 140 | 0 | 37 | 0 | 50 | 20 | 149 | 40 | 90 | 0 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 80 | 80 | 0 | 0 | 16 | 0 | 194 | 0 | 50 | 0 | 42 | 65 | 81 | 90 | 98 | 44 | 16 | 13 | 0 | 100 | 100 | 280 | 327 | 198 | 78 | 91 | 39 | 0 | 10 | 51 | 85 | 0 | 16 | 19 | 5 | 33 | 20 | 164 | 96 | 56 | 20 | 0 | 56 | 60 | 53 | 50 | 120 | 270 | 56 | 86 | 47 | 78 | 0 | 45 | 5 | 260 | 23 | 8 | 10 | 215 | 0 | 0 | 185 | 104 |  | 465 | 0 | 355 | 57 | 83 | 120 | 0 | 0 | 50 | 83 | 40 | 192 | 29 | 64 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 47 | 25 | 43 | 22 | 11 | 11 | 0 | 70 | 120 | 17 | 18 | 140 | 0 | 0 | 174 | 95 | 30 | 0 | 0 |  | 7270 | 2627 | 9897 | 3757 | 465 | 1890 | 1997 | 190 | 160 | 1274 | 164 | 0 | 0 | 102.56
21:00 | 37 | 120 | 0 | 0 | 365 | 83 | 50 | 365 | 242 | 0 | 0 | 450 | 100 | 100 | 100 | 55 | 175 | 0 | 64 | 0 | 91 | 24 | 149 | 40 | 90 | 0 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 80 | 0 | 43 | 65 | 80 | 90 | 98 | 45 | 16 | 19 | 0 | 100 | 100 | 310 | 320 | 195 | 76 | 100 | 39 | 0 | 10 | 51 | 86 | 0 | 16 | 19 | 11 | 33 | 20 | 164 | 91 | 64 | 20 | 0 | 56 | 60 | 53 | 50 | 120 | 266 | 62 | 86 | 47 | 78 | 0 | 46 | 9 | 320 | 23 | 8 | 10 | 300 | 0 | 0 | 185 | 104 |  | 461 | 0 | 365 | 97 | 99 | 120 | 0 | 0 | 49 | 60 | 40 | 193 | 29 | 64 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 45 | 43 | 43 | 22 | 11 | 11 | 0 | 71 | 120 | 16 | 18 | 140 | 0 | 0 | 185 | 95 | 50 | 0 | 0 |  | 7713 | 2713 | 10426 | 3904 | 461 | 1955 | 2302 | 191 | 161 | 1288 | 164 | 0 | 0 | 102.56
22:00 | 37 | 120 | 0 | 0 | 365 | 86 | 76 | 342 | 221 | 0 | 0 | 450 | 100 | 100 | 100 | 55 | 170 | 0 | 103 | 0 | 91 | 50 | 149 | 100 | 90 | 0 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 80 | 0 | 51 | 65 | 80 | 90 | 98 | 45 | 16 | 27 | 0 | 100 | 100 | 290 | 270 | 183 | 76 | 100 | 39 | 0 | 10 | 51 | 85 | 0 | 16 | 19 | 11 | 33 | 20 | 168 | 85 | 64 | 20 | 0 | 56 | 60 | 53 | 50 | 120 | 260 | 36 | 86 | 47 | 78 | 0 | 46 | 10 | 270 | 23 | 8 | 0 | 300 | 0 | 0 | 185 | 0 |  | 461 | 0 | 355 | 95 | 83 | 120 | 0 | 0 | 50 | 60 | 40 | 182 | 35 | 80 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 45 | 43 | 42 | 22 | 11 | 11 | 0 | 70 | 120 | 17 | 19 | 135 | 0 | 0 | 169 | 93 | 50 | 0 | 0 |  | 7554 | 2674 | 10228 | 3769 | 461 | 1925 | 2280 | 190 | 161 | 1274 | 168 | 0 | 0 | 102.57
23:00 | 37 | 120 | 0 | 0 | 200 | 87 | 74 | 320 | 221 | 0 | 0 | 360 | 100 | 100 | 64 | 55 | 120 | 0 | 38 | 0 | 91 | 50 | 149 | 100 | 90 | 0 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 189 | 0 | 50 | 0 | 51 | 65 | 77 | 80 | 100 | 45 | 16 | 27 | 0 | 100 | 100 | 290 | 231 | 183 | 76 | 100 | 39 | 0 | 10 | 51 | 86 | 0 | 16 | 19 | 11 | 33 | 20 | 162 | 87 | 64 | 20 | 0 | 58 | 60 | 53 | 50 | 100 | 263 | 51 | 86 | 47 | 79 | 0 | 45 | 10 | 260 | 23 | 8 | 0 | 300 | 0 | 0 | 197 | 0 |  | 461 | 0 | 258 | 97 | 93 | 120 | 0 | 0 | 48 | 60 | 40 | 185 | 37 | 48 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 45 | 43 | 42 | 18 | 11 | 10 | 0 | 70 | 122 | 17 | 18 | 135 | 0 | 0 | 167 | 95 | 10 | 0 | 0 |  | 7038 | 2516 | 9554 | 3356 | 461 | 1804 | 2188 | 192 | 161 | 1230 | 162 | 0 | 0 | 102.57
24:00 | 37 | 120 | 0 | 0 | 250 | 87 | 74 | 320 | 252 | 0 | 0 | 360 | 100 | 100 | 64 | 55 | 120 | 0 | 85 | 0 | 91 | 50 | 149 | 70 | 90 | 0 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 190 | 0 | 80 | 0 | 51 | 65 | 79 | 80 | 105 | 45 | 16 | 22 | 0 | 100 | 100 | 270 | 301 | 184 | 76 | 100 | 38 | 0 | 10 | 51 | 85 | 0 | 16 | 19 | 11 | 33 | 20 | 158 | 87 | 64 | 20 | 0 | 53 | 60 | 53 | 50 | 130 | 223 | 56 | 86 | 47 | 80 | 0 | 45 | 10 | 310 | 23 | 8 | 0 | 300 | 0 | 0 | 187 | 0 |  | 460 | 0 | 280 | 97 | 99 | 120 | 0 | 0 | 48 | 55 | 40 | 181 | 12 | 48 | 0 | 0 | 0 | 43 | 37 | 102 | 40 | 43 | 45 | 25 | 42 | 22 | 11 | 10 | 0 | 70 | 121 | 17 | 18 | 135 | 0 | 0 | 174 | 70 | 10 | 0 | 0 |  | 7237 | 2475 | 9712 | 3482 | 460 | 1863 | 2133 | 191 | 161 | 1264 | 158 | 0 | 0 | 102.52
KWH | 853000 | 2887920 | 0 | 0 | 7553781 | 1869272 | 1539776 | 8705020 | 5971000 | 120600 | 0 | 8644662 | 2865716 | 793920 | 831192 | 926008 | 4013293 | 0 | 1862000 | 20160 | 829440 | 447552 | 1898400 | 725369 | 1378560 | 114510 | 807168 | 889560 | 1070588 | 1077600 | 423324 | 575000 | 725940 | 693300 | 835300 | 995904 | 0 | 1907880 | 1568000 | 0 | 0 | 362700 | 0 | 4754005 | 0 | 1828718 | 0 | 949440 | 671318 | 782752 | 1744320 | 1848960 | 888000 | 391672 | 410400 | 0 | 2031020 | 2404320 | 7505000 | 7166500 | 4575000 | 1923636 | 585775 | 829440 | 0 | 240000 | 847527 | 831192 | 58936 | 151147 | 433188 | 210060 | 377700 | 328000 | 3202560 | 2180400 | 463608 | 404042 | 12972 | 1324000 | 1397440 | 1023600 | 995000 | 3108763 | 6151722 | 869000 | 1392000 | 889200 | 1927830 | 0 | 824120 | 171000 | 7346630 | 514800 | 184604 | 26880 | 4094830 | 0 | 0 | 331680 | 2250640 |  | 11345455 | 0 | 2861856 | 865440 | 1533120 | 3210240 | 0 | 14320 | 276480 | 506112 | 666375 | 4566017 | 570990 | 909120 | 0 | 0 | 0 | 221144 | 307434 | 999200 | 914100 | 907328 | 491600 | 396000 | 357576 | 462480 | 271080 | 245718 | 0 | 1696145 | 3271600 | 143000 | 171000 | 4304018 | 0 | 0 | 4317709 | 2068629 | 193920 | 0 | 0 |  | 152638762 | 49065206 | 201703968 | 82897000 | 11345455 | 41400957 | 33405775 | 4967745 | 3475880 | 20995624 | 3202560 | 12972 | 0
Fuel Cost | 733580 | 2483611.2 | 0 | 0 | 6496251.66 | 1514110.32 | 1447389.44 | 5310062.2 | 3642310 | 1158966 | 0 | 5791923.54 | 43530226.04 | 4985817.6 | 5552362.56 | 5657908.88 | 2608640.45 | 0 | 2066820 | 313689.6 | 5184000 | 2949367.68 | 18357528 | 4620600.53 | 8257574.4 | 1831014.9 | 5383810.56 | 6342562.8 | 6691175 | 6756552 | 317493 | 431250 | 0 | 0 | 0 | 9421251.84 | 0 | 0 | 0 | 0 | 0 | 3434769 | 0 | 64892168.25 | 0 | 40067211.38 | 0 | 8345577.6 | 7230094.86 | 7616176.96 | 10797340.8 | 11944281.6 | 5807520 | 332921.2 | 0 | 0 | 1848228.2 | 2187931.2 | 6829550 | 4944885 | 3202500 | 1327308.84 | 562344 | 555724.8 | 0 | 220800 | 694972.14 | 781320.48 | 638866.24 | 1121510.74 | 333554.76 | 157545 | 290829 | 246000 | 21905510.4 | 1635300 | 4260557.52 | 311112.34 | 0 | 1376960 | 1453337.6 | 982656 | 895500 | 4010304.27 | 4306205.4 | 990660 | 1489440 | 978120 | 2197726.2 | 0 | 766431.6 | 159030 | 4701843.2 | 386100 | 140299.04 | 465830.4 | 0 | 0 | 0 | 0 | 0 |  | 57861820.5 | 0 | 1917443.52 | 5711904 | 10271904 | 51620659.2 | 0 | 228547.2 | 3113164.8 | 5961999.36 | 4244808.75 | 4520356.83 | 565280.1 | 5618361.6 | 0 | 0 | 0 | 2532098.8 | 3295692.48 | 8952832 | 7906965 | 8075219.2 | 5235540 | 3928320 | 3851093.52 | 508728 | 254815.2 | 186008.526 | 0 | 10295600.15 | 0 | 3299010 | 3666240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 409662706.22 | 213624412.736 | 623287118.956 | 61361231.126 | 57861820.5 | 30732283.13 | 210800297.8 | 10295600.15 | 0 | 230330375.85 | 21905510.4 | 0 | 0
Yesterday Day Peak | 37 | 120 | 0 | 0 | 365 | 88 | 40 | 368 | 217 | 0 | 0 | 380 | 180 | 10 | 40 | 55 | 170 | 0 | 38 | 0 | 15 | 7 | 64 | 30 | 50 | 10 | 40 | 36 | 56 | 55 | 19 | 25 | 30 | 0 | 33 | 42 | 0 | 83 | 80 | 0 | 0 | 16 | 0 | 200 | 0 | 60 | 0 | 42 | 0 | 0 | 68 | 85 | 38 | 16 | 2 | 0 | 120 | 100 | 327 | 327 | 201 | 78 | 0 | 39 | 0 | 10 | 34 | 11 | 0 | 0 | 18 | 0 | 33 | 10 | 116 | 81 | 8 | 20 | 1.9 | 55 | 50 | 50 | 50 | 100 | 266 | 29 | 20 | 47 | 80 | 0 | 11 | 7 | 300 | 22 | 8 | 0 | 149 | 0 | 0 | 150 | 104 |  | 461 | 0 | 0 | 15 | 83 | 120 | 0 | 0 | 0 | 0 | 33 | 192 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 25 | 40 | 43 | 0 | 8 | 0 | 21 | 11 | 11 | 0 | 72 | 125 | 0 | 0 | 192 | 0 | 0 | 181 | 96 | 0 | 0 | 0 |  | 8107.9 | DayPeak
Yesterday Evening Peak | 37 | 120 | 0 | 0 | 365 | 83 | 50 | 365 | 242 | 0 | 0 | 450 | 100 | 100 | 100 | 55 | 175 | 0 | 64 | 0 | 91 | 24 | 149 | 40 | 90 | 0 | 40 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 80 | 0 | 43 | 65 | 80 | 90 | 98 | 45 | 16 | 19 | 0 | 100 | 100 | 310 | 320 | 195 | 76 | 100 | 39 | 0 | 10 | 51 | 86 | 0 | 16 | 19 | 11 | 33 | 20 | 164 | 91 | 64 | 20 | 0 | 56 | 60 | 53 | 50 | 120 | 266 | 62 | 86 | 47 | 78 | 0 | 46 | 9 | 320 | 23 | 8 | 10 | 300 | 0 | 0 | 185 | 104 |  | 461 | 0 | 365 | 97 | 99 | 120 | 0 | 0 | 49 | 60 | 40 | 193 | 29 | 64 | 0 | 0 | 0 | 43 | 38 | 102 | 40 | 43 | 45 | 43 | 43 | 22 | 11 | 11 | 0 | 71 | 120 | 16 | 18 | 140 | 0 | 0 | 185 | 95 | 50 | 0 | 0 |  | 10426 | EvPeak
Forecast for Evening | 37 | 120 | 0 | 0 | 365 | 108 | 78 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 102 | 55 | 200 | 0 | 99 | 100 | 93 | 102 | 149 | 100 | 100 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 89 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 135 | 0 | 51 | 68 | 74 | 80 | 103 | 44 | 16 | 23 | 0 | 150 | 100 | 360 | 360 | 225 | 195 | 0 | 39 | 0 | 10 | 51 | 85 | 48 | 52 | 19 | 11 | 33 | 22 | 164 | 100 | 95 | 22 | 0 | 58 | 62 | 51 | 50 | 163 | 330 | 60 | 86 | 50 | 100 | 0 | 45 | 10 | 341 | 23 | 8 | 200 | 300 | 0 | 0 | 185 | 106 |  | 480 | 32 | 365 | 110 | 99 | 225 | 0 | 54 | 47 | 78 | 40 | 194 | 30 | 110 | 30 | 0 | 0 | 43 | 38 | 102 | 43 | 43 | 46 | 43 | 43 | 22 | 12 | 11 | 0 | 72 | 160 | 17 | 18 | 215 | 0 | 0 | 220 | 95 | 80
Forecast for Day | 37 | 120 | 0 | 0 | 365 | 100 | 78 | 412 | 360 | 98 | 0 | 450 | 150 | 100 | 102 | 55 | 200 | 0 | 99 | 100 | 93 | 102 | 149 | 100 | 100 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 89 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 60 | 0 | 51 | 68 | 74 | 80 | 103 | 44 | 16 | 15 | 0 | 150 | 100 | 360 | 360 | 225 | 78 | 0 | 39 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 8 | 33 | 22 | 124 | 97 | 95 | 22 | 2 | 58 | 62 | 51 | 50 | 163 | 330 | 50 | 86 | 50 | 80 | 0 | 45 | 10 | 341 | 23 | 8 | 0 | 150 | 0 | 0 | 150 | 106 |  | 480 | 0 | 250 | 110 | 99 | 225 | 0 | 0 | 36 | 78 | 40 | 194 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 43 | 43 | 46 | 43 | 0 | 22 | 12 | 11 | 0 | 72 | 160 |  | 18 | 215 | 0 | 0 | 220 | 95 | 80
Generation at 08:00(Today) | 37 | 120 | 0 | 0 | 300 | 27 | 20 | 370 | 250 | 0 | 0 | 430 | 100 | 7 | 14 | 15 | 120 | 0 | 100 | 0 | 7 | 7 | 98 | 10 | 8 | 10 | 12 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 19 | 0 | 83 | 80 | 0 | 0 | 0 | 0 | 189 | 0 | 50 | 0 | 8 | 16 | 15 | 80 | 12 | 24 | 16 | 12 | 0 | 100 | 100 | 335 | 335 | 201 | 76 | 0 | 36 | 0 | 10 | 5 | 21 | 0 | 0 | 19 | 5 | 8 | 13 | 110 | 84 | 8 | 17 | 0.9 | 58 | 60 | 5 | 5 | 163 | 173 | 50 | 20 | 2 | 79 | 0 | 44 | 0 | 320 | 23 | 8 | 0 | 50 | 0 | 0 | 52 | 0 | 0 | 468 | 0 | 250 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 192 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 20 | 25 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 71 | 121 | 0 | 0 | 135 | 0 | 0 | 162 | 32 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6928.3 | 7:00
| Highest Generation |  | 10426 | 21:00
| Day Peak Generation |  | 8107.9 | 12:00
| Evening Peak Generation |  | 10426 | 21:00
| HVDC Max Flow |  | 479 | 9:00
| HVDC EvPeak Flow |  | 461 | 21:00
| Load factor L.F |  | 80.61%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-28
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8107.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6763.4 | MW
Evening Peak Generation : |  | 10426 | MW Hour : | 21:00 | Available Max Generation : |  | 12584 | MW
E.P. Demand (at gen end) : |  | 10426 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10700 | MW
Maximum Generation : |  | 10426 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1884 | MW
Total Gen. (MKWH) : |  | 201.704 | System Load Factor : | 80.61% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -760 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-28
Actual : | 102.48 | Ft.(MSL) , | Rule curve : | 82.92 | Ft.( MSL )
Gas Consumed : | Total = | 1072.01 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 92093514.256
|  | Coal : | 10295600.15 | Oil : | 441130673.65 | Total : | 543519788.056
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3779.7408 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1284.1016 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1150.2952 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1039.3116 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 939.2534 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 757.9412 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 425.3727 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 195.191 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 584.5543 |  |  | 0 | 0%
Total | 0 |  | 10155.7617 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
3) Ghorasal Unit-2,4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Chandraghona-Modunaghat 132 kV Ckt-2 was under shut shut down from 08:17 to 09:27 due to red hot at Y-phase
bus isolator at Madanganj end.
b) Jessore 132 kV capacitor bank was under shut down from 11:35 to 13:16 due to red hot at line isolator.
c) Bheramara 360 MW GT & ST were synchronized at 12:05 & 15:52 respectively.
d) Shahjibazar-Bibiyana 230 kV Ckt-1 was under shut down from 09:49 to 14:08 for D/W.
e) Hasnabad-Meghnaghat 230 kV Ckt-1 was under shut down from 10:04 to 15:33 for C/M.
f) After maintenance Chandpur GT was synchronized at 14:59.
g) Comilla(N)-Shahjibazar 230 kV Ckt-1 was under shut down from 15:40 to 17:52 for D/W.
h) Mongla 132/33 kV T1 & T2 transformers 33 kV incoming breaker tripped at 16:48 showing O/C & E/F and were |  |  |  | About 36MW Power interruption occurred under Mongla S/S
switched on at 16:54. |  |  |  | area from 16:48 to 16:54.
i) Shahjibazar 330 MW CCPP STG was shut down at 02:32(28/06/2018) for all over the cooling system cleaning.
j) Sunamganj 132/33 kV T1 transformer was under shut down from 21:53 to 23:16 for C/M.
k) Madunaghat-Khulshi 132 kV Ckt-1 was shut down at 07:19(28/06/2018) for D/W.
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 37 | 853000 | # 2 Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2887920 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 365 | 7553781
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 50 | 1539776 | Frequency control.
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 83 | 1869272 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 8705020 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 120600 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 242 | 5971000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 450 | 8644662
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 100 | 793920
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 100 | 2865716 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 100 | 831192
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 926008
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 40 | 725369 | Voltage problem
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 423324
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 64 | 1862000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 20160 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 91 | 829440
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 175 | 4013293 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 0 | 114510 | Reserve
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 24 | 447552 | High Voltage
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 40 | 807168 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 889560
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1898400
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 1070588
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 1077600
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 90 | 1378560 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 57 | 1300940 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 693300
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 835300
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 995904
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 300 | 4094830
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 0 | 0 | On test.
| Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 0 | 104 | 2250640 | On test.
| Dhaka area Total |  |  |  | 5199 | 3501 | 69290305
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 362700 | Low demand
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 45 | 888000
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 161 | 3475880 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 195 | 4754005 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 80 | 1828718 | Frequency control.
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 43 | 949440
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 65 | 671318
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 80 | 782752
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1744320 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 391672
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 19 | 410400
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 1848960 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 908 | 18108165
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2031020 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2404320 | Gas shortage
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 195 | 4575000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7505000 | FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7166500 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 39 | 829440 | Engine problem
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 10 | 240000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 76 | 1923636 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 847527
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 86 | 831192
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 58936 | Reserve
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 100 | 585775 | Under maint.
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 433188
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 210060
** | Tripura |  | Imported power | 0 | 160 | 164 | 3202560
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 377700
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 16 | 151147 | Line O/L.
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 328000
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 10 | 26880 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1660 | 33727881
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 91 | 2180400 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 404042
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 64 | 463608 | Low demand
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 12972
| United Mymensingh PPL |  | IPP | 200 | 0 | 185 | 331680 | On test.
| Mymensingh Area Total |  |  |  | 322 | 360 | 3392702
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 56 | 1324000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 60 | 1397440
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 120 | 3108763
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 266 | 6151722 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 53 | 1023600
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 995000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 8 | 184604 | Engine problem
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 62 | 869000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1392000
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 889200
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1927830
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 46 | 824120 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 514800
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 320 | 7346630 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 9 | 171000
| Sylhet Area Total |  |  |  | 1549 | 1284 | 28119709
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 461 | 11345455
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 97 | 865440 | Engine problem
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1533120 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 49 | 276480
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 120 | 3210240 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 506112
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 365 | 2861856 | Gas shortage
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 40 | 666375 | Engine problem
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 0 | 14320 | Reserve
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 50 | 193920 | Engine problem
| Khulna Area Total |  |  |  | 1769 | 1341 | 21473318
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 64 | 909120 | Line O/L.
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 29 | 570990
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 193 | 4566017
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 95 | 2068629
| Barisal Area Total |  |  |  | 462 | 381 | 8114756
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 221144
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 38 | 307434 | Engine problem
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 40 | 914100 | Engine problem
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 907328 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 45 | 491600
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | FGMO
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 185 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 43 | 357576
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 462480
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 271080
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 245718
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 396000 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 102 | 999200
| Rajshahi Area Total |  |  |  | 1123 | 626 | 5573660
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 71 | 1696145
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 120 | 3271600
117 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 143000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 18 | 171000
| Rangpur Area Total |  |  |  | 484 | 225 | 5281745
| Total |  |  |  | 15010 | 10286 | 193082241
| Eastern Grid Total |  |  |  | 11172 | 7713 | 152638762
| Western Grid Total |  |  |  | 3838 | 2573 | 40443479
| National Grid Total |  |  |  | 15010 | 10286 | 193082241
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-27 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6693 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3191 | MW
i) Dhaka area |  |  | 3582 | MW | i) Khulna area |  |  | 1268 | MW
ii) Chittagong area |  |  | 1047 | MW | ii) Rajshahi area |  |  | 1091 | MW
iii) Comilla area |  |  | 932 | MW | iii) Barisal area |  |  | 255 | MW
iv) Mymensingh area |  |  | 724 | MW | iv) Rangpur area |  |  | 577 | MW
v) Sylhet area |  |  | 408 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9884 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 1000 | Netrokona | 88 | 2200 | Central s/s | 70 | 1930
Munsiganj | 102 | 1900 | Jamalpur | 102 | 2200 | Noapara | 74 | 1930
Megnaghat | 44 | 1930 | Sherpur | 86 | 2100 | Jessore | 138 | 2100
Shyampur | 158 | 1300 | Srimongal | 36 | 1930 | Jhenida | 87 | 2100
Bhulta | 165 | 2100 | Shahjibazar | 114 | 2100 | Bottail | 126 | 2000
Madanganj | 48 | 1900 | Fenchuganj | 45 | 2200 | G.K Project | 52 | 1930
Shitalakhya | 108 | 1000 | Kulawara | 41 | 2100 | Faridpur | 144 | 2100
Rahim steel | 3 | 1500 | Sylhet | 134 | 1900 | Madaripur | 126 | 2100
Matuail | 84 | 1000 | Chatak | 23 | 2100 | Gopalganj | 73 | 1930
Ghorasal | 80 | 2100 | Sunamganj | 28 | 100 | Bagerhat | 76 | 2200
Narsingdi | 112 | 2100 | Biani Bazar | 44 | 1930 | Mongla | 36 | 1200
Haripur (SBU) | 80 | 1930 | Comilla (S) | 168 | 2200 | Satkhira | 85 | 2100
Ullon | 87 | 1900 | Comilla(N) | 93 | 2100 | Gallamari | 50 | 2000
Hasnabad | 178 | 2000 | Chandpur | 111 | 2100 | Magura | 42 | 2000
Magbazar | 130 | 1300 | Feni | 110 | 2000 | Chuadanga | 79 | 2100
Maniknagar | 86 | 1300 | Chowmuhani | 172 | 2200 | Barisal | 110 | 2000
Bangabhaban | 40 | 1100 | Ashuganj | 58 | 2200 | Patuakhali | 87 | 2200
Narinda | 78 | 1600 | Daudkandi | 92 | 2200 | Bhandaria | 42 | 2100
Dhanmondi | 119 | 1300 | B.Baria | 124 | 2100 | Ishurdi | 54 | 2100
Lalbag | 48 | 2100 | Ramganj | 29 | 2400 | Ruppur Paromanobik | 1 | 100
Madartek | 98 | 1900 | Madunaghat | 47 | 2100 | Natore | 109 | 2100
Mirpur | 105 | 1200 | Hathazari | 92 | 2000 | Bogra | 226 | 2100
Kalyanpur | 134 | 1300 | Khulshi | 174 | 1600 | Noagaon | 112 | 2100
Gulshan | 79 | 1500 | Halishahar | 132 | 1600 | Rajshahi | 137 | 2100
Uttara | 66 | 1300 | Baraulia | 151 | 1500 | C.Nawabganj | 67 | 2000
Kamrangirchar | 139 | 1900 | Sikalbaha | 36 | 2100 | Amnura | 31 | 100
Savar | 140 | 1900 | Dohazari | 80 | 2200 | Pabna | 111 | 2100
Bhasantec | 43 | 2100 | Cox'sbazar | 86 | 2100 | Shahjadpur | 80 | 2000
Agargaon | 89 | 1900 | Chandraghona | 36 | 2100 | Serajganj | 71 | 2100
Satmosjid | 122 | 1500 | Kaptai | 4 | 2100 | Niyamatpur | 51 | 2100
Tongi | 185 | 1600 | A. Khaer Stl. | 12 | 2000 | Joypurhat | 44 | 2100
Kabirpur | 113 | 1600 | Bakulia | 108 | 1930 | Rangpur | 116 | 100
Basundhara | 86 | 2100 | Julda | 15 | 1500 | Lalmonirhat | 82 | 2000
Manikganj | 224 | 1930 | TK chemical | 6 | 1300 | Saidpur | 104 | 2000
Joydevpur | 107 | 1200 | Modern Steel | 12 | 400 | Purbasadipur | 95 | 2000
New Tongi | 230 | 2100 | Shahmirpur | 30 | 1930 | Thakurgaon | 70 | 2100
Korda | 212 | 2100 | Abul Khair 230 | 190 | 800 | Palashbari | 100 | 2100
Tangail | 155 | 2200 | BSRM | 109 | 1300 | Barapukuria | 46 | 2000
Mymensing | 230 | 2200 | Khagrachhari | 17 | 1930 | Panchagar | 40 | 2000
Kishorganj | 94 | 2200 | Goalpara | 40 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-27
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 393 | 4:00 | 386 | 10:00 | Kaliakoir | 379 | 4:00 | 364 | 15:00
Bheramara | 407 | 18:30 | 397 | 1:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 225 | 1:00 | 218 | 15:00
Ishurdi | 235 | 12:00 | 225 | 5:00 | Comilla (N) | 233 | 6:00 | 227 | 10:00
Ashuganj | 236 | 6:00 | 230 | 16:00 | Hathazari | 222 | 18:30 | 210 | 12:00
Serajganj | 227 | 18:30 | 218 | 22:00 | Megnaghat | 230 | 3:00 | 224 | 12:00
Baghabari | 229 | 9:00 | 220 | 3:00 | Fenchuganj | 239 | 3:00 | 234 | 15:00
Barapukuria | 233 | 6:00 | 224 | 22:00 | Siddhirganj | 225 | 2:00 | 220 | 16:00
Bogra | 226 | 7:00 | 212 | 21:00 | Maniknagar | 224 | 2:00 | 217 | 14:00
Khulna South | 242 | 18:00 | 226 | 20:00 | Old Airport | 226 | 2:00 | 218 | 15:00
Rampura | 223 | 4:00 | 220 | 9:00 | Barisal | 236 | 22:00 | 225 | 19:00
Haripur | 224 | 1:00 | 220 | 11:00 | AKSML | 220 | 3:00 | 205 | 19:00
Hasnabad | 227 | 1:00 | 220 | 11:00 | BSRM | 222 | 3:00 | 211 | 8:00
Aminbazar | 226 | 1:00 | 220 | 12:00 | Bibiyana | 235 | 2:00 | 231 | 8:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 135 | 100 | 132 | 900 | Ramganj | 128 | 2100 | 120 | 2400
Munsiganj | 137 | 1900 | 133 | 1300 | Madanhat | 133 | 600 | 128 | 1200
Megnaghat | 132 | 100 | 130 | 1100 | Hathazari | 131 | 1830 | 125 | 1200
Shyampur | 129 | 100 | 126 | 900 | Khulshi | 128 | 2300 | 120 | 800
Bhulta | 127 | 1830 | 124 | 900 | Halishahar | 131 | 500 | 123 | 800
Madanganj | 126 | 1930 | 131 | 500 | Baraulia | 128 | 2200 | 122 | 1500
Shitalakhya | 138 | 100 | 134 | 1200 | Sikalbaha | 130 | 2200 | 124 | 800
Rahim steal | 134 | 100 | 132 | 1000 | Dohazari | 128 | 2300 | 123 | 1500
Matuail | 135 | 1930 | 131 | 1400 | Cox'sbazar | 126 | 600 | 116 | 1500
Ghorasal | 136 | 100 | 135 | 1000 | Chandraghona | 132 | 500 | 126 | 1500
Narsinghdi | 131 | 400 | 127 | 2100 | Kaptai | 130 | 2400 | 128 | 1500
Haripur (SBU) | 135 | 600 | 132 | 1500 | A. Khaer Stl. | 128 | 400 | 124 | 1000
Ullon | 135 | 100 | 130 | 1300 | Bakulia | 128 | 2300 | 122 | 800
Hasnabad | 137 | 100 | 132 | 900 | Julda | 130 | 2300 | 124 | 1300
Magbazar | 136 | 400 | 130 | 1100 | TK Chemical | 132 | 2300 | 128 | 1600
Maniknagar | 136 | 100 | 131 | 1300 | Modern Steel | 129 | 2200 | 123 | 1200
Bangabhaban | 136 | 100 | 131 | 1300 | Shahmirpur | 129 | 2200 | 123 | 800
Narinda | 136 | 100 | 131 | 1300 | Khagrachhari | 130 | 2200 | 124 | 800
Dhanmondi | 136 | 100 | 131 | 1300 | Goalpara | 137 | 1800 | 130 | 2000
Lalbag | 140 | 200 | 134 | 1600 | Central s/s | 137 | 2300 | 130 | 1900
Madartek | 136 | 500 | 129 | 1400 | Noapara | 136 | 1800 | 125 | 2000
Mirpur | 135 | 400 | 131 | 900 | Jessore | 132 | 1700 | 120 | 2000
Kalyanpur | 137 | 200 | 131 | 1500 | Jhenida | 133 | 1800 | 118 | 2000
Gulshan | 135 | 400 | 131 | 1600 | Bottail | 136 | 900 | 129 | 300
Uttara | 134 | 200 | 127 | 1400 | G.K.Project | 141 | 900 | 133 | 300
Kamrangirchar | 138 | 500 | 132 | 900 | Faridpur | 134 | 1830 | 124 | 2100
Savar | 136 | 200 | 128 | 1200 | Madaripur | 136 | 2300 | 125 | 100
Bhasantec | 134 | 200 | 128 | 1500 | Gopalganj | 139 | 2300 | 126 | 1300
Agargaon | 135 | 200 | 128 | 1600 | Bagerhat | 136 | 1830 | 126 | 2000
Satmosjid | 135 | 400 | 127 | 1400 | Mongla | 134 | 1700 | 125 | 2000
Tongi | 136 | 400 | 130 | 1500 | Satkhira | 134 | 900 | 125 | 2000
Kabirpur | 137 | 800 | 129 | 1500 | Gallamari | 136 | 1700 | 129 | 2000
Basundhara | 133 | 200 | 126 | 900 | Magura | 132 | 1800 | 115 | 2000
Manikganj | 140 | 500 | 131 | 1700 | Chuadanga | 128 | 800 | 111 | 2100
Joydevpur | 138 | 600 | 132 | 1500 | Barisal | 139 | 1700 | 132 | 2100
New Tongi | 136 | 500 | 129 | 900 | Patuakhali | 135 | 1600 | 125 | 200
Kodda | 136 | 1300 | 130 | 700 | Bhandaria | 137 | 1700 | 128 | 2000
Tangail | 136 | 1830 | 128 | 2100 | Ishurdi | 141 | 1800 | 135 | 400
Mymensing | 132 | 600 | 122 | 1900 | Ruppur Paromanobik | 140 | 1800 | 132 | 300
Kishorganj | 130 | 500 | 121 | 2200 | Natore | 138 | 1830 | 129 | 2100
Netrokona | 130 | 500 | 124 | 2000 | Bogra | 134 | 700 | 123 | 2100
Jamalpur | 136 | 900 | 125 | 800 | Noagaon | 130 | 500 | 119 | 2100
Sherpur | 136 | 1100 | 124 | 1900 | Rajshahi | 135 | 1830 | 126 | 2000
Srimongal | 138 | 900 | 135 | 100 | C.Nawabganj | 135 | 1830 | 126 | 500
Shahjibazar | 136 | 1600 | 133 | 800 | Amnura | 136 | 1830 | 128 | 500
Fenchuganj | 136 | 100 | 135 | 700 | Pabna | 135 | 1600 | 126 | 2100
Khulawara | 136 | 700 | 133 | 100 | Shahjadpur | 142 | 1700 | 132 | 1800
Sylhet | 135 | 400 | 132 | 1300 | Serajganj | 135 | 1800 | 127 | 2100
Chatak | 135 | 900 | 132 | 100 | Niyamatpur | 129 | 1830 | 114 | 2100
Sunamganj | 134 | 1600 | 132 | 100 | Joypurhat | 131 | 1830 | 116 | 2100
Biani Bazar | 136 | 600 | 132 | 1200 | Rangpur | 123 | 600 | 107 | 2000
Comilla(s) | 128 | 100 | 121 | 1900 | Lalmonirhat | 118 | 700 | 99 | 2000
Comilla(n) | 136 | 2300 | 133 | 2400 | Saidpur | 121 | 600 | 102 | 2000
Chandpur | 125 | 900 | 115 | 100 | Purbasadipur | 133 | 600 | 120 | 2100
Feni | 120 | 1800 | 114 | 100 | Thakurgaon | 127 | 2000 | 108 | 2100
Chowmuhani | 125 | 700 | 115 | 2400 | Palashbari | 125 | 600 | 112 | 2100
Ashuganj | 137 | 1800 | 134 | 100 | Barapukuria | 133 | 600 | 125 | 2000
Daudkandi | 134 | 1930 | 128 | 1300 | Panchagar | 123 | 600 | 105 | 2100
B.Baria | 137 | 900 | 132 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-06-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 560 | 7237 | 2475 | 9712 |  |  |  | QF-LDC-12
0:30 | 600 | 7195 | 2469.5 | 9664.5 | Date: | 2018-06-27
1:00 | 640 | 7153 | 2464 | 9617
1:30 | 680 | 7035.5 | 2395 | 9430.5
2:00 | 720 | 6918 | 2326 | 9244
2:30 | 710 | 6822.5 | 2153 | 8975.5 | [5 empty] | Gen. at Eve. Peak | 10426 | 10426 MW (21:00 )
3:00 | 700 | 6727 | 1980 | 8707 | [6 empty] | 21:00
3:30 | 710 | 6606.5 | 1932 | 8538.5 | [5 empty] | Gen. at Day Peak | 8107.9 | 8107.9 MW (12:00 )
4:00 | 720 | 6486 | 1884 | 8370 | [6 empty] | 12:00
4:30 | 720 | 6368.5 | 1866.5 | 8235 | [5 empty] | Highest Generation | 10426
5:00 | 720 | 6251 | 1849 | 8100 | [6 empty] | 21:00
5:30 | 580 | 5864 | 1732 | 7596
6:00 | 440 | 5477 | 1615 | 7092
6:30 | 460 | 5422.65 | 1587.5 | 7010.15
7:00 | 480 | 5368.3 | 1560 | 6928.3
7:30 | 470 | 5463.6 | 1557.5 | 7021.1
8:00 | 460 | 5558.9 | 1555 | 7113.9
8:30 | 420 | 5783.95 | 1627 | 7410.95
9:00 | 380 | 6009 | 1699 | 7708
9:30 | 390 | 6122.85 | 1722 | 7844.85
10:00 | 400 | 6236.7 | 1745 | 7981.7
10:30 | 400 | 6155.25 | 1757.5 | 7912.75
11:00 | 400 | 6073.8 | 1770 | 7843.8
11:30 | 400 | 6208.35 | 1767.5 | 7975.85
12:00 | 400 | 6342.9 | 1765 | 8107.9
12:30 | 420 | 6280.45 | 1765 | 8045.45
13:00 | 440 | 6218 | 1765 | 7983
13:30 | 450 | 6324.45 | 1761.5 | 8085.95
14:00 | 460 | 6430.9 | 1758 | 8188.9
14:30 | 450 | 6545.9 | 1773 | 8318.9
15:00 | 440 | 6660.9 | 1788 | 8448.9
15:30 | 440 | 6589.75 | 1766.5 | 8356.25
16:00 | 440 | 6518.6 | 1745 | 8263.6
16:30 | 390 | 6343.2 | 1760 | 8103.2
17:00 | 340 | 6167.8 | 1775 | 7942.8
17:30 | 260 | 6005 | 1850.5 | 7855.5
18:00 | 180 | 5842.2 | 1926 | 7768.2
18:30 | 380 | 6169.6 | 2091 | 8260.6
19:00 | 580 | 6497 | 2256 | 8753
19:30 | 620 | 7299 | 2536 | 9835
20:00 | 460 | 7270 | 2627 | 9897 |  |  |  | Executive Engineer
20:30 | 610 | 7491.5 | 2670 | 10161.5 |  |  |  | Network Operation Division
21:00 | 760 | 7713 | 2713 | 10426
21:30 | 720 | 7633.5 | 2693.5 | 10327
22:00 | 680 | 7554 | 2674 | 10228 |  |  |  |  | Page 6 of 7
22:30 | 580 | 7296 | 2595 | 9891
23:00 | 480 | 7038 | 2516 | 9554
23:30 | 520 | 7137.5 | 2495.5 | 9633
24:00 | 560 | 7237 | 2475 | 9712
10426 MW (21:00 )
8107.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-27 |  | Energy | 201703968
[10 empty] | 2018-06-27 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3482 | 460 | 1863 | 2133 | 191 | 161 | 1264 | 0 | 158
0:30 | 3495 | 467.5 | 1903.5 | 2033.5 | 210.5 | 164 | 1237.5 | 0 | 153 | Date: | 2018-06-27
1:00 | 3508 | 475 | 1944 | 1934 | 230 | 167 | 1211 | 0 | 148
1:30 | 3508.5 | 475 | 1924 | 1847 | 229.5 | 151 | 1148.5 | 0 | 147 | [7 empty] | Total Energy | 201.704 | Total Energy Gen 201.704 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 201.704 MKWHr
2:00 | 3509 | 475 | 1904 | 1760 | 229 | 135 | 1086 | 0 | 146 | [7 empty] | Energy not Served | 0
2:30 | 3421.5 | 475 | 1877.5 | 1684.5 | 230 | 135 | 1009 | 0 | 143 | [7 empty] | Energy Requirement | 201.704
3:00 | 3334 | 475 | 1851 | 1609 | 231 | 135 | 932 | 0 | 140
3:30 | 3330 | 475 | 1841.5 | 1548 | 230.5 | 135 | 843.5 | 0 | 135 | [6 empty] | Shortage
4:00 | 3326 | 475 | 1832 | 1487 | 230 | 135 | 755 | 0 | 130
4:30 | 3329.5 | 475 | 1853 | 1356.5 | 230 | 135 | 731 | 0 | 125
5:00 | 3333 | 475 | 1874 | 1226 | 230 | 135 | 707 | 0 | 120
5:30 | 3322 | 475 | 1704.5 | 975 | 230 | 135 | 635.5 | 0 | 119
6:00 | 3311 | 475 | 1535 | 724 | 230 | 135 | 564 | 0 | 118
6:30 | 3346.5 | 475 | 1497.5 | 646.5 | 222.5 | 136.5 | 570.5 | 0 | 115 |  |  |  |  | Coal
7:00 | 3382 | 475 | 1460 | 569 | 215 | 138 | 577 | 0 | 112
7:30 | 3438 | 475 | 1453.5 | 603 | 206 | 136 | 596 | 0 | 113 |  |  |  | Oil |  |  |  | ,
8:00 | 3494 | 475 | 1447 | 637 | 197 | 134 | 615 | 0 | 114
8:30 | 3449.5 | 477 | 1623.5 | 760.5 | 195.5 | 135.5 | 658 | 0 | 111
9:00 | 3405 | 479 | 1800 | 884 | 194 | 137 | 701 | 0 | 108
9:30 | 3364.5 | 470 | 1740.5 | 1142 | 194.5 | 137 | 688 | 0 | 108
10:00 | 3324 | 461 | 1681 | 1400 | 195 | 137 | 675 | 0 | 108
10:30 | 3311.5 | 461 | 1588 | 1452 | 198 | 137 | 657.5 | 0 | 107
11:00 | 3299 | 461 | 1495 | 1504 | 201 | 137 | 640 | 0 | 106
11:30 | 3350.5 | 461 | 1544 | 1514 | 199 | 150 | 645 | 0 | 111
12:00 | 3402 | 461 | 1593 | 1524 | 197 | 163 | 650 | 0 | 116
12:30 | 3382 | 461 | 1597.5 | 1479 | 194.5 | 162 | 650.5 | 0 | 118
13:00 | 3362 | 461 | 1602 | 1434 | 192 | 161 | 651 | 0 | 120
13:30 | 3362 | 461 | 1602 | 1434 | 192 | 161 | 651 | 0 | 120
14:00 | 3362 | 461 | 1602 | 1434 | 192 | 161 | 651 | 0 | 120
14:30 | 3426 | 461 | 1741 | 1423 | 191 | 160.5 | 687.5 | 0 | 125
15:00 | 3490 | 461 | 1880 | 1412 | 190 | 160 | 724 | 0 | 130
15:30 | 3456.5 | 461 | 1824 | 1420.5 | 188.5 | 160 | 715 | 0 | 129
16:00 | 3423 | 461 | 1768 | 1429 | 187 | 160 | 706 | 0 | 128
16:30 | 3405 | 461 | 1659.5 | 1388.5 | 185 | 160 | 718 | 0 | 125
17:00 | 3387 | 461 | 1551 | 1348 | 183 | 160 | 730 | 0 | 122
17:30 | 3377 | 460.5 | 1496 | 1321.5 | 183.5 | 160 | 732.5 | 0 | 124
18:00 | 3367 | 460 | 1441 | 1295 | 184 | 160 | 735 | 0 | 126
18:30 | 3458.5 | 460.5 | 1571 | 1328.5 | 187 | 160 | 954 | 0 | 141
19:00 | 3550 | 461 | 1701 | 1362 | 190 | 160 | 1173 | 0 | 156
19:30 | 3712 | 465 | 1969 | 1909 | 186 | 160 | 1268 | 0 | 166
20:00 | 3757 | 465 | 1890 | 1997 | 190 | 160 | 1274 | 0 | 164
20:30 | 3830.5 | 463 | 1922.5 | 2149.5 | 190.5 | 160.5 | 1281 | 0 | 164
21:00 | 3904 | 461 | 1955 | 2302 | 191 | 161 | 1288 | 0 | 164
21:30 | 3836.5 | 461 | 1940 | 2291 | 190.5 | 161 | 1281 | 0 | 166
22:00 | 3769 | 461 | 1925 | 2280 | 190 | 161 | 1274 | 0 | 168
22:30 | 3562.5 | 461 | 1864.5 | 2234 | 191 | 161 | 1252 | 0 | 165
23:00 | 3356 | 461 | 1804 | 2188 | 192 | 161 | 1230 | 0 | 162
23:30 | 3419 | 460.5 | 1833.5 | 2160.5 | 191.5 | 161 | 1247 | 0 | 160 | Max Temp. in Dhaka |  | 32.2° C
24:00 | 3482 | 460 | 1863 | 2133 | 191 | 161 | 1264 | 0 | 158
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 201.704 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 201.704 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 87 | 85 | 85 | 85 | 85 | 85 | 88 | 89 | 87 | 87 | 87 | 83 | 81 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 1907880
2 | Kaptai Unit-4 & 5 | 80 | 50 | 50 | 50 | 50 | 50 | 50 | 45 | 50 | 50 | 50 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1568000
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 25 | 25 | 25 | 8 | 8 | 8 | 0 | 0 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 362700
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 204 | 202 | 201 | 201 | 201 | 201 | 207 | 219 | 203 | 195 | 193 | 200 | 200 | 195 | 193 | 196 | 194 | 194 |  | 208 | 193 | 194 | 195 | 195 | 189 | 190 | 4754005
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 80 | 80 | 80 | 80 | 60 | 60 | 60 | 60 | 135 | 100 | 60 | 60 | 60 | 100 | 135 | 80 | 60 | 50 |  | 80 | 60 | 50 | 80 | 80 | 50 | 80 | 1828718
| Dohazari Peaking | 74 | 74 | 76 | 31 | 31 | 0 | [9 empty] | 0 | 16 | 16 |  | 82 | 82 | 81 | 80 | 80 | 77 | 79 | 782752
12 | Hathazari peaking | 64 | 64 | 64 | 32 | 32 | 0 | [9 empty] | 8 | 33 | 33 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 671318
| Daudkandi bangla trak | [17 empty] | 0 |  | 0 | 10 | 10 | 10 | 0 |  |  | 26880
14 | Daudkandi Peaking 52MW | [17 empty] | 0 |  | 26 | 49 | 0 | 0 |  |  |  | 58936
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 102 | 102 | 101 | 102 | 103 | 100 | 100 | 99 | 99 | 37 | 38 | 38 | 38 | 98 | 98 | 37 | 37 | 36 |  | 65 | 62 | 37 | 64 | 103 | 38 | 85 | 1862000
17 | Siddhirganj CCPP-335 MW | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 150 | 150 | 110 |  | 110 | 140 | 140 | 175 | 170 | 120 | 120 | 4013293
18 | Summit Gazipur | 303 | 303 | 303 | 303 | 150 | 48 | 47 | 48 | 48 | 145 | 148 | 149 | 99 | 48 | 50 | 98 | 100 | 100 |  | 100 | 140 | 215 | 300 | 300 | 300 | 300 | 4094830
19 | Ashuganj 195MW Modular | 86 | 86 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 76 | 76 | 76 | 76 | 1923636
20 | Ghorasal ST: Unit-1,2 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 853000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2887920
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 280 | 280 | 280 | 280 | 280 | 320 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 365 | 320 | 270 |  | 300 | 330 | 318 | 365 | 365 | 200 | 250 | 7553781
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2031020
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2404320
32 | Ashuganj Engines TSK | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 38 | 829440
33 | Ashuganj CCPP 225 MW | 183 | 184 | 183 | 183 | 183 | 183 | 200 | 208 | 183 | 183 | 185 | 201 | 193 | 197 | 180 | 183 | 183 | 182 |  | 207 | 183 | 198 | 195 | 183 | 183 | 184 | 4575000
34 | Ashuganj CCPP(South) | 305 | 305 | 305 | 305 | 305 | 301 | 325 | 342 | 301 | 301 | 301 | 327 | 312 | 320 | 315 | 300 | 257 | 250 |  | 255 | 301 | 327 | 320 | 270 | 231 | 301 | 7166500
| Ashuganj CCPP(North) | 300 | 300 | 300 | 300 | 300 | 300 | 325 | 342 | 300 | 300 | 301 | 327 | 305 | 320 | 303 | 295 | 252 | 250 |  | 257 | 280 | 280 | 310 | 290 | 290 | 270 | 7505000
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | [14 empty] | 20 | 30 | 30 | 30 |  | 75 | 70 | 91 | 100 | 100 | 100 | 100 | 585775
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 370 | 375 | 365 | 365 | 368 | 370 | 371 | 375 | 385 | 408 | 300 |  | 300 | 384 | 370 | 365 | 342 | 320 | 320 | 8705020
40 | Meghnaghat CCPP 450MW | 350 | 350 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 301 | 380 | 380 | 380 | 380 | 400 | 400 | 350 |  | 450 | 450 | 450 | 450 | 450 | 360 | 360 | 8644662
41 | Haripur Power CCPP 360MW | 252 | 257 | 261 | 281 | 311 | 311 | 280 | 281 | 255 | 245 | 234 | 217 | 218 | 211 | 221 | 227 | 237 | 251 |  | 261 | 262 | 247 | 242 | 221 | 221 | 252 | 5971000
42 | Mymensingh RPCL 210MW | 85 | 99 | 100 | 99 | 99 | 99 | 97 | 97 | 97 | 98 | 82 | 81 | 77 | 67 | 68 | 83 | 94 | 99 |  | 95 | 100 | 96 | 91 | 85 | 87 | 87 | 2180400
43 | Haripur NEPC 110MW | 55 | 0 | [17 empty] | 26 | 40 | 0 | 0 |  |  |  | 120600
44 | Fenchugonj CCPP-1 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 58 | 52 | 56 | 54 | 55 | 53 | 58 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 58 | 53 | 1324000
45 | Fenchugonj CCPP-2 | 62 | 63 | 63 | 63 | 63 | 60 | 60 | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 60 | 60 | 60 | 59 |  | 59 | 59 | 60 | 60 | 60 | 60 | 60 | 1397440
46 | Shajibazar 330 MW | 283 | 285 | 281 | 284 | 289 | 267 | 275 | 285 | 271 | 266 | 263 | 266 | 270 | 269 | 264 | 262 | 263 | 260 |  | 276 | 260 | 270 | 266 | 260 | 263 | 223 | 6151722
47 | Shahjibazar GT: Unit- 8, 9 | 31 | 20 | 31 | 20 | 20 | 20 | 20 | 30 | 30 | 20 | 30 | 29 | 29 | 29 | 54 | 50 | 51 | 52 |  | 62 | 40 | 56 | 62 | 36 | 51 | 56 | 869000
48 | Shahjibazar 86MW | 86 | 86 | 40 | 40 | 40 | 10 | 10 | 10 | 84 | 50 | 20 | 20 | 20 | 50 | 84 | 84 | 40 | 40 |  | 75 | 86 | 86 | 86 | 86 | 86 | 86 | 1392000
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 45 | 45 | 10 | 10 | 10 | 40 | 45 | 46 | 47 | 47 | 46 | 46 | 47 | 20 | 20 |  | 10 | 47 | 47 | 47 | 47 | 47 | 47 | 889200
50 | Sylhet GT 150 MW | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 78 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 78 | 78 | 78 | 79 | 80 | 1927830
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 42 | 10 | 10 | 11 | 10 | 44 | 43 | 44 | 22 | 12 |  | 43 | 43 | 45 | 46 | 46 | 45 | 45 | 824120
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 |  |  | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 6 |  | 6 | 6 | 5 | 9 | 10 | 10 | 10 | 171000
54 | Hobiganj 11MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 3 | 8 | 8 | 8 | 8 | 8 | 8 | 184604
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 27 | 47 | 50 | 50 | 53 | 53 | 50 | 50 | 22 | 22 |  | 13 | 53 | 53 | 53 | 53 | 53 | 53 | 1023600
56 | Shahjahanulla 25 MW | 23 | 20 | 20 | 23 | 23 | 23 | 15 | 23 | 23 | 23 | 15 | 22 | 22 | 22 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 514800
57 | Summit Bibiana- 2 | 300 | 290 | 280 | 280 | 300 | 280 | 310 | 320 | 290 | 270 | 270 | 300 | 310 | 290 | 320 | 270 | 270 | 265 |  | 260 | 265 | 260 | 320 | 270 | 260 | 310 | 7346630
58 | Southern 55MW | 55 | 55 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 36 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1077600
59 | Sikalbaha (Energis) | 51 | 51 | 51 | 51 | 51 | 8 | 8 | 8 | 26 | 33 | 33 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 43 | 51 | 51 | 51 | 949440
60 | Barabkunda (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 391672
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 423324
62 | Tangail (Doreen) 22MW | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 0 | 0 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 404042
63 | Tripura | 148 | 146 | 140 | 130 | 120 | 118 | 112 | 114 | 108 | 108 | 106 | 116 | 120 | 128 | 130 | 128 | 122 | 126 |  | 156 | 166 | 164 | 164 | 168 | 162 | 158 | 3202560
64 | Malancha, Ctg. EPZ (United) | 31 | 29 | 38 | 37 | 41 | 39 | 34 | 11 | 5 | 3 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 5 |  | 5 | 8 | 13 | 19 | 27 | 27 | 22 | 410400
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 433188
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 3 | 8 | 11 | 8 | 8 | 5 | 11 | 11 | 0 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 5 | 11 | 11 | 11 | 11 | 210060
67 | Jangalia (Summit) 33MW | [10 empty] | 12 | 33 | 33 | 33 | 33 | 33 | 8 | 8 |  | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 377700
68 | Summit Comilla 25MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 10 | 15 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 328000
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 30 | 31 | 31 | 29 | 30 | 30 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 725940
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 |  | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 693300
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 835300
73 | Ghorashal (Regent) | 88 | 88 | 88 | 88 | 88 | 56 | 54 | 54 | 88 | 87 | 87 | 88 | 87 | 88 | 88 | 85 | 56 | 31 |  | 37 | 81 | 83 | 83 | 86 | 87 | 87 | 1869272
76 | Siddhirganj (Desh) | [19 empty] | 10 | 17 | 0 | 0 |  |  |  | 20160
77 | Siddhirganj (Dutch Bangla) | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 15 | 15 | 15 | 15 | 16 | 40 | 30 | 30 |  | 30 | 50 | 50 | 91 | 91 | 91 | 91 | 829440
78 | Gazipur (RPCL) | 50 | 50 | 50 | 24 | 24 | 8 | 8 | 14 | 34 | 38 | 41 | 42 | 42 | 46 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 42 | 995904
79 | Kodda 150MW | 98 | 64 | 34 | 15 | 15 | 15 | 15 | 32 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 98 | 98 | 98 |  | 80 | 149 | 149 | 149 | 149 | 149 | 149 | 1898400
80 | Jamalpur 95MW | 32 | 32 | 8 | 8 | 8 | 0 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 32 | 56 | 64 | 64 | 64 | 64 | 463608
81 | Lakdhanvi 52 MW | [15 empty] | 13 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 151147
82 | Madanganj 102MW | 0 | 10 | 16 | 16 | 16 | 16 | 15 | 15 | 15 | 15 | 24 | 40 | 15 | 15 | 15 | 26 | 30 | 31 |  | 30 | 50 | 64 | 100 | 100 | 64 | 64 | 831192
83 | Pagla (DPA ) | [9 empty] | 21 | 10 | 10 | 10 | 11 | 10 | 10 | 10 | 11 |  | 10 | 11 | 0 | 0 |  |  |  | 114510
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 51 | 51 | 11 | 11 | 11 | 80 | 11 | 11 | 11 | 11 | 85 | 85 | 85 | 42 | 21 |  | 86 | 85 | 85 | 86 | 85 | 86 | 85 | 831192
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 10 | 10 | 0 |  |  | 0 | 30 | 30 | 30 | 30 | 87 | 100 | 30 | 10 | 10 |  | 10 | 10 | 40 | 40 | 100 | 100 | 70 | 725369
86 | Meghnaghat CCPP(Summit) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 140 | 140 | 100 | 110 | 180 | 200 | 135 | 140 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2865716
87 | Meghnaghat (IEL) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 11 | 35 | 10 | 7 | 7 | 12 | 42 | 40 | 35 |  | 25 | 75 | 70 | 100 | 100 | 100 | 100 | 793920
88 | Ghorashal 78MW (MAX) | 74 | 73 | 74 | 74 | 74 | 50 | 50 | 50 | 60 | 60 | 40 | 40 | 40 | 60 | 70 | 50 | 40 | 40 |  | 40 | 73 | 50 | 50 | 76 | 74 | 74 | 1539776
90 | Ashuganj (United) 53MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 240000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 20 | 24 | 80 | 80 | 80 | 68 | 80 | 80 | 80 | 80 | 80 | 80 |  | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 1744320
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 50 | 10 | 10 | 10 | 47 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 |  | 28 | 50 | 50 | 50 | 50 | 50 | 50 | 995000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 40 | 6 | 6 | 6 | 10 | 25 | 30 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 847527
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 40 | 24 | 24 | 7 |  | 7 | 24 | 20 | 24 | 50 | 50 | 50 | 447552
95 | Patenga 50MW | 43 | 43 | 43 | 44 | 44 | 35 | 8 | 6 | 12 | 36 | 38 | 38 | 35 | 36 | 36 | 37 | 37 | 43 |  | 44 | 44 | 44 | 45 | 45 | 45 | 45 | 888000
96 | Chittagong ECPV 108 MW | 105 | 105 | 105 | 60 | 52 | 12 | 12 | 12 | 12 | 73 | 85 | 85 | 92 | 92 | 92 | 92 | 92 | 70 |  | 78 | 90 | 98 | 98 | 98 | 100 | 105 | 1848960
97 | Katpotti 51 MW | 39 | 39 | 39 | 39 | 39 | 6 | 6 | 6 | 6 | 33 | 41 | 40 | 40 | 12 | 14 | 39 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 807168
98 | Bosila 108MW | 90 | 90 | 90 | 90 | 30 | 8 | 8 | 8 | 30 | 91 | 50 | 50 | 37 | 16 | 48 | 51 | 51 | 51 |  | 63 | 90 | 90 | 90 | 90 | 90 | 90 | 1378560
99 | Madanganj-55 MW | 55 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 49 | 55 | 55 | 55 | 55 | 30 | 30 | 30 |  | 30 | 50 | 50 | 55 | 55 | 55 | 55 | 926008
100 | Northern 55 MW | 55 | 55 | 18 | 18 | 18 | 18 | 0 | 18 | 43 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1070588
101 | Kushiara 163 MW CCPP GT | 163 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 163 | 100 | 100 | 100 | 163 | 163 | 100 | 100 | 100 |  | 130 | 163 | 120 | 120 | 120 | 100 | 130 | 3108763
102 | Sarishabari (Solar) | [5 empty] | 0 | 0.3 | 0.9 | 0 | 0.7 | 0.8 | 1.9 | 0 | 0.9 | 1.9 | 1.6 | 0.8 | 0.2 |  | 0 | 0 | 0 |  |  |  |  | 12972
103 | Banco Energy 54MW | 54 | 54 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 36 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 54 | 54 | 54 | 54 | 54 | 54 | 889560
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 189 | 189 | 189 | 189 | 170 | 72 | 32 | 32 | 50 | 150 | 150 | 150 | 100 | 100 | 100 | 125 | 125 | 125 |  | 125 | 175 | 185 | 185 | 185 | 197 | 187 | 331680
112 | Aggreko Aurahati 100MW | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 106 | 105 | 104 | 106 | 104 | 105 | 104 | 103 | 105 | 105 | 105 |  | 106 | 104 | 104 | 104 | 0 |  |  | 2250640
113
114
115
116
117
118 | Eastern Zone Total | 7153 | 6918 | 6727 | 6486 | 6251 | 5477 | 5368.3 | 5558.9 | 6009 | 6236.7 | 6073.8 | 6342.9 | 6218 | 6430.9 | 6660.9 | 6518.6 | 6167.8 | 5842.2 | 0 | 6497 | 7299 | 7270 | 7713 | 7554 | 7038 | 7237 | 152638762
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 46 | 32 | 5 | 5 | 5 | 5 | 5 | 5 | 39 | 45 | 40 | 15 | 45 | 39 | 46 | 46 | 27 | 10 |  | 10 | 57 | 57 | 97 | 95 | 97 | 97 | 865440
124 | Khulna (KPCL-2) | 99 | 100 | 85 | 68 | 66 | 16 | 16 | 16 | 17 | 80 | 83 | 83 | 83 | 49 | 49 | 49 | 49 | 49 |  | 49 | 85 | 83 | 99 | 83 | 93 | 99 | 1533120
125
126 | Khulna (Aggreko) 55MW | [20 empty] | 12 | 0 |  |  |  |  | 14320
127 | Faridpur Peaking | [17 empty] | 17 |  | 50 | 50 | 50 | 49 | 50 | 48 | 48 | 276480
128 | Khulna CCPP 225MW | 150 | 150 | 150 | 150 | 150 | 120 | 120 | 120 | 120 | 145 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3210240
129
130
131
132
133
| Summit Barisal 110 MW | 81 | 48 | 48 | 48 | 48 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 28 | 32 | 32 | 32 |  | 25 | 64 | 64 | 64 | 80 | 48 | 48 | 909120
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 96 | 97 | 97 | 96 | 95 | 61 | 11 | 12 | 93 | 98 | 96 | 96 | 95 | 95 | 95 | 96 | 98 | 98 |  | 70 | 96 | 95 | 95 | 93 | 95 | 70 | 2068629
137 | Bhola CCPP 194MW | 186 | 187 | 186 | 189 | 180 | 194 | 196 | 191 | 190 | 176 | 190 | 192 | 189 | 188 | 189 | 188 | 189 | 154 |  | 188 | 170 | 192 | 193 | 182 | 185 | 181 | 4566017
| Bhola (Venture) 33MW | 33 | 33 | 30 | 29 | 29 | 23 | 17 | 16 | 16 | 20 | 20 | 20 | 17 | 22 | 23 | 15 | 19 | 17 |  | 27 | 29 | 29 | 29 | 35 | 37 | 12 | 570990
140 | Bangla Trak Noapara | [20 empty] | 30 | 30 | 50 | 50 | 10 | 10 | 193920
141 | Noapara (KZA) 40MW | 40 | 40 | 40 | 40 | 40 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 24 | 8 | 24 | 33 | 8 | 8 |  | 16 | 40 | 40 | 40 | 40 | 40 | 40 | 666375
142 | Gopalganj Peaking | 52 | 47 | 30 | 14 | 0 | [9 empty] | 0 | 9 | 10 | 18 |  | 58 | 58 | 83 | 60 | 60 | 60 | 55 | 506112
143 | Bheramara GT-1,2,3 | 16 | 0
144
145 | Bheramara HVDC | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 475 | 479 | 461 | 461 | 461 | 461 | 461 | 461 | 461 | 461 | 460 |  | 461 | 465 | 465 | 461 | 461 | 461 | 460 | 11345455
146 | Bheramara 360 MW | 157 | 157 | 0 | [10 empty] | 49 | 30 | 35 | 120 | 330 |  | 360 | 355 | 355 | 365 | 355 | 258 | 280 | 2861856
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 70 | 71 | 71 | 71 | 71 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 69 | 68 | 67 | 66 | 67 |  | 70 | 69 | 70 | 71 | 70 | 70 | 70 | 1696145
151 | Barapukuria Unit-3 | 160 | 158 | 160 | 159 | 159 | 159 | 143 | 125 | 122 | 123 | 129 | 125 | 122 | 125 | 122 | 120 | 117 | 117 |  | 120 | 117 | 120 | 120 | 120 | 122 | 121 | 3271600
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | 43 | 0 | [15 empty] | 0 |  | 0 | 0 | 43 | 43 | 43 | 43 | 43 | 221144
| Sirajgonj Unit-1 225MW (Gas) | 178 | 174 | 171 | 173 | 178 | 171 | 179 | 189 | 190 | 174 | 172 | 192 | 188 | 184 | 191 | 174 | 172 | 159 |  | 137 | 143 | 140 | 140 | 135 | 135 | 135 | 4304018
157 | Sirajgonj Unit-1 225MW (Oil) | [24 empty] | 0
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 173 | 170 | 168 | 169 | 173 | 168 | 175 | 184 | 179 | 171 | 168 | 181 | 182 | 180 | 187 | 170 | 169 | 151 |  | 153 | 178 | 174 | 185 | 169 | 167 | 174 | 4317709
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | 38 | 25 | 0 | [6 empty] | 0 | [6 empty] | 5 | 13 |  | 38 | 38 | 38 | 38 | 38 | 38 | 37 | 307434
161 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 17 | 21 | 21 | 22 | 18 | 20 | 22 | 20 | 10 |  | 10 | 22 | 22 | 22 | 22 | 18 | 22 | 462480
162 | Bogra (EPL) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 271080
163 | Ullapara (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 |  | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 245718
164 | Amnura 50MW | 40 | 40 | 40 | 40 | 40 | 33 | 33 | 33 | 40 | 40 | 40 | 40 | 33 | 40 | 40 | 40 | 25 | 25 |  | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 914100
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 16 | 16 | 16 |  | 16 | 25 | 43 | 43 | 43 | 43 | 43 | 907328
166 | Katakhali Peaking | 45 | 45 | 45 | 45 | 45 | 0 | [11 empty] | 0 |  | 47 | 47 | 47 | 45 | 45 | 45 | 45 | 491600
167 | Santahar Peaking | 41 | 42 | 26 | 0 | [13 empty] | 0 |  | 41 | 42 | 43 | 43 | 42 | 42 | 42 | 357576
168 | Rajlanka 52 MW | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 25 | 25 | 43 | 43 | 43 | 25 | 396000
169 | Chapainawabganj-100 MW | 100 | 90 | 25 | 0 | [6 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 90 | 102 | 102 | 102 | 102 | 102 | 102 | 999200
170
171
172 | Rangpur GT | 15 | 15 | 15 | 0 | [13 empty] | 0 |  | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 143000
173 | Saidpur GT | 18 | 18 | 18 | 18 | 0 | [12 empty] | 0 |  | 18 | 18 | 18 | 18 | 19 | 18 | 18 | 171000
175
176
177
178 | Western Zone Total | 2464 | 2326 | 1980 | 1884 | 1849 | 1615 | 1560 | 1555 | 1699 | 1745 | 1770 | 1765 | 1765 | 1758 | 1788 | 1745 | 1775 | 1926 | 0 | 2256 | 2536 | 2627 | 2713 | 2674 | 2516 | 2475 | 49065206
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953