## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:May 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-05-05 |  | 2023-04-01 |  | 2022-05-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14511 | 2023-05-30 | 15648 | 2023-04-19 | 13954 | 2022-05-16 | 15648 | 2023-04-19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
2 | Minimum Generation (MW) | 4959 | 2023-05-18 | 5602 | 2023-04-01 | 4396 | 2022-05-21 | - | -
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 14511 | 2023-05-30 | 15648 | 2023-04-19 | 13954 | 2022-05-16 | 15648 | 2023-04-19
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 15395 | 2023-05-08 | 13415 | 2023-04-19 | 11993 | 2022-05-24 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15600 | 2023-05-31 | 16221 | 2023-04-30 | 13954 | 2022-05-16 | 16096 | 2023-04-19
|  |  | 21:00 |  | 19:30 |  | 12:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 12886.871 |  | 12833.0667 |  | 12277.0968
7 | Average Generation (MW) at Day Peak | 11447.9032 |  | 11504.2 |  | 10010.6129
8 | Maximum Power Import from India, BIPTC (MW) | 961 | 2022-05-05 | 936 | 2023-04-24 | 934 | 2022-05-26 | 956 | 27/3/2019
|  |  | 22:30 |  | 11:30 |  | 7:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 180 | 2022-05-28 | 165 | 2023-04-04 | 174 | 2022-05-18 | 194 | 12/06/19
|  |  | 16:00 |  | 19:00 |  | 18:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 1995 | 2023-05-15 | 1291 | 2023-04-16 | - | - | 4395 | 04/10/2022
|  |  | 20:00 |  | 21:00 |  | - |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 11496 | 2023-05-15 | 14599 | 2023-04-16 | - | - | 13200 | 04/10/2022
|  | - | 20:00 | - | 21:00 | - | - |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-05-01 | 0 | 2023-04-01 | - | -
|  |  | 21:00 |  | 21:00
13 | Generation During Min. Load Shed (MW) at Evening Peak | 11274 | 2023-05-01 | 10593 | 2023-04-01 | - | -
|  |  | 21:00 |  | 21:00
14 | Maximum Load Shed (MW) at Day Peak | 2489 | 2023-05-16 | 1167 | 2023-04-15 | - | -
|  |  | 12:00 |  | 21:00
15 | Generation During Max. Load Shed (MW) at Day Peak | 10144 | 2023-05-16 | 12715 | 2023-04-15 | - | -
|  |  | 12:00 |  | 21:00
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-05-01 | 0 | 2023-04-01 | - | -
|  |  | 21:00 |  | 12:00
17 | Generation During Min. Load Shed (MW) at Day Peak | 9578 | 2023-05-01 | 9272 | 2023-04-01 | - | -
|  |  | 21:00 |  | 12:00
18 | Nos. of Days Load Shed at Evening Peak | 23 |  | 21 |  | -
19 | Nos. of Days Load Shed at Day Peak | 25 |  | 15 |  | -
20 | Gross Generation of BPDB (MKWH) | 1885.6965 |  | 1652.1779 |  | 1760.1344 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 62.0427 |  | 47.9101 |  | 75.5671
22 | Net Generation of BPDB (MKWH) | 1823.6538 |  | 1604.2678 |  | 1684.5673
23 | Net Generation of IPP (MKWH) | 4615.9365 |  | 4861.0541 |  | 4686.772
24 | Net Generation of REB (MKWH) | 122.5788 |  | 114.4874 |  | 117.2486
24 | Net Generation of Rental Power Plant (MKWH) | 357.0366 |  | 397.804 |  | 517.426
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6919.2058 |  | 6977.6134 |  | 7006.0139 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4252.0612 |  | 4284.183 |  | 4216.1115 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 161.3514 |  | 117.8792 |  | 296.4446 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1442.64 |  | 1634.0628 |  | 1740.5311 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 9.6847 |  | 9.4966 |  | 27.4557 |  | 104.66 | Sep-22
30 | Energy Generation by Solar (MKWH) | 48.4734 |  | 47.6176 |  | 33.0386 |  | 40.58 | March-22
31 | Energy Generation by Coal (MKWH) | 1067.0377 |  | 932.2843 |  | 767.9994 |  | 950.96 | Sep'22
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 766.1342 |  | 678.729 |  | 725.8023 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 80.7771 |  | 74.4409 |  | 83.2694 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:May 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14511 | 2023-05-30 | 21:00
Generation Period
| Dhaka | MW | 5036.85
| Chattogram | MW | 1399
| Cumilla | MW | 1283
| Mymensingh | MW | 1087
| Sylhet | MW | 614
a) | Total supply in East zone | MW | 9419.85
| Khulna | MW | 1669.8
| Barisal | MW | 399
| Rajshahi | MW | 1378
| Rangpur | MW | 880
b) | Total supply in West zone | MW | 4326.8
c) | Total supply in both zone ( a+b) | MW | 13746.65
Ref: | 27.21.0000.603.16.087.20.674 | Date: 18/06/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:May 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 500 | 2023-05-02 | 19:00
| b) Ishurdi end | MW | 418 | 2023-05-23 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1160 | 2023-05-11 | 19:30
| b) Ishurdi end | MW | 58 | 2023-05-12 | 22:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.48
| b) Ishurdi end | MKWH | 104.23
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | -
| b) Ishurdi end | MKWH | -
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW
| b)Serajganj end | MW | 700 | 2023-05-12 | 15:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 450 | 2023-05-17 | 8:00
| b)Sirajganj end | MW | 16 | 2023-05-02 | 19:30
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.02
| b)Sirajganj end | MKWH | 230.642
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 227.8
| b)Sirajganj end | MKWH | 0.02
30 | Transmission loss of EWI /NO-2 | % | 1.153
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/14 | Page: 1/3 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2023 | Month: May 2023
Name of the | Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station | Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
| Bogura | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-05-01 09:31 | 2023-05-01 10:36 | 1:05 | E/O | Red hot | 0 | 0
| Bogura | Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-05-01 09:29 | 2023-05-01 10:37 | 1:08 | E/O | Red Hot | 0 | 0
| Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-05-24 11:22 | 2023-05-24 14:45 | 3:23 | E/O | T-3 33KV Extension Bus coupler Isolator (R-Phase) Loop Maintenance work. | 6 | 20.3
| Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-05-11 21:54 | 2023-05-11 22:40 | 0:46 | E/O | Inst O/C , Ins E/F due to Thundering and rain fall | 0 | 0
| Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-05-24 11:22 | 2023-05-24 14:45 | 3:23 | E/O | T-3 33KV Extension Bus coupler Isolator (R-Phase) Loop Maintenance work. | 6 | 20.3
| Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-4 LT | 2023-05-08 23:49 | 2023-05-08 23:59 | 0:10 | E/O | T-3 / T-4 33KV bus coupler flashing. | 26 | 4.3333
| Bogura | Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-05-12 11:05 | 2023-05-12 11:57 | 0:52 | T | 432B G.C.B Braker Faulty. | 0 | 0
| Bogura | Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-05-12 11:58 | 2023-05-13 13:41 | 25:43 | E/O | Breaker faulty. | 0 | 0
| Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-05-18 06:30 | 2023-05-18 07:37 | 1:07 | T | Fasitola feeder fault | 5 | 5.5833
| Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2023-05-18 06:30 | 2023-05-18 07:37 | 1:07 | T | Fasitola feeder fault | 5 | 5.5833
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-05-08 07:06 | 2023-05-08 08:18 | 1:12 | E/O | Red Hot has become visible at R-phase of 33kV T3+T4 section BUS DS | 0 | 0
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-05-17 07:21 | 2023-05-17 09:02 | 1:41 | E/O | Red Hot has become visible at T-4 132kV BUS DS(DS-441). | 0 | 0
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-05-22 21:32 | 2023-05-22 23:25 | 1:53 | E/O | 33 KVBus Red hot | 25 | 47.0833
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-05-31 08:35 | 2023-05-31 10:20 | 1:45 | E/O | T3-T4, 33Kv Bus Cuppler Red hot. | 24 | 42
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-05-08 07:05 | 2023-05-08 08:18 | 1:13 | E/O | Red Hot has become visible at R-phase of 33kV T3+T4 section BUS DS | 15 | 18.25
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-05-17 07:20 | 2023-05-17 09:03 | 1:43 | E/O | Red Hot has become visible at T-4 132kV BUS DS(DS-441). | 10 | 17.1667
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-05-22 21:32 | 2023-05-22 23:25 | 1:53 | E/O | 33 KVBus Red hot | 25 | 47.0833
| Bogura | Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-05-31 08:34 | 2023-05-31 10:21 | 1:47 | E/O | T3-T4 33 kv Bus Cuppler Red hot. | 26 | 46.3667
| Bogura | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T HT | 2023-05-06 11:09 | 2023-05-06 12:17 | 1:08 | E/O | Red hot maintenance work at 33KV NESCO CB PGCB. | 0 | 0
| Bogura | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2023-05-04 09:15 | 2023-05-04 11:22 | 2:07 | E/O | Cable Fault at 33KV Side. | 0 | 0
| Bogura | Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-5, 424T LT | 2023-05-06 11:09 | 2023-05-06 12:19 | 1:10 | E/O | Red hot maintenance work at 33KV NESCO CB PGCB end. | 0 | 0
| Bogura | Panchagarh 132/33kV Grid Sub-Station | 407T HT | 2023-05-23 13:25 | 2023-05-23 14:26 | 1:01 | T | Due to storm suddenly. | 0 | 0
| Bogura | Panchagarh 132/33kV Grid Sub-Station | 407T HT | 2023-05-25 22:29 | 2023-05-25 22:58 | 0:29 | T | Heavy rain & storm | 0 | 0
| Bogura | Panchagarh 132/33kV Grid Sub-Station | 407T LT | 2023-05-23 13:25 | 2023-05-23 14:26 | 1:01 | T | Due to storm suddenly. | 0 | 0
| Bogura | Panchagarh 132/33kV Grid Sub-Station | 407T LT | 2023-05-25 22:29 | 2023-05-25 22:59 | 0:30 | T | Heavy rain & storm. | 0 | 0
| Bogura | Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-05-10 20:06 | 2023-05-10 22:24 | 2:18 | E/O | T1 - 33Kv B-Phase bussing Red hot maintenance | 0 | 0
| Bogura | Chapai 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-05-10 20:03 | 2023-05-10 22:26 | 2:23 | E/O | T1-33 Kv Bussing red hot maintenance | 0 | 0
| Bogura | Chapai 132/33kV Grid Sub-Station | T-3 (425T) HT | 2023-05-06 21:38 | 2023-05-06 22:49 | 1:11 | E/O | Red Hot maintenance | 18 | 21.3
| Bogura | Chapai 132/33kV Grid Sub-Station | T-3 (425T) HT | 2023-05-22 23:52 | 2023-05-23 01:15 | 1:23 | E/O | Red Hot Maintenance | 20 | 27.6667
| Bogura | Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-05-06 21:38 | 2023-05-06 22:49 | 1:11 | E/O | 33 KV T-03 bus section DS red Hot maintenance | 18 | 21.3
| Bogura | Chapai 132/33kV Grid Sub-Station | T-3 (425T) LT | 2023-05-22 23:51 | 2023-05-23 01:17 | 1:26 | E/O | Red Hot Maintenance | 20 | 28.6667
| Bogura | Chapai 132/33kV Grid Sub-Station | T-4 (435T) HT | 2023-05-06 21:38 | 2023-05-06 22:49 | 1:11 | E/O | 33 kv bus section red hot maintenance | 7 | 8.2833
| Bogura | Chapai 132/33kV Grid Sub-Station | T-4 (435T) HT | 2023-05-22 11:53 | 2023-05-23 01:14 | 13:21 | E/O | Red Hot Maintenance | 5 | 66.75
| Bogura | Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2023-05-06 21:38 | 2023-05-06 22:49 | 1:11 | E/O | 33 kv bus section red hot maintenance | 7 | 8.2833
| Bogura | Chapai 132/33kV Grid Sub-Station | T-4 (435T) LT | 2023-05-22 13:52 | 2023-05-23 01:16 | 11:24 | E/O | Red Hot Maintenance | 5 | 57
| Bogura | Naogaon 132/33kV Grid Sub-Station | T-1 LT | 2023-05-16 18:41 | 2023-05-16 20:45 | 2:04 | T | stormy weather and thundering. | 36 | 74.4
| Bogura | Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-05-16 18:41 | 2023-05-16 20:26 | 1:45 | T | stormy weather and thundering. | 36 | 63
| Bogura | Naogaon 132/33kV Grid Sub-Station | T-3 HT | 2023-05-06 10:18 | 2023-05-06 12:20 | 2:02 | E/O | Emergency redhot maintenance of NESCO Baludanga 33 kV feeder on T3 33 kV bus. | 0 | 0
| Bogura | Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-05-06 10:17 | 2023-05-06 12:22 | 2:05 | E/O | Emergency redhot maintenance of NESCO Baludanga 33 kV feeder on T3 33 kV bus. | 35 | 72.9167
| Bogura | Naogaon 132/33kV Grid Sub-Station | T-3 LT | 2023-05-16 18:41 | 2023-05-16 19:10 | 0:29 | E/O | stormy weather and thundering. | 42 | 20.3
| Bogura | Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2023-05-08 08:42 | 2023-05-08 09:28 | 0:46 | E/O | Red hot problem chapai feeder under T-1 33 KV Bus side | 0 | 0
| Bogura | Niamatpur 132/33kV Grid Sub-Station | 407T HT | 2023-05-09 16:04 | 2023-05-09 17:59 | 1:55 | E/O | 33 kV bus Red hot. | 0 | 0
| Bogura | Niamatpur 132/33kV Grid Sub-Station | 407T LT | 2023-05-08 08:42 | 2023-05-08 09:28 | 0:46 | E/O | Red hot problem chapai feeder under T-1 33 KV Bus side | 21 | 16.1
| Bogura | Niamatpur 132/33kV Grid Sub-Station | 407T LT | 2023-05-09 16:04 | 2023-05-09 18:00 | 1:56 | E/O | 33kV bus Red hot. | 24 | 46.4
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-05-02 11:50 | 2023-05-02 16:02 | 4:12 | E/O | Gas leakage testing of 33kV TR-01 | 0 | 0
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-05-08 11:20 | 2023-05-08 17:47 | 6:27 | E/O | Tr-01 33 Kv CB (408B) Gas leakage Restoration. | 0 | 0
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-05-18 15:56 | 2023-05-18 18:31 | 2:35 | E/O | Heavy flashing and Red hot on 33kv T-1 Bus. | 13.5 | 34.875
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-05-31 14:41 | 2023-05-31 16:30 | 1:49 | E/O | Gas leakage of tr-1 33KV CB | 10 | 18.1667
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T HT | 2023-05-31 17:41 | 2023-05-31 19:02 | 1:21 | E/O | Gas leakage of tr-1 33KV CB | 10 | 13.5
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-05-02 11:49 | 2023-05-02 16:03 | 4:14 | E/O | Gas leakage testing of 33kV TR-01 | 0 | 0
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-05-08 11:20 | 2023-05-08 17:48 | 6:28 | E/O | Tr-01 33 Kv CB (408B) Gas leakage Restoration. | 0 | 0
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-05-18 15:56 | 2023-05-18 18:32 | 2:36 | E/O | Heavy flashing and Red hot on 33kv T-1 Bus. | 13.5 | 35.1
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-05-31 11:52 | 2023-05-31 16:31 | 4:39 | E/O | Gas leakage of T1 33kv CB | 0 | 0
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-05-31 17:40 | 2023-05-31 19:03 | 1:23 | E/O | Gas leakage of tr-1 33KV CB | 10 | 13.8333
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 416T HT | 2023-05-17 14:24 | 2023-05-17 15:37 | 1:13 | E/O | Due to flasing in 33KV BUS section-1,maintenance work done by NESCO & PBS . | 32 | 38.9333
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 416T LT | 2023-05-17 14:22 | 2023-05-17 15:38 | 1:16 | E/O | Due to flasing in 33KV BUS section-1,maintenance work done by NESCO & PBS . | 32 | 40.5333
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 33 KV BUS | 2023-05-17 14:28 | 2023-05-17 15:32 | 1:04 | E/O | Due to flasing in 33KV BUS section-1,maintenance work done by NESCO & PBS . | 32 | 34.1333
| Bogura | Jaldhaka 132/33kV Grid Sub-Station | 33 KV BUS | 2023-05-18 16:00 | 2023-05-18 18:28 | 2:28 | E/O | Heavy flashing and Red hot on 33kv T-1 Bus. | 0 | 0
| Bogura | Kurigram 132/33kV Grid Sub-Station | Transformer T-1 (Tr-403T) HT | 2023-05-08 23:02 | 2023-05-08 23:40 | 0:38 | E/O | TR-01 Transformer R-phase LT bushing red-hot. | 12 | 7.6
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) HT | 2023-05-26 09:21 | 2023-05-26 11:25 | 2:04 | E/O | Bus isolator connector changing works of Nilphamari Nesco-1 33kV feeder. | 0 | 0
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) HT | 2023-05-28 13:13 | 2023-05-28 15:04 | 1:51 | E/O | For 33kv EPZ Feeder Work. | 0 | 0
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-05-26 09:20 | 2023-05-26 11:26 | 2:06 | E/O | Bus isolator connector changing works of Nilphamari Nesco-1 33kV feeder. | 0 | 0 |  | 3.2
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-05-28 10:54 | 2023-05-28 10:58 | 0:04 | T | 33kv EPZ Feeder Fault. | 48 | 3.2 |  | 4.8
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-05-28 13:12 | 2023-05-28 15:05 | 1:53 | E/O | For 33kv EPZ Feeder Work. | 0 | 0 |  | 63
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-05-04 09:48 | 2023-05-04 11:42 | 1:54 | E/O | NESCO, Saidpur, Golahat 33 KV Bus coupler Isolator Red hot | 16 | 30.4 |  | 74.4
| Bogura | Saidpur 132/33kV Grid Sub-Station | TR-3 (424T) LT | 2023-05-28 10:54 | 2023-05-28 11:00 | 0:06 | T | 33kv EPZ Feeder Fault. | 48 | 4.8 |  | 5.5833
[5 empty] | Total : | 162:25 |  | Unserved Energy: |  | 1081.4917 |  | 5.5833
| Page: 2/4 | [8 empty] | QF-LDC-26 |  | 156.5667
Chattogram Grid Circle :
122 | Chattogram | Bakulia 132/33kV Grid Sub-Station | T-3 (422T) HT | 2023-05-04 10:12 | 2023-05-04 11:51 | 1:39 | T | Overcurrent, Earthfault at 33KV side. | 0 | 0
126 | Chattogram | Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2023-05-15 08:20 | 2023-05-25 13:06 | 244:46 | E/O | Increasing of transformer capacity(G2G project work). | 0 | 0
127 | Chattogram | Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T HT | 2023-05-26 12:55 | 2023-05-26 14:11 | 1:16 | E/O | Increasing Transformer Capacity. | 0 | 0
129 | Chattogram | Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T LT | 2023-05-26 12:54 | 2023-05-26 14:12 | 1:18 | E/O | Increasing Transformer Capacity. | 0 | 0
130 | Chattogram | Khulshi 132/33kV Grid Sub-Station | 405T (T1) HT | 2023-05-31 05:31 | 2023-05-31 06:48 | 1:17 | E/O | Due to red hot detection | 0 | 0
131 | Chattogram | Khulshi 132/33kV Grid Sub-Station | 405T (T1) LT | 2023-05-31 05:31 | 2023-05-31 06:48 | 1:17 | E/O | Due to red hot detection | 0 | 0
133 | Chattogram | Rampur 230/132/33 kV GIS Grid Sub-Station | 132kV BUS-02 | 2023-05-28 09:31 | 2023-05-28 10:48 | 1:17 | E/O | gas filling at 263GC1 | 0 | 0
137 | Chattogram | Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 HT | 2023-05-11 16:54 | 2023-05-11 17:41 | 0:47 | E/O | Due to break bird nest. With the approval of Grid Incharge & BPDB Authorized person. | 0 | 0
138 | Chattogram | Sholosohor 132/33kV Grid Sub-Station | TRAFO-01 HT | 2023-05-13 10:50 | 2023-05-14 01:26 | 14:36 | E/O | auxliary transformer -2 fuse maintenance | 0 | 0
155 | Chattogram | Khagrachori 132/33kV Grid Sub-Station | TR-1 LT | 2023-05-12 19:51 | 2023-05-12 20:09 | 0:18 | T | Fault occured at Matiranga feeder and Trip coil failure of Matiranga 33kV Breaker. | 7 | 2.1
156 | Chattogram | Khagrachori 132/33kV Grid Sub-Station | TR-2 LT | 2023-05-12 19:51 | 2023-05-12 20:09 | 0:18 | T | Fault occured at Matiranga feeder and Trip coil failure of Matiranga 33kV Breaker. | 7 | 2.1
159 | Chattogram | Coxsbazar 132/33kV Grid Sub-Station | 405T-T1 HT | 2023-05-09 18:38 | 2023-05-09 18:56 | 0:18 | T | Over Load (Over Current) | 70 | 21
160 | Chattogram | Coxsbazar 132/33kV Grid Sub-Station | 415T-T2 LT | 2023-05-08 20:15 | 2023-05-08 20:26 | 0:11 | T | Overload | 50 | 9.1667
164 | Chattogram | Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-05-21 22:32 | 2023-05-21 23:44 | 1:12 | E/O | Red Hot maintenance at 33kv BUS by PDB Satkania. | 45 | 54
166 | Chattogram | Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2023-05-21 22:32 | 2023-05-21 23:44 | 1:12 | E/O | Red Hot maintenance at 33kv BUS by PDB Satkania. | 45 | 54
167 | Chattogram | Kalurghat 132/33kV Grid Sub-Station | TRFO-01(506T) LT | 2023-05-27 15:49 | 2023-05-28 17:48 | 25:59 | T | B PH Fault | 0 | 0
[5 empty] | Total : | 297:41 |  | Unserved Energy: |  | 142.3667
Cumilla Grid Circle :
185 | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-05-15 20:50 | 2023-05-15 23:40 | 2:50 | T | Under ground cable fault | 0 | 0
186 | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-05-16 13:26 | 2023-05-16 15:42 | 2:16 | E/O | 33 kv side cable maintenance work | 0 | 0
188 | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-05-15 20:50 | 2023-05-15 23:42 | 2:52 | T | Under ground cable fault. | 0 | 0
189 | Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-05-16 13:26 | 2023-05-16 15:43 | 2:17 | E/O | 33 kv side cable maintenance work | 0 | 0
191 | Cumilla | Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-05-15 23:08 | 2023-05-15 23:33 | 0:25 | T | 33kv reb-2 and doreen 22MW feeder fault | 19 | 7.9167
193 | Cumilla | Ramganj 132/33kV Grid Sub-Station | Transformer -02 HT | 2023-05-07 17:47 | 2023-05-07 18:28 | 0:41 | E/O | Red Hot work of Tr-2 33 KV Bus-02 (Raipur feeder DS) Of Transformer.-02 | 40 | 27.3333
194 | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-05-16 22:03 | 2023-05-16 22:15 | 0:12 | T | Nabinogor feeder fault. | 0 | 0
195 | Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | 403T LT | 2023-05-23 16:12 | 2023-05-23 16:20 | 0:08 | E/O | 33kv side voltage problem | 0 | 0
200 | Cumilla | Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-05-22 10:33 | 2023-05-22 11:45 | 1:12 | E/O | Red-hot maintenance | 12 | 14.4
201 | Cumilla | Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-05-22 10:31 | 2023-05-22 11:46 | 1:15 | E/O | Red-hot maintenance | 12 | 15
202 | Cumilla | Kulaura 132/33kV Grid Sub-Station | TR-1 LT | 2023-05-31 04:17 | 2023-05-31 04:58 | 0:41 | T | due to 33kv comolganj feedef fault | 30 | 20.5
203 | Cumilla | Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2023-05-31 04:17 | 2023-05-31 04:58 | 0:41 | T | Due to 33kV comolganj feeder fault | 30 | 20.5
204 | Cumilla | Shahjibazar 132/33kV Grid Sub-Station | TR-02 LT | 2023-05-08 10:30 | 2023-05-08 10:34 | 0:04 | T | BPDB Hobiganj old feeder trip. | 20 | 1.3333
206 | Cumilla | Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-05-02 09:01 | 2023-05-02 09:38 | 0:37 | E/O | For emergency load cintrol As Instructed By NLDC. | 32 | 19.7333
215 | Cumilla | Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2023-05-13 09:40 | 2023-05-13 09:55 | 0:15 | E/O | Tr-3 33kV Breaker SF6 Gass refill work. | 0 | 0
216 | Cumilla | Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 LT | 2023-05-13 09:40 | 2023-05-13 09:55 | 0:15 | E/O | Tr-3 33kV Breaker SF6 Gass refill work. | 0 | 0
220 | Cumilla | Chhatak 132/33kV Grid Sub-Station | T-1 LT | 2023-05-16 16:04 | 2023-05-16 16:10 | 0:06 | T | 33kv Sunamganj Feeder Fault | 0 | 0
229 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T1 LT | 2023-05-18 08:03 | 2023-05-18 09:35 | 1:32 | T | 33kv Bus section -2 - Bus PT (R-phase) burst | 19 | 29.1333
230 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T2 HT | 2023-05-04 11:55 | 2023-05-04 12:34 | 0:39 | T | 33 kV Shekhghat CT Burst | 50 | 32.5
231 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T2 HT | 2023-05-18 08:03 | 2023-05-18 12:58 | 4:55 | T | 33kv Bus section -2 - Bus PT (R-phase) burst. | 34 | 167.1667
232 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T2 LT | 2023-05-04 11:55 | 2023-05-04 12:35 | 0:40 | T | 33 KV Shekhghat CT Burst | 50 | 33.3333
233 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T2 LT | 2023-05-18 08:03 | 2023-05-18 12:58 | 4:55 | T | 33kv Bus section -2 - Bus PT (R-phase) burst | 34 | 167.1667
235 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-05-04 11:55 | 2023-05-04 12:37 | 0:42 | T | 33 KV Shekhghat CT Burst | 33 | 23.1
236 | Cumilla | Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-05-18 08:03 | 2023-05-18 09:34 | 1:31 | T | 33kv Bus section -2 - Bus PT (R-phase) burst | 22 | 33.3667
[5 empty] | Total : | 31:41 |  | Unserved Energy: |  | 612.4833
Dhaka (North) Grid Circle :
243 | Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-05-21 20:38 | 2023-05-21 21:16 | 0:38 | T | distance protection relay operated in source side (zone-1,y-phase) | 20 | 12.6667
247 | Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-05-21 20:38 | 2023-05-21 21:16 | 0:38 | T | kabirpur - manikganj circuit -1 distance protection relay operation ( zone-1, Y- Phase). | 20 | 12.6667
249 | Dhaka (N) | Bhaluka 132/33kV Grid Sub-Station | Transformer- 01 LT | 2023-05-29 08:17 | 2023-05-29 08:36 | 0:19 | T | 33 kv Feeder no 13 trip | 55 | 17.4167
251 | Dhaka (N) | Bhaluka 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-05-29 08:17 | 2023-05-29 08:36 | 0:19 | T | 33 kv Feeder no 13 trip | 55 | 17.4167
259 | Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-05-08 10:28 | 2023-05-08 11:25 | 0:57 | T | 33KV AT-1 R-Phase cable Blust | 40 | 38
261 | Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-05-13 14:18 | 2023-05-13 19:11 | 4:53 | E/O | GT-2 Fault | 50 | 244.1667
277 | Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 33 kV BUS | 2023-05-20 15:40 | 2023-05-20 17:16 | 1:36 | E/O | PBS issue | 38 | 60.8
280 | Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-05-23 13:32 | 2023-05-23 16:12 | 2:40 | E/O | 33 kV bus maintenance by PBS | 20 | 53.3333
281 | Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-05-23 13:32 | 2023-05-23 16:12 | 2:40 | E/O | 33 kV bus maintenance by PBS | 20 | 53.3333
285 | Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-05-23 12:34 | 2023-05-23 16:12 | 3:38 | E/O | 33 kV bus maintenance by PBS | 20 | 72.6667
287 | Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | T-02 HT | 2023-05-12 02:30 | 2023-05-12 12:28 | 9:58 | E/O | X-former LT side neutral grounding fail | 20 | 199.3333
288 | Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | T-02 LT | 2023-05-12 02:30 | 2023-05-12 12:30 | 10:00 | E/O | X-former LT side neutral grounding fail | 20 | 200
302 | Dhaka (N) | Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan HT | 2023-05-26 06:32 | 2023-05-26 06:48 | 0:16 | T | over current , earth fault | 0 | 0
303 | Dhaka (N) | Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan HT | 2023-05-26 12:06 | 2023-05-26 17:10 | 5:04 | T | over current, earth fault | 0 | 0
304 | Dhaka (N) | Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan LT | 2023-05-26 06:32 | 2023-05-26 06:50 | 0:18 | T | over current, earth fault | 0 | 0
305 | Dhaka (N) | Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan LT | 2023-05-26 12:06 | 2023-05-26 17:11 | 5:05 | T | over current, earth fault | 0 | 0
306 | Dhaka (N) | Ashuganj 230/132/33kV Sub-Station | T-3 Kalabagan LT | 2023-05-30 08:07 | 2023-05-30 08:27 | 0:20 | T | Over Current, Earth fault | 0 | 0
307 | Dhaka (N) | Kallyanpur 132/33kV Grid Sub-Station | GT-3 (132kV) HT | 2023-05-07 16:51 | 2023-05-07 16:57 | 0:06 | E/O | TO Remove foreign partical. | 0 | 0
308 | Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-05-19 04:50 | 2023-05-19 07:23 | 2:33 | E/O | Old tower dismantling work in Switch yard | 0 | 0
309 | Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-05-19 04:47 | 2023-05-19 07:23 | 2:36 | E/O | Old tower dismantling work | 0 | 0
310 | Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | T2 HT | 2023-05-19 04:50 | 2023-05-19 07:24 | 2:34 | E/O | Old tower dismantling work in Switch yard | 0 | 0
311 | Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | T2 LT | 2023-05-19 04:47 | 2023-05-19 07:24 | 2:37 | E/O | Old tower dismantling work in Switch yard | 0 | 0
312 | Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | T3 HT | 2023-05-19 04:51 | 2023-05-19 07:25 | 2:34 | E/O | Old tower dismantling work in Switch yard | 0 | 0
313 | Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | T3 LT | 2023-05-19 04:48 | 2023-05-19 07:25 | 2:37 | E/O | Old tower dismantling work in Switch yard | 0 | 0
320 | Dhaka (N) | Savar 132/33kV Grid Sub-Station | T-3 LT | 2023-05-06 06:53 | 2023-05-06 07:02 | 0:09 | T | 33 KV feeder fault | 0 | 0
323 | Dhaka (N) | Savar 132/33kV Grid Sub-Station | Bus-B | 2023-05-08 10:07 | 2023-05-08 16:13 | 6:06 | E/O | 33 kV DPBS-3 maintenance work | 0 | 0
324 | Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2023-05-08 13:19 | 2023-05-08 15:59 | 2:40 | E/O | Shutdown taken by Tangail PBS due to red hot maintenance work. | 120 | 320
326 | Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 LT | 2023-05-08 13:19 | 2023-05-08 16:01 | 2:42 | E/O | Shutdown taken by Tangail PBS due to red hot maintenance work. | 120 | 324
331 | Dhaka (N) | Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 HT | 2023-05-09 22:58 | 2023-05-10 01:02 | 2:04 | E/O | Redhot | 0 | 0
332 | Dhaka (N) | Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 LT | 2023-05-09 22:57 | 2023-05-10 01:02 | 2:05 | E/O | Red Hot | 0 | 0
333 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-05-05 00:30 | 2023-05-05 02:38 | 2:08 | E/O | Red hot to T1 & T2 X-former 33KV bus B-phase,Work by Jamalpur PBS | 25 | 53.3333
334 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-05-11 23:43 | 2023-05-12 01:25 | 1:42 | E/O | 33 kv switching-01 feeder 33kv bus to D.S Loop replace work due to red hot. | 10 | 17
336 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-05-18 04:34 | 2023-05-18 04:46 | 0:12 | T | 33kv Nandina feeder faulty | 2 | 0.4
338 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-05-05 00:30 | 2023-05-05 02:38 | 2:08 | E/O | Red hot to T1 & T2 X-former 33KV bus B-phase,Work by Jamalpur PBS | 25 | 53.3333
339 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-05-11 23:43 | 2023-05-12 01:25 | 1:42 | E/O | 33 kv switching-01 feeder 33kv bus to D.S Loop replace work due to red hot. | 10 | 17
341 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-05-18 04:34 | 2023-05-18 04:46 | 0:12 | T | 33kv Nandina feeder Faulty | 2 | 0.4
343 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-05-05 00:30 | 2023-05-05 02:38 | 2:08 | E/O | Red hot to T1 & T2 X-former 33KV bus B-phase,Work by Jamalpur PBS | 25 | 53.3333
344 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-05-11 23:43 | 2023-05-12 01:25 | 1:42 | E/O | 33 kv switching-01 feeder 33kv bus to D.S Loop replace work due to red hot. | 10 | 17
346 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-05-18 04:34 | 2023-05-18 04:46 | 0:12 | T | 33kv Nandina feeder faulty. | 2 | 0.4
347 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-05-05 00:30 | 2023-05-05 02:38 | 2:08 | E/O | Red hot to T1 & T2 X-former 33KV bus B-phase,Work by Jamalpur PBS | 25 | 53.3333
348 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-05-11 23:43 | 2023-05-12 01:25 | 1:42 | E/O | 33 kv switching-01 feeder 33kv bus to D.S Loop replace work due to red hot. | 10 | 17
350 | Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-05-18 04:34 | 2023-05-18 04:46 | 0:12 | T | 33kv Nandina feeder faulty. | 2 | 0.4
353 | Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Tr-1 (404T) LT | 2023-05-24 20:39 | 2023-05-24 21:58 | 1:19 | E/O | T-2, Bus-section Y-phase Red hot of bpdb | 70 | 92.1667
354 | Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-05-19 06:17 | 2023-05-19 06:28 | 0:11 | E/O | T-2 ,33Kv Bushing Side yarn is Remove From Y-B,Phase | 0 | 0
355 | Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) HT | 2023-05-29 15:03 | 2023-05-29 15:53 | 0:50 | E/O | T-02 Transfomer bushing Y- Phase temperature high | 0 | 0
356 | Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Tr-2 (414T) LT | 2023-05-29 15:03 | 2023-05-29 15:54 | 0:51 | E/O | T-02 Transformer Bushing Y- phase temperature high | 0 | 0
367 | Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) HT | 2023-05-27 13:38 | 2023-05-27 13:46 | 0:08 | E/O | Transportation of T-3 transformer | 0 | 0
368 | Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-05-27 13:37 | 2023-05-27 13:47 | 0:10 | E/O | Transportation of T-3 transformer | 0 | 0
375 | Dhaka (N) | Sherpur 132/33kV Grid Sub-Station | Transformer- 02 HT | 2023-05-16 13:52 | 2023-05-16 14:53 | 1:01 | E/O | SPBS Bay-03 33 Kv Bus side Red hot | 16 | 16.2667
376 | Dhaka (N) | Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-05-16 13:52 | 2023-05-16 14:54 | 1:02 | E/O | SPBS Work | 16 | 16.5333
377 | Dhaka (N) | Sherpur 132/33kV Grid Sub-Station | Transformer- 03 HT | 2023-05-24 09:43 | 2023-05-24 12:23 | 2:40 | E/O | T-04 bus Extension | 10 | 26.6667
378 | Dhaka (N) | Sherpur 132/33kV Grid Sub-Station | Transformer- 03 LT | 2023-05-24 09:42 | 2023-05-24 12:24 | 2:42 | E/O | T-04 Bus Extension | 10 | 27
380 | Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-28 09:26 | 2023-05-28 10:00 | 0:34 | T | 33kV Korotiya Feeder fault | 32 | 18.1333
382 | Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-28 09:26 | 2023-05-28 10:03 | 0:37 | T | 33kV Korotiya Feeder fault | 32 | 19.7333
384 | Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-28 09:26 | 2023-05-28 10:02 | 0:36 | T | 33kV Korotiya Feeder fault | 32 | 19.2
385 | Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-4 HT | 2023-05-30 10:35 | 2023-05-30 11:12 | 0:37 | E/O | Work on 33kv shakhipur feeder | 0 | 0
386 | Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-4 LT | 2023-05-30 10:34 | 2023-05-30 11:12 | 0:38 | E/O | Work on 33kv shakhipur feeder | 0 | 0
[5 empty] | Total : | 110:46 |  | Unserved Energy: |  | 2144.4333
Dhaka (South) Grid Circle :
394 | Dhaka (S) | Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2023-05-23 18:02 | 2023-05-23 18:07 | 0:05 | T | 230kV Siddirganj - Maniknagar line-1 Trip | 0 | 0
431 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-02 14:45 | 2023-05-02 15:39 | 0:54 | E/O | PBS 33kv Sonargaon feeder corrective maintenance work. | 25 | 22.5
432 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-20 09:07 | 2023-05-20 10:24 | 1:17 | E/O | T1 33 kv busbar Redhot maintenance near 33 kv buscoupler | 30 | 38.5 | 22.5
433 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-01 16:03 | 2023-05-01 16:35 | 0:32 | T | Due to PBS 33kv Sonargaon Feeder fault. | 25 | 13.3333 | 38.5
434 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-02 14:45 | 2023-05-02 15:39 | 0:54 | E/O | PBS 33kv Sonargaon feeder corrective maintenance work. | 25 | 22.5 | 13.3333
435 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-20 09:07 | 2023-05-20 10:24 | 1:17 | E/O | Near 33 kv buscupler Redhot maintenance | 30 | 38.5 | 22.5
436 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-30 09:32 | 2023-05-30 10:58 | 1:26 | T | Auxiliary -01 trip due to Bird drop in Fuse, Fuse Phase R,Y loop out. | 31 | 44.4333 | 38.5
437 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-30 13:56 | 2023-05-30 14:23 | 0:27 | T | Over load | 70 | 31.5 | 44.4333
438 | Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-01 16:03 | 2023-05-01 16:34 | 0:31 | T | Due to PBS 33kv Sonargoan feeder fault. | 31 | 16.0167
448 | Dhaka (S) | Lalbag 132/33kV Grid Sub-Station | Tr-Load LT | 2023-05-30 09:30 | 2023-05-30 10:40 | 1:10 | E | Maintenance | 0 | 0
449 | Dhaka (S) | Lalbag 132/33kV Grid Sub-Station | Tr-Load LT | 2023-05-30 12:46 | 2023-05-30 12:51 | 0:05 | T | Overload | 45 | 3.75
454 | Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-2 HT | 2023-05-10 06:49 | 2023-05-10 08:41 | 1:52 | E/O | Due to red hot maintenance Bay 105 | 0 | 0
456 | Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-05-10 06:49 | 2023-05-10 08:42 | 1:53 | E/O | Due to red hot maintenance Bay 105 | 0 | 0
457 | Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-05-27 14:13 | 2023-05-27 14:19 | 0:06 | E/O | Due to sparking of 33kv Bus coupler DS | 6 | 0.6
464 | Dhaka (S) | Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2023-05-16 20:25 | 2023-05-16 21:36 | 1:11 | T | PBS Feeder Trip | 0 | 0
[5 empty] | Total : | 13:40 |  | Unserved Energy: |  | 231.6333
HVDC Grid Circle :
467 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bus-1 | 2023-05-18 10:38 | 2023-05-18 14:25 | 3:47 | E/O | Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1) | 0 | 0
469 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-05-05 15:15 | 2023-05-05 17:54 | 2:39 | T | short ckt by snake | 33 | 87.45
470 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-05-05 15:15 | 2023-05-05 17:54 | 2:39 | T | Short ckt by snake | 33 | 87.45
471 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-05-05 15:50 | 2023-05-06 15:41 | 23:51 | E/O | Maintenance Work | 0 | 0
472 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-05-07 11:36 | 2023-05-07 12:10 | 0:34 | E/O | 132/33 kv T-1 LT Bushing Burn | 28 | 15.8667
473 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-05-05 15:15 | 2023-05-06 15:48 | 24:33 | T | Short ckt by snake | 28 | 687.4
474 | HVDC | Ishurdi 132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-05-07 11:36 | 2023-05-07 12:10 | 0:34 | E/O | Bushing Burn | 28 | 15.8667
479 | HVDC | Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 HT | 2023-05-18 11:00 | 2023-05-18 14:31 | 3:31 | E/O | Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1) | 0 | 0
480 | HVDC | Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 LT | 2023-05-18 10:40 | 2023-05-18 14:33 | 3:53 | E/O | Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1) | 0 | 0
482 | HVDC | Pabna 132/33kV Grid Sub-Station | T-1 LT | 2023-05-02 12:50 | 2023-05-02 12:57 | 0:07 | T | 33 KV Pailanpur (NESCO) Trip by DIR. O/C Trip and DIR. E/F Trip. | 35 | 4.0833
483 | HVDC | Ruppur 132/11kV Grid Sub-Station | TR-02 HT | 2023-05-24 12:48 | 2023-05-25 17:32 | 28:44 | E/O | 11kv Transformer Feeder-2 Trip | 0 | 0
484 | HVDC | Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-05-25 12:40 | 2023-05-25 13:50 | 1:10 | E/O | Red Maintenance | 0 | 0
485 | HVDC | Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-05-06 19:40 | 2023-05-06 20:25 | 0:45 | E/O | Red-hot Maintenance R-Phase LT Bushing . | 8 | 6
486 | HVDC | Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2023-05-25 17:26 | 2023-05-25 18:21 | 0:55 | E/O | Maintenance of PBS feeder | 10 | 9.1667
493 | HVDC | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-05-16 19:04 | 2023-05-17 01:46 | 6:42 | E/O | 33 kV T1A incommer trip for 33kV kaligonj feeder(WZPDCL) loop disconnect | 25 | 167.5
494 | HVDC | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 HT | 2023-05-25 17:29 | 2023-05-25 19:12 | 1:43 | E/O | Red hot maintenance 33kV kaligonj feeder (WZPDCL) | 30 | 51.5
495 | HVDC | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-05-16 18:45 | 2023-05-17 01:47 | 7:02 | T | Due to 33kV feeder fault | 1 | 7.0333
496 | HVDC | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-05-25 16:56 | 2023-05-25 19:12 | 2:16 | E/O | Red hot maintenance 33kV kaligonj feeder (WZPDCL) | 30 | 68
497 | HVDC | Jhenaidah 132/33kV Grid Sub-Station | Transformer T-2 LT | 2023-05-16 18:45 | 2023-05-16 19:16 | 0:31 | T | Due to 33kV feeder fault | 1 | 0.51667
498 | HVDC | Kushtia 132/33kV Grid Sub-Station | T2 HT | 2023-05-01 07:12 | 2023-05-01 08:34 | 1:22 | E/O | 33 KV Poradah Feeder Red Hot Maintenance By PBS Kushtia . | 35 | 47.8333
500 | HVDC | Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-05-01 07:11 | 2023-05-01 08:35 | 1:24 | E/O | 33 KV Poradah Feeder Red Hot Maintenance By PBS,Kushtia . | 35 | 49
502 | HVDC | Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-05-24 14:15 | 2023-05-24 15:16 | 1:01 | E/O | Under ground cable maintenance. | 20 | 20.3333
503 | HVDC | Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-05-24 17:36 | 2023-05-24 19:17 | 1:41 | E/O | PBS one feeder under ground cable maintenance. | 25 | 42.0833
504 | HVDC | Magura 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-05-24 14:14 | 2023-05-24 15:17 | 1:03 | E/O | Under ground cable maintenance. | 20 | 21
505 | HVDC | Magura 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-05-24 17:36 | 2023-05-24 19:18 | 1:42 | E/O | PBS one feeder under ground cable maintenance. | 25 | 42.5
[5 empty] | Total : | 124:09 |  | Unserved Energy: |  | 1430.5833
Khulna Grid Circle :
506 | Khulna | Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-05-15 10:24 | 2023-05-15 10:56 | 0:32 | T | Due to 33kv Nolcity(PBS),Muladi (PBS) Feeder fault | 72 | 38.4
507 | Khulna | Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-05-15 10:24 | 2023-05-15 10:57 | 0:33 | T | Due to 33kv Nolcity(PBS),Muladi (PBS) Feeder fault | 72 | 39.6
508 | Khulna | Barishal 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-05-15 11:42 | 2023-05-15 13:28 | 1:46 | E/O | For check the transformer | 0 | 0
509 | Khulna | Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-05-15 10:24 | 2023-05-15 13:29 | 3:05 | T | Due to 33kv Nolcity(PBS),Muladi (PBS) Feeder fault | 72 | 222
511 | Khulna | Barishal 230/132kV Grid Sub-Station | 230kV BUS | 2023-05-13 10:18 | 2023-05-13 13:12 | 2:54 | E/O | Connecting 230kv BUS-1 to GIS Bay | 0 | 0
514 | Khulna | Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-05-26 08:26 | 2023-05-26 09:08 | 0:42 | E/O | Red hot maintenances | 0 | 0
516 | Khulna | Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-05-26 08:26 | 2023-05-26 09:09 | 0:43 | E/O | Red hot maintenances | 0 | 0
518 | Khulna | Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-03 HT | 2023-05-22 11:02 | 2023-05-23 17:59 | 30:57 | E/O | Project work | 0 | 0
519 | Khulna | Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-03 LT | 2023-05-22 10:59 | 2023-05-23 18:01 | 31:02 | E/O | Project work | 0 | 0
520 | Khulna | Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 HT | 2023-05-22 11:01 | 2023-05-23 18:00 | 30:59 | E/O | Project work | 0 | 0
521 | Khulna | Payra 400/132/33kV Grid Sub-Station | 132/33 kV Transformer-04 LT | 2023-05-22 11:00 | 2023-05-23 18:02 | 31:02 | E/O | Project work | 0 | 0
529 | Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-05-01 16:29 | 2023-05-01 16:52 | 0:23 | T | REB-6&7 fault | 10 | 3.8333
533 | Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-05-01 06:44 | 2023-05-01 07:01 | 0:17 | T | REB-8,fault (instt o/c,instt E/F) | 50 | 14.1667
534 | Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-05-01 16:29 | 2023-05-01 16:53 | 0:24 | T | REB-6&7 fault | 10 | 4
538 | Khulna | Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-05-01 06:44 | 2023-05-01 07:02 | 0:18 | T | REB-8,fault (instt o/c,instt E/F) | 50 | 15
539 | Khulna | Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-05-01 16:29 | 2023-05-01 16:49 | 0:20 | T | REB-6&7 fault | 10 | 3.3333
549 | Khulna | Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2023-05-04 18:55 | 2023-05-04 19:27 | 0:32 | T | Aux-01 Fuse Fault | 27.5 | 14.6667
551 | Khulna | Madaripur 132/33kV Grid Sub-Station | T1-405T LT | 2023-05-04 18:55 | 2023-05-04 19:28 | 0:33 | T | Aux-01 Fuse Fault | 27.5 | 15.125
552 | Khulna | Madaripur 132/33kV Grid Sub-Station | T2-415T HT | 2023-05-04 18:55 | 2023-05-04 19:37 | 0:42 | T | Aux-01 Fuse Fault | 27.5 | 19.25
559 | Khulna | Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-05-19 20:43 | 2023-05-19 21:07 | 0:24 | T | 33KV Sharsha & Benapole Feeder Fault | 10 | 4
560 | Khulna | Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-05-19 20:43 | 2023-05-19 21:07 | 0:24 | T | 33KV Sharsha & Benapole Feeder Fault | 10 | 4
561 | Khulna | Goalpara 132/33kV Grid Sub-Station | T-5 HT | 2023-05-21 06:10 | 2023-05-21 10:29 | 4:19 | E/O | Red Hot | 0 | 0
562 | Khulna | Goalpara 132/33kV Grid Sub-Station | T-5 LT | 2023-05-21 06:09 | 2023-05-21 10:30 | 4:21 | E/O | Red hot | 0 | 0
563 | Khulna | Goalpara 132/33kV Grid Sub-Station | T-6 HT | 2023-05-09 06:50 | 2023-05-09 08:12 | 1:22 | E/O | Red Hot | 0 | 0
564 | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-05-03 10:35 | 2023-05-03 10:42 | 0:07 | T | Crow burnt & effected on 33kv bus section-3 | 22 | 2.5667
566 | Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-05-03 10:35 | 2023-05-03 10:42 | 0:07 | T | Crow burnt & effected on 33kv bus section-3 | 22 | 2.5667
572 | Khulna | Noapara 132/33kV Grid Sub-Station | T-2 HT | 2023-05-21 21:23 | 2023-05-21 22:20 | 0:57 | E/O | 33kV Bus Shutdown Due to REB-1 33kV feeder Bus Side DS Red hot Maintenance | 18 | 17.1
573 | Khulna | Noapara 132/33kV Grid Sub-Station | T-2 LT | 2023-05-21 21:22 | 2023-05-21 22:21 | 0:59 | E/O | 33kV Bus Shutdown Due to REB-1 33kV feeder Bus Side DS Red hot Maintenance | 18 | 17.7
574 | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-05-15 18:58 | 2023-05-15 19:05 | 0:07 | T | 33 KV Chandanimahal Feeder fault. | 17 | 1.9833
575 | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-1 (403T) LT | 2023-05-23 20:11 | 2023-05-23 20:28 | 0:17 | T | 33kv chandanimahal Feeder fault. | 3 | 0.85
578 | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-05-15 18:58 | 2023-05-15 19:02 | 0:04 | T | 33KV Chandanimahal Feeder fault. | 17 | 1.1333
579 | Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-05-23 20:11 | 2023-05-23 20:27 | 0:16 | T | 33kv chandanimahal Feeder fault. | 3 | 0.8
582 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-16 22:32 | 2023-05-17 00:38 | 2:06 | E/O | Red Hot Maintenance | 0 | 0
583 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-17 16:03 | 2023-05-17 17:33 | 1:30 | E/O | 33 kv bus DS red hot maintenance | 5 | 7.5
584 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-18 21:15 | 2023-05-18 22:23 | 1:08 | E/O | 33 kv bus DS loop change | 30 | 34
585 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-20 10:10 | 2023-05-20 13:10 | 3:00 | E/O | Feeder interchange by WZPDCL | 0 | 0
586 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-23 07:57 | 2023-05-23 18:12 | 10:15 | E/O | SAS Commissioning | 0 | 0
587 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-24 08:14 | 2023-05-24 17:59 | 9:45 | E/O | SAS commissioning | 0 | 0
588 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-25 09:26 | 2023-05-25 13:01 | 3:35 | E/O | SAS Pre-Commissioning by WGNDP. | 0 | 0
589 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-16 22:31 | 2023-05-17 00:38 | 2:07 | E/O | Red Hot Maintenance | 0 | 0
590 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-17 01:21 | 2023-05-17 01:25 | 0:04 | E/O | 33kV Bus Section DS Red Hot | 7 | 0.46667
591 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-17 16:02 | 2023-05-17 17:34 | 1:32 | E/O | 33 kv bus DS red hot maintenance | 5 | 7.6667
592 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-18 19:29 | 2023-05-18 20:11 | 0:42 | T | 33kv Cement factory feeder Trip & 33kv Bus Isolator loop open. | 30 | 21
593 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-18 21:15 | 2023-05-18 22:28 | 1:13 | E/O | 33 bus Ds loop change. | 30 | 36.5
594 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-20 10:09 | 2023-05-20 13:09 | 3:00 | E/O | Feeder Interchange by WZPDCL | 0 | 0
595 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-23 07:56 | 2023-05-23 18:13 | 10:17 | E/O | SAS Commissioning | 0 | 0
596 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-24 08:13 | 2023-05-24 18:00 | 9:47 | E/O | SAS commissioning | 0 | 0
597 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-25 09:25 | 2023-05-25 13:02 | 3:37 | E/O | SAS Pre-Commissioning by WGNDP. | 0 | 0
600 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-05-17 16:04 | 2023-05-17 17:35 | 1:31 | E/O | 33 kv bus DS red hot maintenance | 17 | 25.7833
601 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-05-18 21:16 | 2023-05-18 22:24 | 1:08 | E/O | 33 kv bus DS loop change | 13 | 14.7333
602 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-05-25 16:27 | 2023-05-25 17:21 | 0:54 | E/O | SAS pre-Commissioning | 0 | 0
603 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-05-29 09:55 | 2023-05-29 13:28 | 3:33 | E/O | Differential Relay Work. | 0 | 0
604 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-05-30 11:33 | 2023-05-30 14:16 | 2:43 | E/O | SAS | 0 | 0
605 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 HT | 2023-05-31 09:46 | 2023-05-31 19:07 | 9:21 | E/O | Replace relay | 0 | 0
606 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-16 22:27 | 2023-05-16 22:34 | 0:07 | E/O | For Trying to close 33kV Labonchora (WZPDCL) Feeder | 9 | 1.05
607 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-17 16:03 | 2023-05-17 17:36 | 1:33 | E/O | 33 kv bus DS red hot maintenance | 17 | 26.35
608 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-18 19:29 | 2023-05-18 22:40 | 3:11 | E/O | 33 kv bus DS loop change | 43 | 136.8833
609 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-25 16:26 | 2023-05-25 17:22 | 0:56 | E/O | SAS pre-Commissioning | 0 | 0
610 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-29 09:54 | 2023-05-29 13:29 | 3:35 | E/O | Differential Relay Work. | 0 | 0
611 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-30 11:32 | 2023-05-30 14:17 | 2:45 | E/O | SAS | 0 | 0
612 | Khulna | Gollamari 132/33kV Grid Sub-Station | Tr-2 LT | 2023-05-31 09:45 | 2023-05-31 19:09 | 9:24 | E/O | Replace relay | 0 | 0
621 | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 HT | 2023-05-23 23:33 | 2023-05-24 02:01 | 2:28 | E/O | Emergency | 5 | 12.3333
622 | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-05-07 02:49 | 2023-05-07 03:31 | 0:42 | T | 33kV seven circle feeder fault | 14 | 9.8
623 | Khulna | Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-05-23 23:33 | 2023-05-24 02:02 | 2:29 | E/O | Emergency | 5 | 12.4167
624 | Khulna | Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-05-07 02:49 | 2023-05-07 03:32 | 0:43 | T | 33kV seven circle feeder fault | 14 | 10.0333
625 | Khulna | Rampal 400/230kV Grid Sub-Station | ICT-1 HT | 2023-05-27 12:33 | 2023-05-27 18:22 | 5:49 | T | Due to trip of differential protection relay | 0 | 0
626 | Khulna | Rampal 400/230kV Grid Sub-Station | ICT-1 LT | 2023-05-27 12:33 | 2023-05-28 11:32 | 22:59 | T | Due to trip of differential protection relay | 0 | 0
627 | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) HT | 2023-05-26 08:06 | 2023-05-26 09:56 | 1:50 | E/O | Red hot maintenance at Kalaroa & Ashasuni 33 KV feeder source side isolator. | 0 | 0
628 | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-1 (T-1) LT | 2023-05-26 08:05 | 2023-05-26 09:57 | 1:52 | E/O | Red hot maintenance at Kalaroa & Ashasuni 33 KV feeder source side isolator. | 0 | 0
629 | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) HT | 2023-05-03 14:39 | 2023-05-03 14:58 | 0:19 | E/O | Auxiliary transformer -2 fuse connection work | 0 | 0
630 | Khulna | Satkhira 132/33kV Grid Sub-Station | Transformer-2 (T-2) LT | 2023-05-03 14:39 | 2023-05-03 14:59 | 0:20 | E/O | Auxiliary transformer -2 fuse connection work | 30 | 10
[5 empty] | Total : | 295:18 |  | Unserved Energy: |  | 808.5917
| Total outage period of Sub-station Equipment : |  |  |  |  | 1035:40 | Hours
| T = Tripping | [7 empty] | Executive Engineer
| E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:May 2023
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Bogura | Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-05-25 21:59 | 2023-05-25 23:46 | 1:47 | E/O | abnormal weather condition | 0 | 0
Bogura | Bogura 132/33kV Grid Sub-Station | New Bogura-1 | 2023-05-17 12:16 | 2023-05-17 12:49 | 0:33 | E/O | Trip | 0 | 0
Bogura | Bogura 132/33kV Grid Sub-Station | New Bogura-1 | 2023-05-20 09:23 | 2023-05-20 19:37 | 10:14 | T | S/D | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-05-18 04:53 | 2023-05-18 05:24 | 0:31 | E/O | Rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-05-18 04:53 | 2023-05-18 05:25 | 0:32 | E/O | Rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Bogra 132KV Line-1 | 2023-05-17 12:18 | 2023-05-17 12:49 | 0:31 | E/O | Unknown | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2023-05-23 14:58 | 2023-05-23 16:34 | 1:36 | E/O | Storm & rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-1 | 2023-05-25 22:05 | 2023-05-25 23:44 | 1:39 | E/O | Strom & Rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Sherpur 132 KV Line-2 | 2023-05-25 22:05 | 2023-05-26 08:20 | 10:15 | E/O | storm & Rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Confidance UN-1 | 2023-05-23 14:58 | 2023-05-23 16:32 | 1:34 | E/O | Storm & Rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Confidance UN-1 | 2023-05-25 22:02 | 2023-05-25 22:44 | 0:42 | E/O | Strom & Rain | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Confidance UN-2 | 2023-05-18 04:15 | 2023-05-18 06:46 | 2:31 | E/O | Over Voltage | 0 | 0
Bogura | Bogura 230/132kV Grid Sub-Station | Confidance UN-2 | 2023-05-25 22:05 | 2023-05-26 10:25 | 12:20 | E/O | storm & Rain | 0 | 0
Bogura | Sirajgonj 230 kV Switching Station | SNWPCL (Unit-04) | 2023-05-31 07:43 | 2023-05-31 11:59 | 4:16 | T | Bay ds Yellow Phase Red hot. | 0 | 0
Bogura | Chapai 132/33kV Grid Sub-Station | Chapai-Rajshahi | 2023-05-06 10:59 | 2023-05-11 21:50 | 130:51 | T | Chapai -Rohanpur 132kV Line 1020A Flow | 0 | 0
Bogura | Chapai 132/33kV Grid Sub-Station | Chapai-Amnura | 2023-05-06 10:59 | 2023-05-11 21:50 | 130:51 | T | Chapai-Rohanpur 132kV line 1020A Flow | 0 | 0
Bogura | Naogaon 132/33kV Grid Sub-Station | Nao-Joy Ckt-1 | 2023-05-11 23:04 | 2023-05-11 23:26 | 0:22 | E/O | Stormy weather and lightning. | 24 | 8.8
Bogura | Natore 132/33kV Grid Sub-Station | Ishurdi-1 | 2023-05-18 03:32 | 2023-05-18 04:05 | 0:33 | E/O | Stome | 0 | 0
Bogura | Natore 132/33kV Grid Sub-Station | Rajshahi-1 | 2023-05-16 20:11 | 2023-05-16 20:35 | 0:24 | T | A bannar flow over the wind on natore rajshahi TL 1. | 0 | 0
Bogura | Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-1 | 2023-05-16 20:10 | 2023-05-16 20:37 | 0:27 | T | Work on Natore edge. | 0 | 0
Bogura | Rajshahi 132/33kV Grid Sub-Station | 132 kV PPP 50 Mw | 2023-05-18 12:16 | 2023-05-18 13:50 | 1:34 | T | Oil leakage by CVT(Y-Phase) | 22 | 34.4667
Bogura | Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2023-05-16 18:18 | 2023-05-16 19:32 | 1:14 | T | Over loading | 0 | 0
Bogura | Mithapukur 132/33kV Grid Sub-Station | Confidence-1 | 2023-05-20 02:26 | 2023-05-20 03:33 | 1:07 | E/O | Bad weather. | 0 | 0
Bogura | Mithapukur 132/33kV Grid Sub-Station | Confidence-2 | 2023-05-16 18:18 | 2023-05-16 19:23 | 1:05 | T | Over loading | 0 | 0
Bogura | Saidpur 132/33kV Grid Sub-Station | Saidpur-Jaldhaka CKT-02 | 2023-05-17 01:28 | 2023-05-17 02:11 | 0:43 | E/O | Due to abnornal cloudy weather as well as slow rain. | 0 | 0
|  |  |  | Total : | 318:12 |  | Unserved Energy: |  | 43.2667
Chattogram Grid Circle :
Chattogram | Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2023-05-12 08:35 | 2023-05-12 11:33 | 2:58 | T | Corrective Maintenance | 0 | 0
Chattogram | Khulshi 132/33kV Grid Sub-Station | Khulshi-Bakalia Circuit-1 | 2023-05-12 07:10 | 2023-05-12 11:34 | 4:24 | E/O | Fault at Bph. | 0 | 0
Chattogram | Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Madunaghat Ckt-1 | 2023-05-25 11:41 | 2023-05-25 11:54 | 0:13 | T | integration with NLDC under 400kv GNDP | 0 | 0
Chattogram | Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-05-21 20:21 | 2023-05-21 22:40 | 2:19 | T | Ordered by NLDC | 0 | 0
Chattogram | Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-05-29 08:35 | 2023-05-29 16:49 | 8:14 | T | Load flow control by NLDC. | 0 | 0
Chattogram | Baroirhat 132/33kV Grid Sub-Station | PHP | 2023-05-21 20:22 | 2023-05-21 22:40 | 2:18 | T | Ordered by NLDC | 0 | 0
Chattogram | Baroirhat 132/33kV Grid Sub-Station | PHP | 2023-05-29 08:35 | 2023-05-29 16:50 | 8:15 | T | Load flow control by NLDC. | 0 | 0
Chattogram | GPH 230/33kV Grid Sub-Station | HATHAZARI-2 | 2023-05-11 13:06 | 2023-05-11 13:41 | 0:35 | E/O | Distance Trip distance: 0.5km | 0 | 0
Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-05-09 10:05 | 2023-05-09 11:03 | 0:58 | T | gantry structure clean | 0 | 0
Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-05-22 02:20 | 2023-05-22 02:52 | 0:32 | E/O | Tripped by distence, Zone;-01 B-phase | 0 | 0
Chattogram | Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-01 | 2023-05-16 11:29 | 2023-05-18 17:19 | 53:50 | T | Kaptai PS work | 0 | 0
Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-05-06 14:31 | 2023-05-06 15:17 | 0:46 | T | High Temparature Maintenance at R-ph CT Clamp | 0 | 0
Chattogram | Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-05-26 05:37 | 2023-05-26 17:22 | 11:45 | E/O | Storm weather | 0 | 0
Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-05-09 10:42 | 2023-05-14 18:14 | 127:32 | T | Over current flow through the Hathazari ckt | 0 | 0
Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Sikalbaha ckt | 2023-05-16 21:50 | 2023-05-18 11:15 | 37:25 | T | Due to the increase in load of hathazari circuit. | 0 | 0
Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-05-09 10:41 | 2023-05-14 18:14 | 127:33 | T | Over current flow through the Hathazari ckt | 0 | 0
Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-T.K. chemical complex | 2023-05-16 21:49 | 2023-05-18 11:16 | 37:27 | T | Due to the increase in load of hathazari circuit. | 0 | 0
Chattogram | Madunaghat 132/33kV Grid Sub-Station | Madunaghat-Kulshi-1 | 2023-05-22 11:01 | 2023-05-22 16:54 | 5:53 | T | For development work by 400kv GNDP project. | 0 | 0
Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Dohazari ckt-1 | 2023-05-06 14:33 | 2023-05-06 15:16 | 0:43 | T | Emergency maintenance at Dohazari end. | 0 | 0
|  |  |  | Total : | 433:40 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla | Chandpur 132/33kV Grid Sub-Station | Chandpur-Kachua Ckt-2 | 2023-05-23 14:46 | 2023-05-23 15:20 | 0:34 | E/O | Unknown | 0 | 0
Cumilla | Chandpur 132/33kV Grid Sub-Station | Chandpur-Desh Energy Ckt-2 | 2023-05-27 14:41 | 2023-05-27 15:03 | 0:22 | E/O | Unknown | 0 | 0
Cumilla | Chandpur 132/33kV Grid Sub-Station | 100MW(GT) Power Plant Incomer (T4) | 2023-05-27 14:41 | 2023-05-27 15:50 | 1:09 | E/O | None | 0 | 0
Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-1 | 2023-05-15 22:56 | 2023-05-16 | 1:04 | T | For SF6 gas refilling on SM nagor end. | 0 | 0
Cumilla | Daudkandi 132/33kV Grid Sub-Station | Cumilla(N)-1 | 2023-05-23 13:07 | 2023-05-23 14:27 | 1:20 | E/O | Weather is not good. | 0 | 0
Cumilla | Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2023-05-27 16:10 | 2023-05-27 16:34 | 0:24 | E/O | Heavy Stone | 0 | 0
Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-05-17 09:43 | 2023-05-17 10:48 | 1:05 | E/O | Fault | 0 | 0
Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-05-26 00:10 | 2023-05-26 00:45 | 0:35 | E/O | bad weather. | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-05-21 22:25 | 2023-05-21 23:03 | 0:38 | E/O | Thunder and stormy weather | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-05-26 00:11 | 2023-05-26 00:16 | 0:05 | E/O | Bad weather | 0 | 0
Cumilla | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-05-21 23:18 | 2023-05-21 23:49 | 0:31 | E/O | By Fault | 0 | 0
Cumilla | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-1 | 2023-05-27 16:53 | 2023-05-27 17:01 | 0:08 | E/O | Fault at A phase | 0 | 0
Cumilla | Sreemongol 132/33kV Grid Sub-Station | Sreemangal-Fenchugonj circuit-2 | 2023-05-21 23:18 | 2023-05-21 23:49 | 0:31 | E/O | By fault | 0 | 0
Cumilla | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-05-21 23:18 | 2023-05-21 23:23 | 0:05 | E/O | Bad weather | 0 | 0
Cumilla | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-05-27 16:53 | 2023-05-27 17:03 | 0:10 | E/O | Stormy Weather. | 0 | 0
Cumilla | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-05-21 23:18 | 2023-05-21 23:23 | 0:05 | E/O | Bad weather | 0 | 0
Cumilla | Sunamganj 132/33kV Grid Sub-Station | Chhatak-Sunamgonj CKT-1 | 2023-05-26 00:37 | 2023-05-26 00:56 | 0:19 | E/O | VT fuse fail | 10 | 3.1667
|  |  |  | Total : | 9:05 |  | Unserved Energy: |  | 3.1667
Dhaka (North) Grid Circle :
Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-05-18 06:38 | 2023-05-18 06:45 | 0:07 | E/O | None | 10 | 1.1667
Dhaka (N) | Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 01 | 2023-05-31 14:46 | 2023-05-31 15:18 | 0:32 | T | Project... 01 | 0 | 0
Dhaka (N) | Bhaluka 132/33kV Grid Sub-Station | Mymensingh- Bhaluka 132 kV Ckt- 02 | 2023-05-31 15:21 | 2023-05-31 17:25 | 2:04 | T | Project.. 01 | 0 | 0
Dhaka (N) | Dummy | Aminbazar-1 | 2023-05-30 10:30 | 2023-05-30 10:42 | 0:12 | E/O | thundering | 0 | 0
Dhaka (N) | Dummy | Aminbazar-1 | 2023-05-31 10:25 | 2023-05-31 10:30 | 0:05 | E/O | thundering | 0 | 0
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Rajendrapur Ckt-1 | 2023-05-21 20:31 | 2023-05-21 21:20 | 0:49 | E/O | Lighting | 0 | 0
Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Ashuganj Ckt-2 | 2023-05-25 23:17 | 2023-05-26 | 0:43 | E/O | Bad weather condition | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-05-03 13:48 | 2023-05-03 15:05 | 1:17 | E/O | Strom & Heavy Wind flow | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-05-23 13:20 | 2023-05-23 13:40 | 0:20 | E/O | Thunderstorm. | 0 | 0
Dhaka (N) | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-1 | 2023-05-17 10:31 | 2023-05-17 12:49 | 2:18 | E/O | None | 0 | 0
Dhaka (N) | Aminbazar 400/230/132kV Grid Sub-Station | Gopalganj-2 | 2023-05-04 17:31 | 2023-05-04 18:22 | 0:51 | E/O | Gopalgonj -2 Distant trip | 0 | 0
Dhaka (N) | Ashuganj 230/132/33kV Sub-Station | Sreepur 230 kV Ckt-2 | 2023-05-25 23:16 | 2023-05-26 00:01 | 0:45 | E/O | None | 0 | 0
Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2023-05-19 04:54 | 2023-05-19 07:46 | 2:52 | T | Old tower dismantling work in Switch yard | 0 | 0
Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-05-17 15:39 | 2023-05-17 17:29 | 1:50 | T | Bill board banner remove works. | 0 | 0
Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | Aminbazar-2 | 2023-05-19 04:56 | 2023-05-19 07:46 | 2:50 | T | Old tower dismantling work in Switch yard | 0 | 0
Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | Uttara Old | 2023-05-19 04:03 | 2023-05-19 07:48 | 3:45 | T | Old tower dismantling work in Switch yard | 0 | 0
Dhaka (N) | Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-05-19 04:03 | 2023-05-19 07:48 | 3:45 | T | Old tower dismantling work in Switch yard | 0 | 0
Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | Manikganj-1 | 2023-05-21 20:36 | 2023-05-21 21:17 | 0:41 | E/O | Earth fault | 0 | 0
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-05-21 16:04 | 2023-05-21 17:10 | 1:06 | E/O |  | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2023-05-08 13:20 | 2023-05-08 13:26 | 0:06 | E/O | Trip | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2023-05-10 16:58 | 2023-05-10 17:20 | 0:22 | E/O | Distance C ph Z1 | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2023-05-11 16:31 | 2023-05-11 16:37 | 0:06 | E/O | Distance Relay,C-Phase,Z3 | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-1 | 2023-05-11 17:30 | 2023-05-11 18:28 | 0:58 | E/O | Distance Relay,C-Phase | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2023-05-08 13:20 | 2023-05-08 13:27 | 0:07 | E/O | Trip | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2023-05-10 16:58 | 2023-05-10 17:20 | 0:22 | E/O | Distance C ph Z1 | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2023-05-11 16:31 | 2023-05-11 16:38 | 0:07 | E/O | Distance Relay,C-Phase,Z3 | 0 | 0
Dhaka (N) | Kishoreganj 132/33kV Grid Sub-Station | Mymensingh Ckt-2 | 2023-05-11 17:30 | 2023-05-11 19:07 | 1:37 | E/O | Distance Relay,C-Phase,Z3 | 0 | 0
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | 50 MW Solar Plant | 2023-05-23 17:43 | 2023-05-23 18:34 | 0:51 | E/O | Bad weather | 0 | 0
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Kaliakair-1 | 2023-05-25 21:39 | 2023-05-25 22:34 | 0:55 | E/O | Thunder storm | 0 | 0
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-05-17 12:29 | 2023-05-17 17:27 | 4:58 | T | Due to maintenance work at RPCl End. | 0 | 0
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | RPCL-1 | 2023-05-24 12:36 | 2023-05-24 14:55 | 2:19 | T | Work on RPCL LINE -1&2 | 0 | 0
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-05-23 10:30 | 2023-05-23 14:54 | 4:24 | T | Work at RPCL End | 0 | 0
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | RPCL-2 | 2023-05-23 16:50 | 2023-05-24 14:56 | 22:06 | E/O | Rain & Thunder | 0 | 0
|  |  |  | Total : | 66:10 |  | Unserved Energy: |  | 1.1667
Dhaka (South) Grid Circle :
Dhaka (S) | Maniknagar 132/33kV Grid Sub-Station | Matuail Single Ckt | 2023-05-06 15:18 | 2023-05-10 14:54 | 95:36 | T | Matuail Ckt.CB. E/F Trip at Matuail Substation end. | 0 | 0
Dhaka (S) | Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-01 | 2023-05-21 21:16 | 2023-05-21 22:45 | 1:29 | E/O | Storm | 0 | 0
Dhaka (S) | Rampura 230/132kV Grid Sub-Station | Bhulta Ckt-02 | 2023-05-02 12:39 | 2023-05-02 16:03 | 3:24 | T | Abnormal sound at Line CVT-2340 ( R-phase) | 0 | 0
Dhaka (S) | Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-05-31 10:17 | 2023-05-31 10:28 | 0:11 | E/O |  | 0 | 0
Dhaka (S) | Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-05-31 11:08 | 2023-05-31 13:18 | 2:10 | E/O | Distance protection 21/1 BN( yellow phase to Neutral) High Impedance 87TEE(FDR) | 0 | 0
Dhaka (S) | Rampura 230/132kV Grid Sub-Station | Moghbazar-02 | 2023-05-21 21:41 | 2023-05-21 21:50 | 0:09 | E/O | Storm | 0 | 0
Dhaka (S) | Rampura 230/132kV Grid Sub-Station | Ullon-02 | 2023-05-18 09:59 | 2023-05-20 17:47 | 55:48 | T | Shutdown For NLCD | 0 | 0
Dhaka (S) | Haripur 230/132kV Grid Sub-Station | Madanganj-2 | 2023-05-16 19:58 | 2023-05-16 20:36 | 0:38 | E/O | Thunderstorm | 0 | 0
Dhaka (S) | Haripur 230/132kV Grid Sub-Station | Siddhirganj-2 | 2023-05-25 12:54 | 2023-05-25 18:40 | 5:46 | E/O | None | 0 | 0
Dhaka (S) | Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-05-06 15:33 | 2023-05-06 15:42 | 0:09 | E/O | None | 0 | 0
Dhaka (S) | Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-05-04 08:45 | 2023-05-04 14:32 | 5:47 | T | Ordered by NLDC(For 132KV Haripur ckt-1 S/D Purpose) | 0 | 0
Dhaka (S) | Madanganj 132/33kV Grid Sub-Station | Madanganj -Shitalakhya 132 kv Ckt | 2023-05-15 08:37 | 2023-05-23 11:31 | 194:54 | T | Overload Problem of 132KV Madanganj-Fatulla ckt, NLDC Forced S/D this Feeder | 0 | 0
Dhaka (S) | Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2023-05-15 08:33 | 2023-05-15 08:53 | 0:20 | E/O | When 132KV Madanganj-Fatullah ckt Forced S/D by NLDC, then 132KV Madanganj-Haripur CKT-2 tripped by Overload. | 0 | 0
Dhaka (S) | Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-2 | 2023-05-16 19:58 | 2023-05-16 20:42 | 0:44 | E/O | Rain & stormy condition | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2023-05-06 15:19 | 2023-05-06 15:49 | 0:30 | E/O | heavy rain ,litining | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | Haripur 1 | 2023-05-25 12:54 | 2023-05-25 13:29 | 0:35 | E/O | Trip | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | Haripur 2 | 2023-05-25 13:36 | 2023-05-25 18:37 | 5:01 | T | Corrective maintenance | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | Ullon 1 | 2023-05-25 12:54 | 2023-05-25 13:12 | 0:18 | E/O | Trip | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-05-06 15:19 | 2023-05-06 17:51 | 2:32 | E/O | littining | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-05-08 12:51 | 2023-05-08 19:27 | 6:36 | T | Corrective Maintenance in CB at Dutchbangla plant end & work done by Dutchbangla Authority.(They apply work request with out Grounding). | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-05-06 15:19 | 2023-05-06 16:01 | 0:42 | E/O | HEAVY RAIN | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-05-06 15:19 | 2023-05-06 15:57 | 0:38 | E/O | LBB INITIATION, LITTINING | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-05-25 13:30 | 2023-05-25 14:26 | 0:56 | T | Corrective maintenance | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 210MW PDB L3 | 2023-05-06 15:19 | 2023-05-06 15:56 | 0:37 | E/O | HEAVY RAIN | 0 | 0
Dhaka (S) | Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2023-05-23 18:02 | 2023-05-25 21:05 | 51:03 | E/O | z1 trip | 0 | 0
Dhaka (S) | Hasnabad 132/33kV Grid Substation | Aggreko (Brahmongaon) | 2023-05-21 21:56 | 2023-05-22 00:28 | 2:32 | T | 132 kv Reserve bus isolator Red phase sparking | 0 | 0
Dhaka (S) | Hasnabad 132/33kV Grid Substation | Aggreko Aourahati | 2023-05-22 08:44 | 2023-05-22 13:34 | 4:50 | E/O | Unknown | 0 | 0
|  |  |  | Total : | 443:55 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
HVDC | Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-1 | 2023-05-26 07:09 | 2023-05-26 18:15 | 11:06 | T | for project work | 0 | 0
HVDC | Ishurdi 132/33kV Grid Sub-Station | 132 kv Natore-2 | 2023-05-26 07:10 | 2023-05-26 18:15 | 11:05 | T | For project work | 0 | 0
HVDC | Ishurdi 132/33kV Grid Sub-Station | 230/132 kV T02 Incoming | 2023-05-18 10:40 | 2023-05-18 14:33 | 3:53 | T | Red hot maintenance in 132 kv Ishwardi-Bheramara ckt-2 ( Bus-1) | 0 | 0
HVDC | Ishurdi 230/132kV Grid Sub-Station | 230 kV Ghorashal 1 | 2023-05-03 14:38 | 2023-05-03 15:26 | 0:48 | T | triped | 0 | 0
HVDC | Shahjadpur 132/33kV Grid Sub-Station | 132 KV Shahjadpur-Sirajgonj | 2023-05-23 15:01 | 2023-05-23 17:08 | 2:07 | E/O |  | 26 | 55.0333
HVDC | Bheramara 230/132kV Grid Sub-Station | Ishurdi 1 | 2023-05-21 22:35 | 2023-05-22 02:30 | 3:55 | T | O/C | 0 | 0
HVDC | Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2023-05-18 11:54 | 2023-05-18 14:40 | 2:46 | E/O | Distance, Zone-2, 9.79km, Over current,,, | 0 | 0
|  |  |  | Total : | 35:40 |  | Unserved Energy: |  | 55.0333
Khulna Grid Circle :
Khulna | Barishal 132/33kV Grid Sub-Station | 132kv Bhandaria ckt | 2023-05-25 15:33 | 2023-05-25 15:41 | 0:08 | E/O | Due to storm at Barishal. | 38 | 5.0667
Khulna | Barishal 230/132kV Grid Sub-Station | Bhola Ckt-2 | 2023-05-17 13:29 | 2023-05-17 14:33 | 1:04 | E/O | EFSTFW | 0 | 0
Khulna | Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-02 | 2023-05-08 08:31 | 2023-05-08 17:25 | 8:54 | T | Transport the spare materials beneath the 230kV Tower. | 0 | 0
Khulna | Faridpur 132/33kV Grid Sub-Station | 132 KV Gopalganj (400kv) ckt-1 | 2023-05-24 09:54 | 2023-05-24 21:35 | 11:41 | T | unknown | 0 | 0
Khulna | Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-1 | 2023-05-07 22:28 | 2023-05-08 00:30 | 2:02 | T | Red hot | 0 | 0
Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-03 | 2023-05-21 09:57 | 2023-05-21 21:31 | 11:34 | T | Project work shutdown | 0 | 0
Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-04 | 2023-05-23 10:04 | 2023-05-23 22:43 | 12:39 | T | Project work | 0 | 0
Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2023-05-24 09:48 | 2023-05-24 21:30 | 11:42 | T | Project work 400kv substation | 0 | 0
Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-02 | 2023-05-25 09:15 | 2023-05-25 17:56 | 8:41 | T | Gopalganj side project work | 0 | 0
Khulna | Shariatpur 132/33kV Grid Sub-Station | Madaripur-Shariatpur CKT-02 | 2023-05-06 15:36 | 2023-05-06 16:33 | 0:57 | T | Madaripur-Shariatpur ckt-2, line voltage unbalance | 0 | 0
Khulna | Khulna (C) 132/33kV Grid Sub-Station | North-WestCkt-1 | 2023-05-14 12:45 | 2023-05-14 16:10 | 3:25 | T | Maintenance Work. | 0 | 0
Khulna | Khulna (C) 132/33kV Grid Sub-Station | North- West Ckt-2 | 2023-05-14 12:46 | 2023-05-14 16:10 | 3:24 | T | Maintenance Work. | 0 | 0
Khulna | Bagerhat 132/33kV Grid Sub-Station | Bagerhat-Mongla 2 | 2023-05-18 07:52 | 2023-05-18 08:54 | 1:02 | E/O | Unknown | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E03 Gollamari-Khulna(S) Line-1 | 2023-05-24 15:51 | 2023-05-24 20:15 | 4:24 | T | Project work SAS | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E03 Gollamari-Khulna(S) Line-1 | 2023-05-25 17:44 | 2023-05-25 18:36 | 0:52 | T | SAS Pre-Commissioning | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E05 Gollamari-Khulna(S) Line-2 | 2023-05-25 19:09 | 2023-05-25 19:55 | 0:46 | T | SAS Pre-Commissioning | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2023-05-21 09:09 | 2023-05-21 18:42 | 9:33 | T | Pre commissioning of SAS. | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2023-05-25 13:13 | 2023-05-25 14:36 | 1:23 | T | SAS Pre-Commissioning by WGNDP. | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E01 Gollamari-Gopalgonj Line - 1 | 2023-05-30 08:17 | 2023-05-30 20:52 | 12:35 | T | PW | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E07 Gollamari-Gopalgonj Line - 2 | 2023-05-22 09:03 | 2023-05-22 17:23 | 8:20 | T | Pre commissioning of SAS. | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E07 Gollamari-Gopalgonj Line - 2 | 2023-05-25 14:51 | 2023-05-25 16:16 | 1:25 | T | PW | 0 | 0
Khulna | Gollamari 132/33kV Grid Sub-Station | E07 Gollamari-Gopalgonj Line - 2 | 2023-05-31 08:34 | 2023-05-31 19:40 | 11:06 | T | Alarm event, control and measurement cheking at 132 kv Gopalganj Ckt-2 | 0 | 0
Khulna | Satkhira 132/33kV Grid Sub-Station | Khulna South-2 (L-2) | 2023-05-23 18:31 | 2023-05-23 20:22 | 1:51 | E/O | Due to heavy storm and thundering | 0 | 0
|  |  |  | Total : | 129:28 |  | Unserved Energy: |  | 5.0667
Total outage period of Sub-station Equipment :
T = Tripping |  |  |  |  | 1436:10 | Hours
E/O = Emergency Outage
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/14 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: May 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-05-21 15:30 | 2023-05-21 17:40 | 2:10 | S/O | 33kV Bus-Coupler Red-Hot Maintenance Work by BPBS& NESCO. | 12.5 | 27.0833
Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-05-21 15:30 | 2023-05-21 17:42 | 2:12 | S/O | 33kV Bus-Coupler Red-Hot Maintenance Work by BPBS& NESCO. | 12.5 | 27.5
Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-4 HT | 2023-05-21 15:30 | 2023-05-21 17:40 | 2:10 | S/O | 33kV Bus-Coupler Red-Hot Maintenance Work by BPBS& NESCO. | 12.5 | 27.0833
Bogura | Bogura 132/33kV Grid Sub-Station | Transformer-4 LT | 2023-05-21 15:30 | 2023-05-21 17:42 | 2:12 | S/O | 33kV Bus-Coupler Red-Hot Maintenance Work by BPBS& NESCO. | 12.5 | 27.5
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 HT | 2023-05-15 07:05 | 2023-05-15 10:45 | 3:40 | S/O | 33KV Busbar maintenance work of different distribution utility | 24 | 88
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 HT | 2023-05-27 08:14 | 2023-05-27 09:22 | 1:08 | S/O | 33 kv bus shutdown for maintenance work | 0 | 0
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-05-15 07:04 | 2023-05-15 10:47 | 3:43 | S/O | 33KV Busbar maintenance work of different distribution utility. | 24 | 89.2
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 406T MTR1 LT | 2023-05-27 08:13 | 2023-05-27 09:23 | 1:10 | S/O | 33 kv bus shutdown for maintenance work | 12 | 14
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 HT | 2023-05-15 07:08 | 2023-05-15 10:44 | 3:36 | S/O | 33KV Busbar maintenance work of different distribution utility | 24 | 86.4
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 HT | 2023-05-27 08:01 | 2023-05-27 09:29 | 1:28 | S/O | 33 kv bus shutdown for maintenance work | 0 | 0
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2023-05-15 07:06 | 2023-05-15 10:46 | 3:40 | S/O | 33KV Busbar maintenance work of different distribution utility | 24 | 88
Bogura | Mahasthangarh 132/33kV Grid Sub-Station | 416T MTR 2 LT | 2023-05-27 08:00 | 2023-05-27 09:30 | 1:30 | S/O | 33 kv bus shutdown for maintenance work | 12 | 18
Bogura | Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-05-27 07:10 | 2023-05-27 08:45 | 1:35 | S/O | 33KV bus couplar red hot maintenance | 20 | 31.6667
Bogura | Purbasadipur 132/33kV Grid Sub-Station | T-4 Transformer LT | 2023-05-22 15:12 | 2023-05-22 18:50 | 3:38 | S/O | relay change and tripping testing | 12 | 43.6
Bogura | Thakurgaon 132/33kV Grid Sub-Station | 422T HT | 2023-05-01 06:01 | 2023-05-01 09:11 | 3:10 | S/O | Red hot removing of Y phase loop | 0 | 0
Bogura | Thakurgaon 132/33kV Grid Sub-Station | 432T HT | 2023-05-01 09:55 | 2023-05-02 12:14 | 26:19 | S/O | T-3 (33 KV) Bus Isolator R & Y Phase Red hot | 7 | 184.2167
Bogura | Thakurgaon 132/33kV Grid Sub-Station | 432T LT | 2023-05-01 09:55 | 2023-05-02 12:14 | 26:19 | S/O | T-3 (33 kv) Bus Isolator Red hot R & y Phase | 7 | 184.2167
Bogura | Amnura 132/33kV Grid Sub-Station | T-2 (416T) HT | 2023-05-05 07:42 | 2023-05-05 14:46 | 7:04 | S/O | 33 kv bus(section -3)DS_Y-Phase loop change . | 0 | 0
Bogura | Amnura 132/33kV Grid Sub-Station | T-2 (416T) LT | 2023-05-05 07:41 | 2023-05-05 14:49 | 7:08 | S/O | 33KV Bus (section -3) loop change at DS_Y-Phase. | 0 | 0
Bogura | Natore 132/33kV Grid Sub-Station | TR-1 (405 T) HT | 2023-05-17 06:32 | 2023-05-17 08:20 | 1:48 | S/O | T-1 LT R-phase CT- x- former D/S loop change. | 0 | 0
Bogura | Natore 132/33kV Grid Sub-Station | TR-1 (405 T) LT | 2023-05-17 06:30 | 2023-05-17 08:21 | 1:51 | S/O | T-1 LT R-phase CT- x- former D/S loop change. | 0 | 0
Bogura | Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-1 425T HT | 2023-05-30 06:20 | 2023-05-30 08:40 | 2:20 | S/O | 33 kv bus coupler maintenance. | 0 | 0
Bogura | Lalmonirhat 132/33kV Grid Sub-Station | Transformer T-1 425T LT | 2023-05-30 06:20 | 2023-05-30 08:40 | 2:20 | S/O | 33 kv bus coupler maintenance. | 0 | 0
Bogura | Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) HT | 2023-05-31 07:25 | 2023-05-31 10:04 | 2:39 | S/O | 33Kv Bus Coupler Ds Maintenance. | 0 | 0
Bogura | Saidpur 132/33kV Grid Sub-Station | TR-5 (434T) LT | 2023-05-31 07:24 | 2023-05-31 10:05 | 2:41 | S/O | 33Kv Bus Coupler DS Maintenance. | 0 | 0
|  |  |  | Total : | 117:31 |  | Unserved Energy: |  | 936.4667
Chattogram Grid Circle :
Chattogram | Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) HT | 2023-05-25 21:50 | 2023-05-25 22:30 | 0:40 | S/O | Due to Red Hot at 33kV CT Clamp of TR-03 | 0 | 0
Chattogram | Halishahar 132/33kV Grid Sub-Station | 423T(TR-3) LT | 2023-05-25 21:49 | 2023-05-25 22:33 | 0:44 | S/O | Due to Red Hot at 33kV CT Clamp of TR-03 | 0 | 0
Chattogram | Juldah 132/33kV Grid Sub-Station | 133/33 KV T-2 416T LT | 2023-05-15 08:18 | 2023-05-25 13:22 | 245:04 | S/O | Increasing of transformer capacity(G2G project work). | 0 | 0
Chattogram | Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) HT | 2023-05-11 09:30 | 2023-05-11 15:18 | 5:48 | S/O | On Job Training | 0 | 0
Chattogram | Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) HT | 2023-05-05 10:32 | 2023-05-05 12:17 | 1:45 | S/O | 230k v GCB Investigation work | 0 | 0
Chattogram | Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) LT | 2023-05-05 10:34 | 2023-05-05 12:17 | 1:43 | S/O | 230kv GCB Investigation work | 0 | 0
Chattogram | Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 HT | 2023-05-24 15:25 | 2023-05-24 15:45 | 0:20 | S/O | Integration with LDC | 0 | 0
Chattogram | Sholosohor 132/33kV Grid Sub-Station | TRAFO-02 LT | 2023-05-24 15:22 | 2023-05-24 15:45 | 0:23 | S/O | integration with LDC | 0 | 0
Chattogram | BSRM 230/33kV Grid Sub-Station | 230/33 kV Transformer-1 (125/140 MVA) HT | 2023-05-07 09:50 | 2023-05-07 16:13 | 6:23 | S/O | Yearly/ Half-yearly maintenance, S/D taken by BSRM Authority. | 0 | 0
Chattogram | Khagrachori 132/33kV Grid Sub-Station | TR-1 HT | 2023-05-05 08:09 | 2023-05-05 09:49 | 1:40 | S/O | To remove oil leakage at HT bushing(R-phase). | 0 | 0
Chattogram | Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-05-07 05:59 | 2023-05-07 06:45 | 0:46 | S/O | for high temperature maintenance. | 45 | 34.5
Chattogram | Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 LT | 2023-05-07 05:59 | 2023-05-07 06:45 | 0:46 | S/O | S/D taken for high temperature maintenance. | 45 | 34.5
|  |  |  | Total : | 266:02 |  | Unserved Energy: |  | 69
Cumilla Grid Circle :
Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-2 HT | 2023-05-24 10:40 | 2023-05-24 13:00 | 2:20 | S/O | PDB 33 KV kashba palpara feeder red hot maintenance. | 20 | 46.6667
Cumilla | Cumilla(S) 132/33kV Grid Sub-Station | TR-2 LT | 2023-05-24 10:40 | 2023-05-24 13:00 | 2:20 | S/O | PDB 33 KV Ksahba palpara feeder red hot maintenance. | 0 | 0
Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-05-06 09:03 | 2023-05-06 13:33 | 4:30 | S/O | Corrective Maintenance Work | 0 | 0
Cumilla | Daudkandi 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-05-06 09:03 | 2023-05-06 13:36 | 4:33 | S/O | Corrective Maintenance Work | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-05-13 10:10 | 2023-05-13 17:42 | 7:32 | S/O | None | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | TR-04 LT | 2023-05-13 10:08 | 2023-05-13 17:45 | 7:37 | S/O | TR-04,33 kv Bus maintenance by BPDB | 40 | 304.6667
Cumilla | Chhatak 132/33kV Grid Sub-Station | T-2 HT | 2023-05-13 09:10 | 2023-05-13 15:21 | 6:11 | S/O | 33 kv SPPM Feeder DS Change | 5 | 30.9167
Cumilla | Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2023-05-13 09:08 | 2023-05-13 15:22 | 6:14 | S/O | DS Change of SPPM 33kv feeder. | 5 | 31.1667
Cumilla | Sylhet 132/33kV Grid Sub-Station | T4 HT | 2023-05-31 06:26 | 2023-05-31 07:57 | 1:31 | S/O | Maintenance and Replacement of T9 X-Former PDB | 0 | 0
Cumilla | Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-05-31 06:25 | 2023-05-31 07:57 | 1:32 | S/O | Maintenance and Replacement of T9 X-Former PDB | 0 | 0
|  |  |  | Total : | 44:20 |  | Unserved Energy: |  | 413.4167
Dhaka (North) Grid Circle :
Dhaka (N) | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-05-02 14:42 | 2023-05-02 18:28 | 3:46 | S/O | PBS Red-hot maintenance | 0 | 0
Dhaka (N) | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-05-16 08:54 | 2023-05-16 10:15 | 1:21 | S/O | Redhot Maintenance | 0 | 0
Dhaka (N) | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-05-02 14:42 | 2023-05-02 18:28 | 3:46 | S/O | PBS Red Hot maintenance | 0 | 0
Dhaka (N) | Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-05-16 07:54 | 2023-05-16 10:15 | 2:21 | S/O | Redhot Maintenance | 0 | 0
Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-05-13 09:31 | 2023-05-13 11:45 | 2:14 | S/O | Red Hot Remove & various nut bolt tightning . | 0 | 0
Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-05-29 11:06 | 2023-05-29 17:32 | 6:26 | S/O | GT-4 X-former 33 kv side Bushing clamp conector change | 0 | 0
Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-05-13 12:12 | 2023-05-13 13:46 | 1:34 | S/O | Red Hot Remove & various nut bolt tightning. | 0 | 0
Dhaka (N) | Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-05-29 11:05 | 2023-05-29 17:34 | 6:29 | S/O | GT-4 X-former 33 kv side Bushing clamp conector change | 0 | 0
Dhaka (N) | Dummy | 404T HT | 2023-05-30 08:12 | 2023-05-30 10:10 | 1:58 | S/O | yearly maintenance | 0 | 0
Dhaka (N) | Dummy | 404T LT | 2023-05-30 08:10 | 2023-05-30 10:12 | 2:02 | S/O | yearly maintenance (updated) | 0 | 0
Dhaka (N) | Dummy | 424T HT | 2023-05-31 08:12 | 2023-05-31 10:30 | 2:18 | S/O | yearly maintenance | 0 | 0
Dhaka (N) | Dummy | 424T LT | 2023-05-31 08:10 | 2023-05-31 10:31 | 2:21 | S/O | yearly maintenance (updated) | 0 | 0
Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | GT-2 HT | 2023-05-09 06:48 | 2023-05-09 09:28 | 2:40 | S/O | B-Phase & Y-Phase cable change of Auxilary X-Former-1. | 0 | 0
Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | GT-2 LT | 2023-05-09 06:47 | 2023-05-09 09:29 | 2:42 | S/O | B-Phase & Y-Phase cable change of Auxilary X-Former-1. | 0 | 0
Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2023-05-09 14:19 | 2023-05-09 15:25 | 1:06 | S/O | Bushing Hot - Spot Maintenance. | 0 | 0
Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | GT-4 HT | 2023-05-17 14:35 | 2023-05-17 15:06 | 0:31 | S/O | Installation of digital multifunction meter | 0 | 0
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2023-05-03 13:11 | 2023-05-03 14:29 | 1:18 | S/O | Ds Work | 0 | 0
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) HT | 2023-05-31 06:54 | 2023-05-31 19:01 | 12:07 | S/O | None | 50 | 605.8333
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2023-05-03 13:11 | 2023-05-03 14:30 | 1:19 | S/O | Ds work | 0 | 0
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) HT | 2023-05-22 13:19 | 2023-05-22 15:16 | 1:57 | S/O | 33kv red hot (33kv work) | 40 | 78
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-4 (436T) LT | 2023-05-22 13:19 | 2023-05-22 15:17 | 1:58 | S/O | 33kv red hot | 40 | 78.6667
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) HT | 2023-05-03 06:36 | 2023-05-03 08:11 | 1:35 | S/O | Ds work | 0 | 0
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) HT | 2023-05-07 13:16 | 2023-05-07 14:23 | 1:07 | S/O | Redhot maintenance | 20 | 22.3333
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2023-05-03 06:35 | 2023-05-03 08:12 | 1:37 | S/O | Ds work | 0 | 0
Dhaka (N) | Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) LT | 2023-05-07 13:15 | 2023-05-07 14:26 | 1:11 | S/O | Redhot maintenance | 20 | 23.6667
Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 LT | 2023-05-11 14:27 | 2023-05-11 16:25 | 1:58 | S/O | Under frequency relay configure | 0 | 0
Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-05-11 14:26 | 2023-05-11 16:24 | 1:58 | S/O | 33kv under frequency relay configure | 0 | 0
Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-05-11 16:27 | 2023-05-11 16:50 | 0:23 | S/O | Shutdown for 33kv under frequency relay configure | 0 | 0
Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 HT | 2023-05-23 12:34 | 2023-05-23 16:12 | 3:38 | S/O | 33 kV bus maintenance by PBS | 20 | 72.6667
Dhaka (N) | Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-05-11 16:26 | 2023-05-11 16:51 | 0:25 | S/O | Shutdown for 33kv incomer -2 under frequency relay configure | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | T-1 HT | 2023-05-02 09:29 | 2023-05-09 18:14 | 176:45 | S/O | Relay panel changing work | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | T-1 LT | 2023-05-02 09:28 | 2023-05-09 18:15 | 176:47 | S/O | Relay panel changing work | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | T-2 HT | 2023-05-15 10:11 | 2023-05-21 17:46 | 151:35 | S/O | Relay Panel Changing Work | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | T-2 LT | 2023-05-15 10:11 | 2023-05-21 17:46 | 151:35 | S/O | Relay Panel changing Work. | 0 | 0
Dhaka (N) | Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 HT | 2023-05-19 07:22 | 2023-05-19 18:45 | 11:23 | S/O | Red hot maintenance | 0 | 0
Dhaka (N) | Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2023-05-19 07:22 | 2023-05-19 18:45 | 11:23 | S/O | Redhot Maintenance | 0 | 0
Dhaka (N) | Savar 132/33kV Grid Sub-Station | T-3 HT | 2023-05-08 10:07 | 2023-05-08 16:13 | 6:06 | S/O | 33 kV DPBS-3 maintenance work | 0 | 0
Dhaka (N) | Savar 132/33kV Grid Sub-Station | T-3 LT | 2023-05-08 10:07 | 2023-05-08 16:13 | 6:06 | S/O | 33 kV DPBS-3 maintenance work | 0 | 0
Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 HT | 2023-05-22 08:43 | 2023-05-22 09:55 | 1:12 | S/O | Ifad 33 kv feeder loopout from 33kv bus | 70 | 84
Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | XFR, T-2 LT | 2023-05-22 08:43 | 2023-05-22 09:55 | 1:12 | S/O | Ifad 33 kv feeder loop out from 33 kv bus | 70 | 84
Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 HT | 2023-05-22 12:28 | 2023-05-22 14:25 | 1:57 | S/O | 33kv Bus DS change of 33 kv radio feeder | 70 | 136.5
Dhaka (N) | Kabirpur 132/33kV Grid Sub-Station | XFR, T-3 LT | 2023-05-22 12:28 | 2023-05-22 14:26 | 1:58 | S/O | Due to 33kv bus DS blade change of 33kv radio feeder | 70 | 137.6667
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-05-17 14:42 | 2023-05-17 16:18 | 1:36 | S/O | 33Kv Sharishabari PDB Bus loop change. | 15 | 24
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 HT | 2023-05-29 08:01 | 2023-05-29 09:10 | 1:09 | S/O | Maintenance work due to temperature rise. | 12 | 13.8
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-05-17 14:42 | 2023-05-17 16:18 | 1:36 | S/O | 33Kv Sharishabari PDB Bus loop change. | 15 | 24
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-05-29 08:01 | 2023-05-29 09:10 | 1:09 | S/O | Maintenance work due to temperature rise. | 12 | 13.8
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-05-17 14:42 | 2023-05-17 16:23 | 1:41 | S/O | 33Kv Sharishabari PDB Bus loop change. | 15 | 25.25
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | T-2 LT | 2023-05-17 14:42 | 2023-05-17 16:18 | 1:36 | S/O | 33Kv Sharishabari PDB Bus loop change. | 15 | 24
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) HT | 2023-05-15 06:30 | 2023-05-15 09:54 | 3:24 | S/O | 33kv bus DS red hot | 120 | 408
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Transformer-1 (404T) LT | 2023-05-15 06:29 | 2023-05-15 09:54 | 3:25 | S/O | 33kv bus DS red hot | 120 | 410
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-1 HT | 2023-05-02 14:18 | 2023-05-02 15:35 | 1:17 | S/O | 33kv bus Red hot | 35 | 44.9167
Dhaka (N) | Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-05-02 14:18 | 2023-05-02 15:36 | 1:18 | S/O | 33kv bus Red hot | 35 | 45.5
|  |  |  | Total : | 792:16 |  | Unserved Energy: |  | 2356.6
Dhaka (South) Grid Circle :
Dhaka (S) | Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) HT | 2023-05-26 07:46 | 2023-05-26 07:53 | 0:07 | S/O | None | 0 | 0
Dhaka (S) | Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) LT | 2023-05-26 07:45 | 2023-05-26 07:54 | 0:09 | S/O | None | 0 | 0
Dhaka (S) | Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2023-05-20 09:30 | 2023-05-20 15:40 | 6:10 | S/O | MTR-2 Realy Change. | 0 | 0
Dhaka (S) | Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2023-05-27 09:15 | 2023-05-27 21:17 | 12:02 | S/O | Relay change | 0 | 0
Dhaka (S) | Siddhirganj 230/132kV Grid Sub-Station | MTR 2 LT | 2023-05-20 09:30 | 2023-05-20 15:40 | 6:10 | S/O | MTR-2 Realy Change. | 0 | 0
Dhaka (S) | Keranigonj 230/132/33kV Grid Sub-Station | TR-2 HT | 2023-05-16 06:03 | 2023-05-16 09:36 | 3:33 | S/O | Maintenance work for Red Hot at 33kv equipment side DS conneting loop clamp (B -Phase) & high temperature at different joint. | 0 | 0
Dhaka (S) | Keranigonj 230/132/33kV Grid Sub-Station | TR-2 LT | 2023-05-16 06:02 | 2023-05-16 09:37 | 3:35 | S/O | Maintenance work for Red Hot at 33kv equipment side DS conneting loop clamp (B -Phase) & high temperature at different joint. | 0 | 0
Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-1 HT | 2023-05-29 08:21 | 2023-05-29 12:22 | 4:01 | S/O | 33kv bus section DS maintenance work. | 25 | 100.4167
Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-1 LT | 2023-05-29 08:21 | 2023-05-29 12:27 | 4:06 | S/O | 33kv bus section DS maintenance work. | 25 | 102.5
Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-2 HT | 2023-05-29 08:22 | 2023-05-29 12:22 | 4:00 | S/O | 33kv bus section DS maintenance work. | 25 | 100
Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | TR-2 LT | 2023-05-29 08:22 | 2023-05-29 12:30 | 4:08 | S/O | 33kv bus section DS maintenance work. | 25 | 103.3333
Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | Aux Tr-1 HT | 2023-05-29 08:24 | 2023-05-29 12:11 | 3:47 | S/O | 33kv bus section DS maintenance work. | 25 | 94.5833
Dhaka (S) | Nawabganj 132/33kV Grid Sub-Station | Aux Tr-1 LT | 2023-05-29 08:23 | 2023-05-29 12:12 | 3:49 | S/O | 33kv bus section DS maintenance work. | 25 | 95.4167
Dhaka (S) | Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2023-05-19 06:25 | 2023-05-19 13:13 | 6:48 | S/O | T-2 Transformer Bay XLPE Cable relocate | 25 | 170
Dhaka (S) | Narshingdi 132/33kV Grid Sub-Station | T-3 HT | 2023-05-12 05:58 | 2023-05-12 08:48 | 2:50 | S/O | Tr-3 132kV PT Change For Oil Lekage. | 15 | 42.5
|  |  |  | Total : | 65:15 |  | Unserved Energy: |  | 808.75
HVDC Grid Circle :
HVDC | Bheramara 230/132kV Grid Sub-Station | Transformer-2 HT | 2023-05-13 08:15 | 2023-05-13 13:56 | 5:41 | S/O | fire Extinguishing Water pipe maintenance | 0 | 0
HVDC | Bheramara 230/132kV Grid Sub-Station | Transformer-2 LT | 2023-05-13 08:15 | 2023-05-13 13:58 | 5:43 | S/O | fire Extinguishing Water pipe maintenance | 0 | 0
HVDC | Kushtia 132/33kV Grid Sub-Station | T2 HT | 2023-05-30 07:04 | 2023-05-30 08:11 | 1:07 | S/O | 33Kv sostipur(pbs) feeder red hot maintenance(y Phase) | 40 | 44.6667
HVDC | Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-05-30 07:02 | 2023-05-30 08:12 | 1:10 | S/O | 33Kv sostipur(pbs) feeder red hot maintenance(y Phase) | 40 | 46.6667
|  |  |  | Total : | 13:41 |  | Unserved Energy: |  | 91.3333
Khulna Grid Circle :
Khulna | Bhandaria 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-05-09 07:12 | 2023-05-09 08:13 | 1:01 | S/O | Sub station upgradation work of WZPDCL BHANDARIA. | 10 | 10.1667
Khulna | Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-05-09 07:12 | 2023-05-09 08:14 | 1:02 | S/O | Sub station upgradation of WZPDCL Bhandaria. | 10 | 10.3333
Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-05-06 09:12 | 2023-05-06 12:40 | 3:28 | S/O | 132kV Circuit Breaker Maintenance work | 0 | 0
Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-05-19 07:22 | 2023-05-19 09:19 | 1:57 | S/O | 33 kv Bus section-1 red hot maintenance | 40 | 78
Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-05-06 09:12 | 2023-05-06 12:41 | 3:29 | S/O | 132kV Circuit Breaker Maintenance Work | 0 | 0
Khulna | Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-05-19 07:21 | 2023-05-19 09:20 | 1:59 | S/O | 33 kv Bus section-1 red hot maintenance. | 40 | 79.3333
Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-05-19 10:32 | 2023-05-19 18:22 | 7:50 | S/O | T-1 R-B phase red hot maintenance | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-05-20 15:24 | 2023-05-20 16:38 | 1:14 | S/O | 33 kv incoming DS clamp & parts measurement | 16 | 19.7333
Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 HT | 2023-05-26 06:08 | 2023-05-26 11:25 | 5:17 | S/O | Maintenance work of D/S of Auxiliary TR-1 | 10 | 52.8333
Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-05-19 10:31 | 2023-05-19 18:23 | 7:52 | S/O | T-1 R-B phase Red hot maintenance | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-05-20 15:23 | 2023-05-20 16:39 | 1:16 | S/O | 33 kv incoming DS clamp & parts measurement. | 16 | 20.2667
Khulna | Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-05-26 06:07 | 2023-05-26 11:26 | 5:19 | S/O | Maintenance work of D/S of Auxiliary TR-1 | 10 | 53.1667
Khulna | Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2023-05-05 10:16 | 2023-05-05 12:40 | 2:24 | S/O | Aux Tr -1 loop maintenance | 8 | 19.2
Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T HT | 2023-05-05 06:21 | 2023-05-05 14:18 | 7:57 | S/O | 132/33 KV TR-3 B PHASE POLE CHANGE FOR GAS LEAKAGE. | 0 | 0
Khulna | Khulna (C) 132/33kV Grid Sub-Station | Tr-3 405T LT | 2023-05-05 06:20 | 2023-05-05 14:20 | 8:00 | S/O | 132/33KV TR-3 B PHASE POLE CHANGE FOR GAS LEAKAGE. | 0 | 0
Khulna | Narail 132/33kV Grid Sub-Station | TR2 (413-T) HT | 2023-05-19 07:10 | 2023-05-19 08:42 | 1:32 | S/O | 33 KV T2 and busbar shutdown for Red Hot maintenance. | 0 | 0
Khulna | Narail 132/33kV Grid Sub-Station | TR2 (413-T) LT | 2023-05-19 07:10 | 2023-05-19 08:44 | 1:34 | S/O | 33 KV T2 and busbar shutdown for Red Hot maintenance. | 15 | 23.5
Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) HT | 2023-05-04 07:07 | 2023-05-04 08:27 | 1:20 | S/O | TR-02 SHUT DOWN FOR HOT SPOT MAINTENANCE WORK. | 0 | 0
Khulna | Bagerhat 132/33kV Grid Sub-Station | Transformer-2 (413 T) LT | 2023-05-04 07:06 | 2023-05-04 08:27 | 1:21 | S/O | TR-02 SHUT DOWN FOR HOT SPOT MAINTENANCE WORK. | 0 | 0
|  |  |  | Total : | 65:52 |  | Unserved Energy: |  | 366.5333
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  |  | 1364:57 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/12 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: May 2023
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle:
Bogura | Bogura 230/132kV Grid Sub-Station | Bogra 132KV Line-1 | 2023-05-20 09:22 | 2023-05-20 19:36 | 10:14 | S/O | 132kV Bogura Ckt.-1 Bkr. Replacement work. | 0 | 0
Bogura | Naogaon 132/33kV Grid Sub-Station | Nao-Bog Ckt-1 | 2023-05-04 07:01 | 2023-05-04 11:19 | 4:18 | S/O | Maintanance work of Bogura s/s. | 0 | 0
Bogura | Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-1 | 2023-05-30 09:51 | 2023-05-30 10:45 | 0:54 | S/O | Oil Leakage Maintenance Work. | 0 | 0
Bogura | Rajshahi 230/132/33kV Grid Sub-Station | Rajshahi ckt-02 | 2023-05-04 07:37 | 2023-05-04 10:09 | 2:32 | S/O | None | 0 | 0
Bogura | Rajshahi 230/132/33kV Grid Sub-Station | Chapainawabganj | 2023-05-16 12:03 | 2023-05-16 13:50 | 1:47 | S/O | Line DS Nut bolt titing | 0 | 0
|  |  |  | Total : | 19:45 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Chattogram | Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Khulshi Ckt-1 | 2023-05-23 14:21 | 2023-05-23 16:22 | 2:01 | S/O | Integration with NLDC under 400kv GND project | 0 | 0
Chattogram | Sholosohor 132/33kV Grid Sub-Station | Sholoshahar-Madunaghat Ckt-1 | 2023-05-22 11:00 | 2023-05-22 16:54 | 5:54 | S/O | Development Work | 0 | 0
Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Kaptai-01 | 2023-05-20 09:09 | 2023-05-20 16:06 | 6:57 | S/O | Conductor maintenance work | 0 | 0
Chattogram | Hathazari 230/132/33kV Grid Sub-Station | Raojan-01 | 2023-05-10 08:42 | 2023-05-10 17:15 | 8:33 | S/O | Trimming tree. | 0 | 0
Chattogram | Shikalbaha 230/132kV Grid Sub-Station | Hathazari - 01 | 2023-05-02 13:27 | 2023-05-02 15:57 | 2:30 | S/O | None | 0 | 0
|  |  |  | Total : | 25:55 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Cumilla | Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2023-05-01 08:29 | 2023-05-03 00:35 | 40:06 | S/O | Ashuganj end CB Problem | 0 | 0
Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-05-10 05:38 | 2023-05-10 07:36 | 1:58 | S/O | Shahjibazar Sub-station Hot spot maintenance work. | 0 | 0
Cumilla | Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Shahjibazar Circuit-2 | 2023-05-31 08:52 | 2023-05-31 14:48 | 5:56 | S/O | String maintenance | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-05-10 05:41 | 2023-05-10 07:36 | 1:55 | S/O | Redhot maintenance at CB: 852 D/S loop jont | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-05-17 09:48 | 2023-05-17 10:50 | 1:02 | S/O | Due to remove fault. | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-05-26 00:17 | 2023-05-26 00:46 | 0:29 | S/O | Due to remove fault | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-Ashuganj Ckt-03 | 2023-05-17 09:59 | 2023-05-17 10:13 | 0:14 | S/O | Due to fault remove. | 0 | 0
Cumilla | Shahjibazar 132/33kV Grid Sub-Station | BPDB 60 MW | 2023-05-10 05:41 | 2023-05-10 07:36 | 1:55 | S/O | Redhot maintenance at CB: 852 D/S loop jont | 0 | 0
Cumilla | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-1 | 2023-05-21 23:24 | 2023-05-21 23:46 | 0:22 | S/O | Maintenance | 0 | 0
Cumilla | Fenchuganj 230/132/33kV Grid Sub-Station | Sreemongal-2 | 2023-05-21 23:24 | 2023-05-21 23:46 | 0:22 | S/O | Maintenance | 0 | 0
|  |  |  | Total : | 54:19 |  | Unserved Energy: |  | 0
Dhaka (North) Grid Circle :
Dhaka (N) | Joydebpur 132/33kV Grid Sub-Station | Joydebpur- Kodda ckt-2 | 2023-05-17 13:33 | 2023-05-17 14:16 | 0:43 | S/O | Installation of digital multi-function meter | 0 | 0
Dhaka (N) | Tongi 230/132/33kV Grid Sub-Station | Tongi-Ghorashal Ckt-1 | 2023-05-12 05:27 | 2023-05-12 07:50 | 2:23 | S/O | Shutdown taken by Ghorashal substation with concern nldc | 0 | 0
Dhaka (N) | Jamalpur 132/33kV Grid Sub-Station | Mymensingh Ckt-01 | 2023-05-28 11:35 | 2023-05-28 13:45 | 2:10 | S/O | LA MAINTENANCE WORK MYMENSINGH SIDE | 0 | 0
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-1 | 2023-05-26 11:36 | 2023-05-26 15:17 | 3:41 | S/O | Transportation of T-3 transformer from its pad to T-2 pad | 0 | 0
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-1 | 2023-05-27 18:20 | 2023-05-27 21:22 | 3:02 | S/O | T-3 shifting work | 0 | 0
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-1 | 2023-05-28 11:35 | 2023-05-28 13:44 | 2:09 | S/O | LA connection | 0 | 0
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-2 | 2023-05-26 15:20 | 2023-05-26 18:33 | 3:13 | S/O | Due to TR2 Transformer shifting work safety purposes | 0 | 0
Dhaka (N) | Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Jamalpur Ckt-2 | 2023-05-27 17:23 | 2023-05-27 18:00 | 0:37 | S/O | T-3 shifting work | 0 | 0
|  |  |  | Total : | 17:58 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Dhaka (S) | Maniknagar 230/132kV Grid Sub-Station | 230kV Siddhirganj-Maniknagar ckt-1 | 2023-05-29 05:41 | 2023-05-29 13:45 | 8:04 | S/O | ERS-02 Tower Work | 0 | 0
Dhaka (S) | Haripur 230/132kV Grid Sub-Station | Madanganj-1 | 2023-05-04 08:48 | 2023-05-04 14:30 | 5:42 | S/O | From other end. | 0 | 0
Dhaka (S) | Madanganj 132/33kV Grid Sub-Station | Madanganj -Haripur 132 kv Ckt-1 | 2023-05-04 08:47 | 2023-05-04 14:31 | 5:44 | S/O | None | 0 | 0
Dhaka (S) | Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 102 MW 132 kv Ckt | 2023-05-06 07:28 | 2023-05-06 08:10 | 0:42 | S/O | Closing coil replacement of CB | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 100MW Dutch Bangla | 2023-05-08 06:48 | 2023-05-08 11:52 | 5:04 | S/O | Corrective maintenance. | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-05-20 09:28 | 2023-05-20 15:40 | 6:12 | S/O | SPMD Dhaka-1 will troubleshoot the faulty RET670 relay of MTR-2 transformer bay.Work at 230 kv Site. | 0 | 0
Dhaka (S) | Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-05-27 09:13 | 2023-05-27 21:19 | 12:06 | S/O | Relay changing work in 230kv sub station.No interruption. | 0 | 0
Dhaka (S) | Siddhirganj 230/132kV Grid Sub-Station | Maniknagar 1 | 2023-05-29 05:41 | 2023-05-29 12:53 | 7:12 | S/O | Order of NLDC | 0 | 0
Dhaka (S) | Sonargaon 132/33kV Grid Sub-Station | Daudkandi-2 | 2023-05-21 09:06 | 2023-05-21 11:54 | 2:48 | S/O | Tower No-77 Jumper Loop Opened. | 0 | 0
Dhaka (S) | Fatullah 132/33kV Grid Sub-Station | 132 kV Hasnabad | 2023-05-30 08:49 | 2023-05-30 19:38 | 10:49 | S/O | Removal of LILO between Hasnabad and Fatullah Grid at Agreeko Powerpalnt. Shutdown was taken by NLDC. | 0 | 0
Dhaka (S) | Hasnabad 132/33kV Grid Substation | Aggreko (Brahmongaon) | 2023-05-23 10:08 | 2023-05-23 12:23 | 2:15 | S/O | Reserve Bus R-DS finger maintenance | 0 | 0
Dhaka (S) | Hasnabad 132/33kV Grid Substation | Aggreko Aourahati | 2023-05-10 08:28 | 2023-05-10 13:03 | 4:35 | S/O | Main Bus DS finger change maintenace | 0 | 0
Dhaka (S) | Mogbazar 132/33kV Grid Sub-Station | Rampura 1 | 2023-05-30 05:36 | 2023-05-30 06:40 | 1:04 | S/O | Yearly Maintenance | 0 | 0
|  |  |  | Total : | 72:17 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
HVDC | Ishurdi 132/33kV Grid Sub-Station | 132 kV Bheramara -2 | 2023-05-26 07:43 | 2023-05-26 16:20 | 8:37 | S/O | DS Loop Maintenance | 0 | 0
HVDC | Bheramara 230/132kV Grid Sub-Station | Ishurdi 2 | 2023-05-26 07:43 | 2023-05-26 16:22 | 8:39 | S/O | MAINTENANCE WORK ISHURDI SIDE | 0 | 0
|  |  |  | Total : | 17:16 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna | Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-2 | 2023-05-08 08:06 | 2023-05-08 17:24 | 9:18 | S/O | Maintenance Work Payra End | 0 | 0
Khulna | Faridpur 132/33kV Grid Sub-Station | 132 KV 50MW Power Station ckt-1 | 2023-05-16 09:17 | 2023-05-16 17:02 | 7:45 | S/O | Scheduled Shutdown For power station. | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gopalganj North-2 | 2023-05-23 10:02 | 2023-05-23 21:23 | 11:21 | S/O | Aldc | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-05-21 09:03 | 2023-05-21 18:41 | 9:38 | S/O | Such pre commissioning at gallamari end. | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-05-25 13:15 | 2023-05-25 14:50 | 1:35 | S/O | Instructed by ALDC | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-05-28 11:24 | 2023-05-28 12:36 | 1:12 | S/O | Testing | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-1 | 2023-05-30 08:18 | 2023-05-30 20:51 | 12:33 | S/O | Aldc | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2023-05-22 09:04 | 2023-05-22 17:24 | 8:20 | S/O | Aldc | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2023-05-25 14:50 | 2023-05-25 16:10 | 1:20 | S/O | Instructed by ALDC | 0 | 0
Khulna | Gopalganj 132/33kV Grid Sub-Station | Gallamari-2 | 2023-05-28 12:48 | 2023-05-28 13:13 | 0:25 | S/O | Testing | 0 | 0
Khulna | Madaripur 132/33kV Grid Sub-Station | Gopaganj North CKT-01 | 2023-05-01 08:07 | 2023-05-01 15:21 | 7:14 | S/O | Maintenance work | 0 | 0
Khulna | Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-05-28 14:20 | 2023-05-28 14:48 | 0:28 | S/O | Tree Trimming. | 0 | 0
Khulna | Khulna(S) 230/132kV Grid Sub-Station | Gallamari Ckt-1 | 2023-05-24 15:50 | 2023-05-24 20:16 | 4:26 | S/O | According to ALDC instruction. | 0 | 0
|  |  |  | Total : | 75:35 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  |  | 283:05 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:May 2023
| Area | Previous Month (April' 2023) |  |  |  | Current Month (May '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 12 | 24 | 59 | 95 | 27 | 63 | 60 | 150
2 | Dhaka (South) Grid Circle. | 19 | 3 | 13 | 35 | 16 | 26 | 28 | 70
3 | Chattogram Grid Circle. | 14 | 18 | 9 | 41 | 21 | 14 | 17 | 52
4 | Cumilla Grid Circle. | 16 | 25 | 28 | 69 | 16 | 25 | 20 | 61
5 | Khulna Grid Circle. | 14 | 12 | 38 | 64 | 44 | 50 | 32 | 126
6 | HVDC Grid Circle | 28 | 24 | 12 | 64 | 9 | 21 | 6 | 36
7 | Bogura Grid Circle. | 14 | 35 | 26 | 75 | 20 | 71 | 30 | 121
8 | Others |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 117 | 141 | 185 | 443 |  |  |  | 616
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:May2023
| Area | Previous Month (April' 2023) |  |  |  | Current Month (May '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 155.76 | 188.85 | 564.17 | 908.78 | 156.83 | 1989.57 | 2356.6 | 4503
2 | Dhaka (South) Grid Circle. | 1031.51 | 20.83 | 17.5 | 1069.84 | 109.03 | 122.6 | 808.75 | 1040.38
3 | Chattogram Grid Circle. | 67.12 | 289.33 | 0 | 356.45 | 34.37 | 108 | 69 | 211.37
4 | Cumilla Grid Circle. | 114.87 | 472.53 | 409.31 | 996.71 | 536.02 | 79.64 | 413.4167 | 1029.0767
5 | Khulna Grid Circle. | 137.216 | 129.73 | 276.6 | 543.546 | 449.16 | 364.5 | 366.53 | 1180.19
6 | HVDC Grid Circle | 5302.9 | 231.93 | 0 | 5534.83 | 873.93 | 611.681 | 91.33 | 1576.941
7 | Bogura Grid Circle. | 76.31 | 990.07 | 404.3667 | 1470.7467 | 191.04 | 933.73 | 936.47 | 2061.24
8 | Others |  |  |  | 0 |  |  |  | 0
9 | Total | 6885.686 | 2323.27 | 1671.9467 | 10880.9027 | 6885.686 | 2323.27 | 1671.9467 | 11602.1977
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:May2023
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 34 | 20 | 54 | 7 | 6 | 41 | 4501.03
2 | Dhaka (South) | 5031.6 | 9 | 8 | 17 | 3 | 3 | 13 | 1040.38
3 | Chattogram | 2042 | 6 | 2 | 8 | 4 | 2 | 2 | 211.36
4 | Khulna | 2434 | 37 | 10 | 47 | 15 | 9 | 23 | 1175.125
5 | HVDC | 5954.3 | 18 | 2 | 23 | 1 | 3 | 16 | 1521.917
6 | Bogura | 3145.6 | 39 | 15 | 54 | 2 | 2 | 50 | 2017.96
7 | Cumilla | 2981 | 15 | 4 | 19 | 3 | 6 | 10 | 1025.9
8 | Others | - | - | - |  | - | - | - | 0
| Total | 30390.1 | [6 empty] | 11493.672
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.96%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.93%
4 | Khulna | 99.92%
5 | HVDC | 99.94% | [6 empty] | Executive Engineer
6 | Bogura | 99.95% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:May 2023
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 1 |  | 1 | 1 | - |  | - | 1.17
2 | Dhaka (South) | 990.29 | - | - | - | - | - | - | - | - | -
3 | Chattogram | 917 | - | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | 1 |  | 1 | 1 |  |  |  | 5.07
5 | HVDC | 1325 | - | 1 |  | 1 | - | - | 1 | - | 55.03
6 | Bogura | 1803.3 | - | 2 |  | 2 | 2 | - |  | - | 43.27
7 | Cumilla | 1648.16 | - | 1 |  | 1 |  | 1 | - | - | 3.1667
8 | Others | - |  |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [8 empty] | 107.7067
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.96%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogura | 99.94% | [7 empty] | Information Management Division
7 | Cumilla | 99.96% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:May2023
Type of | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2023-05-01 | 10 | - | 8 | 30hr12 min | 1 | 01hr20 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/5 |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:May2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Bogura 132/33kV Grid Sub-Station | 1 | 3:23 | 20.3
Bogura 132/33kV Grid Sub-Station | 1 | 0:10 | 20.3
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:07 | 4.3333
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:07 | 5.5833
Joydebpur 132/33kV Grid Sub-Station | 1 | 1:53 | 5.5833
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 1:45 | 47.0833
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 1:13 | 42
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:43 | 18.25
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:53 | 17.1667
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:47 | 47.0833
Sirajganj 132/33kV Grid Sub-Station | 1 | 1:11 | 46.3667
Chapai 132/33kV Grid Sub-Station | 1 | 1:23 | 21.3
Chapai 132/33kV Grid Sub-Station | 1 | 1:11 | 27.6667
Chapai 132/33kV Grid Sub-Station | 1 | 1:26 | 21.3
Chapai 132/33kV Grid Sub-Station | 1 | 1:11 | 28.6667
Chapai 132/33kV Grid Sub-Station | 1 | 13:21 | 8.2833
Chapai 132/33kV Grid Sub-Station | 1 | 1:11 | 66.75
Chapai 132/33kV Grid Sub-Station | 1 | 11:24 | 8.2833
Chapai 132/33kV Grid Sub-Station | 1 | 2:04 | 57
Naogaon 132/33kV Grid Sub-Station | 1 | 1:45 | 74.4
Naogaon 132/33kV Grid Sub-Station | 1 | 2:05 | 63
Naogaon 132/33kV Grid Sub-Station | 1 | 0:29 | 72.9167
Naogaon 132/33kV Grid Sub-Station | 1 | 0:46 | 20.3
Niamatpur 132/33kV Grid Sub-Station | 1 | 1:56 | 16.1
Niamatpur 132/33kV Grid Sub-Station | 1 | 2:35 | 46.4
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:49 | 34.875
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:21 | 18.1667
Jaldhaka 132/33kV Grid Sub-Station | 1 | 6:28 | 13.5
Jaldhaka 132/33kV Grid Sub-Station | 1 | 4:39 | 35.1
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:23 | 13.8333
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:13 | 38.9333
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:16 | 40.5333
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:04 | 34.1333
Page: 2/5 |  |  |  | QF-LDC-32
Month:May2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Kurigram 132/33kV Grid Sub-Station | 1 | 0:04 | 7.6
Saidpur 132/33kV Grid Sub-Station | 1 | 1:54 | 3.2
Saidpur 132/33kV Grid Sub-Station | 1 | 1:52 | 30.4
Saidpur 132/33kV Grid Sub-Station | 1 | 1:08 | 4.8
Naogaon 132/33kV Grid Sub-Station | 1 | 0:22 | 8.8
Rajshahi 132/33kV Grid Sub-Station | 1 | 1:34 | 34.4667
Bogura 132/33kV Grid Sub-Station | 1 | 2:10 | 27.0833
Bogura 132/33kV Grid Sub-Station | 1 | 2:12 | 27.5
Bogura 132/33kV Grid Sub-Station | 1 | 2:10 | 27.0833
Bogura 132/33kV Grid Sub-Station | 1 | 2:12 | 27.5
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 3:40 | 88
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 3:43 | 89.2
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 1:10 | 14
Mahasthangarh 132/33kV Grid Sub-Station | 1 | 3:36 | 86.4
Purbasadipur 132/33kV Grid Sub-Station | 1 | 3:40 | 88
Purbasadipur 132/33kV Grid Sub-Station | 1 | 1:30 | 18
Purbasadipur 132/33kV Grid Sub-Station | 1 | 1:35 | 31.6667
Purbasadipur 132/33kV Grid Sub-Station | 1 | 3:38 | 43.6
Thakurgaon 132/33kV Grid Sub-Station | 1 | 26:19 | 184.2167
Thakurgaon 132/33kV Grid Sub-Station | 1 | 26:19 | 184.2167
Khagrachori 132/33kV Grid Sub-Station | 1 | 0:18 | 2.1
Khagrachori 132/33kV Grid Sub-Station | 1 | 0:18 | 2.1
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:18 | 21
Coxsbazar 132/33kV Grid Sub-Station | 1 | 0:11 | 9.1667
Dohazari 132/33kV Grid Sub-Station | 1 | 1:12 | 54
Dohazari 132/33kV Grid Sub-Station | 1 | 1:12 | 54
Dohazari 132/33kV Grid Sub-Station | 1 | 0:46 | 34.5
Dohazari 132/33kV Grid Sub-Station | 1 | 0:46 | 34.5
Feni 132/33kV Grid Sub-Station | 1 | 0:25 | 7.9167
Ramganj 132/33kV Grid Sub-Station | 1 | 0:41 | 27.3333
Kulaura 132/33kV Grid Sub-Station | 1 | 1:12 | 14.4
Kulaura 132/33kV Grid Sub-Station | 1 | 1:15 | 15
Kulaura 132/33kV Grid Sub-Station | 1 | 0:41 | 20.5
Kulaura 132/33kV Grid Sub-Station | 1 | 0:41 | 20.5
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:04 | 1.3333
Shahjibazar 132/33kV Grid Sub-Station | 1 | 0:37 | 19.7333
Sylhet 132/33kV Grid Sub-Station | 1 | 2:01 | 29.1333
Sylhet 132/33kV Grid Sub-Station | 1 | 2:02 | 32.5
Sylhet 132/33kV Grid Sub-Station | 1 | 0:11 | 167.1667
Sylhet 132/33kV Grid Sub-Station | 1 | 5:11 | 33.3333
Sylhet 132/33kV Grid Sub-Station | 1 | 1:23 | 167.1667
Sylhet 132/33kV Grid Sub-Station | 1 | 1:23 | 23.1
Sylhet 132/33kV Grid Sub-Station | 1 | 0:42 | 33.3667
Sunamganj 132/33kV Grid Sub-Station | 1 | 0:19 | 3.1667
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 2:20 | 46.6667
Chhatak 132/33kV Grid Sub-Station | 1 | 6:11 | 304.6667
Chhatak 132/33kV Grid Sub-Station | 1 | 6:14 | 30.9167
Sylhet 132/33kV Grid Sub-Station | 1 | 1:31 | 31.1667
Page: 3/5 |  |  |  | QF-LDC-32
Month:May2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
Manikganj 132/33kV Grid Sub-Station | 1 | 0:38 | 12.6667
Manikganj 132/33kV Grid Sub-Station | 1 | 0:38 | 12.6667
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:19 | 17.4167
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:19 | 17.4167
Joydebpur 132/33kV Grid Sub-Station | 1 | 0:57 | 38
Joydebpur 132/33kV Grid Sub-Station | 1 | 4:53 | 244.1667
Sreepur 230/132/33kV Grid Sub-Station | 1 | 1:36 | 60.8
Sreepur 230/132/33kV Grid Sub-Station | 1 | 2:40 | 53.3333
Sreepur 230/132/33kV Grid Sub-Station | 1 | 2:40 | 53.3333
Sreepur 230/132/33kV Grid Sub-Station | 1 | 3:38 | 72.6667
Tongi 230/132/33kV Grid Sub-Station | 1 | 9:58 | 199.3333
Tongi 230/132/33kV Grid Sub-Station | 1 | 10:00 | 200
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:40 | 320
Kabirpur 132/33kV Grid Sub-Station | 1 | 2:42 | 324
Jamalpur 132/33kV Grid Sub-Station | 1 | 2:08 | 53.3333
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:42 | 17
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:12 | 0.4
Jamalpur 132/33kV Grid Sub-Station | 1 | 2:08 | 53.3333
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:42 | 17
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:12 | 0.4
Jamalpur 132/33kV Grid Sub-Station | 1 | 2:08 | 53.3333
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:42 | 17
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:12 | 0.4
Jamalpur 132/33kV Grid Sub-Station | 1 | 2:08 | 53.3333
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:42 | 17
Jamalpur 132/33kV Grid Sub-Station | 1 | 0:12 | 0.4
Kishoreganj 132/33kV Grid Sub-Station | 1 | 1:19 | 92.1667
Sherpur 132/33kV Grid Sub-Station | 1 | 1:01 | 16.2667
Sherpur 132/33kV Grid Sub-Station | 1 | 1:02 | 16.5333
Sherpur 132/33kV Grid Sub-Station | 1 | 2:40 | 26.6667
Sherpur 132/33kV Grid Sub-Station | 1 | 2:42 | 27
Tangail 132/33kV Grid Sub-Station | 1 | 0:34 | 18.1333
Tangail 132/33kV Grid Sub-Station | 1 | 0:37 | 19.7333
Tangail 132/33kV Grid Sub-Station | 1 | 0:36 | 19.2
Page: 4/5 |  |  |  | QF-LDC-32
Month:May2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
Manikganj 132/33kV Grid Sub-Station | 1 | 0:07 | 1.1667
Kodda 132/33kV Grid Sub-Station | 1 | 12:07 | 605.8333
Kodda 132/33kV Grid Sub-Station | 1 | 1:57 | 78
Kodda 132/33kV Grid Sub-Station | 1 | 1:58 | 78.6667
Kodda 132/33kV Grid Sub-Station | 1 | 1:07 | 22.3333
Kodda 132/33kV Grid Sub-Station | 1 | 1:11 | 23.6667
Sreepur 230/132/33kV Grid Sub-Station | 1 | 3:38 | 72.6667
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:12 | 84
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:12 | 84
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:57 | 136.5
Kabirpur 132/33kV Grid Sub-Station | 1 | 1:58 | 137.6667
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:36 | 24
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:09 | 13.8
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:36 | 24
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:09 | 13.8
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:41 | 25.25
Jamalpur 132/33kV Grid Sub-Station | 1 | 1:36 | 24
Mymensingh 132/33kV Grid Sub-Station | 1 | 3:24 | 408
Mymensingh 132/33kV Grid Sub-Station | 1 | 3:25 | 410
Tangail 132/33kV Grid Sub-Station | 1 | 1:17 | 44.9167
Tangail 132/33kV Grid Sub-Station | 1 | 1:18 | 45.5
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:54 | 22.5
Sonargaon 132/33kV Grid Sub-Station | 1 | 1:17 | 38.5
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:32 | 13.3333
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:54 | 22.5
Sonargaon 132/33kV Grid Sub-Station | 1 | 1:17 | 38.5
Sonargaon 132/33kV Grid Sub-Station | 1 | 1:26 | 44.4333
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:27 | 31.5
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:31 | 16.0167
Lalbag 132/33kV Grid Sub-Station | 1 | 1:10 | 3.75
Nawabganj 132/33kV Grid Sub-Station | 1 | 0:06 | 0.6
Nawabganj 132/33kV Grid Sub-Station | 1 | 4:01 | 100.4167
Nawabganj 132/33kV Grid Sub-Station | 1 | 4:06 | 102.5
Nawabganj 132/33kV Grid Sub-Station | 1 | 4:00 | 100
Nawabganj 132/33kV Grid Sub-Station | 1 | 4:08 | 103.3333
Nawabganj 132/33kV Grid Sub-Station | 1 | 3:47 | 94.5833
Nawabganj 132/33kV Grid Sub-Station | 1 | 3:49 | 95.4167
Narshingdi 132/33kV Grid Sub-Station | 1 | 6:48 | 170
Narshingdi 132/33kV Grid Sub-Station | 1 | 2:50 | 42.5
Ishurdi 132/33kV Grid Sub-Station | 1 | 2:39 | 87.45
Ishurdi 132/33kV Grid Sub-Station | 1 | 2:39 | 87.45
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:34 | 15.8667
Ishurdi 132/33kV Grid Sub-Station | 1 | 24:33 | 687.4
Ishurdi 132/33kV Grid Sub-Station | 1 | 0:34 | 15.8667
Page:5/5 |  |  |  | QF-LDC-32
Month:May2023
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
| Total Nos.of | Total | Total | Remarks
Sub-station | Interruption | Duration of | Unserved
|  | Interruption | Energy
Pabna 132/33kV Grid Sub-Station | 1 | 0:07 | 4.0833
Shahjadpur 132/33kV Grid Sub-Station | 1 | 0:45 | 6
Shahjadpur 132/33kV Grid Sub-Station | 1 | 0:55 | 9.1667
Jhenaidah 132/33kV Grid Sub-Station | 1 | 6:42 | 167.5
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:43 | 51.5
Jhenaidah 132/33kV Grid Sub-Station | 1 | 7:02 | 7.0333
Jhenaidah 132/33kV Grid Sub-Station | 1 | 2:16 | 68
Jhenaidah 132/33kV Grid Sub-Station | 1 | 0:31 | 0.51667
Kushtia 132/33kV Grid Sub-Station | 1 | 1:22 | 47.8333
Kushtia 132/33kV Grid Sub-Station | 1 | 1:24 | 49
Magura 132/33kV Grid Sub-Station | 1 | 1:01 | 20.3333
Magura 132/33kV Grid Sub-Station | 1 | 1:41 | 42.0833
Magura 132/33kV Grid Sub-Station | 1 | 1:03 | 21
Magura 132/33kV Grid Sub-Station | 1 | 1:42 | 42.5
Shahjadpur 132/33kV Grid Sub-Station | 1 | 2:07 | 55.0333
Kushtia 132/33kV Grid Sub-Station | 1 | 1:07 | 44.6667
Kushtia 132/33kV Grid Sub-Station | 1 | 1:10 | 46.6667
Barishal 132/33kV Grid Sub-Station | 1 | 0:32 | 38.4
Barishal 132/33kV Grid Sub-Station | 1 | 0:33 | 39.6
Barishal 132/33kV Grid Sub-Station | 1 | 3:05 | 222
Gopalganj 132/33kV Grid Sub-Station | 1 | 0:23 | 3.8333
Gopalganj 132/33kV Grid Sub-Station | 1 | 0:17 | 14.1667
Gopalganj 132/33kV Grid Sub-Station | 1 | 0:24 | 4
Gopalganj 132/33kV Grid Sub-Station | 1 | 0:18 | 15
Gopalganj 132/33kV Grid Sub-Station | 1 | 0:20 | 3.3333
Madaripur 132/33kV Grid Sub-Station | 1 | 0:32 | 14.6667
Madaripur 132/33kV Grid Sub-Station | 1 | 0:33 | 15.125
Madaripur 132/33kV Grid Sub-Station | 1 | 0:42 | 19.25
Benapole 132/33kV Grid Sub-Station | 1 | 0:24 | 4
Benapole 132/33kV Grid Sub-Station | 1 | 0:24 | 4
Khulna (C) 132/33kV Grid Sub-Station | 1 | 0:07 | 2.5667
Khulna (C) 132/33kV Grid Sub-Station | 1 | 0:07 | 2.5667
Noapara 132/33kV Grid Sub-Station | 1 | 0:57 | 17.1
Noapara 132/33kV Grid Sub-Station | 1 | 0:59 | 17.7
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:07 | 1.9833
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:17 | 0.85
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:04 | 1.1333
Bagerhat 132/33kV Grid Sub-Station | 1 | 0:16 | 0.8
Gollamari 132/33kV Grid Sub-Station | 1 | 2:06 | 0
Gollamari 132/33kV Grid Sub-Station | 1 | 1:30 | 7.5
Gollamari 132/33kV Grid Sub-Station | 1 | 1:08 | 34
Gollamari 132/33kV Grid Sub-Station | 1 | 2:07 | 0.46667
Gollamari 132/33kV Grid Sub-Station | 1 | 0:04 | 7.6667
Gollamari 132/33kV Grid Sub-Station | 1 | 1:32 | 21
Gollamari 132/33kV Grid Sub-Station | 1 | 0:42 | 36.5
Gollamari 132/33kV Grid Sub-Station | 1 | 1:31 | 25.7833
Gollamari 132/33kV Grid Sub-Station | 1 | 1:08 | 14.7333
Gollamari 132/33kV Grid Sub-Station | 1 | 0:07 | 1.05
Gollamari 132/33kV Grid Sub-Station | 1 | 1:33 | 26.35
Gollamari 132/33kV Grid Sub-Station | 1 | 3:11 | 136.8833
Mongla 132/33kV Grid Sub-Station | 1 | 2:28 | 12.3333
Mongla 132/33kV Grid Sub-Station | 1 | 0:42 | 9.8
Mongla 132/33kV Grid Sub-Station | 1 | 2:29 | 12.4167
Mongla 132/33kV Grid Sub-Station | 1 | 0:43 | 10.0333
Satkhira 132/33kV Grid Sub-Station | 1 | 0:20 | 10
Barishal 132/33kV Grid Sub-Station | 1 | 0:08 | 5.0667
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:01 | 10.1667
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:02 | 10.3333
Faridpur 132/33kV Grid Sub-Station | 1 | 1:57 | 78
Faridpur 132/33kV Grid Sub-Station | 1 | 1:59 | 79.3333
Gopalganj 132/33kV Grid Sub-Station | 1 | 7:50 | 19.7333
Gopalganj 132/33kV Grid Sub-Station | 1 | 1:14 | 52.8333
Gopalganj 132/33kV Grid Sub-Station | 1 | 5:17 | 20.2667
Gopalganj 132/33kV Grid Sub-Station | 1 | 1:16 | 53.1667
Gopalganj 132/33kV Grid Sub-Station | 1 | 5:19 | 19.2
Madaripur 132/33kV Grid Sub-Station | 1 | 2:24 | 23.5
Grand Total | 216 | 496:46 | 11601.3833
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 |  |  | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station |  |  |  | 2022-05-01
Month:May 2023
Sl. No | Sub-station | Date and time | Load (MW)
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-05-08 13:00 | 65
2 | Agargaon 230/132kV Grid Sub-Station | 2023-05-10 15:00 | 100
3 | Banani 132/33kV Grid Sub-Station | 2023-05-09 13:00 | 88
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-05-09 10:00 | 28
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-05-09 16:00 | 202
6 | BashundharaCement 132/33kV Sub-Station | 2023-05-03 10:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2023-05-30 21:00 | 270
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-05-31 19:00 | 156
9 | Charsaidpur 132/33kV Sub-Station | 2023-05-29 09:00 | 93
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-05-10 12:00 | 42
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-05-07 19:30 | 130
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-05-10 13:00 | 168
13 | Dummy | 2023-05-30 02:00 | 50
14 | Fatullah 132/33kV Grid Sub-Station | 2023-05-11 15:00 | 73
15 | Ghorashal 230/132/33kV Sub-Station | 2023-05-28 07:00 | 0
16 | Gulshan 132/33kV Grid Sub-Station | 2023-05-10 15:00 | 88
17 | HaripurSBU 132/33kV Sub-Station | 2023-05-22 21:00 | 167
18 | Hasnabad 132/33kV Grid Substation | 2023-05-16 19:00 | 119
19 | Joydebpur 132/33kV Grid Sub-Station | 2023-05-31 20:00 | 183
20 | Kabirpur 132/33kV Grid Sub-Station | 2023-05-07 19:30 | 318
21 | Kallyanpur 132/33kV Grid Sub-Station | 2023-05-31 19:30 | 126
22 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-05-16 19:30 | 90
23 | Kazla 132/33kV Grid Sub-Station | 2023-05-30 06:00 | 166
24 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-05-31 19:00 | 74
25 | Kodda 132/33kV Grid Sub-Station | 2023-05-21 19:00 | 333
26 | Lalbag 132/33kV Grid Sub-Station | 2023-05-31 19:00 | 95
27 | Madanganj 132/33kV Grid Sub-Station | 2023-05-10 | 46
28 | Madartek 132/33kV Grid Sub-Station | 2023-05-31 22:00 | 100.02
29 | Manikganj 132/33kV Grid Sub-Station | 2023-05-31 21:00 | 133
30 | Maniknagar 132/33kV Grid Sub-Station | 2023-05-10 13:00 | 112
31 | Matuail 132/33kV Grid Sub-Station | 2023-05-29 15:00 | 112
32 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-05-22 12:00 | 108
33 | Mirpur 132/33kV Grid Sub-Station | 2023-05-31 19:30 | 175
34 | Mogbazar 132/33kV Grid Sub-Station | 2023-05-10 14:00 | 154
35 | Motijheel 132/33kV Grid Sub-Station | 2023-05-10 16:00 | 51
36 | Munshiganj 132/33kV Grid Sub-Station | 2023-05-07 23:00 | 116
37 | Narinda 132/33kV Grid Sub-Station | 2023-05-31 19:00 | 82
38 | Narshingdi 132/33kV Grid Sub-Station | 2023-05-12 21:00 | 189
39 | Nawabganj 132/33kV Grid Sub-Station | 2023-05-10 | 56.4
40 | New Tongi 132/33kV Grid Sub-Station | 2023-05-08 12:00 | 90.8
41 | Postogola 132/33kV Grid Sub-Station | 2023-05-31 21:00 | 65
42 | Purbachal 132/33kV Grid Sub-Station | 2023-05-31 | 46
43 | Rahim Steel 132/33kV Sub-Station | 2023-05-16 12:00 | 54
44 | Rajendrapur 132/33kV Grid Sub-Station | 2023-05-27 12:00 | 104
45 | Satmasjid 132/33kV Grid Sub-Station | 2023-05-10 16:00 | 135
46 | Savar 132/33kV Grid Sub-Station | 2023-05-16 18:30 | 207
47 | Shitalakhya 132/33kV Grid Sub-Station | 2023-05-29 09:00 | 180.8
48 | Shyampur 132/33kV Grid Sub-Station | 2023-05-10 10:00 | 180
49 | Siddhirganj 132/33kV Grid Sub-Station | 2023-05-22 16:00 | 122
50 | Sonargaon 132/33kV Grid Sub-Station | 2023-05-21 11:00 | 100
51 | Sreepur 230/132/33kV Grid Sub-Station | 2023-05-08 19:00 | 69.62
52 | Srinagar 132/33kV Grid Sub-Station | 2023-05-08 21:00 | 50.48
53 | Tongi 230/132/33kV Grid Sub-Station | 2023-05-30 21:00 | 113
54 | Ullon 132/33kV Grid Sub-Station | 2023-05-31 | 48
55 | Uttara 132/33kV Grid Sub-Station | 2023-05-10 15:00 | 81
56 | UttaraNew 132/33kV Grid Sub-Station | 2023-05-10 13:00 | 60
57 | Zigatola 132/33kV Grid Sub-Station | 2023-05-30 10:00 | 122
58 | Agrabad 132/33kV Grid Sub-Station | 2023-05-10 17:00 | 88
59 | AKS 132/33kV Grid Sub-Station | 2023-05-22 19:30 | 26
60 | AKSML 230/33kV Grid Sub-Station | 2023-05-03 11:00 | 120
61 | Bakulia 132/33kV Grid Sub-Station | 2023-05-08 20:00 | 119
Page: 2/3 |  |  | QF-LDC-33
Month:May 2023
62 | Baroaulia 132/33kV Grid Sub-Station | 2023-05-31 08:00 | 73
63 | Baroirhat 132/33kV Grid Sub-Station | 2023-05-11 20:00 | 69
64 | BSRM 230/33kV Grid Sub-Station | 2023-05-31 12:00 | 170
65 | Chandraghona 132/33kV Grid Sub-Station | 2023-05-08 21:00 | 34
66 | Coxsbazar 132/33kV Grid Sub-Station | 2023-05-07 20:00 | 138.5
67 | Dohazari 132/33kV Grid Sub-Station | 2023-05-02 19:00 | 102
68 | GPH 230/33kV Grid Sub-Station | 2023-05-27 15:00 | 97
69 | Halishahar 132/33kV Grid Sub-Station | 2023-05-13 10:00 | 126
70 | Hathazari 230/132/33kV Grid Sub-Station | 2023-05-10 19:00 | 86
71 | Juldah 132/33kV Grid Sub-Station | 2023-05-02 19:00 | 32
72 | Kalurghat 132/33kV Grid Sub-Station | 2023-05-04 11:00 | 41
73 | Kaptai 132/33kV Sub-Station | 2023-05-03 18:00 | 5
74 | Khagrachori 132/33kV Grid Sub-Station | 2023-05-07 19:00 | 36
75 | Khulshi 132/33kV Grid Sub-Station | 2023-05-07 19:30 | 201
76 | KSRM 132/33kV Grid Sub-Station | 2023-05-13 18:00 | 70
77 | Madunaghat 132/33kV Grid Sub-Station | 2023-05-10 18:30 | 61
78 | Matarbari 132/33kV Sub-Station | 2023-05-10 | 51
79 | Mirsorai 230/33kV Grid Sub-Station | 2023-05-16 19:00 | 6.5
80 | Modern Steel 132/11kV Grid Sub-Station | 2023-05-01 | 0
81 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-05-21 18:30 | 37
82 | Rangamati 132/33kV Grid Sub-Station | 2023-05-01 19:00 | 18
83 | Shahmirpur 132/33kV Grid Sub-Station | 2023-05-03 19:00 | 63.3
84 | Shikalbaha 132/33kV Sub-Station | 2023-05-10 19:00 | 40
85 | Sholosohor 132/33kV Grid Sub-Station | 2023-05-08 19:00 | 43
86 | SSM 132/33kV Grid Sub-Station | 2023-05-02 09:00 | 18
87 | TK chemical 132kV Grid Sub-Station | 2023-05-10 19:00 | 34
88 | Ashuganj 230/132/33kV Sub-Station | 2023-05-11 23:00 | 81
89 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-05-11 19:30 | 188
90 | Chandpur 132/33kV Grid Sub-Station | 2023-05-08 21:00 | 75
91 | Chauddagram 132/33kV Grid Sub-Station | 2023-05-06 20:00 | 73
92 | Chowmuhani 132/33kV Grid Sub-Station | 2023-05-29 21:00 | 233
93 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-05-11 19:30 | 205
94 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-05-11 01:00 | 182
95 | Daudkandi 132/33kV Grid Sub-Station | 2023-05-11 19:30 | 152
96 | Feni 132/33kV Grid Sub-Station | 2023-05-22 20:00 | 140
97 | Kachua 132/33kV Grid Sub-Station | 2023-05-22 20:00 | 92
98 | PHP 132/33kV Sub-Station | 2023-05-25 18:30 | 11
99 | Ramganj 132/33kV Grid Sub-Station | 2023-05-11 19:30 | 132
100 | Bhaluka 132/33kV Grid Sub-Station | 2023-05-30 21:00 | 186
101 | Jamalpur 132/33kV Grid Sub-Station | 2023-05-02 19:00 | 173
102 | Kishoreganj 132/33kV Grid Sub-Station | 2023-05-05 21:00 | 148
103 | Mymensingh 132/33kV Grid Sub-Station | 2023-05-06 21:00 | 180
104 | Netrakona 132/33kV Grid Sub-Station | 2023-05-28 19:30 | 142
105 | Sherpur 132/33kV Grid Sub-Station | 2023-05-02 20:00 | 156
106 | Tangail 132/33kV Grid Sub-Station | 2023-05-30 22:00 | 242
107 | Beanibazar 132/33kV Grid Sub-Station | 2023-05-09 19:00 | 80
108 | Chhatak 132/33kV Grid Sub-Station | 2023-05-09 19:00 | 34
109 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-05-07 19:00 | 51
110 | Kulaura 132/33kV Grid Sub-Station | 2023-05-29 18:00 | 52
111 | Shahjibazar 132/33kV Grid Sub-Station | 2023-05-30 21:00 | 131
112 | Sreemongol 132/33kV Grid Sub-Station | 2023-05-30 20:00 | 74
113 | Sunamganj 132/33kV Grid Sub-Station | 2023-05-31 19:30 | 55
114 | Sylhet 132/33kV Grid Sub-Station | 2023-05-31 19:00 | 179
115 | Bagerhat 132/33kV Grid Sub-Station | 2023-05-10 22:00 | 104
116 | Benapole 132/33kV Grid Sub-Station | 2023-05-12 23:00 | 68
117 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-05-21 20:00 | 66
118 | Chuadanga 132/33kV Grid Sub-Station | 2023-05-10 21:00 | 114
119 | Faridpur 132/33kV Grid Sub-Station | 2023-05-12 23:00 | 164
120 | Goalpara 132/33kV Grid Sub-Station | 2023-05-21 23:00 | 44
121 | Gollamari 132/33kV Grid Sub-Station | 2023-05-08 13:00 | 73
122 | Gopalganj 132/33kV Grid Sub-Station | 2023-05-22 22:00 | 111.8
123 | Jashore 132/33kV Grid Sub-Station | 2023-05-31 21:00 | 159
124 | Jhenaidah 132/33kV Grid Sub-Station | 2023-05-31 21:00 | 142
125 | Khulna (C) 132/33kV Grid Sub-Station | 2023-05-17 12:00 | 111
Page: 3/3 |  |  | QF-LDC-33
Month:May 2023
126 | Kushtia 132/33kV Grid Sub-Station | 2023-05-21 19:30 | 150
127 | Madaripur 132/33kV Grid Sub-Station | 2023-05-11 22:00 | 112
128 | Magura 132/33kV Grid Sub-Station | 2023-05-22 20:00 | 66
129 | Mongla 132/33kV Grid Sub-Station | 2023-05-16 09:00 | 40
130 | Narail 132/33kV Grid Sub-Station | 2023-05-21 22:00 | 60
131 | Noapara 132/33kV Grid Sub-Station | 2023-05-19 19:00 | 59
132 | Rajbari 132/33kV Grid Sub-Station | 2023-05-21 19:30 | 76
133 | Satkhira 132/33kV Grid Sub-Station | 2023-05-11 22:00 | 141
134 | Shariatpur 132/33kV Grid Sub-Station | 2023-05-30 22:00 | 81
135 | Barguna 132/33kV Grid Sub-Station | 2023-05-09 23:00 | 24
136 | Barishal 132/33kV Grid Sub-Station | 2023-05-31 19:00 | 117
137 | Barishal 230/132kV Grid Sub-Station | 2023-05-07 19:30 | 114
138 | Bhandaria 132/33kV Grid Sub-Station | 2023-05-10 21:00 | 54
139 | Borhanuddin 230/33kV Grid Sub-Station | 2023-05-11 01:00 | 70
140 | Patuakhali 132/33kV Grid Sub-Station | 2023-05-23 01:00 | 137
141 | Payra 400/132/33kV Grid Sub-Station | 2023-05-04 21:00 | 28
142 | Amnura 132/33kV Grid Sub-Station | 2023-05-09 22:00 | 62
143 | Bhangura 132/33kV Grid Sub-Station | 2023-05-10 19:30 | 52
144 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-05-07 19:00 | 70
145 | Bogura 132/33kV Grid Sub-Station | 2023-05-31 22:00 | 185
146 | Chapai 132/33kV Grid Sub-Station | 2023-05-11 22:00 | 70
147 | Ishurdi 132/33kV Grid Sub-Station | 2023-05-06 20:00 | 79
148 | Joypurhat 132/33kV Grid Sub-Station | 2023-05-10 19:30 | 70
149 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-05-10 19:30 | 80
150 | Naogaon 132/33kV Grid Sub-Station | 2023-05-07 21:00 | 139
151 | Natore 132/33kV Grid Sub-Station | 2023-05-31 20:00 | 160
152 | Niamatpur 132/33kV Grid Sub-Station | 2023-05-09 21:00 | 97
153 | Pabna 132/33kV Grid Sub-Station | 2023-05-25 19:00 | 124
154 | Rahanpur_I 400/132kV Grid Sub-Station | 2023-05-28 17:00 | 200
155 | Rajshahi 132/33kV Grid Sub-Station | 2023-05-31 22:00 | 176
156 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-05-12 23:00 | 41
157 | Ruppur 132/11kV Grid Sub-Station | 2023-05-29 15:00 | 6.6
158 | Shahjadpur 132/33kV Grid Sub-Station | 2023-05-07 19:30 | 122
159 | Sirajganj 132/33kV Grid Sub-Station | 2023-05-07 19:30 | 116
160 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-05-30 20:00 | 66
161 | Jaldhaka 132/33kV Grid Sub-Station | 2023-05-31 21:00 | 86
162 | Kurigram 132/33kV Grid Sub-Station | 2023-05-03 19:00 | 71
163 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-05-12 20:00 | 51
164 | Mithapukur 132/33kV Grid Sub-Station | 2023-05-24 19:30 | 54
165 | Palashbari 132/33kV Grid Sub-Station | 2023-05-09 19:30 | 142
166 | Panchagarh 132/33kV Grid Sub-Station | 2023-05-12 20:00 | 65
167 | Purbasadipur 132/33kV Grid Sub-Station | 2023-05-16 19:30 | 156
168 | Rangpur 132/33kV Grid Sub-Station | 2023-05-11 19:30 | 155
169 | Saidpur 132/33kV Grid Sub-Station | 2023-05-11 20:00 | 109
170 | Thakurgaon 132/33kV Grid Sub-Station | 2023-05-16 19:30 | 101
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:May 2023
Area | MW | Date | Hour | Remarks
Dhaka | 5809 | 2023-05-28 | 2:00
Chattogram | 1458.9 | 2023-05-29 | 20:00
Cumilla | 1412 | 2023-05-29 | 20:00
Mymensingh | 1087 | 2023-05-30 | 21:00
Sylhet | 614 | 2023-05-30 | 20:00
Khulna | 1774.8 | 2023-05-22 | 22:00
Barishal | 498.8 | 2023-05-09 | 22:00
Rajshahi | 1481.8 | 2023-05-10 | 20:00
Rangpur | 949 | 2023-05-11 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [5 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:May 2023
SL. | 400 KV Substation | Rated | Maxm |  | Minm | Date and Time
No. |  | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 414 | 2023-05-16 20:00 | 383 | 2023-05-06 12:00
2 | Ashuganj 400/230kV GIS Sub-Station | 400 | 389 | 2023-05-25 12:00 | 389 | 2023-05-25 12:00
3 | Bhulta 400/230kV Grid Sub-Station | 400 | 397 | 2023-05-23 18:00 | 368 | 2023-05-17 08:00
4 | Bibiana 400/230kV Sub-Station | 400 | 413 | 2023-05-23 18:00 | 385 | 2023-05-24 09:00
5 | BIPTC | 400 | 408 | 2023-05-16 20:00 | 386 | 2023-05-29 15:00
6 | Gopalganj 400/132kV Grid Sub-Station | 400 | 419 | 2023-05-16 20:00 | 387 | 2023-05-06 12:00
7 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 407 | 2023-05-23 18:00 | 374 | 2023-05-10 11:00
8 | Madunaghat_I 400/230kV Grid Sub-Station | 400 | 423 | 2023-05-14 19:30 | 352 | 2023-05-13 08:00
9 | Payra 400kV Sub-Station | 400 | 420 | 2023-05-16 20:00 | 403 | 2023-05-06 12:00
10 | Rampal 400/230kV Grid Sub-Station | 400 | 412.16 | 2023-05-26 20:00 | 388.52 | 2023-05-27 19:00
|  | Rated | Maxm |  | Minm | Date and Time
SL. | Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
No. | 230 KV Substation | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 255 | 2023-05-11 23:00 | 218 | 2023-05-23 11:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 243 | 2023-05-18 19:00 | 199 | 2023-05-15 09:00
3 | Agargaon 230/132kV Grid Sub-Station | 230 | 231 | 2023-05-25 15:00 | 180 | 2023-05-07 07:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-05-14 19:30 | 209 | 2023-05-10 19:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 244 | 2023-05-03 17:00 | 221 | 2023-05-22 23:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 255 | 2023-05-17 15:00 | 221 | 2023-05-13 03:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 236 | 2023-05-18 05:00 | 213 | 2023-05-31 19:30
8 | BSRM 230/33kV Grid Sub-Station | 230 | 243 | 2023-05-13 21:00 | 206 | 2023-05-13 08:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-05-03 19:00 | 218 | 2023-05-20 10:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 245 | 2023-05-02 22:00 | 233 | 2023-05-10 12:00
11 | GPH 230/33kV Grid Sub-Station | 230 | 243 | 2023-05-13 21:00 | 198 | 2023-05-18 06:00
12 | Haripur 230/132kV Grid Sub-Station | 230 | 235 | 2023-05-02 03:00 | 218 | 2023-05-16 19:30
13 | Hasnabad 230/132kV Grid Sub-Station | 230 | 237 | 2023-05-03 19:00 | 218 | 2023-05-20 10:00
14 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 244 | 2023-05-14 18:30 | 206 | 2023-05-13 08:00
15 | Ishurdi 230/132kV Grid Sub-Station | 230 | 243 | 2023-05-16 20:00 | 224 | 2023-05-10 01:00
16 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 248 | 2023-05-13 19:30 | 214 | 2023-05-04 21:00
17 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 236 | 2023-05-16 20:00 | 218 | 2023-05-20 10:00
18 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 243 | 2023-05-16 20:00 | 217 | 2023-05-27 19:00
19 | Maniknagar 230/132kV Grid Sub-Station | 230 | 236 | 2023-05-01 18:30 | 218 | 2023-05-16 19:00
20 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 241 | 2023-05-01 05:00 | 222 | 2023-05-17 04:00
21 | Mirsorai 230/33kV Grid Sub-Station | 230 | 242 | 2023-05-09 23:00 | 210 | 2023-05-13 08:00
22 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 245 | 2023-05-16 20:00 | 221 | 2023-05-10 19:00
23 | Rampura 230/132kV Grid Sub-Station | 230 | 237 | 2023-05-23 18:00 | 218 | 2023-05-11 09:00
24 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 242 | 2023-05-13 19:30 | 209 | 2023-05-18 06:00
25 | Shyampur 230/132kV Grid Sub-Station | 230 | 236 | 2023-05-01 07:00 | 217 | 2023-05-20 10:00
26 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 239 | 2023-05-21 06:00 | 208 | 2023-05-27 17:00
27 | Sirajgonj 230 kV Switching Station | 230 | 242 | 2023-05-16 20:00 | 227 | 2023-05-20 09:00
28 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-05-16 20:00 | 223 | 2023-05-31 12:00
29 | Tongi 230/132/33kV Grid Sub-Station | 230 | 239 | 2023-05-23 18:00 | 200 | 2023-05-28 14:00
Page: 2/3
| Month:May 2023 |  |  |  |  | QF-LDC-35
SL. | Substation | Rated | Maxm |  | Minm | Date and Time
No. | 132 KV Substation | Voltage | Voltage | Date and Time | Voltage |  | Remarks
|  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-14 19:00 | 126 | 2023-05-06 11:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 | 114 | 2023-05-18 06:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-15 23:00 | 115 | 2023-05-18 05:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 19:00 | 123 | 2023-05-06 11:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 140 | 2023-05-01 | 132 | 2023-05-10 12:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-23 19:00 | 118 | 2023-05-21 22:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 | 118 | 2023-05-13 08:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-23 18:00 | 125 | 2023-05-06 11:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-01 06:00 | 124 | 2023-05-10 12:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-15 21:00 | 128 | 2023-05-21 23:00 |  | 16/06/22
11 | Barishal 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-15 21:00 | 119 | 2023-05-22 23:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-14 19:30 | 122 | 2023-05-15 10:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-14 19:30 | 115 | 2023-05-18 06:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-23 18:00 | 119 | 2023-05-10 12:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 139 | 2023-05-14 18:00 | 123 | 2023-05-25 23:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 139 | 2023-05-26 02:00 | 124 | 2023-05-09 18:30
17 | Benapole 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-16 20:00 | 118 | 2023-05-22 19:30
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-17 09:00 | 113 | 2023-05-10 03:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 145 | 2023-05-23 20:00 | 120 | 2023-05-21 23:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-18 06:00 | 129 | 2023-05-10 11:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 139 | 2023-05-16 20:00 | 126 | 2023-05-10 19:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 136 | 2023-05-05 05:00 | 117 | 2023-05-20 10:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-18 04:00 | 124 | 2023-05-10 19:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-18 04:00 | 124 | 2023-05-10 19:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 136 | 2023-05-21 19:30 | 127 | 2023-05-06 12:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 138 | 2023-05-23 18:00 | 123 | 2023-05-10 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-03 19:00 | 113 | 2023-05-12 08:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-14 19:30 | 119 | 2023-05-18 06:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-18 05:00 | 125 | 2023-05-05 14:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 139 | 2023-05-16 20:00 | 125 | 2023-05-15 11:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 139 | 2023-05-03 19:00 | 116 | 2023-05-21 06:00
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 136 | 2023-05-10 18:30 | 125 | 2023-05-08
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 139 | 2023-05-16 22:00 | 113 | 2023-05-13 05:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-16 19:00 | 113 | 2023-05-10 19:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-14 17:00 | 113 | 2023-05-01 04:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-03 19:00 | 121 | 2023-05-21 06:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-03 19:00 | 123 | 2023-05-20 10:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-23 18:00 | 125 | 2023-05-06 12:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 20:00 | 122 | 2023-05-06 09:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 142.6 | 2023-05-05 14:00 | 124.6 | 2023-05-22 15:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 02:00 | 116 | 2023-05-18 06:00
42 | Dummy | 132 | 132 | 2023-05-30 02:00 | 132 | 2023-05-30 02:00
43 | Faridpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-16 20:00 | 122 | 2023-05-22 23:00
44 | Fatullah 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-23 18:00 | 123 | 2023-05-20 10:00
45 | Feni 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 22:00 | 115 | 2023-05-21 02:00
46 | Goalpara 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-23 19:00 | 125 | 2023-05-21 22:00
47 | Gollamari 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-23 18:30 | 123 | 2023-05-09 11:00
48 | Gopalganj 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 20:00 | 123 | 2023-05-22 12:00
49 | Gulshan 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-23 18:00 | 124 | 2023-05-06 12:00
50 | Halishahar 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-15 23:00 | 117 | 2023-05-13 08:00
51 | HaripurSBU 132/33kV Sub-Station | 132 | 138 | 2023-05-02 18:00 | 125 | 2023-05-16 19:30
52 | Hasnabad 132/33kV Grid Substation | 132 | 139 | 2023-05-23 19:00 | 121 | 2023-05-23 11:00
53 | Ishurdi 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 20:00 | 127 | 2023-05-10 12:00
54 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-18 04:00 | 115 | 2023-05-31 04:00
55 | Jamalpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-21 19:00 | 113 | 2023-05-26 23:00
56 | Jashore 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 20:00 | 120 | 2023-05-22 19:00
57 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-16 20:00 | 124 | 2023-05-10 19:00
58 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-05-03 15:00 | 128 | 2023-05-17 08:00
59 | Joypurhat 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-18 05:00 | 113 | 2023-05-31 21:00
60 | Juldah 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-09 23:00 | 120 | 2023-05-15 10:00
61 | Kabirpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-23 18:00 | 118 | 2023-05-06 10:00
62 | Kachua 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 22:00 | 114 | 2023-05-20 12:00
63 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-05-13 | 122 | 2023-05-23 12:00
64 | Kalurghat 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-14 19:30 | 116 | 2023-05-18 06:00
65 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-03 21:00 | 119 | 2023-05-23 12:00
66 | Kaptai 132/33kV Sub-Station | 132 | 144 | 2023-05-14 19:00 | 123 | 2023-05-17 08:00
67 | Kazla 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-01 06:00 | 124 | 2023-05-10 13:00
68 | Khagrachori 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 01:00 | 117 | 2023-05-13 08:00
69 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 20:00 | 123 | 2023-05-27 19:00
70 | Khulshi 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 | 115 | 2023-05-13 08:00
71 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 135 | 2023-05-11 18:00 | 115 | 2023-05-06 19:00
Page: 3/3 | [5 empty] | QF-LDC-35
Month:May 2023
72 | Kodda 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 19:30 | 120 | 2023-05-23 16:00
73 | KSRM 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-13 21:00 | 114 | 2023-05-18 06:00
74 | Kulaura 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-10 18:00 | 131 | 2023-05-28 19:00
75 | Kurigram 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-18 05:00 | 114 | 2023-05-28 20:00
76 | Kushtia 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-18 05:00 | 123 | 2023-05-12 19:30
77 | Lalbag 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-06 20:00 | 126 | 2023-05-02 12:00
78 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-18 05:00 | 116 | 2023-05-10 19:00
79 | Madanganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-21 22:00 | 120 | 2023-05-15 07:00
80 | Madaripur 132/33kV Grid Sub-Station | 132 | 136 | 2023-05-01 07:00 | 121 | 2023-05-28 06:00
81 | Madartek 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-23 18:00 | 125 | 2023-05-06 11:00
82 | Madunaghat 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-14 19:30 | 116 | 2023-05-18 06:00
83 | Magura 132/33kV Grid Sub-Station | 132 | 145 | 2023-05-16 20:00 | 122 | 2023-05-11 20:00
84 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-18 04:00 | 120 | 2023-05-10 19:00
85 | Manikganj 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 19:30 | 120 | 2023-05-24 16:00
86 | Maniknagar 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-01 06:00 | 124 | 2023-05-10 12:00
87 | Matarbari 132/33kV Sub-Station | 132 | 142 | 2023-05-14 19:30 | 113 | 2023-05-01 04:00
88 | Matuail 132/33kV Grid Sub-Station | 132 | 137.4 | 2023-05-03 19:00 | 125.8 | 2023-05-22 10:00
89 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 20:00 | 121 | 2023-05-06 10:00
90 | Mirpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-05-16 20:00 | 121 | 2023-05-06 12:00
91 | Mithapukur 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-18 04:00 | 115 | 2023-05-10 19:00
92 | Modern Steel 132/11kV Grid Sub-Station | 132 | 143 | 2023-05-16 | 119 | 2023-05-18 06:00
93 | Mogbazar 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-23 18:00 | 126 | 2023-05-06 12:00
94 | Mongla 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-16 20:00 | 118 | 2023-05-27 19:00
95 | Motijheel 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-18 06:00 | 124 | 2023-05-10 12:00
96 | Munshiganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-06 10:00 | 123 | 2023-05-16 19:00
97 | Mymensingh 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-17 09:00 | 113 | 2023-05-02
98 | Naogaon 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-18 05:00 | 115 | 2023-05-10 19:00
99 | Narail 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-16 20:00 | 120 | 2023-05-08 19:00
100 | Narshingdi 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-21 22:00 | 117 | 2023-05-16 19:30
101 | Natore 132/33kV Grid Sub-Station | 132 | 139 | 2023-05-18 05:00 | 123 | 2023-05-10 19:00
102 | Nawabganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-14 19:00 | 125 | 2023-05-02 14:00
103 | Netrakona 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-17 09:00 | 114 | 2023-05-10 11:00
104 | New Tongi 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 20:00 | 121 | 2023-05-10 12:00
105 | Niamatpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-18 04:00 | 113 | 2023-05-31 19:30
106 | Noapara 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-16 20:00 | 122 | 2023-05-27 19:00
107 | Pabna 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-16 20:00 | 125 | 2023-05-10 19:00
108 | Palashbari 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-18 05:00 | 114 | 2023-05-10 19:00
109 | Panchagarh 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-03 04:00 | 115 | 2023-05-30 02:00
110 | Patuakhali 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-12 18:00 | 131 | 2023-05-05
111 | PHP 132/33kV Sub-Station | 132 | 139 | 2023-05-17 19:00 | 113 | 2023-05-20 12:00
112 | Postogola 132/33kV Grid Sub-Station | 132 | 140 | 2023-05-23 18:00 | 120 | 2023-05-23 11:00
113 | Purbachal 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-23 18:00 | 119 | 2023-05-10 12:00
114 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 147 | 2023-05-11 04:00 | 114 | 2023-05-30 02:00
115 | Rahim Steel 132/33kV Sub-Station | 132 | 138 | 2023-05-02 18:00 | 125 | 2023-05-16 19:30
116 | Rajbari 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-16 20:00 | 120 | 2023-05-20 21:00
117 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 20:00 | 118 | 2023-05-24 15:00
118 | Rajshahi 132/33kV Grid Sub-Station | 132 | 139.5 | 2023-05-18 05:00 | 124 | 2023-05-10 19:00
119 | Ramganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-16 22:00 | 113 | 2023-05-12 08:00
120 | Rangamati 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-16 | 116 | 2023-05-18 06:00
121 | Rangpur 132/33kV Grid Sub-Station | 132 | 144 | 2023-05-18 04:00 | 113 | 2023-05-10 19:00
122 | Ruppur 132/11kV Grid Sub-Station | 132 | 141 | 2023-05-23 18:00 | 127 | 2023-05-10 11:00
123 | Saidpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-18 04:00 | 117 | 2023-05-30 02:00
124 | Satkhira 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 20:00 | 118 | 2023-05-27 19:00
125 | Satmasjid 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-23 18:00 | 123 | 2023-05-10 12:00
126 | Savar 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-16 20:00 | 120 | 2023-05-27 03:00
127 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 146 | 2023-05-18 06:00 | 133 | 2023-05-07 11:00
128 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-14 14:00 | 128 | 2023-05-28 19:00
129 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 | 117 | 2023-05-13 07:00
130 | Shariatpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-30 02:00 | 119 | 2023-05-22 23:00
131 | Sherpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-17 09:00 | 113 | 2023-05-10 03:00
132 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-02 18:00 | 118 | 2023-05-23 11:00
133 | Sholosohor 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-16 | 114 | 2023-05-18 06:00
134 | Shyampur 132/33kV Grid Sub-Station | 132 | 138 | 2023-05-23 18:00 | 122 | 2023-05-20 10:00
135 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 137 | 2023-05-01 04:00 | 126 | 2023-05-15 11:00
136 | Sirajganj 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-23 16:00 | 125 | 2023-05-10 20:00
137 | Sonargaon 132/33kV Grid Sub-Station | 132 | 139 | 2023-05-02 18:00 | 124 | 2023-05-13 12:00
138 | Sreemongol 132/33kV Grid Sub-Station | 132 | 136 | 2023-05-10 18:00 | 128 | 2023-05-28 22:00
139 | Srinagar 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-06 20:00 | 126 | 2023-05-02 14:00
140 | SSM 132/33kV Grid Sub-Station | 132 | 146 | 2023-05-14 19:30 | 122 | 2023-05-15 10:00
141 | Sunamganj 132/33kV Grid Sub-Station | 132 | 135 | 2023-05-10 18:00 | 121 | 2023-05-09 18:30
142 | Sylhet 132/33kV Grid Sub-Station | 132 | 134 | 2023-05-10 18:00 | 129 | 2023-05-09 15:00
143 | Tangail 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-18 06:00 | 119 | 2023-05-06 08:00
144 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 142 | 2023-05-03 04:00 | 113 | 2023-05-30 03:00
145 | TK chemical 132kV Grid Sub-Station | 132 | 142 | 2023-05-09 23:00 | 113 | 2023-05-18 06:00
146 | Ullon 132/33kV Grid Sub-Station | 132 | 143 | 2023-05-23 18:00 | 125 | 2023-05-06 12:00
147 | Uttara 132/33kV Grid Sub-Station | 132 | 136 | 2023-05-16 20:00 | 121 | 2023-05-07 17:00
148 | UttaraNew 132/33kV Grid Sub-Station | 132 | 135 | 2023-05-13 20:00 | 121 | 2023-05-06 12:00
149 | Zigatola 132/33kV Grid Sub-Station | 132 | 141 | 2023-05-06 20:00 | 126 | 2023-05-02 12:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 |  |  |  |  | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:May 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 448 | 460.1402 | 2023-05-16 16:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 448 | 460.1402 | 2023-05-16 16:00
Ashuganj 400/230kV GIS Sub-Station | Interbus-01 | 400/230 | 164 | 174.29 | 2023-05-25 12:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -347 | 370.5523 | 2023-05-24 08:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -347 | 370.5523 | 2023-05-24 08:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -207 | 213.1901 | 2023-05-23 21:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -201 | 207.3692 | 2023-05-23 21:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 256 | 269.429 | 2023-05-17 09:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 256 | 269.429 | 2023-05-17 09:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 471 | 473.1448 | 2023-05-26 15:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -183.8 | 193.6612 | 2023-05-31 21:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | 300.52 | 315.1571 | 2023-05-27 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -186 | 186.0027 | 2023-05-23
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -194 | 194.0412 | 2023-05-21 13:00
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -194 | 194.0412 | 2023-05-21 13:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 319 | 324.5936 | 2023-05-07 06:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 319 | 324.5936 | 2023-05-07 06:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -86 | 96.1509 | 2023-05-21 23:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -86 | 96.1509 | 2023-05-21 23:00
Rahanpur_I 400/132kV Grid Sub-Station | AT-1 -Gen | 400/132 | 235 | 240.2603 | 2023-05-23 13:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 191 | 209.4684 | 2023-05-10 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 191 | 209.4684 | 2023-05-10 13:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 192 | 199.4492 | 2023-05-08 23:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 192 | 199.4492 | 2023-05-08 23:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 197 | 204.5336 | 2023-05-08 23:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 45 | 50.0899 | 2023-05-31 21:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 150 | 167.7051 | 2023-05-25 19:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 184 | 200.639 | 2023-05-10 20:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 148 | 162.8742 | 2023-05-10 20:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 196 | 203.3027 | 2023-05-12 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 179 | 192.5669 | 2023-05-10 19:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 233 | 241.3669 | 2023-05-10 19:00
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 89 | 89.0898 | 2023-05-03 20:00
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 89 | 89.0898 | 2023-05-03 20:00
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -124 | 128.8449 | 2023-05-13 09:00
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -135 | 135.0037 | 2023-05-12 13:00
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 202 | 205.1828 | 2023-05-31 14:00
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 198 | 203.973 | 2023-05-10 20:00
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 266 | 274.8036 | 2023-05-10 20:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 202 | 213.4596 | 2023-05-25 22:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 199 | 209.9762 | 2023-05-25 22:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 252 | 252.5074 | 2023-05-14 14:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 0 | 0 | 2023-05-28 07:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 0 | 0 | 2023-05-28 07:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 158 | 178.4741 | 2023-05-16 19:30
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 158 | 178.4741 | 2023-05-16 19:30
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 158 | 178.4741 | 2023-05-16 19:30
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 94 | 99.96 | 2023-05-23 11:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 94 | 99.96 | 2023-05-23 11:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 94 | 99.96 | 2023-05-23 11:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 53 | 149.6964 | 2023-05-18 13:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 53 | 149.6964 | 2023-05-18 13:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 53 | 149.6964 | 2023-05-18 13:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 53 | 149.6964 | 2023-05-18 13:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 125 | 143.2655 | 2023-05-10 20:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 125 | 143.2655 | 2023-05-10 20:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 101 | 113.6002 | 2023-05-22 21:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -202 | 224.5173 | 2023-05-22 22:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -202 | 224.5173 | 2023-05-22 22:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 154 | 160.7234 | 2023-05-21 20:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2023-05-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 154 | 160.7234 | 2023-05-21 20:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -138 | 145.4648 | 2023-05-21 21:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -138 | 145.4648 | 2023-05-21 21:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -178 | 186.3035 | 2023-05-21 21:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 176 | 192.9171 | 2023-05-10 13:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 220 | 239.2405 | 2023-05-23 18:30
Rajshahi 230/132/33kV Grid Sub-Station | ATR-01 (704T) | 230/132 | -80 | 80.7527 | 2023-05-10 19:30
Page: 1/2 |  |  |  |  | QF-LDC-36
Month:May 2023
Rajshahi 230/132/33kV Grid Sub-Station | ATR-02 (714T) | 230/132 | -88 | 88.278 | 2023-05-09 05:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2023-05-01 10:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 0 | 0 | 2023-05-01
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 131 | 222.623 | 2023-05-28 19:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 169 | 216.9263 | 2023-05-30 12:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 191 | 286.0944 | 2023-05-22 18:30
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 236 | 262.9677 | 2023-05-10 19:30
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 236 | 262.9677 | 2023-05-10 19:30
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 118 | 132.8345 | 2023-05-20 10:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 118 | 132.8345 | 2023-05-20 10:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 180 | 180.025 | 2023-05-27 21:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 180 | 180.025 | 2023-05-27 21:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 173.5 | 174.2547 | 2023-05-25 19:30
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 215 | 215.0581 | 2023-05-01 03:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 212 | 215.3787 | 2023-05-09 23:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 212 | 215.3787 | 2023-05-09 23:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 212 | 215.3787 | 2023-05-09 23:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:May-2023 | [6 empty] | (For Evening Peak) | [7 empty] | Month:May-2023 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-05-01 | 11274 | 11274 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-01 | 9578 | 9578 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-02 | 13336 | 13542 | 197 | 21:00 | 25 | 0 | 0 | 0 | 30 | 120 | 22 | 0 | 0 | - | 2023-05-02 | 11833 | 11958 | 119 | 12:00 | 32 | 0 | 0 | 0 | 25 | 37 | 25 | 0 | 0 | -
2023-05-03 | 12366 | 12413 | 45 | 13:00 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 |  | 2023-05-03 | 12598 | 12647 | 47 | 12:00 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-04 | 12411 | 12411 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-04 | 11374 | 11426 | 50 | 12:00 | 20 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | -
2023-05-05 | 12938 | 12938 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-05 | 10675 | 10675 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-06 | 14097 | 14163 | 63 | 21:00 | 15 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | - | 2023-05-06 | 12047 | 12112 | 62 | 12:00 | 0 | 0 | 0 | 0 | 0 | 62 | 0 | 0 | 0 | -
2023-05-07 | 14331 | 14802 | 450 | 21:00 | 0 | 0 | 70 | 0 | 130 | 200 | 0 | 0 | 50 | - | 2023-05-07 | 12796 | 13003 | 198 | 12:00 | 41 | 50 | 0 | 0 | 35 | 25 | 47 | 0 | 0 | -
2023-05-08 | 13965 | 15395 | 1356 | 21:00 | 134 | 0 | 251 | 204 | 213 | 284 | 103 | 32 | 135 | - | 2023-05-08 | 15395 | 13600 | 1251 | 12:00 | 375 | 285 | 0 | 55 | 210 | 218 | 89 | 0 | 19 | -
2023-05-09 | 13752 | 15300 | 1478 | 22:00 | 172 | 200 | 292 | 150 | 221 | 258 | 93 | 0 | 92 | - | 2023-05-09 | 12970 | 13600 | 793 | 12:00 | 140 | 145 | 0 | 100 | 198 | 120 | 30 | 0 | 60 | -
2023-05-10 | 14035 | 14500 | 444 | 21:00 | 23 | 64 | 0 | 30 | 168 | 109 | 0 | 0 | 50 | - | 2023-05-10 | 13382 | 14250 | 829 | 12:00 | 190 | 185 | 0 | 25 | 185 | 192 | 22 | 0 | 30 | -
2023-05-11 | 13501 | 14300 | 763 | 21:00 | 60 | 134 | 221 | 98 | 250 | 0 | 0 | 0 | 0 | - | 2023-05-11 | 12836 | 13900 | 1016 | 12:00 | 220 | 181 | 70 | 150 | 190 | 115 | 0 | 0 | 90 | -
2023-05-12 | 13806 | 14130 | 312 | 20:00 | 0 | 0 | 70 | 0 | 147 | 85 | 10 | 0 | 0 | - | 2023-05-12 | 11764 | 11905 | 154 | 12:00 | 64 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | -
2023-05-13 | 12349 | 14400 | 1959 | 21:00 | 850 | 51 | 64 | 190 | 300 | 190 | 119 | 0 | 195 | - | 2023-05-13 | 10749 | 12800 | 1959 | 12:00 | 800 | 312 | 0 | 97 | 327 | 176 | 71 | 0 | 176 | -
2023-05-14 | 11025 | 12732 | 1630 | 21:00 | 710 | 0 | 0 | 356 | 119 | 173 | 0 | 0 | 272 | - | 2023-05-14 | 9774 | 12000 | 2126 | 12:00 | 1100 | 0 | 0 | 246 | 330 | 190 | 40 | 0 | 220 | -
2023-05-15 | 11496 | 13585 | 1995 | 20:00 | 631 | 142 | 0 | 251 | 418 | 225 | 102 | 0 | 226 | - | 2023-05-15 | 9984 | 12200 | 2116 | 12:00 | 980 | 91 | 0 | 240 | 266 | 270 | 50 | 0 | 219 | -
2023-05-16 | 11082 | 12000 | 877 | 19:00 | 253 | 91 | 0 | 0 | 301 | 232 | 0 | 0 | 0 | - | 2023-05-16 | 10144 | 12750 | 2489 | 12:00 | 1147 | 115 | 0 | 375 | 353 | 278 | 49 | 0 | 172 | -
2023-05-17 | 11950 | 11950 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-17 | 9376 | 9376 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-18 | 11823 | 11823 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-18 | 9855 | 9855 | 68 | 12:00 | 15 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | -
2023-05-19 | 12641 | 12641 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-19 | 10278 | 10278 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-20 | 13626 | 14250 | 596 | 21:00 | 90 | 0 | 0 | 0 | 240 | 140 | 0 | 0 | 126 | - | 2023-05-20 | 10970 | 11500 | 506 | 12:00 | 290 | 81 | 0 | 0 | 135 | 0 | 0 | 0 | 0 | -
2023-05-21 | 12533 | 12900 | 350 | 19:30 | 0 | 140 | 25 | 0 | 145 | 0 | 0 | 40 | 0 | - | 2023-05-21 | 11795 | 12800 | 960 | 12:00 | 660 | 130 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | -
2023-05-22 | 13937 | 14251 | 300 | 21:00 | 0 | 55 | 25 | 0 | 160 | 35 | 0 | 25 | 0 | - | 2023-05-22 | 11750 | 12148 | 380 | 12:00 | 0 | 258 | 0 | 0 | 122 | 0 | 0 | 0 | 0 | -
2023-05-23 | 8346 | 8346 | 0 | 1:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-23 | 12221 | 13000 | 744 | 9:00 | 190 | 180 | 0 | 0 | 284 | 90 | 0 | 0 | 0 | -
2023-05-24 | 12646 | 12700 | 52 | 19:30 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | - | 2023-05-24 | 10034 | 10800 | 732 | 12:00 | 485 | 130 | 0 | 0 | 110 | 7 | 0 | 0 | 0 | -
2023-05-25 | 13507 | 13563 | 53 | 20:00 | 0 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | - | 2023-05-25 | 11747 | 11747 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-26 | 12548 | 12600 | 50 | 19:30 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | - | 2023-05-26 | 10284 | 10284 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-27 | 12821 | 12821 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-05-27 | 10780 | 11050 | 258 | 12:00 | 0 | 0 | 0 | 0 | 253 | 0 | 0 | 0 | 5 | -
2023-05-28 | 14136 | 14218 | 78 | 21:00 | 18 | 0 | 0 | 25 | 10 | 25 | 0 | 0 | 0 | - | 2023-05-28 | 11786 | 12069 | 270 | 12:00 | 170 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-05-29 | 14336 | 14950 | 586 | 21:00 | 60 | 0 | 178 | 138 | 15 | 85 | 10 | 0 | 100 |  | 2023-05-29 | 11934 | 12800 | 827 | 12:00 | 454 | 213 | 0 | 0 | 85 | 60 | 15 | 0 | 0
2023-05-30 | 14511 | 15000 | 467 | 21:00 | 53 | 45 | 73 | 65 | 95 | 63 | 0 | 43 | 30 |  | 2023-05-30 | 11850 | 13300 | 1386 | 12:00 | 667 | 204 | 98 | 0 | 226 | 135 | 0 | 0 | 56
2023-05-31 | 14368 | 15600 | 1177 | 21:00 | 270 | 124 | 160 | 0 | 190 | 181 | 137 | 43 | 72 |  | 2023-05-31 | 12326 | 13800 | 1408 | 12:00 | 500 | 170 | 140 | 125 | 171 | 172 | 20 | 30 | 80
15456
| Max. L/S | - | 1537 | - | [10 empty] | Max. L/S | - |  | 1638
| Min. L/S | - | 54 | - | [10 empty] | Min. L/S | - |  | 0
| No. of Days | - | 31 | - | [10 empty] | No. of Days | - | 31
| Average L/S |  | 21566 | [11 empty] | Average L/S |  | 19669
|  | - | - | - | [11 empty] | - | -
[15 empty] | -324 | 141 | 12
[15 empty] | -2051 | 2051 | 13
[15 empty] | -1707 | 2226 | 14
[15 empty] | -2089 | 2216 | 15
[15 empty] | -918 | 2606 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | -624 | 530 | 20
[15 empty] | -367 | 1005 | 21
[15 empty] | -314 | 398 | 22
[15 empty] | 0 | 779 | 23
[15 empty] | -54 | 766 | 24
[15 empty] | -56 | 0 | 25
[15 empty] | -52 | 0 | 26
[15 empty] | 0 | 270 | 27
[15 empty] | -82 | 283 | 28
[15 empty] | #REF! | #REF! | 29
[15 empty] | #REF! | #REF! | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Sl.No | Month:May 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14511 | 2023-05-30 | 21:00
2 | Maximum Day Peak Genaration | MW | 15395 | 2023-05-08 | 12:00
3 | Maximum Evening Peak Demand | MW | 15600 | 2023-05-31 | 21:00
4 | Minimum Generation | MW | 4959 | 2023-05-18 | 6:00
5 | Average of the daily evening peak Genaration | MW | 12886.871 | - | -
6 | Average of the daily day peak Genaration | MW | 11447.9032 | - | -
7 | Maximum load shed | MW | 1995 | 2023-05-15 | 20:00
8 | Minimum load shed | MW | 0 | 2023-05-01 | 21:00
9 | Total nos. of load shed days | Day | 23 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 492.8387 | - | -
11 | Total Generation | MkWh | 7747.3826 | - | -
12 | Total Generation by BPDB | MkWh | 1885.6965 | % of total Gen. | 24.34%
13 | Total Generation by IPP | MkWh | 2134.6311 | '' | 27.55%
14 | A) Total Generation by Generation Companies | MkWh | 2481.3054 | '' | 32.03%
| B) Total Generation by REB | MkWh | 122.5788 | " | 1.582%
| C) Total Generation by RENTAL | MkWh | 357.0366 | " | 4.608%
| D) Total Imported from India (BIPTC) | MkWh | 662.0478 | " | 8.545%
| E) Total Imported from Tripura, India (A.C) | MkWh | 104.0864 | " | 1.344%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4252.0612 | % of total Gen. | 54.88%
| B) Oil | MkWh | 1603.9914 | '' | 20.7%
| C) Hydro | MkWh | 9.6847 | '' | 0.125%
| D) Solar | MkWh | 48.4734 | '' | 0.6257%
| E) Coal | MkWh | 1067.0377 | '' | 13.77%
| F) BIPTC (Import from India) | MkWh | 662.0478 | '' | 8.545%
| G) A.C (Import from Tripura, India) | MkWh | 104.0864 | '' | 1.344%
16 | Maximun of the daily total Generation . | MkWh | 305.3341 | 2023-05-09
17 | Monthly Load factor | % | 80.7771 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 35642.1674 | - | -
| A) Gas | M.Taka | 4876.4826 | - | -
| B) Liquid fuel | M.Taka | 19547.2084 | - | -
| C) Coal | M.Taka | 7410.3937 | - | -
| D) BIPTC (Import from India) | M.Taka | 3058.6606 | - | -
| E) Tripura(Import from India) | M.Taka | 749.4221 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1489.2453 | 2023-05-02
| A) Gas | M.Taka | 177.5197 | 2023-05-24
| B) Liquid fuel | M.Taka | 999.6169 | 2023-05-02
| C) Coal | M.Taka | 326.4965 | 2023-05-04
| D) BIPTC (Import from India) | M.Taka | 103.9013 | 2023-05-18
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 6.9277
| B) Excluding Hydro & Solar | Taka/kWhR | 6.9785
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 76.2 | 31/05/2023 | 06:00
b) | Actual | FT (MSL) | 72.79 | 31/05/2023 | 06:00
22 | Peak Genaration of May 2022 | MW | 11993 | 2022-05-24 | 12:00
23 | Peak Demand of May 2022 | MW | 13954 | 2022-05-16 | 12:00
24 | Maximum peak Generation recorded upto 31/05/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 31/05/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/11/2022 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | bar: FGMO Status 1 to FGMO Status 24; FGMO Status 28 to FGMO Status 31
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | bar: FGMO Status 1 to FGMO Status 31
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | bar: FGMO Status 1 to FGMO Status 11; FGMO Status 18 to FGMO Status 31
8 | Ashuganj 225 MW CCPP | APSCL | 221 | bar: FGMO Status 1 to FGMO Status 31
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | bar: FGMO Status 1 to FGMO Status 31
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | bar: FGMO Status 1 to FGMO Status 14; FGMO Status 25 to FGMO Status 31
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
due to gas shortage