## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on forecasted generation & Demand of national grid on | [6 empty] | 2018-06-29 | Friday
|  | Date (day): | 2018-06-29 |  | Friday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 11112 | MW |  |  | (b) At Evening Peak Hour : |  | 12503 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2018-06-28 | 2018-06-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | Gas | PDB | 2*55 | 110 | 85 | 37 | 37 | 37 | 37 |  | 48 | # 2 under maint
| Ghorasal ST: Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 120 | 120 | 120 | 120 | 50 |  | Gas shortage
| Ghorasal ST: Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal ST: Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
2 | Ghorasal ST: Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 363 | 350 | 365 | 365
3 | Ghorashal 78MW (MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 74 | 76 | 78 | 78
4 | Ghorashal (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 87 | 88 | 100 | 108
5 | Haripur GT: Unit-1, 2 |  | Gas | SBU, PDB | 2*32 | 64 | 40 | 0 | 0 | 0 | 0 | 40 |  | Under shut down.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 390 | 365 | 412 | 412 |  |  | FGMO
7 | Haripur NEPC 110MW |  | HFO | IPP | 8*15 | 110 | 110 | 0 | 0 | 98 | 98 |  | 12 | Engine problem
8 | Haripur Power CCPP 360MW |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 151 | 271 | 360 | 360
9 | Meghnaghat CCPP 450MW |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 420 | 400 | 450 | 450
10 | Meghnaghat (IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 11 | 92 | 100 | 100
11 | Meghnaghat CCPP(Summit) |  | HSD | IPP | 2*110+1*110 | 305 | 305 | 140 | 145 | 150 | 305
12 | Madanganj 102MW |  | HFO | QRPP | 6*17 | 102 | 100 | 48 | 52 | 102 | 102
13 | Madanganj-55 MW |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
14 | Keraniganj (Powerpac) 100MW |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 100 | 100 | 100
15 | Narshingdi (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 0 | 22
16 | Siddhirgonj ST 210MW |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 | 115 |  | Gas shortage
17 | Siddhirgonj GT Unit-1& 2 |  | Gas | EGCB | 2*105 | 210 | 210 | 99 | 0 | 0 | 0 |  |  | Gas shortage
18 | Siddhirganj (Desh) |  | HSD | QRPP | 96*1.2 | 100 | 100 | 0 | 0 | 100 | 100
19 | Siddhirganj (Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 10 | 89 | 93 | 93 |  | 7 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | Gas | EGCB | 1*217 | 217 | 217 | 160 | 170 | 200 | 200
21 | Pagla (DPA ) |  | HSD | QRPP | 100*0.5 | 50 | 50 | 11 | 51 | 50 | 50
22 | Gagnagar (Orion) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 64 | 102 | 102
23 | Katpotti 51 MW |  | HFO | IPP | 7*7.9 | 51 | 51 | 39 | 39 | 40 | 40 |  | 11 | Engine problem
24 | Banco Energy 54MW |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
25 | Kodda 150MW |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 149 | 0 | 149
26 | Northern 55 MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 56 | 55 | 55
27 | Southern 55MW |  | HFO | IPP | 3*19.3 | 55 | 55 | 36 | 55 | 55 | 55
28 | Bosila 108MW |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 75 | 75 | 100 | 100
29 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 57 | 56 | 58 | 58 |  | 22 | Engine problem
30 | Summit Maona |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
31 | Summit Rupganj |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
32 | Gazipur (RPCL) |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 50 | 52 | 52
33 | Tongi GT |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
34 | Summit Gazipur |  | HFO | IPP | 18*17.076 | 300 | 300 | 201 | 303 | 150 | 300
| APR Energy , Keranigonj |  | HSD | IPP | 236*1.4 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Bramhangoan 100 MW (Aggreko) |  | HSD | IPP | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On test
| Aggreko Aurahati 100MW |  | HSD | IPP | 0.85*23+0.95*91 | 0 | 0 | 0 | 32 | 106 | 106
| Dhaka area Total |  |  |  |  | 5435 | 5199 | 2995 | 3479 | 3808 | 4292 | 205 | 575
35 | Chittagong ST-1 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas Shortage
36 | Raozan 25 MW (RPCL) |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 25 | 25
37 | Patenga 50MW |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 45 | 44 | 44
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 168 | 168 | 169 | 169 |  | 61 | # 2 under maint
39 | Sikalbaha ST 60MW |  | Gas | PDB | 1*60 | 60 | 40 | 0 | 0 | 0 | 0 |  | 40 | Under maint.
40 | Sikalbaha 225MW |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 201 | 197 | 225 | 225
41 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 135 | 135 | 60 | 135
42 | Sikalbaha (Energis) |  | HFO | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 51 | 14 | 42 | 51 | 51
43 | Hathazari peaking |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 64 | 68 | 68
44 | Dohazari Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 0 | 74 | 74
45 | Juldah (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 80 | 80 |  | 20 | Engine problem
46 | Barabkunda (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 23 | 15 | 23
47 | Chittagong ECPV 108 MW |  | HFO | IPP | 16*7 | 108 | 108 | 99 | 98 | 103 | 103 |  | 5 | Engine problem
| Chittagong area Total |  |  |  |  | 1641 | 1561 | 768 | 884 | 930 | 1013 | 360 | 132
48 | Ashuganj ST: Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Under maint.
| Ashuganj ST: Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 100 | 150 | 150 |  | 129
| Ashuganj ST: Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 10 | 100 | 100 | 100 | 34 |  | Gas shortage
49 | Ashuganj CCPP 225 MW |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 157 | 164 | 225 | 225 |  |  | FGMO
50 | Ashuganj CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 368 | 305 | 360 | 360 |  |  | FGMO
51 | Ashuganj CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 305 | 360 | 360 |  |  | FGMO
52 | Ashuganj Engines TSK |  | Gas | APSCL | 14*3.968 | 53 | 45 | 39 | 39 | 39 | 39
53 | Ashuganj (Precision) 55MW |  | Gas | RPP | 15*4 | 55 | 55 | 0 | 0 | 0 | 0 |  | 55 | Under maint.
54 | Ashuganj (United) 53MW |  | Gas | QRPP | 14*4 | 53 | 53 | 10 | 5 | 10 | 10 | 43 |  | Gas shortage
55 | Ashuganj 195MW Modular |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 78 | 78 | 78 | 195 | 0
56 | Ashuganj (Midland) 51MW |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
57 | B.Baria (Aggreko) 85MW |  | Gas | QRPP | 86*1.10 | 85 | 85 | 85 | 86 | 85 | 85
58 | Daudkandi Peaking 52MW |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 48
59 | Chandpur CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 30 | 101 | 100 | 100 |  | 163
60 | Feni (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19
61 | Feni, Mohipal (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 8 | 11
** | Tripura |  |  | Imported power | 0 | 160 | 160 | 128 | 168 | 124 | 164
62 | Jangalia (Summit) 33MW |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
63 | Lakdhanvi 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 14 | 52 | 52
64 | Summit Comilla 25MW |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 18 | 22 | 22
65 | Daudkandi bangla trak |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 120 | 0 | 200
| Comilla Area Total |  |  |  |  | 2601 | 2541 | 1397 | 1717 | 1816 | 2224 | 212 | 347
66 | Mymensingh RPCL 210MW |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 61 | 47 | 97 | 100 | 102 |  | Gas shortage
67 | Tangail (Doreen) 22MW |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
68 | Jamalpur 95MW |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 95 | 95 | 95
69 | Sarishabari (Solar) |  | Solar | IPP | 1*3 | 3 | 3 | 2.9 | 0 | 2 | 0
| United Mymensingh PPL |  | HFO | IPP | 200 | 0 | 0 | 150 | 174 | 150 | 185
| Mymensingh Area Total |  |  |  |  | 330 | 322 | 238.9 | 336 | 366 | 402 | 102 | 0
70 | Fenchugonj CCPP-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 58 | 60 | 58 | 58
71 | Fenchugonj CCPP-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 60 | 62 | 62 | 62
72 | Kushiara 163 MW CCPP GT |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
73 | Shajibazar 330 MW |  | Gas | PDB | 3*110 | 330 | 330 | 190 | 196 | 330 | 330
74 | Fenchugonj (Barakatullah) 51MW |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
75 | Fenchuganj (EPL) 44MW |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 50 | 50 | 50 | 50
76 | Hobiganj 11MW |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 8 | 8
77 | Shahjibazar GT: Unit- 8, 9 |  | Gas | PDB | 2*35 | 70 | 66 | 54 | 61 | 50 | 60 |  | 6
78 | Shahjibazar 86MW |  | Gas | RPP | 32*2.90 | 86 | 86 | 85 | 86 | 86 | 86
79 | Shahjibazar (EPL) 50MW |  | Gas | RPP | 27*2.0 | 50 | 50 | 45 | 47 | 50 | 50
80 | Sylhet GT 150 MW |  | Gas | PDB | 1*142 | 142 | 142 | 80 | 78 | 80 | 100
81 | Sylhet GT 20 MW |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
82 | Sylhet (EPL) 50MW |  | Gas | RPP | 27*2 | 50 | 50 | 43 | 44 | 45 | 45
83 | Shahjahanulla 25 MW |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 23 | 23 | 23
84 | Summit Bibiana- 2 |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 320 | 341 | 341 |  |  | FGMO
85 | Sylhet (Desh) 10MW |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 11 | 10 | 10
| Sylhet Area Total |  |  |  |  | 1594 | 1549 | 1152 | 1262 | 1407 | 1437 | 0 | 26
86 | Bheramara GT-1,2,3 |  | HSD | PDB | 3*20 | 60 | 46 | 0 | 0 | 0 | 32
| Bheramara (HVDC ) |  | 0 | Imported power | 1*500 | 500 | 500 | 473 | 473 | 463 | 470
87 | Khulna (KPCL-1 & 3) |  | HFO | IPP | 19*6.5 | 110 | 110 | 69 | 64 | 110 | 110
88 | Khulna (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 104 | 99 | 99
89 | Faridpur Peaking |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 49 | 36 | 47
90 | Khulna CCPP 225MW |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 170 | 225 | 225 |  |  | FGMO
91 | Gopalganj Peaking |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 60 | 78 | 78
92 | Bheramara 360 MW |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 3 | 167 | 250 | 365 | 45 |  | Gas shortage
93 | Noapara (KZA) 40MW |  | HFO | QRPP | 5*8.5 | 40 | 40 | 40 | 33 | 40 | 40
94 | Khulna (Aggreko) 55MW |  | HSD | QRPP | 71*0.85 | 55 | 55 | 0 | 53 | 0 | 54
95 | Bangla Trak Noapara |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 79 | 80 | 80
| Khulna Area Total |  |  |  |  | 1783 | 1769 | 721 | 1252 | 1381 | 1600 | 45 | 0
96 | Summit Barisal 110 MW |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 96 | 110 | 110
97 | Barisal GT: Unit-1, 2 |  | HSD | PDB | 2*20 | 40 | 30 | 0 | 0 | 0 | 30
98 | Bhola (Venture) 33MW |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 38 | 30 | 30
99 | Bhola CCPP 194MW |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 189 | 193 | 194 | 194
100 | Bhola Aggreko 95MW |  | Gas | QRPP | 96*1.10 | 95 | 95 | 94 | 97 | 95 | 95
| Barisal Area Total |  |  |  |  | 472 | 462 | 332 | 424 | 429 | 459 | 0 | 0
101 | Baghabari GT 71MW |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
| Baghabari GT 100MW |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint.
102 | Baghabari Peaking 50MW |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 0 | 43
103 | Bera Peaking |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 37 | 0 | 38
104 | Amnura 50MW |  | HFO | QRPP | 7*7.79 | 50 | 50 | 40 | 33 | 43 | 43 |  | 7 | Engine problem
105 | Katakhali (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 25 | 43 | 43 | 43 |  | 7 | Engine problem
106 | Katakhali Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 46 | 46
107 | Sirajgonj Unit-1 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 135 | 135 | 215 | 215
108 | Sirajgonj Unit-2 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 219 | 189 | 220 | 220
| Sirajgonj Unit-3 225MW |  | Gas/HSD | NWPGCL | 1*150+1*75 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Under maint.
109 | Santahar Peaking |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 42 | 43
110 | Bogra (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
111 | Bogra (EPL) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 10 | 11 | 12 | 12
112 | Ullapara (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
113 | Rajlanka 52 MW |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
114 | Chapainawabganj-100 MW |  | HFO | PDB | 12*8.924 | 104 | 104 | 33 | 100 | 100 | 102
| Rajshahi Area Total |  |  |  |  | 1133 | 1123 | 500 | 753 | 797 | 881 | 71 | 123
115 | Barapukuria Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 70 | 60 | 0 | 0 |  |  | Under maint.
116 | Barapukuria Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 114 | 159 | 160 | 160
117 | Rangpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 16 | 0 | 17
118 | Saidpur GT |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 18 | 18
| Rangpur Area Total |  |  |  |  | 564 | 484 | 184 | 252 | 178 | 195 | 0 | 85
| Total |  |  |  |  | 15553 | 15010 | 8287.9 | 10359 | 11112 | 12503 | 995 | 1288
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7744.6541 | 9680 | 10383.6432 | 11683.4675
A. |  | 2018-06-28 | (Yesterday) |  |  |  |  | Thursday
1 | Highest Generation : |  |  | 10359 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 6793.4 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10359 | MW
3 | Day peak Generation : |  |  | 8287.9 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9680 | MW
4 | Evening peak Generation : |  |  | 10359 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 208.3009 | MKWHr | By Solar | 0.013497 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas: | 128.0354 | MKWHr |  | By Oil: | 57.0873 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal: | 4.7279 | MKWHr |  | By Hydro: | 3.8376 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 995 | MW | Dhaka | 3497 | 3497 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 1288 | MW | Chittagong | 927 | 927 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 2283 | MW | Khulna | 1284 | 1284 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1084.73 | MMCFD |  |  | Rajshahi | 1069 | 1069 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 96176495.914 | ii) Oil : | Taka | 452900654.34 | Comilla | 914 | 914 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : | Taka | 9625472.15 | Total | Taka | 558702622.404 | Mymensingh | 644 | 644 |  | 0 |  | 20:00 |  | 0
9 | Export Through E-W Interconnectors : |  |  |  | i) Energy | 7.191 | MKWHr. | Sylhet | 456 | 456 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -820 | MW at | 21:00 | hrs | Barisal | 262 | 262 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -820 | MW at | 21:00 | hrs | Rangpur | 627 | 627 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 9680 | 9680 |  | 0
B. |  | 2018-06-29 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 12503 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 7500 | MW
4 | Reserve(Generation end) |  |  |  | 2503 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 201.082 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6526.4 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 11.3064 | MKWHr. | ii) HVDC Flow at Peak Time |  | 473 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2928 | MKWHr. | iii) Maximum HVDC Flow : |  | 475 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 102.57 |  | (b) Today: | 102.49 |  | (c) Rule Curve: |  | 83.46
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2018-06-28
Plant Name | Ghorasal ST: Unit-1,2 | Ghorasal ST: Unit-3 | Ghorasal ST: Unit-4 | Ghorasal ST: Unit-5 | Ghorasal ST: Unit-7 | Ghorashal (Regent) | Ghorashal 78MW (MAX) | Haripur 412 MW CCPP | Haripur Power CCPP 360MW | Haripur NEPC 110MW | Haripur GT: Unit-1, 2 | Meghnaghat CCPP 450MW | Meghnaghat CCPP(Summit) | Meghnaghat (IEL) | Madanganj 102MW | Madanganj-55 MW | Siddhirganj CCPP-335 MW | Siddhirgonj ST 210MW | Siddhirgonj GT Unit-1& 2 | Siddhirganj (Desh) | Siddhirganj (Dutch Bangla) | Gagnagar (Orion) | Kodda 150MW | Keraniganj (Powerpac) 100MW | Bosila 108MW | Pagla (DPA ) | Katpotti 51 MW | Banco Energy 54MW | Northern 55 MW | Southern 55MW | Narshingdi (Doreen) | Summit Ashulia | Summit Madhabdi | Summit Maona | Summit Rupganj | Gazipur (RPCL) | Tongi GT | Kaptai Unit-1, 2 & 3 | Kaptai Unit-4 & 5 | Chittagong ST-1 (Raozan) | Chittgong ST-2 (Raozan) | Raozan 25 MW (RPCL) | Sikalbaha 225MW (Gas) | Sikalbaha 225MW (Oil) | Sikalbaha GT 150MW (Gas) | Sikalbaha GT 150MW (Oil) | Sikalbaha ST 60MW | Sikalbaha (Energis) | Hathazari peaking | Dohazari Peaking | Juldah (Acorn) | Chittagong ECPV 108 MW | Patenga 50MW | Barabkunda (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj ST: Unit- 3 | Ashuganj ST: Unit- 4 | Ashuganj ST: Unit- 5 | Ashuganj CCPP(North) | Ashuganj CCPP(South) | Ashuganj CCPP 225 MW | Ashuganj 195MW Modular | Chandpur CCPP | Ashuganj Engines TSK | Ashuganj (Precision) 55MW | Ashuganj (United) 53MW | Ashuganj (Midland) 51MW | B.Baria (Aggreko) 85MW | Daudkandi Peaking 52MW | Lakdhanvi 52 MW | Feni (Doreen) 22MW | Feni, Mohipal (Doreen) | Jangalia (Summit) 33MW | Summit Comilla 25MW | Tripura | Mymensingh RPCL 210MW | Jamalpur 95MW | Tangail (Doreen) 22MW | Sarishabari (Solar) | Fenchugonj CCPP-1 | Fenchugonj CCPP-2 | Fenchugonj (Barakatullah) 51MW | Fenchuganj (EPL) 44MW | Kushiara 163 MW CCPP GT | Shajibazar 330 MW | Shahjibazar GT: Unit- 8, 9 | Shahjibazar 86MW | Shahjibazar (EPL) 50MW | Sylhet GT 150 MW | Sylhet GT 20 MW | Sylhet (EPL) 50MW | Sylhet (Desh) 10MW | Summit Bibiana- 2 | Shahjahanulla 25 MW | Hobiganj 11MW | Daudkandi bangla trak | Summit Gazipur | APR Energy , Keranigonj | Bramhangoan 100 MW (Aggreko) | United Mymensingh PPL | Aggreko Aurahati 100MW | EasternBlank | Bheramara (HVDC ) | Bheramara GT-1,2,3 | Bheramara 360 MW | Khulna (KPCL-1 & 3) | Khulna (KPCL-2) | Khulna CCPP 225MW | Khulna 60MW | Khulna (Aggreko) 55MW | Faridpur Peaking | Gopalganj Peaking | Noapara (KZA) 40MW | Bhola CCPP 194MW | Bhola (Venture) 33MW | Summit Barisal 110 MW | Barisal GT: Unit-1, 2 | Baghabari GT 100MW | Baghabari GT 71MW | Baghabari Peaking 50MW | Bera Peaking | Chapainawabganj-100 MW | Amnura 50MW | Katakhali (Northern) | Katakhali Peaking | Rajlanka 52 MW | Santahar Peaking | Bogra (GBB) | Bogra (EPL) | Ullapara (Summit) | Barapukuria Unit-1 | Barapukuria Unit-2 | Barapukuria Unit-3 | Rangpur GT | Saidpur GT | Sirajgonj Unit-1 225MW (Gas) | Sirajgonj Unit-1 225MW (Oil) | Sirajgonj Unit-2 225MW (Gas) | Sirajgonj Unit-2 225MW (Oil) | Bhola Aggreko 95MW | Bangla Trak Noapara | Sirajgonj Unit-3 225 MW(Gas) | Sirajgonj Unit-3 225 MW(Oil) | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 37 | 120 | 0 | 0 | 300 | 87 | 74 | 365 | 258 | 0 | 0 | 430 | 100 | 60 | 16 | 15 | 170 | 0 | 99 | 0 | 50 | 7 | 120 | 10 | 90 | 0 | 40 | 54 | 55 | 55 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 204 | 0 | 50 | 0 | 36 | 65 | 79 | 80 | 105 | 44 | 16 | 30 | 0 | 100 | 100 | 335 | 335 | 205 | 76 | 100 | 38 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 152 | 86 | 24 | 20 | 0 | 53 | 60 | 53 | 50 | 140 | 269 | 50 | 86 | 47 | 79 | 0 | 45 | 10 | 320 | 23 | 8 | 0 | 220 | 0 | 0 | 197 | 0 |  | 464 | 0 | 345 | 10 | 66 | 120 | 0 | 0 | 48 | 9 | 40 | 183 | 17 | 27 | 0 | 0 | 0 | 0 | 0 | 70 | 40 | 43 | 45 | 25 | 0 | 22 | 11 | 10 | 0 | 72 | 126 | 17 | 18 | 135 | 0 | 0 | 183 | 73 | 0 | 0 | 0 |  | 7187 | 2219 | 9406 | 3861 | 464 | 1975 | 1567 | 198 | 161 | 1028 | 152 | 0 | 0 | 102.57
2:00 | 37 | 120 | 0 | 0 | 300 | 87 | 74 | 360 | 271 | 0 | 0 | 430 | 100 | 7 | 16 | 15 | 170 | 0 | 101 | 0 | 7 | 7 | 72 | 10 | 90 | 0 | 39 | 54 | 18 | 55 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 198 | 0 | 49 | 0 | 34 | 65 | 79 | 80 | 105 | 44 | 16 | 38 | 0 | 100 | 100 | 329 | 330 | 203 | 76 | 100 | 38 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 148 | 86 | 8 | 20 | 0 | 58 | 60 | 53 | 50 | 140 | 224 | 51 | 86 | 47 | 79 | 0 | 45 | 10 | 320 | 23 | 8 | 0 | 195 | 0 | 0 | 197 | 0 |  | 465 | 0 | 340 | 10 | 55 | 120 | 0 | 0 | 27 | 8 | 40 | 194 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 70 | 40 | 43 | 45 | 25 | 0 | 22 | 11 | 10 | 0 | 70 | 126 | 17 | 18 | 135 | 0 | 0 | 184 | 72 | 0 | 0 | 0 |  | 6900 | 2181 | 9081 | 3812 | 465 | 1996 | 1351 | 196 | 161 | 952 | 148 | 0 | 0 | 102.57
3:00 | 37 | 120 | 0 | 0 | 300 | 87 | 74 | 365 | 271 | 0 | 0 | 430 | 100 | 7 | 16 | 15 | 165 | 0 | 100 | 0 | 7 | 7 | 64 | 10 | 24 | 0 | 12 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 50 | 0 | 40 | 65 | 77 | 80 | 105 | 45 | 16 | 41 | 0 | 100 | 100 | 335 | 335 | 206 | 76 | 100 | 38 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 33 | 15 | 140 | 85 | 8 | 17 | 0 | 54 | 60 | 53 | 50 | 140 | 142 | 50 | 86 | 47 | 80 | 0 | 45 | 10 | 310 | 23 | 8 | 0 | 47 | 0 | 0 | 151 | 0 |  | 465 | 0 | 326 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 193 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 70 | 40 | 43 | 45 | 8 | 0 | 22 | 11 | 10 | 0 | 71 | 126 | 0 | 0 | 135 | 0 | 0 | 184 | 73 | 0 | 0 | 0 |  | 6449 | 2008 | 8457 | 3720 | 465 | 1996 | 901 | 197 | 161 | 877 | 140 | 0 | 0 | 102.57
4:00 | 37 | 120 | 0 | 0 | 300 | 86 | 74 | 358 | 291 | 0 | 0 | 430 | 100 | 7 | 16 | 15 | 165 | 0 | 102 | 0 | 7 | 7 | 42 | 10 | 19 | 0 | 12 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 25 | 0 | 81 | 80 | 0 | 0 | 16 | 0 | 199 | 0 | 50 | 0 | 40 | 16 | 46 | 80 | 75 | 45 | 16 | 40 | 0 | 100 | 100 | 325 | 320 | 195 | 76 | 100 | 35 | 0 | 10 | 51 | 85 | 0 | 0 | 19 | 11 | 8 | 15 | 136 | 98 | 8 | 17 | 0 | 58 | 60 | 53 | 50 | 140 | 172 | 51 | 86 | 47 | 79 | 0 | 45 | 10 | 320 | 23 | 8 | 0 | 47 | 0 | 0 | 151 | 0 |  | 465 | 0 | 326 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 192 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 12 | 43 | 45 | 8 | 0 | 22 | 11 | 8 | 0 | 73 | 126 | 0 | 0 | 135 | 0 | 0 | 184 | 73 | 0 | 0 | 0 |  | 6311 | 1948 | 8259 | 3695 | 465 | 2023 | 838 | 199 | 161 | 742 | 136 | 0 | 0 | 102.57
5:00 | 37 | 120 | 0 | 0 | 300 | 32 | 50 | 350 | 301 | 0 | 0 | 430 | 100 | 7 | 16 | 15 | 160 | 0 | 100 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 8 | 0 | 81 | 80 | 0 | 0 | 0 | 0 | 196 | 0 | 50 | 0 | 40 | 16 | 45 | 80 | 38 | 44 | 16 | 42 | 0 | 100 | 100 | 330 | 325 | 200 | 76 | 100 | 35 | 0 | 10 | 20 | 51 | 0 | 0 | 19 | 11 | 8 | 15 | 128 | 100 | 8 | 17 | 0 | 58 | 60 | 9 | 5 | 140 | 172 | 51 | 50 | 2 | 79 | 0 | 45 | 10 | 310 | 23 | 8 | 0 | 47 | 0 | 0 | 52 | 0 |  | 464 | 0 | 320 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 191 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 12 | 43 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 72 | 126 | 0 | 0 | 135 | 0 | 0 | 178 | 72 | 0 | 0 | 0 |  | 5783 | 1887 | 7670 | 3690 | 464 | 1711 | 657 | 198 | 161 | 661 | 128 | 0 | 0 | 102.57
6:00 | 37 | 120 | 0 | 0 | 250 | 26 | 20 | 350 | 290 | 0 | 0 | 430 | 100 | 7 | 16 | 15 | 120 | 0 | 100 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 8 | 0 | 82 | 80 | 0 | 0 | 0 | 0 | 177 | 0 | 50 | 0 | 8 | 16 | 23 | 80 | 12 | 38 | 16 | 42 | 0 | 100 | 100 | 280 | 270 | 170 | 76 | 100 | 10 | 0 | 10 | 5 | 20 | 0 | 0 | 19 | 11 | 8 | 15 | 114 | 100 | 8 | 17 | 0 | 54 | 60 | 5 | 5 | 140 | 157 | 51 | 5 | 2 | 79 | 0 | 3 | 10 | 300 | 23 | 8 | 0 | 47 | 0 | 0 | 52 | 0 |  | 465 | 0 | 260 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 194 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 12 | 5 | 0 | 8 | 0 | 18 | 11 | 8 | 0 | 72 | 126 | 0 | 0 | 135 | 0 | 0 | 157 | 32 | 0 | 0 | 0 |  | 5202 | 1723 | 6925 | 3364 | 465 | 1468 | 555 | 198 | 162 | 599 | 114 | 0 | 0 | 102.57
7:00 | 37 | 120 | 0 | 0 | 250 | 27 | 20 | 362 | 261 | 0 | 0 | 430 | 100 | 7 | 15 | 15 | 120 | 0 | 99 | 0 | 7 | 7 | 16 | 10 | 8 | 0 | 12 | 18 | 0 | 17 | 19 | 25 | 32 | 33 | 33 | 8 | 0 | 79 | 80 | 0 | 0 | 0 | 0 | 188 | 0 | 50 | 0 | 8 | 16 | 15 | 80 | 12 | 24 | 16 | 32 | 0 | 100 | 100 | 295 | 287 | 173 | 76 | 30 | 10 | 0 | 10 | 5 | 3 | 0 | 0 | 19 | 8 | 8 | 13 | 98 | 97 | 8 | 17 | 0.4 | 58 | 60 | 5 | 5 | 163 | 152 | 50 | 1 | 2 | 80 | 0 | 3 | 0 | 320 | 23 | 8 | 0 | 47 | 0 | 0 | 52 | 0 |  | 465 | 0 | 250 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 192 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 12 | 8 | 0 | 8 | 0 | 22 | 11 | 5 | 0 | 66 | 121 | 0 | 0 | 135 | 0 | 0 | 157 | 32 | 0 | 0 | 0 |  | 5094.4 | 1699 | 6793.4 | 3316 | 465 | 1446 | 525 | 187 | 159 | 597 | 98 | 0.4 | 0 | 102.57
8:00 | 37 | 120 | 0 | 0 | 300 | 27 | 20 | 370 | 250 | 0 | 0 | 430 | 100 | 7 | 14 | 15 | 120 | 0 | 100 | 0 | 7 | 7 | 98 | 10 | 8 | 10 | 12 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 19 | 0 | 83 | 80 | 0 | 0 | 0 | 0 | 189 | 0 | 50 | 0 | 8 | 16 | 15 | 80 | 12 | 24 | 16 | 12 | 0 | 100 | 100 | 335 | 335 | 201 | 76 | 30 | 36 | 0 | 10 | 5 | 21 | 0 | 0 | 19 | 5 | 8 | 13 | 110 | 84 | 8 | 17 | 0.9 | 58 | 60 | 5 | 5 | 163 | 173 | 50 | 20 | 2 | 79 | 0 | 44 | 0 | 320 | 23 | 8 | 0 | 50 | 0 | 0 | 52 | 0 |  | 468 | 0 | 250 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 192 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 20 | 25 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 71 | 121 | 0 | 0 | 135 | 0 | 0 | 162 | 32 | 0 | 0 | 0 |  | 5486.9 | 1732 | 7218.9 | 3524 | 468 | 1485 | 591 | 192 | 163 | 685 | 110 | 0.9 | 0 | 102.57
9:00 | 37 | 120 | 0 | 0 | 365 | 82 | 30 | 365 | 233 | 0 | 0 | 430 | 130 | 7 | 15 | 15 | 160 | 0 | 101 | 0 | 7 | 7 | 98 | 10 | 47 | 10 | 17 | 18 | 18 | 17 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 84 | 80 | 0 | 0 | 0 | 0 | 203 | 0 | 80 | 0 | 29 | 16 | 15 | 80 | 12 | 25 | 16 | 7 | 0 | 100 | 100 | 310 | 310 | 193 | 77 | 30 | 39 | 0 | 10 | 8 | 21 | 0 | 0 | 19 | 11 | 33 | 13 | 116 | 76 | 8 | 17 | 1.8 | 58 | 60 | 47 | 38 | 163 | 168 | 62 | 20 | 47 | 80 | 0 | 44 | 0 | 330 | 23 | 8 | 0 | 54 | 0 | 0 | 100 | 0 |  | 469 | 0 | 235 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 0 | 190 | 11 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 40 | 25 | 0 | 8 | 0 | 22 | 11 | 8 | 0 | 71 | 121 | 0 | 0 | 135 | 0 | 0 | 172 | 64 | 0 | 0 | 0 |  | 5964.8 | 1779 | 7743.8 | 3584 | 469 | 1695 | 783 | 192 | 164 | 739 | 116 | 1.8 | 0 | 102.57
10:00 | 37 | 120 | 0 | 0 | 365 | 87 | 30 | 372 | 213 | 0 | 0 | 430 | 100 | 7 | 15 | 20 | 175 | 0 | 101 | 0 | 7 | 7 | 98 | 40 | 69 | 11 | 39 | 54 | 54 | 36 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 77 | 80 | 0 | 0 | 8 | 0 | 204 | 0 | 100 | 0 | 42 | 9 | 15 | 80 | 0 | 33 | 16 | 2 | 0 | 150 | 100 | 300 | 300 | 184 | 78 | 30 | 39 | 0 | 10 | 20 | 85 | 0 | 0 | 18 | 11 | 33 | 13 | 118 | 60 | 8 | 17 | 2 | 58 | 60 | 44 | 50 | 163 | 190 | 62 | 84 | 47 | 80 | 0 | 44 | 0 | 300 | 23 | 8 | 0 | 156 | 0 | 0 | 120 | 0 |  | 472 | 0 | 120 | 19 | 27 | 120 | 0 | 0 | 0 | 0 | 33 | 191 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 34 | 40 | 25 | 0 | 8 | 0 | 22 | 10 | 8 | 0 | 72 | 121 | 0 | 0 | 135 | 0 | 0 | 148 | 90 | 0 | 0 | 0 |  | 6393 | 1729 | 8122 | 3518 | 472 | 1827 | 1107 | 193 | 157 | 728 | 118 | 2 | 0 | 102.57
11:00 | 37 | 120 | 0 | 0 | 320 | 87 | 35 | 390 | 193 | 0 | 0 | 400 | 100 | 7 | 38 | 48 | 165 | 0 | 103 | 0 | 7 | 7 | 98 | 50 | 75 | 10 | 39 | 54 | 55 | 36 | 19 | 25 | 32 | 33 | 33 | 33 | 0 | 77 | 80 | 0 | 0 | 16 | 0 | 203 | 0 | 100 | 0 | 0 | 0 | 0 | 80 | 92 | 37 | 16 | 2 | 0 | 145 | 100 | 360 | 300 | 182 | 78 | 30 | 39 | 0 | 10 | 51 | 85 | 0 | 0 | 18 | 11 | 33 | 14 | 120 | 60 | 8 | 17 | 2.5 | 58 | 60 | 46 | 50 | 100 | 190 | 59 | 84 | 46 | 80 | 0 | 43 | 0 | 270 | 22 | 8 | 0 | 193 | 0 | 0 | 120 | 0 |  | 472 | 0 | 65 | 63 | 33 | 120 | 0 | 0 | 0 | 0 | 25 | 192 | 24 | 28 | 0 | 0 | 0 | 0 | 0 | 33 | 40 | 25 | 0 | 8 | 0 | 20 | 10 | 8 | 0 | 71 | 118 | 0 | 0 | 135 | 0 | 0 | 217 | 95 | 0 | 0 | 0 |  | 6444.5 | 1802 | 8246.5 | 3479 | 472 | 1729 | 1327 | 189 | 157 | 771 | 120 | 2.5 | 0 | 102.57
12:00 | 37 | 120 | 0 | 0 | 363 | 87 | 74 | 390 | 151 | 0 | 0 | 420 | 140 | 11 | 48 | 55 | 160 | 0 | 99 | 0 | 10 | 7 | 98 | 70 | 75 | 11 | 39 | 54 | 55 | 36 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 135 | 0 | 14 | 0 | 0 | 80 | 99 | 37 | 16 | 2 | 0 | 100 | 10 | 368 | 265 | 157 | 78 | 30 | 39 | 0 | 10 | 51 | 85 | 0 | 0 | 18 | 11 | 33 | 14 | 128 | 61 | 8 | 17 | 2.9 | 58 | 60 | 47 | 50 | 130 | 190 | 54 | 85 | 45 | 80 | 0 | 43 | 0 | 280 | 22 | 8 | 0 | 201 | 0 | 0 | 150 | 0 |  | 473 | 0 | 3 | 69 | 16 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 40 | 25 | 0 | 8 | 0 | 22 | 10 | 8 | 0 | 70 | 114 | 0 | 0 | 135 | 0 | 0 | 219 | 94 | 0 | 0 | 0 |  | 6550.9 | 1737 | 8287.9 | 3257 | 473 | 1781 | 1488 | 184 | 168 | 806 | 128 | 2.9 | 0 | 102.57
13:00 | 37 | 120 | 0 | 0 | 365 | 88 | 73 | 385 | 143 | 0 | 0 | 420 | 100 | 58 | 48 | 55 | 170 | 0 | 100 | 0 | 50 | 15 | 98 | 100 | 74 | 10 | 39 | 54 | 55 | 36 | 19 | 25 | 23 | 33 | 33 | 47 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 202 | 0 | 120 | 0 | 29 | 0 | 0 | 80 | 98 | 37 | 16 | 2 | 0 | 100 | 100 | 374 | 270 | 145 | 78 | 32 | 39 | 0 | 5 | 51 | 85 | 0 | 0 | 18 | 0 | 33 | 17 | 130 | 60 | 8 | 17 | 1.5 | 58 | 60 | 47 | 50 | 163 | 190 | 51 | 85 | 46 | 80 | 0 | 44 | 0 | 270 | 22 | 8 | 0 | 249 | 0 | 0 | 150 | 0 |  | 473 | 0 | 130 | 64 | 16 | 120 | 0 | 0 | 0 | 0 | 40 | 167 | 18 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 40 | 25 | 0 | 8 | 0 | 22 | 10 | 11 | 0 | 70 | 121 | 0 | 0 | 135 | 0 | 0 | 211 | 97 | 0 | 0 | 0 |  | 6777.5 | 1843 | 8620.5 | 3443 | 473 | 1797 | 1633 | 191 | 168 | 784 | 130 | 1.5 | 0 | 102.57
14:00 | 37 | 120 | 0 | 0 | 365 | 88 | 50 | 350 | 143 | 0 | 0 | 330 | 100 | 90 | 73 | 55 | 175 | 0 | 99 | 0 | 70 | 32 | 98 | 100 | 75 | 10 | 39 | 54 | 56 | 36 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 75 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 80 | 0 | 42 | 0 | 0 | 80 | 98 | 37 | 16 | 2 | 0 | 100 | 100 | 300 | 272 | 166 | 84 | 90 | 37 | 0 | 5 | 51 | 85 | 0 | 0 | 18 | 0 | 33 | 21 | 130 | 47 | 8 | 17 | 1.3 | 58 | 60 | 50 | 50 | 130 | 190 | 58 | 85 | 46 | 80 | 0 | 43 | 10 | 260 | 22 | 8 | 0 | 285 | 0 | 0 | 150 | 0 |  | 468 | 0 | 165 | 81 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 178 | 19 | 48 | 0 | 0 | 0 | 0 | 0 | 33 | 40 | 25 | 0 | 8 | 0 | 22 | 10 | 11 | 0 | 67 | 119 | 0 | 0 | 135 | 0 | 0 | 208 | 97 | 0 | 0 | 0 |  | 6708.3 | 1943 | 8651.3 | 3470 | 468 | 1660 | 1847 | 186 | 155 | 734 | 130 | 1.3 | 0 | 102.56
15:00 | 37 | 120 | 0 | 0 | 365 | 87 | 50 | 350 | 143 | 0 | 0 | 400 | 100 | 91 | 90 | 55 | 180 | 0 | 99 | 0 | 82 | 32 | 98 | 100 | 75 | 10 | 39 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 50 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 135 | 0 | 42 | 0 | 0 | 80 | 98 | 37 | 16 | 2 | 0 | 100 | 100 | 300 | 270 | 175 | 78 | 90 | 39 | 0 | 5 | 51 | 85 | 0 | 0 | 18 | 0 | 33 | 21 | 142 | 46 | 8 | 17 | 2.1 | 59 | 59 | 50 | 50 | 100 | 191 | 50 | 85 | 45 | 80 | 0 | 43 | 11 | 280 | 21 | 8 | 0 | 301 | 0 | 0 | 150 | 0 |  | 475 | 0 | 167 | 87 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 186 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 33 | 40 | 43 | 0 | 18 | 0 | 22 | 10 | 11 | 0 | 67 | 118 | 0 | 0 | 138 | 0 | 0 | 176 | 97 | 0 | 0 | 0 |  | 6872.1 | 1965 | 8837.1 | 3486 | 475 | 1714 | 1926 | 185 | 150 | 757 | 142 | 2.1 | 0 | 102.56
16:00 | 37 | 120 | 0 | 0 | 365 | 87 | 50 | 350 | 133 | 0 | 0 | 400 | 100 | 65 | 48 | 55 | 180 | 0 | 97 | 0 | 40 | 32 | 98 | 50 | 75 | 10 | 39 | 54 | 56 | 36 | 19 | 25 | 30 | 33 | 33 | 45 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 205 | 0 | 60 | 0 | 42 | 0 | 0 | 80 | 98 | 37 | 16 | 2 | 0 | 100 | 100 | 335 | 305 | 186 | 78 | 90 | 39 | 0 | 5 | 51 | 41 | 0 | 0 | 18 | 0 | 33 | 21 | 134 | 46 | 8 | 17 | 0.2 | 59 | 59 | 52 | 50 | 100 | 213 | 59 | 10 | 45 | 80 | 0 | 44 | 11 | 290 | 23 | 10 | 0 | 303 | 0 | 0 | 150 | 0 |  | 475 | 0 | 167 | 80 | 49 | 120 | 0 | 0 | 0 | 0 | 40 | 190 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 59 | 40 | 43 | 0 | 25 | 0 | 22 | 11 | 11 | 0 | 64 | 117 | 0 | 0 | 138 | 0 | 0 | 175 | 95 | 0 | 0 | 0 |  | 6633.2 | 1987 | 8620.2 | 3604 | 475 | 1595 | 1764 | 181 | 150 | 717 | 134 | 0.2 | 0 | 102.56
17:00 | 37 | 120 | 0 | 0 | 365 | 74 | 50 | 355 | 133 | 0 | 0 | 400 | 100 | 40 | 48 | 55 | 180 | 0 | 0 | 0 | 7 | 32 | 98 | 10 | 75 | 10 | 39 | 54 | 55 | 36 | 19 | 25 | 30 | 33 | 33 | 50 | 0 | 70 | 80 | 0 | 0 | 16 | 0 | 195 | 0 | 60 | 0 | 42 | 0 | 0 | 80 | 98 | 37 | 16 | 3 | 0 | 100 | 100 | 300 | 272 | 180 | 78 | 0 | 39 | 0 | 5 | 51 | 11 | 0 | 0 | 19 | 11 | 33 | 15 | 134 | 47 | 8 | 17 | 0.5 | 59 | 60 | 53 | 50 | 163 | 190 | 55 | 10 | 45 | 80 | 0 | 42 | 11 | 285 | 22 | 10 | 0 | 303 | 0 | 0 | 166 | 0 |  | 475 | 0 | 167 | 73 | 108 | 120 | 0 | 0 | 0 | 0 | 40 | 188 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 59 | 12 | 43 | 0 | 25 | 0 | 18 | 11 | 11 | 0 | 64 | 119 | 0 | 0 | 138 | 0 | 0 | 178 | 97 | 0 | 0 | 0 |  | 6284.5 | 2028 | 8312.5 | 3326 | 475 | 1608 | 1726 | 183 | 150 | 710 | 134 | 0.5 | 0 | 102.56
18:00 | 37 | 120 | 0 | 0 | 365 | 74 | 60 | 345 | 251 | 0 | 0 | 350 | 100 | 15 | 15 | 30 | 171 | 0 | 0 | 0 | 7 | 15 | 98 | 10 | 40 | 10 | 12 | 54 | 56 | 36 | 19 | 25 | 31 | 33 | 33 | 41 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 194 | 0 | 60 | 0 | 42 | 0 | 0 | 80 | 98 | 45 | 0 | 6 | 0 | 100 | 100 | 301 | 272 | 196 | 78 | 50 | 39 | 0 | 5 | 12 | 10 | 0 | 0 | 19 | 11 | 33 | 15 | 124 | 47 | 8 | 17 | 0.2 | 59 | 62 | 11 | 10 | 100 | 188 | 47 | 10 | 10 | 79 | 0 | 12 | 11 | 275 | 23 | 10 | 0 | 303 | 0 | 0 | 171 | 0 |  | 473 | 0 | 167 | 22 | 115 | 120 | 0 | 0 | 14 | 18 | 16 | 175 | 18 | 64 | 0 | 0 | 0 | 0 | 10 | 59 | 12 | 16 | 0 | 25 | 0 | 18 | 11 | 11 | 0 | 64 | 152 | 0 | 0 | 138 | 0 | 0 | 168 | 52 | 0 | 0 | 0 |  | 5980.2 | 1938 | 7918.2 | 3338 | 473 | 1384 | 1474 | 216 | 168 | 741 | 124 | 0.2 | 0 | 102.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.55
19:00 | 37 | 120 | 0 | 0 | 320 | 74 | 75 | 348 | 273 | 13 | 0 | 400 | 100 | 10 | 15 | 30 | 170 | 0 | 0 | 5 | 7 | 15 | 110 | 50 | 57 | 10 | 12 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 49 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 215 | 0 | 60 | 0 | 42 | 59 | 0 | 80 | 98 | 44 | 16 | 8 | 0 | 100 | 100 | 354 | 342 | 214 | 78 | 75 | 39 | 0 | 5 | 12 | 40 | 16 | 1 | 19 | 8 | 33 | 15 | 152 | 45 | 40 | 20 | 0 | 60 | 62 | 11 | 13 | 100 | 214 | 59 | 10 | 10 | 80 | 0 | 12 | 11 | 260 | 23 | 10 | 50 | 301 | 0 | 0 | 184 | 0 |  | 473 | 0 | 168 | 29 | 115 | 155 | 0 | 0 | 49 | 20 | 40 | 191 | 31 | 64 | 0 | 0 | 0 | 34 | 38 | 59 | 35 | 43 | 37 | 43 | 40 | 19 | 11 | 11 | 0 | 67 | 160 | 15 | 18 | 135 | 0 | 0 | 171 | 63 | 10 | 0 | 0 |  | 6589 | 2344 | 8933 | 3529 | 473 | 1516 | 1772 | 227 | 168 | 1096 | 152 | 0 | 0 | 102.55
19:30 | 37 | 120 | 0 | 0 | 350 | 88 | 75 | 366 | 271 | 26 | 0 | 400 | 100 | 85 | 30 | 30 | 170 | 0 | 0 | 12 | 40 | 48 | 149 | 100 | 75 | 10 | 39 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 194 | 0 | 125 | 0 | 42 | 64 | 0 | 80 | 98 | 44 | 16 | 10 | 0 | 100 | 100 | 300 | 301 | 173 | 78 | 100 | 39 | 0 | 5 | 12 | 85 | 20 | 8 | 19 | 8 | 33 | 15 | 166 | 47 | 89 | 20 | 0 | 60 | 62 | 50 | 50 | 163 | 190 | 61 | 86 | 10 | 79 | 0 | 44 | 11 | 300 | 23 | 10 | 80 | 301 | 0 | 0 | 184 | 0 |  | 473 | 0 | 168 | 73 | 115 | 170 | 0 | 35 | 50 | 22 | 40 | 187 | 33 | 64 | 0 | 0 | 0 | 43 | 38 | 59 | 40 | 43 | 44 | 43 | 43 | 22 | 11 | 11 | 0 | 65 | 160 | 15 | 18 | 135 | 0 | 0 | 187 | 93 | 51 | 0 | 0 |  | 7315 | 2551 | 9866 | 3441 | 473 | 1897 | 2255 | 225 | 168 | 1241 | 166 | 0 | 0 | 102.55
20:00 | 37 | 120 | 0 | 0 | 350 | 88 | 75 | 365 | 271 | 0 | 0 | 400 | 100 | 65 | 36 | 49 | 170 | 0 | 0 | 0 | 60 | 48 | 149 | 100 | 75 | 10 | 38 | 54 | 55 | 55 | 19 | 25 | 31 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 199 | 0 | 135 | 0 | 42 | 64 | 0 | 80 | 98 | 44 | 16 | 15 | 0 | 100 | 100 | 325 | 323 | 196 | 78 | 100 | 39 | 0 | 5 | 20 | 85 | 0 | 8 | 19 | 11 | 33 | 15 | 166 | 48 | 91 | 20 | 0 | 60 | 62 | 50 | 50 | 163 | 204 | 60 | 86 | 46 | 78 | 0 | 44 | 11 | 270 | 23 | 11 | 80 | 301 | 0 | 0 | 174 | 32 |  | 473 | 0 | 168 | 76 | 115 | 170 | 0 | 23 | 50 | 37 | 40 | 192 | 35 | 64 | 0 | 0 | 0 | 43 | 38 | 59 | 33 | 43 | 47 | 43 | 43 | 22 | 11 | 11 | 0 | 65 | 158 | 17 | 18 | 135 | 0 | 0 | 178 | 96 | 50 | 0 | 0 |  | 7425 | 2553 | 9978 | 3532 | 473 | 1921 | 2248 | 223 | 168 | 1247 | 166 | 0 | 0 | 102.55
21:00 | 37 | 120 | 0 | 0 | 350 | 88 | 76 | 365 | 271 | 0 | 0 | 400 | 145 | 92 | 52 | 55 | 170 | 0 | 0 | 0 | 89 | 64 | 149 | 100 | 75 | 51 | 39 | 54 | 56 | 55 | 19 | 25 | 31 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 197 | 0 | 135 | 0 | 42 | 64 | 0 | 80 | 98 | 45 | 16 | 23 | 0 | 100 | 100 | 305 | 305 | 164 | 78 | 101 | 39 | 0 | 5 | 51 | 86 | 0 | 14 | 19 | 11 | 33 | 18 | 168 | 47 | 95 | 20 | 0 | 60 | 62 | 50 | 50 | 163 | 196 | 61 | 86 | 47 | 78 | 0 | 44 | 11 | 320 | 23 | 11 | 120 | 303 | 0 | 0 | 174 | 32 |  | 473 | 0 | 167 | 64 | 104 | 170 | 0 | 53 | 49 | 60 | 33 | 193 | 38 | 96 | 0 | 0 | 0 | 43 | 37 | 100 | 33 | 43 | 44 | 43 | 42 | 22 | 11 | 11 | 0 | 60 | 159 | 16 | 17 | 135 | 0 | 0 | 189 | 97 | 79 | 0 | 0 |  | 7678 | 2681 | 10359 | 3458 | 473 | 2017 | 2544 | 219 | 168 | 1312 | 168 | 0 | 0 | 102.55
22:00 | 37 | 120 | 0 | 0 | 350 | 88 | 70 | 365 | 271 | 0 | 0 | 400 | 100 | 98 | 100 | 55 | 160 | 0 | 0 | 0 | 91 | 102 | 149 | 100 | 75 | 31 | 39 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 196 | 0 | 135 | 0 | 42 | 64 | 0 | 80 | 98 | 44 | 16 | 27 | 0 | 100 | 100 | 300 | 301 | 183 | 78 | 100 | 39 | 0 | 5 | 51 | 85 | 0 | 25 | 19 | 11 | 33 | 18 | 166 | 48 | 95 | 20 | 0 | 54 | 62 | 50 | 50 | 163 | 189 | 48 | 86 | 47 | 77 | 0 | 44 | 10 | 285 | 23 | 11 | 120 | 303 | 0 | 0 | 174 | 31 |  | 474 | 0 | 167 | 83 | 115 | 170 | 0 | 54 | 49 | 50 | 16 | 187 | 37 | 96 | 0 | 0 | 0 | 43 | 37 | 100 | 40 | 43 | 44 | 43 | 42 | 22 | 11 | 11 | 0 | 65 | 135 | 16 | 18 | 135 | 0 | 0 | 169 | 97 | 81 | 0 | 0 |  | 7648 | 2650 | 10298 | 3426 | 474 | 1977 | 2605 | 200 | 168 | 1282 | 166 | 0 | 0 | 102.55
23:00 | 37 | 120 | 0 | 0 | 349 | 89 | 70 | 364 | 271 | 0 | 0 | 400 | 100 | 45 | 50 | 55 | 160 | 0 | 0 | 0 | 15 | 60 | 149 | 20 | 74 | 11 | 39 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 221 | 0 | 110 | 0 | 42 | 64 | 0 | 80 | 99 | 44 | 16 | 24 | 0 | 100 | 100 | 344 | 345 | 179 | 78 | 100 | 39 | 0 | 5 | 51 | 41 | 0 | 8 | 19 | 11 | 33 | 20 | 166 | 47 | 95 | 20 | 0 | 55 | 62 | 50 | 50 | 163 | 219 | 60 | 86 | 47 | 78 | 0 | 44 | 10 | 270 | 23 | 11 | 0 | 301 | 0 | 0 | 173 | 0 |  | 474 | 0 | 166 | 75 | 115 | 170 | 0 | 0 | 49 | 45 | 33 | 191 | 25 | 96 | 0 | 0 | 0 | 43 | 37 | 100 | 40 | 43 | 0 | 43 | 42 | 22 | 11 | 11 | 0 | 63 | 120 | 16 | 18 | 135 | 0 | 0 | 179 | 97 | 0 | 0 | 0 |  | 7222 | 2459 | 9681 | 3556 | 474 | 1904 | 1987 | 183 | 168 | 1243 | 166 | 0 | 0 | 102.55
24:00 | 37 | 120 | 0 | 0 | 350 | 89 | 70 | 368 | 280 | 0 | 0 | 400 | 145 | 20 | 50 | 55 | 160 | 0 | 0 | 0 | 30 | 60 | 149 | 50 | 74 | 51 | 39 | 54 | 56 | 55 | 19 | 25 | 32 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 204 | 0 | 135 | 0 | 42 | 64 | 0 | 80 | 99 | 44 | 16 | 29 | 0 | 100 | 100 | 322 | 327 | 158 | 78 | 100 | 39 | 0 | 5 | 51 | 86 | 0 | 15 | 19 | 11 | 33 | 20 | 162 | 47 | 95 | 20 | 0 | 55 | 62 | 50 | 50 | 163 | 200 | 61 | 86 | 47 | 78 | 0 | 44 | 10 | 330 | 23 | 11 | 0 | 301 | 0 | 0 | 173 | 0 |  | 473 | 0 | 165 | 75 | 115 | 200 | 0 | 0 | 49 | 45 | 40 | 193 | 31 | 96 | 0 | 0 | 0 | 43 | 37 | 101 | 40 | 43 | 0 | 43 | 43 | 22 | 11 | 11 | 0 | 0 | 119 | 16 | 17 | 135 | 0 | 0 | 190 | 98 | 0 | 0 | 0 |  | 7383 | 2451 | 9834 | 3483 | 473 | 2030 | 2106 | 119 | 168 | 1293 | 162 | 0 | 0 | 102.55
KWH | 853000 | 2868390 | 0 | 0 | 7878272 | 1831636 | 1442560 | 8747010 | 5508000 | 16000 | 0 | 9335162 | 2818880 | 913920 | 980136 | 908477 | 4017474 | 0 | 1685000 | 24000 | 879360 | 664848 | 2321280 | 1108697 | 1320000 | 246100 | 765360 | 1013040 | 992894 | 880000 | 431568 | 600000 | 723420 | 822600 | 835300 | 930384 | 0 | 1947215 | 1890400 | 0 | 0 | 301680 | 0 | 4685741 | 0 | 2030318 | 0 | 829920 | 672744 | 444033 | 1849560 | 1847040 | 960000 | 370464 | 430080 | 0 | 2473750 | 2394302 | 7947400 | 7385250 | 4427000 | 1923636 | 1627200 | 833400 | 0 | 180000 | 870109 | 1478621 | 16256 | 89054 | 445680 | 197100 | 692400 | 404280 | 3292800 | 1609880 | 665380 | 410616 | 13497 | 1330000 | 1448800 | 969000 | 931000 | 3432436 | 4468467 | 1317000 | 1504320 | 869760 | 1928900 | 0 | 914080 | 175860 | 7663320 | 537768 | 219552 | 330240 | 4937889 | 0 | 0 | 3374400 | 84110 |  | 11306364 | 0 | 5028192 | 1052160 | 1343040 | 3268800 | 0 | 119690 | 363360 | 279680 | 557625 | 4677125 | 498424 | 1009920 | 0 | 0 | 0 | 315232 | 149806 | 1264220 | 796610 | 765584 | 385287 | 493920 | 242110 | 486480 | 261000 | 230112 | 0 | 1585745 | 3142200 | 122000 | 134000 | 3563609 | 0 | 0 | 4297845 | 1899625 | 224640 | 0 | 0 |  | 158436476 | 49864405 | 208300881 | 85430281 | 11306364 | 42605109 | 36094558 | 4727945 | 3837615 | 20992712 | 3292800 | 13497 | 0
Fuel Cost | 733580 | 2466815.4 | 0 | 0 | 6775313.92 | 1483625.16 | 1356006.4 | 5335676.1 | 3359880 | 153760 | 0 | 6254558.54 | 42818787.2 | 5739417.6 | 6547308.48 | 5550794.47 | 2611358.1 | 0 | 1870350 | 373440 | 5496000 | 4381348.32 | 22446777.6 | 7062399.89 | 7906800 | 3935139 | 5104951.2 | 7222975.2 | 6205587.5 | 5517600 | 323676 | 450000 | 0 | 0 | 0 | 8801432.64 | 0 | 0 | 0 | 0 | 0 | 2856909.6 | 0 | 63960364.65 | 0 | 44484267.38 | 0 | 7294996.8 | 7245452.88 | 4320441.09 | 11448776.4 | 11931878.4 | 6278400 | 314894.4 | 0 | 0 | 2251112.5 | 2178814.82 | 7232134 | 5095822.5 | 3098900 | 1327308.84 | 1562112 | 558378 | 0 | 165600 | 713489.38 | 1389903.74 | 176215.04 | 660780.68 | 343173.6 | 147825 | 533148 | 303210 | 22522752 | 1207410 | 6114842.2 | 316174.32 | 0 | 1383200 | 1506752 | 930240 | 837900 | 4427842.44 | 3127926.9 | 1501380 | 1609622.4 | 956736 | 2198946 | 0 | 850094.4 | 163549.8 | 4904524.8 | 403326 | 166859.52 | 5723059.2 | 0 | 0 | 0 | 0 | 0 |  | 57662456.4 | 0 | 3368888.64 | 6944256 | 8998368 | 52562304 | 0 | 1910252.4 | 4091433.6 | 3294630.4 | 3552071.25 | 4630353.75 | 493439.76 | 6241305.6 | 0 | 0 | 0 | 3609406.4 | 1605920.32 | 11327411.2 | 6890676.5 | 6813697.6 | 4103306.55 | 4899686.4 | 2607524.7 | 535128 | 245340 | 174194.784 | 0 | 9625472.15 | 0 | 2814540 | 2872960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 427012806.4 | 211875024.404 | 638887830.804 | 64171706.254 | 57662456.4 | 32004789.66 | 221377698.53 | 9625472.15 | 0 | 231522955.81 | 22522752 | 0 | 0
Yesterday Day Peak | 37 | 120 | 0 | 0 | 363 | 87 | 74 | 390 | 151 | 0 | 0 | 420 | 140 | 11 | 48 | 55 | 160 | 0 | 99 | 0 | 10 | 7 | 98 | 70 | 75 | 11 | 39 | 54 | 55 | 36 | 19 | 25 | 32 | 33 | 33 | 42 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 201 | 0 | 135 | 0 | 14 | 0 | 0 | 80 | 99 | 37 | 16 | 2 | 0 | 100 | 10 | 368 | 265 | 157 | 78 | 30 | 39 | 0 | 10 | 51 | 85 | 0 | 0 | 18 | 11 | 33 | 14 | 128 | 61 | 8 | 17 | 2.9 | 58 | 60 | 47 | 50 | 130 | 190 | 54 | 85 | 45 | 80 | 0 | 43 | 0 | 280 | 22 | 8 | 0 | 201 | 0 | 0 | 150 | 0 |  | 473 | 0 | 3 | 69 | 16 | 120 | 0 | 0 | 0 | 0 | 40 | 189 | 17 | 32 | 0 | 0 | 0 | 0 | 0 | 33 | 40 | 25 | 0 | 8 | 0 | 22 | 10 | 8 | 0 | 70 | 114 | 0 | 0 | 135 | 0 | 0 | 219 | 94 | 0 | 0 | 0 |  | 8287.9 | DayPeak
Yesterday Evening Peak | 37 | 120 | 0 | 0 | 350 | 88 | 76 | 365 | 271 | 0 | 0 | 400 | 145 | 92 | 52 | 55 | 170 | 0 | 0 | 0 | 89 | 64 | 149 | 100 | 75 | 51 | 39 | 54 | 56 | 55 | 19 | 25 | 31 | 33 | 33 | 50 | 0 | 88 | 80 | 0 | 0 | 16 | 0 | 197 | 0 | 135 | 0 | 42 | 64 | 0 | 80 | 98 | 45 | 16 | 23 | 0 | 100 | 100 | 305 | 305 | 164 | 78 | 101 | 39 | 0 | 5 | 51 | 86 | 0 | 14 | 19 | 11 | 33 | 18 | 168 | 47 | 95 | 20 | 0 | 60 | 62 | 50 | 50 | 163 | 196 | 61 | 86 | 47 | 78 | 0 | 44 | 11 | 320 | 23 | 11 | 120 | 303 | 0 | 0 | 174 | 32 |  | 473 | 0 | 167 | 64 | 104 | 170 | 0 | 53 | 49 | 60 | 33 | 193 | 38 | 96 | 0 | 0 | 0 | 43 | 37 | 100 | 33 | 43 | 44 | 43 | 42 | 22 | 11 | 11 | 0 | 60 | 159 | 16 | 17 | 135 | 0 | 0 | 189 | 97 | 79 | 0 | 0 |  | 10359 | EvPeak
Forecast for Evening | 37 | 120 | 0 | 0 | 365 | 108 | 78 | 412 | 360 | 98 | 0 | 450 | 305 | 100 | 102 | 55 | 200 | 0 | 0 | 100 | 93 | 102 | 149 | 100 | 100 | 50 | 40 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 89 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 135 | 0 | 51 | 68 | 74 | 80 | 103 | 44 | 16 | 23 | 0 | 150 | 100 | 360 | 360 | 225 | 195 | 100 | 39 | 0 | 10 | 51 | 85 | 48 | 52 | 19 | 11 | 33 | 22 | 164 | 100 | 95 | 22 | 0 | 58 | 62 | 51 | 50 | 163 | 330 | 60 | 86 | 50 | 100 | 0 | 45 | 10 | 341 | 23 | 8 | 200 | 300 | 0 | 0 | 185 | 106 |  | 470 | 32 | 365 | 110 | 99 | 225 | 0 | 54 | 47 | 78 | 40 | 194 | 30 | 110 | 30 | 0 | 0 | 43 | 38 | 102 | 43 | 43 | 46 | 43 | 43 | 22 | 12 | 11 | 0 | 0 | 160 | 17 | 18 | 215 | 0 | 0 | 220 | 95 | 80
Forecast for Day | 37 | 120 | 0 | 0 | 365 | 100 | 78 | 412 | 360 | 98 | 0 | 450 | 150 | 100 | 102 | 55 | 200 | 0 | 0 | 100 | 93 | 102 | 0 | 100 | 100 | 50 | 40 | 54 | 55 | 55 | 0 | 25 | 33 | 33 | 33 | 52 | 0 | 89 | 80 | 0 | 0 | 25 | 0 | 225 | 0 | 60 | 0 | 51 | 68 | 74 | 80 | 103 | 44 | 16 | 15 | 0 | 150 | 100 | 360 | 360 | 225 | 78 | 100 | 39 | 0 | 10 | 51 | 85 | 0 | 52 | 19 | 8 | 33 | 22 | 124 | 97 | 95 | 22 | 2 | 58 | 62 | 51 | 50 | 163 | 330 | 50 | 86 | 50 | 80 | 0 | 45 | 10 | 341 | 23 | 8 | 0 | 150 | 0 | 0 | 150 | 106 |  | 463 | 0 | 250 | 110 | 99 | 225 | 0 | 0 | 36 | 78 | 40 | 194 | 30 | 110 | 0 | 0 | 0 | 0 | 0 | 100 | 43 | 43 | 46 | 43 | 42 | 22 | 12 | 11 | 0 | 0 | 160 |  | 18 | 215 | 0 | 0 | 220 | 95 | 80
Generation at 08:00(Today) | 37 | 120 | 0 | 0 | 280 | 25 | 40 | 300 | 301 | 0 | 0 | 320 | 100 | 7 | 16 | 15 | 110 | 0 | 0 | 0 | 7 | 7 | 0 | 10 | 8 | 0 | 12 | 18 | 18 | 17 | 0 | 25 | 32 | 33 | 33 | 0 | 0 | 80 | 80 | 0 | 0 | 8 | 0 | 216 | 0 | 50 | 0 | 8 | 0 | 0 | 15 | 12 | 18 | 17 | 16 | 0 | 100 | 100 | 337 | 334 | 204 | 78 | 100 | 39 | 0 | 5 | 12 | 11 | 0 | 0 | 19 | 11 | 8 | 12 | 104 | 63 | 8 | 20 | 1.5 | 58 | 62 | 11 | 10 | 100 | 208 | 50 | 10 | 10 | 78 | 0 | 13 | 10 | 320 | 23 | 5 | 0 | 48 | 0 | 0 | 55 | 0 | 0 | 463 | 0 | 95 | 10 | 16 | 120 | 0 | 0 | 0 | 0 | 8 | 154 | 21 | 16 | 0 | 0 | 0 | 0 | 0 | 24 | 40 | 43 | 0 | 8 | 42 | 18 | 11 | 10 | 0 | 0 | 119 | 0 | 0 | 135 | 0 | 0 | 184 | 12 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6793.4 | 7:00
| Highest Generation |  | 10359 | 21:00
| Day Peak Generation |  | 8287.9 | 12:00
| Evening Peak Generation |  | 10359 | 21:00
| HVDC Max Flow |  | 475 | 15:00
| HVDC EvPeak Flow |  | 473 | 21:00
| Load factor L.F |  | 83.78%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2018-06-29
Till now the maximum generation is : - |  |  | 10958 | 21:00 | Hrs on | 2018-05-28
The Summary of Yesterday's |  | 2018-06-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8287.9 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6526.4 | MW
Evening Peak Generation : |  | 10359 | MW Hour : | 21:00 | Available Max Generation : |  | 12503 | MW
E.P. Demand (at gen end) : |  | 10359 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 10359 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2503 | MW
Total Gen. (MKWH) : |  | 208.3009 | System Load Factor : | 83.78% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -820 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2018-06-29
Actual : | 102.49 | Ft.(MSL) , | Rule curve : | 83.46 | Ft.( MSL )
Gas Consumed : | Total = | 1084.73 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 96176495.914
|  | Coal : | 9625472.15 | Oil : | 452900654.34 | Total : | 558702622.404
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3487.3513 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1182.5531 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1058.9334 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 956.6244 |  |  | 0 | 0%
Comilla Area | 0 | 0:00 | 864.6041 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 697.6965 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 394.4147 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 179.7518 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 538.0776 |  |  | 0 | 0%
Total | 0 |  | 9360.007 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
|  |  |  | 1) Barapukuria ST: Unit-1 |  | 10) Ashuganj 55 MW
| Nil |  |  | 2) Khulna ST 110 MW |  | 11) Haripur GT-1,2
3) Ghorasal Unit-2,4,5
4) Baghabari 100 MW
5) Tongi GT
6) Chittagong Unit-1,2
7) Baghabari-71 MW
8) Siddhirganj 210 MW ST
9) Ashuganj unit-3
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
|  | Description |  | Comments on Power Interruption
a) Tongi-Bashundhara 132 kV Ckt-1 tripped at 08:43 from Bashundhara end showing 3-Phase to ground fault relay and was
switched on at 09:02.
b) Tongi-Bashundhara 132 kV Ckt-2 tripped at 08:43 from both ends showing main protection relay and was switched on at
09:09.
c) Mirpur-Aminbazar 132 kV Ckt-1 was under shut down from 09:57 to 17:27 for red hot maintenance.
d) Shahjibazar-Bibiyana 230 kV Ckt-2 was under shut down from 10:10 to 13:45 for development work.
e) Chandpur 150 MW ST was under shut down from 16:34 to 17:05 for TG problem.
f) Cox's bazar 132/33 kV T2 transformer was under shut down from 21:19 to 22:55 for red hot maintenance. |  |  |  | About 20 MW Power interruption occurred under Cox's bazar S/S
g) Barapukuria Unit-2 was forced shut down at 23:38 due to super heater tube leakage. |  |  |  | area from 21:19 to 22:55.
h) Ashuganj Unit-5 tripped at 00:59 (29/06/2018) due to HP bypass quick open and was synchronized at 03:57(29/06/2018).
i) Kodda 132 kV Bus-1 & 2 were shut down at 06:11 (29/06/2018) for development work. |  |  |  | About 90 MW Power interruption occurred under Kodda S/S
area from 06:11 to till now (29/06/2018).
j) Halishahar 132/33 kV T1 & T3 transformers were under shut down from 06:09 to 07:58 (29/06/2018) for corrective |  |  |  | About 40 MW Power interruption occurred under Halishahar S/S
maintenance. |  |  |  | area from 06:09 to 07:58 (29/06/2018).
k) Thakurgaon-Panchagar 132 kV Ckt was under shut down from 05:35 to 07:18 (29/06/2018) for corrective maintenance. |  |  |  | About 30 MW Power interruption occurred under Panchagar S/S
area from 05:35 to 07:18 (29/06/2018).
l) Saidpur-Purbasadipur 132 kV Ckt-2 was under shut from 05:36 to 09:55 (29/06/2018) for corrective maintenance. |  |  |  | About 43 MW Power interruption occurred under Purbasadipur S/S
area from 05:36 to 09:55 (29/06/2018).
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Dispatch Circle
Page 1 of 7

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2018-06-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
1 | Ghorasal ST: Unit-1,2 |  | PDB | 2*55 | 85 | 37 | 853000 | # 2 Under maint.
| Ghorasal ST: Unit-3 |  | PDB | 1*210 | 170 | 120 | 2868390 | Gas shortage
| Ghorasal ST: Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal ST: Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal ST: Unit-7 |  | PDB | 1*243+1*122 | 365 | 350 | 7878272
3 | Ghorashal 78MW (MAX) |  | QRPP | 2*40 | 78 | 76 | 1442560
4 | Ghorashal (Regent) |  | IPP | 34*3.35 | 108 | 88 | 1831636 | Gas shortage
5 | Haripur GT: Unit-1, 2 |  | SBU, PDB | 2*32 | 40 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 365 | 8747010 | FGMO
7 | Haripur NEPC 110MW |  | IPP | 8*15 | 110 | 0 | 16000 | Reserve
8 | Haripur Power CCPP 360MW |  | IPP | 1*235+1*125 | 360 | 271 | 5508000 | Gas shortage
9 | Meghnaghat CCPP 450MW |  | IPP | 2*150+1*150 | 450 | 400 | 9335162 | Frequency control.
10 | Meghnaghat (IEL) |  | QRPP | 12*8.9 | 100 | 92 | 913920 | Engine problem
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 145 | 2818880 | Low demand
12 | Madanganj 102MW |  | QRPP | 6*17 | 100 | 52 | 980136 | Low demand
13 | Madanganj-55 MW |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 908477
14 | Keraniganj (Powerpac) 100MW |  | QRPP | 8*13.45 | 100 | 100 | 1108697
15 | Narshingdi (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 431568 | Engine problem
16 | Siddhirgonj ST 210MW |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj GT Unit-1& 2 |  | EGCB | 2*105 | 210 | 0 | 1685000 | Gas shortage
18 | Siddhirganj (Desh) |  | QRPP | 96*1.2 | 100 | 0 | 24000 | Reserve
19 | Siddhirganj (Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 89 | 879360 | Engine problem
20 | Siddhirganj CCPP-335 MW |  | EGCB | 1*217 | 217 | 170 | 4017474 | Gas shortage
21 | Pagla (DPA ) |  | QRPP | 100*0.5 | 50 | 51 | 246100
22 | Gagnagar (Orion) |  | IPP | 12*8.924 | 102 | 64 | 664848 | Low demand
23 | Katpotti 51 MW |  | IPP | 7*7.9 | 51 | 39 | 765360 | Engine problem
24 | Banco Energy 54MW |  | IPP | 3*18 | 54 | 54 | 1013040
25 | Kodda 150MW |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 2321280
26 | Northern 55 MW |  | IPP | 3*19.3 | 55 | 56 | 992894
27 | Southern 55MW |  | IPP | 3*19.3 | 55 | 55 | 880000
28 | Bosila 108MW |  | IPP | 12*8.775+1*3.5 | 108 | 75 | 1320000 | Engine problem
29 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 56 | 1323420 | Engine problem
30 | Summit Maona |  | SIPP,REB | 4*8.73 | 33 | 33 | 822600
31 | Summit Rupganj |  | SIPP,REB | 4*8.73 | 33 | 33 | 835300
32 | Gazipur (RPCL) |  | IPP | 6*8.9 | 52 | 50 | 930384
33 | Tongi GT |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
34 | Summit Gazipur |  | IPP | 18*17.076 | 300 | 303 | 4937889
| APR Energy , Keranigonj |  | IPP | 236*1.4 | 0 | 0 | 0
| Bramhangoan 100 MW (Aggreko) |  | IPP | 100 | 0 | 0 | 0 | On test.
| Aggreko Aurahati 100MW |  | IPP | 0.85*23+0.95*91 | 0 | 32 | 84110 | On test.
| Dhaka area Total |  |  |  | 5199 | 3479 | 69384767
35 | Chittagong ST-1 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Chittgong ST-2 (Raozan) |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
36 | Raozan 25 MW (RPCL) |  | IPP | 3*8.9 | 25 | 16 | 301680 | Engine problem
37 | Patenga 50MW |  | IPP | 8*6.98 | 50 | 45 | 960000 | Engine problem
38 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 168 | 3837615 | # 5 under maint.
39 | Sikalbaha ST 60MW |  | PDB | 1*60 | 40 | 0 | 0 | Under maint.
40 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 197 | 4685741 | FGMO
41 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2030318
42 | Sikalbaha (Energis) |  | RPP | 4*12.5+2*11.9+1*3+1*1.5 | 51 | 42 | 829920 | Engine problem
43 | Hathazari peaking |  | PDB | 11*8.9 | 98 | 64 | 672744
44 | Dohazari Peaking |  | PDB | 6*17 | 102 | 0 | 444033
45 | Juldah (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1849560 | Engine problem
46 | Barabkunda (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 370464
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 430080
47 | Chittagong ECPV 108 MW |  | IPP | 16*7 | 108 | 98 | 1847040 | Engine problem
| Chittagong area Total |  |  |  | 1561 | 884 | 18259195
48 | Ashuganj ST: Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj ST: Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2473750 | Gas shortage
| Ashuganj ST: Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 2394302 | Gas shortage
49 | Ashuganj CCPP 225 MW |  | APSCL | 1*142+1*75 | 221 | 164 | 4427000 | FGMO
50 | Ashuganj CCPP(North) |  | APSCL | 1*360 | 360 | 305 | 7947400 | FGMO
51 | Ashuganj CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 7385250 | FGMO
52 | Ashuganj Engines TSK |  | APSCL | 14*3.968 | 45 | 39 | 833400 | Engine problem
53 | Ashuganj (Precision) 55MW |  | RPP | 15*4 | 55 | 0 | 0 | Under maint.
54 | Ashuganj (United) 53MW |  | QRPP | 14*4 | 53 | 5 | 180000 | Gas shortage
55 | Ashuganj 195MW Modular |  | IPP | 20*9.73+1*16 | 195 | 78 | 1923636 | Gas shortage
56 | Ashuganj (Midland) 51MW |  | IPP | 6*9.34 | 51 | 51 | 870109
57 | B.Baria (Aggreko) 85MW |  | QRPP | 86*1.10 | 85 | 86 | 1478621
58 | Daudkandi Peaking 52MW |  | PDB | 6*8.92 | 52 | 0 | 16256 | Reserve
59 | Chandpur CCPP |  | PDB | 1*106+1*57 | 163 | 101 | 1627200
60 | Feni (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 19 | 445680
61 | Feni, Mohipal (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 197100
** | Tripura |  | Imported power | 0 | 160 | 168 | 3292800
62 | Jangalia (Summit) 33MW |  | SIPP, PDB | 4*8.73 | 33 | 33 | 692400
63 | Lakdhanvi 52 MW |  | IPP | 6*8.92 | 52 | 14 | 89054 | Line O/L.
64 | Summit Comilla 25MW |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 18 | 404280 | Engine problem
65 | Daudkandi bangla trak |  | IPP | 154*1.4 | 200 | 120 | 330240 | Low demand
| Comilla Area Total |  |  |  | 2541 | 1717 | 37008478
66 | Mymensingh RPCL 210MW |  | IPP | 4*35+1*70 | 202 | 47 | 1609880 | Gas shortage
67 | Tangail (Doreen) 22MW |  | SIPP, PDB | 8*2.90 | 22 | 20 | 410616
68 | Jamalpur 95MW |  | IPP | 12*8.924 | 95 | 95 | 665380
69 | Sarishabari (Solar) |  | IPP | 1*3 | 3 | 0 | 13497
| United Mymensingh PPL |  | IPP | 200 | 0 | 174 | 3374400 | On test.
| Mymensingh Area Total |  |  |  | 322 | 336 | 6073773
70 | Fenchugonj CCPP-1 |  | PDB | 2*32+1*33 | 70 | 60 | 1330000
71 | Fenchugonj CCPP-2 |  | PDB | 2*35+1*35 | 90 | 62 | 1448800
72 | Kushiara 163 MW CCPP GT |  | IPP | 1*109+1*54 | 163 | 163 | 3432436
73 | Shajibazar 330 MW |  | PDB | 3*110 | 330 | 196 | 4468467 | FGMO
74 | Fenchugonj (Barakatullah) 51MW |  | RPP | 19*2.90 | 51 | 50 | 969000
75 | Fenchuganj (EPL) 44MW |  | RPP | 12*3.3+5*2 | 44 | 50 | 931000
76 | Hobiganj 11MW |  | SIPP, REB | 4*2.90 | 11 | 11 | 219552
77 | Shahjibazar GT: Unit- 8, 9 |  | PDB | 2*35 | 66 | 61 | 1317000 | FGMO
78 | Shahjibazar 86MW |  | RPP | 32*2.90 | 86 | 86 | 1504320
79 | Shahjibazar (EPL) 50MW |  | RPP | 27*2.0 | 50 | 47 | 869760
80 | Sylhet GT 150 MW |  | PDB | 1*142 | 142 | 78 | 1928900
81 | Sylhet GT 20 MW |  | PDB | 1*20 | 20 | 0 | 0 | Under maint.
82 | Sylhet (EPL) 50MW |  | RPP | 27*2 | 50 | 44 | 914080 | Engine problem
83 | Shahjahanulla 25 MW |  | SIPP, REB | 3*9.34 | 25 | 23 | 537768
84 | Summit Bibiana- 2 |  | IPP | 1*222+1*119 | 341 | 320 | 7663320 | FGMO
85 | Sylhet (Desh) 10MW |  | RPP | 6*1.95 | 10 | 11 | 175860
| Sylhet Area Total |  |  |  | 1549 | 1262 | 27710263
86 | Bheramara GT-1,2,3 |  | PDB | 3*20 | 46 | 0 | 0 | Reserve
| Bheramara (HVDC ) |  | Imported power | 1*500 | 500 | 473 | 11306364
87 | Khulna (KPCL-1 & 3) |  | IPP | 19*6.5 | 110 | 64 | 1052160 | Engine problem
88 | Khulna (KPCL-2) |  | QRPP | 7*17 | 115 | 104 | 1343040 | Engine problem
89 | Faridpur Peaking |  | PDB | 8*6.89 | 54 | 49 | 363360
90 | Khulna CCPP 225MW |  | NWPGCL | 1*150+1*75 | 230 | 170 | 3268800 | Low demand
91 | Gopalganj Peaking |  | PDB | 16*6.98 | 109 | 60 | 279680
92 | Bheramara 360 MW |  | NWPGCL | 1*278+1*132 | 410 | 167 | 5028192 | Gas shortage
93 | Noapara (KZA) 40MW |  | QRPP | 5*8.5 | 40 | 33 | 557625
94 | Khulna (Aggreko) 55MW |  | QRPP | 71*0.85 | 55 | 53 | 119690
95 | Bangla Trak Noapara |  | IPP | 70*1.4 | 100 | 79 | 224640 | Low demand
| Khulna Area Total |  |  |  | 1769 | 1252 | 23543551
96 | Summit Barisal 110 MW |  | IPP | 7*17.076 | 110 | 96 | 1009920 | Line O/L.
97 | Barisal GT: Unit-1, 2 |  | PDB | 2*20 | 30 | 0 | 0 | Reserve
98 | Bhola (Venture) 33MW |  | RPP | 1*34.50 | 33 | 38 | 498424
99 | Bhola CCPP 194MW |  | PDB | 2*63+1*68 | 194 | 193 | 4677125
100 | Bhola Aggreko 95MW |  | QRPP | 96*1.10 | 95 | 97 | 1899625
| Barisal Area Total |  |  |  | 462 | 424 | 8085094
101 | Baghabari GT 71MW |  | PDB | 1*71 | 71 | 0 | 0 | Under maint.
| Baghabari GT 100MW |  | PDB | 1*100 | 100 | 0 | 0 | Under maint.
102 | Baghabari Peaking 50MW |  | PDB | 6*8.9 | 52 | 43 | 315232
103 | Bera Peaking |  | PDB | 9*8.29 | 71 | 37 | 149806
104 | Amnura 50MW |  | QRPP | 7*7.79 | 50 | 33 | 796610 | Engine problem
105 | Katakhali (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 765584 | Engine problem
106 | Katakhali Peaking |  | PDB | 6*8.7 | 50 | 44 | 385287
107 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | FGMO
108 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 189 | 0 | FGMO
| Sirajgonj Unit-3 225MW |  | NWPGCL | 1*150+1*75 | 0 | 0 | 0
109 | Santahar Peaking |  | PDB | 6*8.7 | 50 | 42 | 242110
110 | Bogra (GBB) |  | RPP | 6*4 | 22 | 22 | 486480
111 | Bogra (EPL) |  | RPP | 5*3.3+5*2 | 10 | 11 | 261000
112 | Ullapara (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 230112
113 | Rajlanka 52 MW |  | IPP | 6*8.92 | 52 | 43 | 493920 | Engine problem
114 | Chapainawabganj-100 MW |  | PDB | 12*8.924 | 104 | 100 | 1264220
| Rajshahi Area Total |  |  |  | 1123 | 618 | 5390361
115 | Barapukuria Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria Unit-2 |  | PDB | 1*125 | 85 | 60 | 1585745
116 | Barapukuria Unit-3 |  | PDB | 1*275 | 274 | 159 | 3142200
117 | Rangpur GT |  | PDB | 1*20 | 20 | 16 | 122000
118 | Saidpur GT |  | PDB | 1*20 | 20 | 17 | 134000
| Rangpur Area Total |  |  |  | 484 | 252 | 4983945
| Total |  |  |  | 15010 | 10224 | 200439427
| Eastern Grid Total |  |  |  | 11172 | 7678 | 158436476
| Western Grid Total |  |  |  | 3838 | 2546 | 42002951
| National Grid Total |  |  |  | 15010 | 10224 | 200439427
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division

## P3
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
Date: | 2018-06-28 | [5 empty] | QF-LDC-09
(a) ENTIRE EASTERN GRID : |  |  | 6438 | MW | (b) ENTIRE WESTERN GRID : |  |  | 3242 | MW
i) Dhaka area |  |  | 3497 | MW | i) Khulna area |  |  | 1284 | MW
ii) Chittagong area |  |  | 927 | MW | ii) Rajshahi area |  |  | 1069 | MW
iii) Comilla area |  |  | 914 | MW | iii) Barisal area |  |  | 262 | MW
iv) Mymensingh area |  |  | 644 | MW | iv) Rangpur area |  |  | 627 | MW
v) Sylhet area |  |  | 456 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  |  | 9680 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 1500 | Kishorganj | 94 | 2200 | Goalpara | 42 | 2100
Munsiganj | 110 | 2400 | Netrokona | 80 | 2000 | Central s/s | 68 | 1930
Sonargaon | 38 | 2400 | Jamalpur | 107 | 2200 | Noapara | 82 | 2100
Shyampur | 152 | 1100 | Sherpur | 84 | 2100 | Jessore | 134 | 2100
Bhulta | 190 | 2200 | Srimongal | 35 | 2100 | Jhenida | 88 | 2100
Madanganj | 44 | 600 | Shahjibazar | 106 | 2200 | Bottail | 120 | 1930
Shitalakhya | 105 | 1600 | Fenchuganj | 48 | 2100 | G.K Project | 52 | 2000
Rahim steel | 3 | 1000 | Kulawara | 41 | 2200 | Faridpur | 150 | 2100
Matuail | 84 | 1000 | Sylhet | 138 | 2000 | Madaripur | 125 | 2100
Ghorasal | 75 | 2100 | Chatak | 27 | 2100 | Gopalganj | 76 | 2100
Narsingdi | 114 | 2100 | Sunamganj | 31 | 2100 | Bagerhat | 70 | 2100
Haripur (SBU) | 80 | 2300 | Biani Bazar | 42 | 1930 | Mongla | 34 | 900
Ullon | 87 | 1900 | Comilla (S) | 168 | 2100 | Satkhira | 82 | 2000
Hasnabad | 188 | 1900 | Comilla(N) | 93 | 2200 | Gallamari | 45 | 1300
Magbazar | 126 | 1300 | Chandpur | 110 | 2000 | Magura | 50 | 2000
Maniknagar | 88 | 1300 | Feni | 118 | 2100 | Chuadanga | 81 | 2200
Bangabhaban | 38 | 1300 | Chowmuhani | 164 | 2200 | Barisal | 110 | 2100
Narinda | 76 | 1300 | Ashuganj | 58 | 2400 | Patuakhali | 90 | 2100
Dhanmondi | 116 | 1400 | Daudkandi | 98 | 2000 | Bhandaria | 38 | 2100
Lalbag | 79 | 2100 | B.Baria | 126 | 2100 | Ishurdi | 50 | 2100
Madartek | 47 | 1900 | Ramganj | 32 | 1900 | Ruppur Paromanobik | 1 | 100
Mirpur | 111 | 1930 | Madunaghat | 59 | 1930 | Natore | 115 | 2100
Kalyanpur | 102 | 1400 | Hathazari | 81 | 1400 | Bogra | 206 | 2100
Gulshan | 134 | 1300 | Khulshi | 198 | 1300 | Noagaon | 104 | 2100
Uttara | 86 | 1300 | Halishahar | 132 | 1700 | Rajshahi | 138 | 2100
Kamrangirchar | 67 | 1200 | Baraulia | 133 | 200 | C.Nawabganj | 67 | 2100
Savar | 130 | 1300 | Sikalbaha | 34 | 1900 | Amnura | 33 | 100
Bhasantec | 140 | 1300 | Dohazari | 76 | 2100 | Pabna | 107 | 2100
Agargaon | 46 | 1900 | Cox'sbazar | 76 | 100 | Shahjadpur | 92 | 2000
Satmosjid | 89 | 1500 | Chandraghona | 34 | 2100 | Serajganj | 76 | 2100
Tongi | 132 | 1500 | Kaptai | 4 | 2000 | Niyamatpur | 51 | 2100
Kabirpur | 192 | 1500 | A. Khaer Stl. | 14 | 1500 | Joypurhat | 44 | 2000
Basundhara | 127 | 2100 | Bakulia | 102 | 2000 | Rangpur | 108 | 100
Manikganj | 105 | 2100 | Julda | 14 | 900 | Lalmonirhat | 82 | 2100
Joydevpur | 224 | 1500 | TK chemical | 6 | 1600 | Saidpur | 102 | 2000
New Tongi | 107 | 1930 | Modern Steel | 12 | 1600 | Purbasadipur | 93 | 2100
Korda | 226 | 2100 | Shahmirpur | 29 | 1500 | Thakurgaon | 68 | 2100
Dhamrai | 19 | 2000 | Abul Khair 230 | 176 | 300 | Palashbari | 93 | 2100
Tangail | 166 | 2100 | BSRM | 116 | 1100 | Barapukuria | 52 | 2100
Mymensing | 226 | 2100 | Khagrachhari | 15 | 2100 | Panchagar | 40 | 2100
Sub Divisional Engineer |  |  | Executive Engineer |  |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  |  | Load Despatch Circle
(1) Honbl. State Minister |  |  | (8) Executive Director (O & M) PGCB. |  |  | (18) C.E. Transmission (1 & 2) PGCB.
Ministry of Power,Energy & Mineral |  |  | (9) Member,Generation,PDB. |  |  | (19) S.E. System Protection,PGCB.
Resources, GOB. |  |  | (10) Member,Distribution,PDB. |  |  | (20) Director,Public Relation,PDB.
(2) Secy (Power Divn.)Ministry of |  |  | (11) Member,Transmission & |  |  | (21) Director Program, PDB.
Power,Energy & Mineral Resources. |  |  | System Operation,PDB. |  |  | (22) S.E. Consumer Affairs,PDB.
(3) Director General,Power cell |  |  | (12) Member,P&D,PDB. |  |  | (23) Director,Project Planning,PDB.
(4) Chairman,BERC |  |  | (13) C.E (P & D), PGCB. |  |  | (24) Director,System Planning,PDB.
(5) Chairman, BPDB. |  |  | (14) G.M. Commercial Operation |  |  | (25) Executive Eng.IMD.
(6) Managing Director, PGCB. |  |  | (15) C.E. Generation,PDB. |  |  | (26) Executive Eng. EMD.
(7) Member(Power & Industry) |  |  | (16) C.E, (P & D),PDB. |  |  | (27) NLDC

## Voltage
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS.
Date: | 2018-06-28
Sub-Station | Maxm | Hour | Minm | Hour | Sub-Station | Maxm | Hour | Minm | Hour
| Voltage |  | Voltage |  |  | Voltage |  | Voltage
400 KV | KV |  | KV |  |  | KV |  | KV
Bibiyana | 393 | 5:00 | 386 | 19:00 | Kaliakoir | 376 | 6:00 | 366 | 19:00
Bheramara | 412 | 14:00 | 400 | 20:00
230 KV | KV |  | KV |  | 230 KV | KV |  | KV
Ghorasal | 230 | 1:00 | 230 | 1:00 | Tongi | 228 | 15:00 | 217 | 10:00
Ishurdi | 235 | 18:00 | 226 | 22:00 | Comilla (N) | 232 | 4:00 | 228 | 10:00
Ashuganj | 238 | 5:00 | 232 | 21:00 | Hathazari | 220 | 11:00 | 210 | 15:00
Serajganj | 229 | 6:00 | 218 | 19:30 | Megnaghat | 228 | 1:00 | 224 | 16:00
Baghabari | 228 | 10:00 | 221 | 23:00 | Fenchuganj | 239 | 13:00 | 233 | 16:00
Barapukuria | 234 | 6:00 | 223 | 24:00 | Siddhirganj | 225 | 5:00 | 221 | 9:00
Bogra | 226 | 6:00 | 210 | 21:00 | Maniknagar | 223 | 22:00 | 218 | 16:00
Khulna South | 240 | 17:00 | 230 | 1:00 | Old Airport | 224 | 22:00 | 219 | 9:00
Rampura | 222 | 1:00 | 219 | 11:00 | Barisal | 234 | 22:00 | 224 | 1:00
Haripur | 222 | 1:00 | 220 | 10:00 | AKSML | 218 | 18:00 | 207 | 1:00
Hasnabad | 225 | 1:00 | 220 | 17:00 | BSRM | 221 | 21:00 | 212 | 15:00
Aminbazar | 225 | 4:00 | 219 | 9:00 | Bibiyana | 232 | 3:00 | 229 | 22:00
132 kV | KV |  | KV |  | 132 kV | KV |  | KV
Siddhirganj | 134 | 100 | 132 | 1000 | B.Baria | 136 | 1000 | 131 | 1900
Munsiganj | 137 | 1930 | 132 | 900 | Ramganj | 129 | 700 | 121 | 1830
Megnaghat | 134 | 1930 | 130 | 500 | Madanhat | 132 | 500 | 127 | 1500
Shyampur | 132 | 2100 | 125 | 1100 | Hathazari | 131 | 800 | 126 | 1600
Bhulta | 126 | 300 | 123 | 900 | Khulshi | 128 | 300 | 122 | 1000
Madanganj | 134 | 300 | 129 | 1900 | Halishahar | 131 | 300 | 123 | 1500
Shitalakhya | 138 | 2100 | 131 | 900 | Baraulia | 128 | 300 | 123 | 1500
Rahim steal | 134 | 100 | 132 | 1000 | Sikalbaha | 129 | 2000 | 125 | 1500
Matuail | 134 | 600 | 130 | 1000 | Dohazari | 128 | 1400 | 122 | 1500
Ghorasal | 135 | 100 | 135 | 200 | Cox'sbazar | 123 | 600 | 117 | 1400
Narsinghdi | 131 | 400 | 127 | 2100 | Chandraghona | 131 | 500 | 126 | 1500
Haripur (SBU) | 135 | 100 | 132 | 1600 | Kaptai | 130 | 1400 | 128 | 1000
Ullon | 134 | 500 | 123 | 1300 | A. Khaer Stl. | 127 | 100 | 123 | 1500
Hasnabad | 137 | 2100 | 132 | 1100 | Bakulia | 127 | 1800 | 124 | 900
Magbazar | 136 | 500 | 130 | 1100 | Julda | 130 | 600 | 125 | 1500
Maniknagar | 136 | 500 | 132 | 1100 | TK Chemical | 132 | 100 | 127 | 1500
Bangabhaban | 136 | 500 | 132 | 1100 | Modern Steel | 129 | 100 | 127 | 1500
Narinda | 136 | 500 | 132 | 1100 | Shahmirpur | 129 | 300 | 124 | 900
Dhanmondi | 134 | 500 | 123 | 1300 | Khagrachhari | 130 | 400 | 126 | 1500
Lalbag | 135 | 2100 | 129 | 900 | Goalpara | 137 | 1400 | 131 | 200
Madartek | 135 | 500 | 130 | 1300 | Central s/s | 138 | 1700 | 131 | 200
Mirpur | 136 | 1300 | 131 | 1600 | Noapara | 135 | 1400 | 129 | 100
Kalyanpur | 134 | 1830 | 132 | 900 | Jessore | 133 | 1800 | 124 | 100
Gulshan | 134 | 400 | 129 | 1600 | Jhenida | 132 | 700 | 118 | 2100
Uttara | 132 | 600 | 124 | 1100 | Bottail | 137 | 1400 | 128 | 2100
Kamrangirchar | 136 | 2000 | 130 | 900 | G.K.Project | 142 | 1800 | 135 | 2000
Savar | 133 | 400 | 129 | 900 | Faridpur | 133 | 2300 | 125 | 100
Bhasantec | 133 | 600 | 129 | 1100 | Madaripur | 135 | 1830 | 126 | 100
Agargaon | 133 | 300 | 130 | 1100 | Gopalganj | 136 | 2200 | 124 | 100
Satmosjid | 133 | 600 | 130 | 900 | Bagerhat | 135 | 1400 | 128 | 100
Tongi | 135 | 100 | 128 | 1500 | Mongla | 134 | 600 | 126 | 1200
Kabirpur | 134 | 600 | 123 | 2100 | Satkhira | 136 | 1400 | 129 | 100
Basundhara | 131 | 400 | 120 | 1000 | Gallamari | 137 | 1400 | 130 | 300
Manikganj | 139 | 600 | 132 | 2100 | Magura | 131 | 700 | 115 | 2100
Joydevpur | 138 | 700 | 132 | 1500 | Chuadanga | 127 | 700 | 110 | 2100
New Tongi | 135 | 400 | 126 | 1700 | Barisal | 139 | 2200 | 134 | 100
Kodda | 136 | 1300 | 132 | 900 | Patuakhali | 135 | 500 | 130 | 100
Dhamrai | 131 | 2400 | 128 | 2100 | Bhandaria | 135 | 600 | 129 | 200
Tangail | 135 | 500 | 125 | 2200 | Ishurdi | 142 | 1800 | 135 | 2000
Mymensing | 132 | 1700 | 119 | 2100 | Ruppur Paromanobik | 141 | 1800 | 133 | 2100
Kishorganj | 128 | 1100 | 122 | 100 | Natore | 139 | 1800 | 128 | 2100
Netrokona | 130 | 700 | 118 | 2000 | Bogra | 135 | 600 | 122 | 2100
Jamalpur | 134 | 900 | 125 | 600 | Noagaon | 130 | 1800 | 119 | 2100
Sherpur | 136 | 1000 | 126 | 2100 | Rajshahi | 138 | 1700 | 127 | 2100
Srimongal | 138 | 1000 | 134 | 2100 | C.Nawabganj | 135 | 1800 | 127 | 2100
Shahjibazar | 136 | 1000 | 132 | 1900 | Amnura | 138 | 1600 | 128 | 1300
Fenchuganj | 135 | 100 | 133 | 1900 | Pabna | 135 | 700 | 125 | 2100
Khulawara | 135 | 500 | 133 | 1930 | Shahjadpur | 142 | 1800 | 137 | 1200
Sylhet | 135 | 500 | 131 | 1900 | Serajganj | 135 | 1800 | 125 | 2100
Chatak | 135 | 700 | 130 | 1900 | Niyamatpur | 129 | 1700 | 114 | 2100
Sunamganj | 134 | 500 | 132 | 100 | Joypurhat | 131 | 1800 | 115 | 2000
Biani Bazar | 135 | 600 | 129 | 1900 | Rangpur | 126 | 600 | 105 | 2100
Comilla(s) | 128 | 1200 | 121 | 1830 | Lalmonirhat | 122 | 600 | 95 | 2100
Comilla(n) | 136 | 700 | 124 | 1500 | Saidpur | 123 | 700 | 108 | 100
Chandpur | 125 | 700 | 124 | 2200 | Purbasadipur | 130 | 1800 | 116 | 2100
Feni | 125 | 1100 | 115 | 2400 | Thakurgaon | 128 | 600 | 108 | 2100
Chowmuhani | 123 | 700 | 114 | 2400 | Palashbari | 128 | 600 | 109 | 2100
Ashuganj | 136 | 1300 | 134 | 1900 | Barapukuria | 134 | 600 | 125 | 2100
Daudkandi | 135 | 1930 | 128 | 1100 | Panchagar | 123 | 600 | 102 | 2100
Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
Network Operation Division | [5 empty] | Network Operation Division
Page 7 of 7

## L-Curve
Date | 2018-06-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 680 | 7383 | 2451 | 9834 |  |  |  | QF-LDC-12
0:30 | 710 | 7285 | 2335 | 9620 | Date: | 2018-06-28
1:00 | 740 | 7187 | 2219 | 9406
1:30 | 720 | 7043.5 | 2200 | 9243.5
2:00 | 700 | 6900 | 2181 | 9081
2:30 | 670 | 6674.5 | 2094.5 | 8769 | [5 empty] | Gen. at Eve. Peak | 10359 | 10359 MW (21:00 )
3:00 | 640 | 6449 | 2008 | 8457 | [6 empty] | 21:00
3:30 | 580 | 6380 | 1978 | 8358 | [5 empty] | Gen. at Day Peak | 8287.9 | 8287.9 MW (12:00 )
4:00 | 520 | 6311 | 1948 | 8259 | [6 empty] | 12:00
4:30 | 450 | 6047 | 1917.5 | 7964.5 | [5 empty] | Highest Generation | 10359
5:00 | 380 | 5783 | 1887 | 7670 | [6 empty] | 21:00
5:30 | 360 | 5492.5 | 1805 | 7297.5
6:00 | 340 | 5202 | 1723 | 6925
6:30 | 340 | 5148.2 | 1711 | 6859.2
7:00 | 340 | 5094.4 | 1699 | 6793.4
7:30 | 340 | 5290.65 | 1715.5 | 7006.15
8:00 | 340 | 5486.9 | 1732 | 7218.9
8:30 | 350 | 5725.85 | 1755.5 | 7481.35
9:00 | 360 | 5964.8 | 1779 | 7743.8
9:30 | 400 | 6178.9 | 1754 | 7932.9
10:00 | 440 | 6393 | 1729 | 8122
10:30 | 450 | 6418.75 | 1765.5 | 8184.25
11:00 | 460 | 6444.5 | 1802 | 8246.5
11:30 | 500 | 6497.7 | 1769.5 | 8267.2
12:00 | 540 | 6550.9 | 1737 | 8287.9
12:30 | 530 | 6664.2 | 1790 | 8454.2
13:00 | 520 | 6777.5 | 1843 | 8620.5
13:30 | 490 | 6742.9 | 1893 | 8635.9
14:00 | 460 | 6708.3 | 1943 | 8651.3
14:30 | 450 | 6790.2 | 1954 | 8744.2
15:00 | 440 | 6872.1 | 1965 | 8837.1
15:30 | 390 | 6752.65 | 1976 | 8728.65
16:00 | 340 | 6633.2 | 1987 | 8620.2
16:30 | 310 | 6458.85 | 2007.5 | 8466.35
17:00 | 280 | 6284.5 | 2028 | 8312.5
17:30 | 260 | 6132.35 | 1983 | 8115.35
18:00 | 240 | 5980.2 | 1938 | 7918.2
18:30 | 310 | 6284.6 | 2141 | 8425.6
19:00 | 380 | 6589 | 2344 | 8933
19:30 | 580 | 7315 | 2551 | 9866
20:00 | 700 | 7425 | 2553 | 9978 |  |  |  | Executive Engineer
20:30 | 760 | 7551.5 | 2617 | 10168.5 |  |  |  | Network Operation Division
21:00 | 820 | 7678 | 2681 | 10359
21:30 | 790 | 7663 | 2665.5 | 10328.5
22:00 | 760 | 7648 | 2650 | 10298 |  |  |  |  | Page 6 of 7
22:30 | 670 | 7435 | 2554.5 | 9989.5
23:00 | 580 | 7222 | 2459 | 9681
23:30 | 630 | 7302.5 | 2455 | 9757.5
24:00 | 680 | 7383 | 2451 | 9834
10359 MW (21:00 )
8287.9 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2018-06-28 |  | Energy | 208300881 | [5 empty] | 1
[11 empty] | 2018-06-28 | [5 empty] | QF-LDC-11
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA
0:00 | 3483 | 473 | 2030 | 2106 | 119 | 168 | 1293 | 0 | 162
0:30 | 3672 | 468.5 | 2002.5 | 1836.5 | 158.5 | 164.5 | 1160.5 | 0 | 157 |  | Date: | 2018-06-28
1:00 | 3861 | 464 | 1975 | 1567 | 198 | 161 | 1028 | 0 | 152
1:30 | 3836.5 | 464.5 | 1985.5 | 1459 | 197 | 161 | 990 | 0 | 150 | [8 empty] | Total Energy | 208.3009 | Total Energy Gen 208.301 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 208.301 MKWHr
2:00 | 3812 | 465 | 1996 | 1351 | 196 | 161 | 952 | 0 | 148 | [8 empty] | Energy not Served | 0
2:30 | 3766 | 465 | 1996 | 1126 | 196.5 | 161 | 914.5 | 0 | 144 | [8 empty] | Energy Requirement | 208.3009
3:00 | 3720 | 465 | 1996 | 901 | 197 | 161 | 877 | 0 | 140
3:30 | 3707.5 | 465 | 2009.5 | 869.5 | 198 | 161 | 809.5 | 0 | 138 | [7 empty] | Shortage
4:00 | 3695 | 465 | 2023 | 838 | 199 | 161 | 742 | 0 | 136
4:30 | 3692.5 | 464.5 | 1867 | 747.5 | 198.5 | 161 | 701.5 | 0 | 132
5:00 | 3690 | 464 | 1711 | 657 | 198 | 161 | 661 | 0 | 128
5:30 | 3527 | 464.5 | 1589.5 | 606 | 198 | 161.5 | 630 | 0 | 121
6:00 | 3364 | 465 | 1468 | 555 | 198 | 162 | 599 | 0 | 114
6:30 | 3340 | 465 | 1457 | 540 | 192.5 | 160.5 | 598 | 0 | 106 | [5 empty] | Coal
7:00 | 3316 | 465 | 1446 | 525 | 187 | 159 | 597 | 0 | 98
7:30 | 3420 | 466.5 | 1465.5 | 558 | 189.5 | 161 | 641 | 0 | 104 |  |  |  |  | Oil |  |  |  | ,
8:00 | 3524 | 468 | 1485 | 591 | 192 | 163 | 685 | 0 | 110
8:30 | 3554 | 468.5 | 1590 | 687 | 192 | 163.5 | 712 | 0 | 113
9:00 | 3584 | 469 | 1695 | 783 | 192 | 164 | 739 | 0 | 116
9:30 | 3551 | 470.5 | 1761 | 945 | 192.5 | 160.5 | 733.5 | 0 | 117
10:00 | 3518 | 472 | 1827 | 1107 | 193 | 157 | 728 | 0 | 118
10:30 | 3498.5 | 472 | 1778 | 1217 | 191 | 157 | 749.5 | 0 | 119
11:00 | 3479 | 472 | 1729 | 1327 | 189 | 157 | 771 | 0 | 120
11:30 | 3368 | 472.5 | 1755 | 1407.5 | 186.5 | 162.5 | 788.5 | 0 | 124
12:00 | 3257 | 473 | 1781 | 1488 | 184 | 168 | 806 | 0 | 128
12:30 | 3350 | 473 | 1789 | 1560.5 | 187.5 | 168 | 795 | 0 | 129
13:00 | 3443 | 473 | 1797 | 1633 | 191 | 168 | 784 | 0 | 130
13:30 | 3443 | 473 | 1797 | 1633 | 191 | 168 | 784 | 0 | 130
14:00 | 3443 | 473 | 1797 | 1633 | 191 | 168 | 784 | 0 | 130
14:30 | 3464.5 | 474 | 1755.5 | 1779.5 | 188 | 159 | 770.5 | 0 | 136
15:00 | 3486 | 475 | 1714 | 1926 | 185 | 150 | 757 | 0 | 142
15:30 | 3545 | 475 | 1654.5 | 1845 | 183 | 150 | 737 | 0 | 138
16:00 | 3604 | 475 | 1595 | 1764 | 181 | 150 | 717 | 0 | 134
16:30 | 3465 | 475 | 1601.5 | 1745 | 182 | 150 | 713.5 | 0 | 134
17:00 | 3326 | 475 | 1608 | 1726 | 183 | 150 | 710 | 0 | 134
17:30 | 3332 | 474 | 1496 | 1600 | 199.5 | 159 | 725.5 | 0 | 129
18:00 | 3338 | 473 | 1384 | 1474 | 216 | 168 | 741 | 0 | 124
18:30 | 3433.5 | 473 | 1450 | 1623 | 221.5 | 168 | 918.5 | 0 | 138
19:00 | 3529 | 473 | 1516 | 1772 | 227 | 168 | 1096 | 0 | 152
19:30 | 3441 | 473 | 1897 | 2255 | 225 | 168 | 1241 | 0 | 166
20:00 | 3532 | 473 | 1921 | 2248 | 223 | 168 | 1247 | 0 | 166
20:30 | 3495 | 473 | 1969 | 2396 | 221 | 168 | 1279.5 | 0 | 167
21:00 | 3458 | 473 | 2017 | 2544 | 219 | 168 | 1312 | 0 | 168
21:30 | 3442 | 473.5 | 1997 | 2574.5 | 209.5 | 168 | 1297 | 0 | 167
22:00 | 3426 | 474 | 1977 | 2605 | 200 | 168 | 1282 | 0 | 166
22:30 | 3491 | 474 | 1940.5 | 2296 | 191.5 | 168 | 1262.5 | 0 | 166
23:00 | 3556 | 474 | 1904 | 1987 | 183 | 168 | 1243 | 0 | 166
23:30 | 3519.5 | 473.5 | 1967 | 2046.5 | 151 | 168 | 1268 | 0 | 164 |  | Max Temp. in Dhaka |  | 33.8° C
24:00 | 3483 | 473 | 2030 | 2106 | 119 | 168 | 1293 | 0 | 162
Executive Engineer
Network Operation Division
Page 5 of 7
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 208.301 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 208.301 MKWHr
Note on W13: Author:

## Generation
,. | 2018-06-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Kaptai Unit-1, 2 & 3 | 81 | 81 | 81 | 81 | 81 | 82 | 79 | 83 | 84 | 77 | 77 | 88 | 88 | 75 | 70 | 70 | 70 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1947215
2 | Kaptai Unit-4 & 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1890400
3 | Chittagong ST-1 (Raozan)
4 | Chittgong ST-2 (Raozan)
5 | Raozan 25 MW (RPCL) | 16 | 16 | 16 | 16 | 0 |  |  |  | 0 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 301680
6 | Sikalbaha 225MW (Gas)
7 | Sikalbaha 225MW (Oil) | 204 | 198 | 202 | 199 | 196 | 177 | 188 | 189 | 203 | 204 | 203 | 201 | 202 | 195 | 195 | 205 | 195 | 194 |  | 215 | 194 | 199 | 197 | 196 | 221 | 204 | 4685741
8 | Sikalbaha ST 60MW
9 | Sikalbaha GT 150MW (Gas)
10 | Sikalbaha GT 150MW (Oil) | 50 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 100 | 100 | 135 | 120 | 80 | 135 | 60 | 60 | 60 |  | 60 | 125 | 135 | 135 | 135 | 110 | 135 | 2030318
| Dohazari Peaking | 79 | 79 | 77 | 46 | 45 | 23 | 15 | 15 | 15 | 15 | 0 | [15 empty] | 444033
12 | Hathazari peaking | 65 | 65 | 65 | 16 | 16 | 16 | 16 | 16 | 16 | 9 | 0 | [8 empty] | 59 | 64 | 64 | 64 | 64 | 64 | 64 | 672744
| Daudkandi bangla trak | [19 empty] | 50 | 80 | 80 | 120 | 120 | 0 | 0 | 330240
14 | Daudkandi Peaking 52MW | [19 empty] | 16 | 20 | [5 empty] | 16256
15 | Siddhirgonj ST 210MW
16 | Siddhirgonj GT Unit-1& 2 | 99 | 101 | 100 | 102 | 100 | 100 | 99 | 100 | 101 | 101 | 103 | 99 | 100 | 99 | 99 | 97 | 0 | [9 empty] | 1685000
17 | Siddhirganj CCPP-335 MW | 170 | 170 | 165 | 165 | 160 | 120 | 120 | 120 | 160 | 175 | 165 | 160 | 170 | 175 | 180 | 180 | 180 | 171 |  | 170 | 170 | 170 | 170 | 160 | 160 | 160 | 4017474
18 | Summit Gazipur | 220 | 195 | 47 | 47 | 47 | 47 | 47 | 50 | 54 | 156 | 193 | 201 | 249 | 285 | 301 | 303 | 303 | 303 |  | 301 | 301 | 301 | 303 | 303 | 301 | 301 | 4937889
19 | Ashuganj 195MW Modular | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 77 | 78 | 78 | 78 | 78 | 84 | 78 | 78 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1923636
20 | Ghorasal ST: Unit-1,2 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 853000
21 | Ghorasal ST: Unit-3 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2868390
22 | Ghorasal ST: Unit-4
23 | Ghorasal ST: Unit-5
24
25 | Ghorasal ST: Unit-7 | 300 | 300 | 300 | 300 | 300 | 250 | 250 | 300 | 365 | 365 | 320 | 363 | 365 | 365 | 365 | 365 | 365 | 365 |  | 320 | 350 | 350 | 350 | 350 | 349 | 350 | 7878272
26
28 | Ashuganj ST: Unit- 3
29 | Ashuganj ST: Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 150 | 145 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2473750
30 | Ashuganj ST: Unit- 5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 10 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2394302
32 | Ashuganj Engines TSK | 38 | 38 | 38 | 35 | 35 | 10 | 10 | 36 | 39 | 39 | 39 | 39 | 39 | 37 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 833400
33 | Ashuganj CCPP 225 MW | 205 | 203 | 206 | 195 | 200 | 170 | 173 | 201 | 193 | 184 | 182 | 157 | 145 | 166 | 175 | 186 | 180 | 196 |  | 214 | 173 | 196 | 164 | 183 | 179 | 158 | 4427000
34 | Ashuganj CCPP(South) | 335 | 330 | 335 | 320 | 325 | 270 | 287 | 335 | 310 | 300 | 300 | 265 | 270 | 272 | 270 | 305 | 272 | 272 |  | 342 | 301 | 323 | 305 | 301 | 345 | 327 | 7385250
| Ashuganj CCPP(North) | 335 | 329 | 335 | 325 | 330 | 280 | 295 | 335 | 310 | 300 | 360 | 368 | 374 | 300 | 300 | 335 | 300 | 301 |  | 354 | 300 | 325 | 305 | 300 | 344 | 322 | 7947400
35 | Ashuganj (Precision) 55MW
36 | Chandpur CCPP | 100 | 100 | 100 | 100 | 100 | 100 | 30 | 30 | 30 | 30 | 30 | 30 | 32 | 90 | 90 | 90 | 0 | 50 |  | 75 | 100 | 100 | 101 | 100 | 100 | 100 | 1627200
37 | Tongi GT
38 | Haripur GT: Unit-1, 2
39 | Haripur 412 MW CCPP | 365 | 360 | 365 | 358 | 350 | 350 | 362 | 370 | 365 | 372 | 390 | 390 | 385 | 350 | 350 | 350 | 355 | 345 |  | 348 | 366 | 365 | 365 | 365 | 364 | 368 | 8747010
40 | Meghnaghat CCPP 450MW | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 430 | 400 | 420 | 420 | 330 | 400 | 400 | 400 | 350 |  | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 9335162
41 | Haripur Power CCPP 360MW | 258 | 271 | 271 | 291 | 301 | 290 | 261 | 250 | 233 | 213 | 193 | 151 | 143 | 143 | 143 | 133 | 133 | 251 |  | 273 | 271 | 271 | 271 | 271 | 271 | 280 | 5508000
42 | Mymensingh RPCL 210MW | 86 | 86 | 85 | 98 | 100 | 100 | 97 | 84 | 76 | 60 | 60 | 61 | 60 | 47 | 46 | 46 | 47 | 47 |  | 45 | 47 | 48 | 47 | 48 | 47 | 47 | 1609880
43 | Haripur NEPC 110MW | [17 empty] | 0 |  | 13 | 26 | 0 |  |  |  |  | 16000
44 | Fenchugonj CCPP-1 | 53 | 58 | 54 | 58 | 58 | 54 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 59 | 59 | 59 | 59 |  | 60 | 60 | 60 | 60 | 54 | 55 | 55 | 1330000
45 | Fenchugonj CCPP-2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 59 | 59 | 60 | 62 |  | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 1448800
46 | Shajibazar 330 MW | 269 | 224 | 142 | 172 | 172 | 157 | 152 | 173 | 168 | 190 | 190 | 190 | 190 | 190 | 191 | 213 | 190 | 188 |  | 214 | 190 | 204 | 196 | 189 | 219 | 200 | 4468467
47 | Shahjibazar GT: Unit- 8, 9 | 50 | 51 | 50 | 51 | 51 | 51 | 50 | 50 | 62 | 62 | 59 | 54 | 51 | 58 | 50 | 59 | 55 | 47 |  | 59 | 61 | 60 | 61 | 48 | 60 | 61 | 1317000
48 | Shahjibazar 86MW | 86 | 86 | 86 | 86 | 50 | 5 | 1 | 20 | 20 | 84 | 84 | 85 | 85 | 85 | 85 | 10 | 10 | 10 |  | 10 | 86 | 86 | 86 | 86 | 86 | 86 | 1504320
49 | Shahjibazar (EPL) 50MW | 47 | 47 | 47 | 47 | 2 | 2 | 2 | 2 | 47 | 47 | 46 | 45 | 46 | 46 | 45 | 45 | 45 | 10 |  | 10 | 10 | 46 | 47 | 47 | 47 | 47 | 869760
50 | Sylhet GT 150 MW | 79 | 79 | 80 | 79 | 79 | 79 | 80 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 79 |  | 80 | 79 | 78 | 78 | 77 | 78 | 78 | 1928900
51 | Sylhet GT 20 MW
52 | Sylhet (EPL) 50MW | 45 | 45 | 45 | 45 | 45 | 3 | 3 | 44 | 44 | 44 | 43 | 43 | 44 | 43 | 43 | 44 | 42 | 12 |  | 12 | 44 | 44 | 44 | 44 | 44 | 44 | 914080
53 | Sylhet (Desh) 10MW | 10 | 10 | 10 | 10 | 10 | 10 | 0 | [6 empty] | 10 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 175860
54 | Hobiganj 11MW | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 |  | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 219552
55 | Fenchugonj (Barakatullah) 51MW | 53 | 53 | 53 | 53 | 9 | 5 | 5 | 5 | 47 | 44 | 46 | 47 | 47 | 50 | 50 | 52 | 53 | 11 |  | 11 | 50 | 50 | 50 | 50 | 50 | 50 | 969000
56 | Shahjahanulla 25 MW | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 | 21 | 23 | 22 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 537768
57 | Summit Bibiana- 2 | 320 | 320 | 310 | 320 | 310 | 300 | 320 | 320 | 330 | 300 | 270 | 280 | 270 | 260 | 280 | 290 | 285 | 275 |  | 260 | 300 | 270 | 320 | 285 | 270 | 330 | 7663320
58 | Southern 55MW | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 880000
59 | Sikalbaha (Energis) | 36 | 34 | 40 | 40 | 40 | 8 | 8 | 8 | 29 | 42 | 0 | 14 | 29 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 829920
60 | Barabkunda (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 0 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 370464
61 | Narshingdi (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 431568
62 | Tangail (Doreen) 22MW | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 410616
63 | Tripura | 152 | 148 | 140 | 136 | 128 | 114 | 98 | 110 | 116 | 118 | 120 | 128 | 130 | 130 | 142 | 134 | 134 | 124 |  | 152 | 166 | 166 | 168 | 166 | 166 | 162 | 3292800
64 | Malancha, Ctg. EPZ (United) | 30 | 38 | 41 | 40 | 42 | 42 | 32 | 12 | 7 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 6 |  | 8 | 10 | 15 | 23 | 27 | 24 | 29 | 430080
65 | Feni (Doreen) 22MW | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 445680
66 | Feni, Mohipal (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 11 | 11 | 11 | 11 | 0 | 0 | 0 | 0 | 11 | 11 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 197100
67 | Jangalia (Summit) 33MW | 33 | 33 | 33 | 8 | 8 | 8 | 8 | 8 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 692400
68 | Summit Comilla 25MW | 15 | 15 | 15 | 15 | 15 | 15 | 13 | 13 | 13 | 13 | 14 | 14 | 17 | 21 | 21 | 21 | 15 | 15 |  | 15 | 15 | 15 | 18 | 18 | 20 | 20 | 404280
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 23 | 32 | 30 | 30 | 30 | 31 |  | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 723420
71 | Summit Maona | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 822600
72 | Summit Rupganj | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 835300
73 | Ghorashal (Regent) | 87 | 87 | 87 | 86 | 32 | 26 | 27 | 27 | 82 | 87 | 87 | 87 | 88 | 88 | 87 | 87 | 74 | 74 |  | 74 | 88 | 88 | 88 | 88 | 89 | 89 | 1831636
76 | Siddhirganj (Desh) | [19 empty] | 5 | 12 | 0 |  |  |  |  | 24000
77 | Siddhirganj (Dutch Bangla) | 50 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 10 | 50 | 70 | 82 | 40 | 7 | 7 |  | 7 | 40 | 60 | 89 | 91 | 15 | 30 | 879360
78 | Gazipur (RPCL) | 42 | 25 | 25 | 25 | 8 | 8 | 8 | 19 | 42 | 33 | 33 | 42 | 47 | 50 | 50 | 45 | 50 | 41 |  | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 930384
79 | Kodda 150MW | 120 | 72 | 64 | 42 | 16 | 16 | 16 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 |  | 110 | 149 | 149 | 149 | 149 | 149 | 149 | 2321280
80 | Jamalpur 95MW | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 40 | 89 | 91 | 95 | 95 | 95 | 95 | 665380
81 | Lakdhanvi 52 MW | [19 empty] | 1 | 8 | 8 | 14 | 25 | 8 | 15 | 89054
82 | Madanganj 102MW | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 14 | 15 | 15 | 38 | 48 | 48 | 73 | 90 | 48 | 48 | 15 |  | 15 | 30 | 36 | 52 | 100 | 50 | 50 | 980136
83 | Pagla (DPA ) | [6 empty] | 0 | 10 | 10 | 11 | 10 | 11 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 51 | 31 | 11 | 51 | 246100
84 | B.Baria (Aggreko) 85MW | 85 | 85 | 85 | 85 | 51 | 20 | 3 | 21 | 21 | 85 | 85 | 85 | 85 | 85 | 85 | 41 | 11 | 10 |  | 40 | 85 | 85 | 86 | 85 | 41 | 86 | 1478621
85 | Keraniganj (Powerpac) 100MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 50 | 70 | 100 | 100 | 100 | 50 | 10 | 10 |  | 50 | 100 | 100 | 100 | 100 | 20 | 50 | 1108697
86 | Meghnaghat CCPP(Summit) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 130 | 100 | 100 | 140 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 145 | 100 | 100 | 145 | 2818880
87 | Meghnaghat (IEL) | 60 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 11 | 58 | 90 | 91 | 65 | 40 | 15 |  | 10 | 85 | 65 | 92 | 98 | 45 | 20 | 913920
88 | Ghorashal 78MW (MAX) | 74 | 74 | 74 | 74 | 50 | 20 | 20 | 20 | 30 | 30 | 35 | 74 | 73 | 50 | 50 | 50 | 50 | 60 |  | 75 | 75 | 75 | 76 | 70 | 70 | 70 | 1442560
90 | Ashuganj (United) 53MW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 180000
91 | Juldah (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1849560
92 | Fenchuganj (EPL) 44MW | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 38 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 10 |  | 13 | 50 | 50 | 50 | 50 | 50 | 50 | 931000
93 | Ashuganj (Midland) 51MW | 51 | 51 | 51 | 51 | 20 | 5 | 5 | 5 | 8 | 20 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 12 |  | 12 | 12 | 20 | 51 | 51 | 51 | 51 | 870109
94 | Gagnagar (Orion) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 15 | 32 | 32 | 32 | 32 | 15 |  | 15 | 48 | 48 | 64 | 102 | 60 | 60 | 664848
95 | Patenga 50MW | 44 | 44 | 45 | 45 | 44 | 38 | 24 | 24 | 25 | 33 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 45 |  | 44 | 44 | 44 | 45 | 44 | 44 | 44 | 960000
96 | Chittagong ECPV 108 MW | 105 | 105 | 105 | 75 | 38 | 12 | 12 | 12 | 12 | 0 | 92 | 99 | 98 | 98 | 98 | 98 | 98 | 98 |  | 98 | 98 | 98 | 98 | 98 | 99 | 99 | 1847040
97 | Katpotti 51 MW | 40 | 39 | 12 | 12 | 12 | 12 | 12 | 12 | 17 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 12 |  | 12 | 39 | 38 | 39 | 39 | 39 | 39 | 765360
98 | Bosila 108MW | 90 | 90 | 24 | 19 | 8 | 8 | 8 | 8 | 47 | 69 | 75 | 75 | 74 | 75 | 75 | 75 | 75 | 40 |  | 57 | 75 | 75 | 75 | 75 | 74 | 74 | 1320000
99 | Madanganj-55 MW | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 48 | 55 | 55 | 55 | 55 | 55 | 55 | 30 |  | 30 | 30 | 49 | 55 | 55 | 55 | 55 | 908477
100 | Northern 55 MW | 55 | 18 | 18 | 18 | 18 | 18 | 0 | 18 | 18 | 54 | 55 | 55 | 55 | 56 | 55 | 56 | 55 | 56 |  | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 992894
101 | Kushiara 163 MW CCPP GT | 140 | 140 | 140 | 140 | 140 | 140 | 163 | 163 | 163 | 163 | 100 | 130 | 163 | 130 | 100 | 100 | 163 | 100 |  | 100 | 163 | 163 | 163 | 163 | 163 | 163 | 3432436
102 | Sarishabari (Solar) | [6 empty] | 0.4 | 0.9 | 1.8 | 2 | 2.5 | 2.9 | 1.5 | 1.3 | 2.1 | 0.2 | 0.5 | 0.2 |  | 0 | [6 empty] | 13497
103 | Banco Energy 54MW | 54 | 54 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1013040
104 | APR Energy , Keranigonj
105 | Bramhangoan 100 MW (Aggreko)
106 | United Mymensingh PPL | 197 | 197 | 151 | 151 | 52 | 52 | 52 | 52 | 100 | 120 | 120 | 150 | 150 | 150 | 150 | 150 | 166 | 171 |  | 184 | 184 | 174 | 174 | 174 | 173 | 173 | 3374400
112 | Aggreko Aurahati 100MW | [21 empty] | 32 | 32 | 31 | 0 |  | 84110
113
114
115
116
117
118 | Eastern Zone Total | 7187 | 6900 | 6449 | 6311 | 5783 | 5202 | 5094.4 | 5486.9 | 5964.8 | 6393 | 6444.5 | 6550.9 | 6777.5 | 6708.3 | 6872.1 | 6633.2 | 6284.5 | 5980.2 |  | 6589 | 7315 | 7425 | 7678 | 7648 | 7222 | 7383 | 158436476
120
121
122 | Khulna 60MW
123 | Khulna (KPCL-1 & 3) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 19 | 63 | 69 | 64 | 81 | 87 | 80 | 73 | 22 |  | 29 | 73 | 76 | 64 | 83 | 75 | 75 | 1052160
124 | Khulna (KPCL-2) | 66 | 55 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 27 | 33 | 16 | 16 | 49 | 49 | 49 | 108 | 115 |  | 115 | 115 | 115 | 104 | 115 | 115 | 115 | 1343040
125
126 | Khulna (Aggreko) 55MW | [20 empty] | 35 | 23 | 53 | 54 |  |  | 119690
127 | Faridpur Peaking | 48 | 27 | 0 | [14 empty] | 14 |  | 49 | 50 | 50 | 49 | 49 | 49 | 49 | 363360
128 | Khulna CCPP 225MW | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 155 | 170 | 170 | 170 | 170 | 170 | 200 | 3268800
129
130
131
132
133
| Summit Barisal 110 MW | 27 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 28 | 32 | 32 | 48 | 48 | 48 | 64 | 64 |  | 64 | 64 | 64 | 96 | 96 | 96 | 96 | 1009920
Barisal GT: Unit-1, 2
136 | Bhola Aggreko 95MW | 73 | 72 | 73 | 73 | 72 | 32 | 32 | 32 | 64 | 90 | 95 | 94 | 97 | 97 | 97 | 95 | 97 | 52 |  | 63 | 93 | 96 | 97 | 97 | 97 | 98 | 1899625
137 | Bhola CCPP 194MW | 183 | 194 | 193 | 192 | 191 | 194 | 192 | 192 | 190 | 191 | 192 | 189 | 167 | 178 | 186 | 190 | 188 | 175 |  | 191 | 187 | 192 | 193 | 187 | 191 | 193 | 4677125
| Bhola (Venture) 33MW | 17 | 18 | 24 | 23 | 23 | 18 | 18 | 10 | 11 | 18 | 24 | 17 | 18 | 19 | 20 | 18 | 18 | 18 |  | 31 | 33 | 35 | 38 | 37 | 25 | 31 | 498424
140 | Bangla Trak Noapara | 0 | [18 empty] | 10 | 51 | 50 | 79 | 81 |  |  | 224640
141 | Noapara (KZA) 40MW | 40 | 40 | 0 | [6 empty] | 33 | 25 | 40 | 40 | 40 | 40 | 40 | 40 | 16 |  | 40 | 40 | 40 | 33 | 16 | 33 | 40 | 557625
142 | Gopalganj Peaking | 9 | 8 | 0 | [14 empty] | 18 |  | 20 | 22 | 37 | 60 | 50 | 45 | 45 | 279680
143 | Bheramara GT-1,2,3
144
145 | Bheramara HVDC | 464 | 465 | 465 | 465 | 464 | 465 | 465 | 468 | 469 | 472 | 472 | 473 | 473 | 468 | 475 | 475 | 475 | 473 |  | 473 | 473 | 473 | 473 | 474 | 474 | 473 | 11306364
146 | Bheramara 360 MW | 345 | 340 | 326 | 326 | 320 | 260 | 250 | 250 | 235 | 120 | 65 | 3 | 130 | 165 | 167 | 167 | 167 | 167 |  | 168 | 168 | 168 | 167 | 167 | 166 | 165 | 5028192
147
148
149 | Barapukuria Unit-1
150 | Barapukuria Unit-2 | 72 | 70 | 71 | 73 | 72 | 72 | 66 | 71 | 71 | 72 | 71 | 70 | 70 | 67 | 67 | 64 | 64 | 64 |  | 67 | 65 | 65 | 60 | 65 | 63 |  | 1585745
151 | Barapukuria Unit-3 | 126 | 126 | 126 | 126 | 126 | 126 | 121 | 121 | 121 | 121 | 118 | 114 | 121 | 119 | 118 | 117 | 119 | 152 |  | 160 | 160 | 158 | 159 | 135 | 120 | 119 | 3142200
152 | Baghabari GT 71MW
153 | Baghabari GT 100MW
156 | Baghabari Peaking 50MW | [19 empty] | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 315232
| Sirajgonj Unit-1 225MW (Gas) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 138 | 138 | 138 | 138 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 3563609
157 | Sirajgonj Unit-1 225MW (Oil) | [7 empty] | 0
158 | Sirajgonj Unit-2 225MW (Gas)
| Sirajgonj Unit-2 225MW (Oil) | 183 | 184 | 184 | 184 | 178 | 157 | 157 | 162 | 172 | 148 | 217 | 219 | 211 | 208 | 176 | 175 | 178 | 168 |  | 171 | 187 | 178 | 189 | 169 | 179 | 190 | 4297845
Sirajgonj Unit-3 225 MW(Gas)
159 | Sirajgonj Unit-3 225 MW(Oil)
160 | Bera Peaking | [17 empty] | 10 |  | 38 | 38 | 38 | 37 | 37 | 37 | 37 | 149806
161 | Bogra (GBB) | 22 | 22 | 22 | 22 | 22 | 18 | 22 | 22 | 22 | 22 | 20 | 22 | 22 | 22 | 22 | 22 | 18 | 18 |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 486480
162 | Bogra (EPL) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 261000
163 | Ullapara (Summit) | 10 | 10 | 10 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 230112
164 | Amnura 50MW | 40 | 40 | 40 | 12 | 12 | 12 | 12 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 12 | 12 |  | 35 | 40 | 33 | 33 | 40 | 40 | 40 | 796610
165 | Katakhali (Northern) | 43 | 43 | 43 | 43 | 43 | 5 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 43 | 43 | 43 | 16 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 765584
166 | Katakhali Peaking | 45 | 45 | 45 | 45 | 0 | [14 empty] | 37 | 44 | 47 | 44 | 44 | 0 |  | 385287
167 | Santahar Peaking | [19 empty] | 40 | 43 | 43 | 42 | 42 | 42 | 43 | 242110
168 | Rajlanka 52 MW | 25 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 18 | 25 | 25 | 25 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 493920
169 | Chapainawabganj-100 MW | 70 | 70 | 70 | 40 | 40 | 40 | 35 | 35 | 35 | 34 | 33 | 33 | 33 | 33 | 33 | 59 | 59 | 59 |  | 59 | 59 | 59 | 100 | 100 | 100 | 101 | 1264220
170
171
172 | Rangpur GT | 17 | 17 | 0 | [16 empty] | 15 | 15 | 17 | 16 | 16 | 16 | 16 | 122000
173 | Saidpur GT | 18 | 18 | 0 | [16 empty] | 18 | 18 | 18 | 17 | 18 | 18 | 17 | 134000
175
176
177
178 | Western Zone Total | 2219 | 2181 | 2008 | 1948 | 1887 | 1723 | 1699 | 1732 | 1779 | 1729 | 1802 | 1737 | 1843 | 1943 | 1965 | 1987 | 2028 | 1938 | 0 | 2344 | 2551 | 2553 | 2681 | 2650 | 2459 | 2451 | 49864405
177
178 | Western Zone Total | 1739 | 1733 | 1361 | 1359 | 1275 | 1200 | 1113 | 1104 | 1237 | 1525 | 1361 | 1364 | 1267 | 1221 | 1288 | 1290 | 1492 | 1587 | 0 | 2291 | 2149 | 2113 | 2138 | 2057 | 2047 | 2028 | 37879953