## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:September 2023
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2023-09-01 |  | 2023-08-01 |  | 2022-09-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 14938 | 2023-09-16 | 14889 | 2023-08-30 | 13761 | 2022-09-07 | 15648 | 2023-04-19
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 21:00
2 | Minimum Generation (MW) | 9737 | 2023-09-22 | 8071 | 2023-08-01 | 8864 | 2022-09-15 | 9737 | 2023-09-22
|  |  | 6:00 |  | 6:00 |  | 6:00 |  | 6:00
3 | Maximum Evening Peak Generation (MW) | 14938 | 2023-09-16 | 14889 | 2023-08-30 | 13712 | 2022-09-01 | 15648 | 2023-04-19
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 13849 | 2023-09-17 | 13382 | 2023-08-29 | 11999 | 2022-09-08 | 13415 | 2023-04-19
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 15370 | 2023-09-30 | 14889 | 2023-08-30 | 14695 | 2022-09-01 | 16096 | 2023-04-19
|  |  | 20:00 |  | 21:00 |  | 20:00 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 14065.4 |  | 13968.6452 |  | 13055.1 |  | - | -
7 | Average Generation (MW) at Day Peak | 12351.2667 |  | 12169.7097 |  | 11203.2667 |  | - | -
8 | Maximum Power Import from India, BIPTC (MW) | 940 | 2023-09-25 | 936 | 2023-08-29 | 919 | 2022-09-30 | 956 | 27/3/2019
|  |  | 24':30 |  | 4:30 |  | 11:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 174 | 2023-09-13 | 170 | 2023-08-05 | 184 | 2022-09-10 | 194 | 12/06/19
|  |  | 23:00 |  | 19:00 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 822 | 2023-09-05 | 634 | 2023-08-19 | 1471 | 2022-09-28 | 4395 | 04/10/2022
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 21:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 14489 | 2023-09-05 | 14036 | 2023-08-19 | 12904 | 2022-09-28 | 13200 | 04/10/2022
|  | - | 21:00 | - | 21:00 | - | 21:00 |  | 21:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | 2023-09-21 | 0 | 2023-08-28 | 0 | 2022-09-13 | - | -
|  |  | 19:30 |  | 19:30 |  | 19:00 | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | 12861 | 2023-09-21 | 13253 | 2023-08-08 | 11790 | 2022-09-13 | - | -
|  |  | 19:30 |  | 19:30 |  | 19:00 | - | -
14 | Maximum Load Shed (MW) at Day Peak | 763 | 2023-09-06 | 1042 | 2023-08-17 | 1235 | 2022-09-06 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | 12621 | 2023-09-06 | 12309 | 2023-08-17 | 10112 | 2022-09-06 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
16 | Minimum Load Shed (MW) at Day Peak | 0 | 2023-09-21 | 0 | 2023-08-08 | 0 | 2022-09-02 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | 11696 | 2023-09-21 | 10921 | 2023-08-08 | 11272 | 2022-09-02 | - | -
|  |  | 12:00 |  | 12:00 |  | 12:00 | - | -
18 | Nos. of Days Load Shed at Evening Peak | 12 |  | 26 |  | 29 |  | - | -
19 | Nos. of Days Load Shed at Day Peak | 19 |  | 22 |  | 20 |  | - | -
20 | Gross Generation of BPDB (MKWH) | 1988.9761 |  | 2157.9023 |  | 1767.5579 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 43.3331 |  | 186.3465 |  | 88.5941 |  | - | -
22 | Net Generation of BPDB (MKWH) | 1945.643 |  | 1971.5558 |  | 1678.9638 |  | - | -
23 | Net Generation of IPP (MKWH) | 5025.8758 |  | 4950.6608 |  | 5416.8526 |  | - | -
24 | Net Generation of REB (MKWH) | 114.4824 |  | 132.336 |  | 111.5457 |  | - | -
24 | Net Generation of Rental Power Plant (MKWH) | 249.813 |  | 273.6692 |  | 401.8248 |  | - | -
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7335.8142 |  | 7328.2218 |  | 7609.1868 |  | 7842.9924 | April'22
26 | Energy Generation by Gas (MKWH) | 4256.6062 |  | 4451.0325 |  | 4050.2118 |  | 4256.61 | Sep'23
27 | Energy Generation by Diesel (MKWH) | 88.1703 |  | 171.571 |  | 582.493 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1117.1117 |  | 1284.8303 |  | 1974.4688 |  | 2365.7466 | April'22
29 | Energy Generation by Hydro (MKWH) | 135.9844 |  | 128.7252 |  | 104.6574 |  | 135.98 | Sep'23
30 | Energy Generation by Solar (MKWH) | 36.0858 |  | 32.4167 |  | 34.9866 |  | 40.67 | July-23
31 | Energy Generation by Coal (MKWH) | 1044.1876 |  | 1079.4416 |  | 950.9634 |  | 1044.1876 | Sep'23
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 745.1102 |  | 758.441 |  | 744.831 |  | 776.67 | August-22
33 | Monthly Load Factor (%) | 77.424 |  | 81.9186 |  | 91.3054 |  | 92.62 | August-22

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:September 2023
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 14938 | 2023-09-16 | 21:00
Generation Period
| Dhaka | MW | 5090.74
| Chattogram | MW | 1395.3
| Cumilla | MW | 1356
| Mymensingh | MW | 1161
| Sylhet | MW | 540
a) | Total supply in East zone | MW | 9543.04
| Khulna | MW | 1841
| Barisal | MW | 463.5
| Rajshahi | MW | 1527.6
| Rangpur | MW | 906
b) | Total supply in West zone | MW | 4738.1
c) | Total supply in both zone ( a+b) | MW | 14281.14
Ref: | 27.21.0000.603.16.087.20.711 | Date: 18/10/2023
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:September 2023
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS
| b) Ishurdi end | MW | 276 | 2023-09-07 | 18:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 1140 | 2023-09-12 | 11':00
| b) Ishurdi end | MW
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 0.043627
| b) Ishurdi end | MKWH | 97.9215
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 94.9838
| b) Ishurdi end | MKWH | 0.077016
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW
| b)Serajganj end | MW | 666 | 2023-09-21 | 14:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 380 | 2023-09-22 | 16:00
| b)Sirajganj end | MW
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0
| b)Sirajganj end | MKWH | 338.808
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 334.6206
| b)Sirajganj end | MKWH | 0
30 | Transmission loss of EWI /NO-2 | % | 1.236%
31 | Maximum power Export through EWI/ NO-3
| a) Gopalganj end | AMPS | 2286 | 06.09.2023 | 12:30
|  | MW | 1516
| b) Aminbazar end | AMPS | -
|  | MW | -
32 | Maximum power Import through EWI/ NO-3
| a) Gopalganj end | AMPS | -
|  | MW | -
| b) Aminbazar end | AMPS | 2268 | 06.09.2023 | 12:30
|  | MW | 1500
33 | Daily Maximum Energy Export through EWI/NO-3
| a) Gopalganj end | MWh | 62936.96 | 06.09.2023 | N/A
| a) Aminbazar end | MWh | - | -
34 | Daily Maximum Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | - | - | N/A
| a) Aminbazar end | MWh | 62928.7
35 | Total Energy Export through EWI/ NO-3 |  |  | N/A
| a) Gopalganj end | MWh | 688876.544
| b) Aminbazar end (ckt-1 ) | MWh | -
36 | Total Energy Import through EWI/ NO-3
| a) Gopalganj end | MWh | -
| b) Aminbazar end (ckt-2 ) | MWh | 688683
37 | Transmission loss of EWI/ NO-3 from QF-GMD-10 | % | 0.028
* Data Collected from Daily Reports and Respective Substations
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
[9 empty] | QF-LDC-23 | 8
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: September 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2023-09-21 06:10 | 2023-09-21 07:34 | 1:24 | E/O | 33KV CT Terminal Temperature high. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-09-22 14:01 | 2023-09-22 21:07 | 7:06 | T | Trip due to 86/96 relay | 30 | 213 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) HT | 2023-09-22 14:35 | 2023-09-22 21:07 | 6:32 | E/O | GT-3 ,33 kV incomer PT ( R -phase) Change | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-09-22 14:01 | 2023-09-22 21:10 | 7:09 | T | 132 kV 86/91 OPTD Relay & 33 kV( 86-1,86-2) OPTD Relay | 60 | 429 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-09-22 14:01 | 2023-09-22 14:32 | 0:31 | T | over Load | 30 | 15.5 | Power interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-09-18 22:03 | 2023-09-19 16:45 | 18:42 | E/O | 132/33KV T-1 Transformer CB Hydraulic pressure low. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-09-12 02:20 | 2023-09-12 02:24 | 0:04 | E/O | 132kV CB Main protection and Backup protection operated due hydraulic pressure. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 LT | 2023-09-14 18:06 | 2023-09-16 14:30 | 44:24 | E/O | 132 KV CB (Hydrolic Circuit) Problem. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-3 LT | 2023-09-01 06:18 | 2023-09-01 06:30 | 0:12 | T | L-43 Feeder Trip (Aralia) | 48 | 9.6 | Power interruption
Savar 132/33kV Grid Sub-Station | T-3 LT | 2023-09-11 14:49 | 2023-09-11 15:03 | 0:14 | T | 33 KV Feeder Fault of L-32, L-37 | 54 | 12.6 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 01 HT | 2023-09-01 09:58 | 2023-09-01 10:10 | 0:12 | T | Haluaghat 33 kv feeder R phase flashing & loop burn out. | 75 | 15 | Power interruption
Sherpur 132/33kV Grid Sub-Station | Transformer- 02 LT | 2023-09-01 09:58 | 2023-09-01 10:10 | 0:12 | T | Haluaghat 33 kv feeder R phase flashing & loop burn out. | 75 | 15 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-09-22 15:43 | 2023-09-22 18:05 | 2:22 | T | Due to pbs 33kv feeder CT blast. | 10 | 23.6667 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 LT | 2023-09-29 11:37 | 2023-09-29 12:26 | 0:49 | T | Due to pbs 33kv feeder CT blast. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-09-06 23:43 | 2023-09-07 00:58 | 1:15 | E/O | REB 33kv Bus Red hot | 35 | 43.75 | Power interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-2 LT | 2023-09-22 15:43 | 2023-09-22 18:05 | 2:22 | T | Due to pbs 33 kV feeder CT blast | 10 | 23.6667 | No interruption
Tangail 132/33kV Grid Sub-Station | Tr-1 LT | 2023-09-02 11:42 | 2023-09-02 11:52 | 0:10 | T | Ghatail & Doreen 33kV feeder faulty. | 60 | 10 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-09-18 22:37 | 2023-09-18 23:55 | 1:18 | E/O | Red hot at 33kv kachuadanga feeder (BPDB) | 130 | 169 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 LT | 2023-09-02 11:42 | 2023-09-02 11:52 | 0:10 | T | Ghatail & Doreen 33kV feeder fault. | 60 | 10 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | T-01 HT | 2023-09-10 11:56 | 2023-09-10 13:30 | 1:34 | E/O | R- Phase neutral grounding fail. | 150 | 235 | Power interruption | 1:34
|  |  | Total : | 96:42 |  | Unserved Energy: |  | 1224.7833 |  | 1:15
2:27
Dhaka (South) Grid Circle : | [9 empty] | 1:49
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2023-09-26 22:10 | 2023-09-26 23:25 | 1:15 | E/O | To minimize Red hot of 132 KV Bus of B phase | 60 | 75 | Power interruption | 1:09
Bhulta 132/33kV Grid Sub-Station | GT2 HT | 2023-09-26 06:54 | 2023-09-26 09:21 | 2:27 | E/O | Due to emergency maint.work | 45 | 110.25 | Power interruption | 0:12
Bhulta 132/33kV Grid Sub-Station | GT2 LT | 2023-09-05 13:59 | 2023-09-05 15:48 | 1:49 | E/O | Red hot maintenance | 50 | 90.8333 | Power interruption | 2:56
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2023-09-03 02:35 | 2023-09-03 03:41 | 1:06 | T | Thunder storm | 28 | 30.8 | Power interruption | 2:57
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2023-09-04 08:38 | 2023-09-04 08:59 | 0:21 | T | 33 kv Zinzira-1 feeder faulty,but CB does not trip. As a result,T-2 33kv CB and 33 kv bus trip. | 22 | 7.7 | Power interruption | 0:59
Hasnabad 132/33kV Grid Substation | 132/33kV 414 T-2 LT | 2023-09-26 08:38 | 2023-09-26 08:54 | 0:16 | T | 33Kv Zinzira-1 feeder fault | 23 | 6.1333 | Power interruption | 1:36
Madanganj 132/33kV Grid Sub-Station | GT-1 HT | 2023-09-12 22:17 | 2023-09-16 12:46 | 86:29 | T | 33 KV GT-1 incomer breaker B phase faulty | 0 | 0 | No interruption | 1:17
Madanganj 132/33kV Grid Sub-Station | GT-2 HT | 2023-09-12 22:17 | 2023-09-12 23:51 | 1:34 | T | 33KV GT-1 Incomer CB Pole Problem | 32 | 50.1333 | Power interruption | 1:42
Munshiganj 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-09-26 06:52 | 2023-09-26 09:21 | 2:29 | E/O | 33KV Bus-2 Red Hot Maintenance by PBS | 40 | 99.3333 | Power interruption | 0:40
Narshingdi 132/33kV Grid Sub-Station | T-2 HT | 2023-09-05 14:56 | 2023-09-05 15:12 | 0:16 | T | Over Current | 40 | 10.6667 | Power interruption | 0:10
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 HT | 2023-09-28 05:30 | 2023-09-28 12:20 | 6:50 | T | PRV Fault | 0 | 0 | No interruption | 3:03
Sonargaon 132/33kV Grid Sub-Station | Tr-1 HT | 2023-09-10 15:08 | 2023-09-10 15:54 | 0:46 | E/O | 33Kv Bus Coupler Jumper Out From C.B (Redhot Maintenance). S/D taken by PBS. | 25 | 19.1667 | Power interruption | 1:02
|  |  | Total : | 105:38 |  | Unserved Energy: |  | 500.0167 |  | 1:28
1:33
Chattogram Grid Circle :
Bakulia 132/33kV Grid Sub-Station | T-2 (412T) HT | 2023-09-07 14:47 | 2023-09-07 14:51 | 0:04 | T | Due to CB Testing. | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | TR-1, 406T HT | 2023-09-12 07:51 | 2023-09-12 09:00 | 1:09 | E/O | Red hot maintenance | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2023-09-19 20:15 | 2023-09-19 21:38 | 1:23 | E/O | Wasa 33 kv feeder faulty cable change PBS | 20 | 27.6667 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-1 HT | 2023-09-08 09:34 | 2023-09-08 09:46 | 0:12 | E/O | For Station Supply fuse cut. | 12 | 2.4 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | MT-02 HT | 2023-09-26 12:47 | 2023-09-26 13:51 | 1:04 | T | Winding temperature high. | 60 | 64 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 LT | 2023-09-17 13:05 | 2023-09-17 14:15 | 1:10 | T | Tripped showing over current,lockout relays. | 23 | 26.8333 | Power interruption
Hathazari 230/132/33kV Grid Sub-Station | T-02 LT | 2023-09-17 13:05 | 2023-09-17 14:15 | 1:10 | T | Tripped showing over current,lockout relays. | 43 | 50.1667 | Power interruption
KSRM 132/33kV Grid Sub-Station | Transformer-01 HT | 2023-09-04 09:42 | 2023-09-04 15:55 | 6:13 | E/O | emergency shutdown due to 33 kv feeder maintenance, checking, cleaning and tightness check. | 0 | 0 | No interruption
Khagrachori 132/33kV Grid Sub-Station | TR-1 LT | 2023-09-13 16:11 | 2023-09-13 16:24 | 0:13 | T | 33 kv mohalchari trip | 10 | 2.1667 | Power interruption
Khagrachori 132/33kV Grid Sub-Station | TR-2 LT | 2023-09-13 16:11 | 2023-09-13 16:24 | 0:13 | T | 33 kv mohalchari trip | 10 | 2.1667 | Power interruption
Khulshi 132/33kV Grid Sub-Station | 405T (T1) LT | 2023-09-23 10:27 | 2023-09-23 13:45 | 3:18 | E/O | 33kv Outdoor Bus Conductor change R-phase in 33kv Outdoor Bus Section-1. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | T-2 33kV BUS | 2023-09-30 19:26 | 2023-09-30 19:26 | 0:00 | E/O | For emergency red hot maintenance work at bus isolator(R-ph) of 33kv Mohora-3 ckt by BPDB. | 0 | 0 | No interruption
Madunaghat 132/33kV Grid Sub-Station | TR-1(507T) LT | 2023-09-29 12:23 | 2023-09-29 13:21 | 0:58 | E/O | Emergency Red hot maintenance work by BPDB | 42 | 40.6 | Power interruption
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 HT | 2023-09-29 16:43 | 2023-09-29 17:16 | 0:33 | T | None | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | TR-1 LT | 2023-09-09 06:33 | 2023-09-09 08:38 | 2:05 | E/O | RED HOT MAINTENANCE | 0 | 0 | No interruption
Shahmirpur 132/33kV Grid Sub-Station | 416T HT | 2023-09-29 15:25 | 2023-09-29 21:20 | 5:55 | E/O | Transformer Trip at 14:07 (Differential Relay trip(87/87N) signal and T2 Protection General Trip signal) due to 33 kv karnafully Tunnel feeder trip . | 0 | 0 | No interruption
|  |  | Total : | 25:40 |  | Unserved Energy: |  | 216
Cumilla Grid Circle :
Beanibazar 132/33kV Grid Sub-Station | 132 KV Transformer TR-01 LT | 2023-09-07 22:19 | 2023-09-07 23:09 | 0:50 | T | 33 kv jokigong Fedder CT problem. | 58 | 48.3333 | Power interruption
Beanibazar 132/33kV Grid Sub-Station | 132KV Transformer TR-02 LT | 2023-09-07 22:19 | 2023-09-07 23:10 | 0:51 | T | 33 kv jokigong Fedder CT problem | 58 | 49.3 | Power interruption
Chandpur 132/33kV Grid Sub-Station | 402T HT | 2023-09-17 13:10 | 2023-09-17 13:44 | 0:34 | E/O | Due to grid fail | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 422T HT | 2023-09-17 13:10 | 2023-09-17 13:44 | 0:34 | E/O | Due to grid fail | 0 | 0 | No interruption
Chauddagram 132/33kV Grid Sub-Station | 132 kv T-1 HT | 2023-09-28 21:11 | 2023-09-28 22:19 | 1:08 | E/O | Red hot restoration work at 33KV bus DS side loop. | 28 | 31.7333 | Power interruption
Chhatak 132/33kV Grid Sub-Station | T-2 LT | 2023-09-30 17:56 | 2023-09-30 18:05 | 0:09 | T | over current | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2 | 2023-09-23 18:44 | 2023-09-23 19:06 | 0:22 | E/O | Red hot maintenance. | 30 | 11 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | TR2-425T LT | 2023-09-17 23:15 | 2023-09-18 02:51 | 3:36 | E/O | 33KV Incoming Y-Phase Isulator Top Nut "RED-HOT". Load Shear to T-1 Bus. | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | TR3 | 2023-09-10 07:54 | 2023-09-10 13:05 | 5:11 | E/O | Red Hot Maintenance Of 33kv VCB Y phase And Incoming DS | 20 | 103.6667 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-03 HT | 2023-09-04 07:44 | 2023-09-04 08:28 | 0:44 | T | over current | 34 | 24.9333 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-09-04 07:44 | 2023-09-04 08:28 | 0:44 | T | over current | 34 | 24.9333 | Power interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV T-04 LT | 2023-09-21 17:55 | 2023-09-21 20:51 | 2:56 | E/O | Redhot Remove. | 5 | 14.6667 | Power interruption
Fenchuganj 230/132/33kV Grid Sub-Station | TR-02 HT | 2023-09-18 01:41 | 2023-09-18 02:07 | 0:26 | T | Thunder | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) HT | 2023-09-01 06:35 | 2023-09-01 08:43 | 2:08 | E/O | Redhot maintenance by BREB | 28 | 59.7333 | Power interruption
Feni 132/33kV Grid Sub-Station | T-1(405T) LT | 2023-09-29 06:45 | 2023-09-29 09:42 | 2:57 | E/O | Redhot Maintenance | 15 | 44.25 | Power interruption
Feni 132/33kV Grid Sub-Station | T-2(415T) HT | 2023-09-09 09:30 | 2023-09-09 10:40 | 1:10 | E/O | Redhot maintenance 33KV side R phase bushing of 132/33KV Transfomer T-02. | 0 | 0 | No interruption
Sreemongol 132/33kV Grid Sub-Station | 132/33kv T-3 HT | 2023-09-18 08:15 | 2023-09-18 08:25 | 0:10 | E/O | 33kv Gas Refill Work. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T1 LT | 2023-09-22 07:11 | 2023-09-22 07:30 | 0:19 | T |  | 25 | 7.9167 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T2 HT | 2023-09-24 18:29 | 2023-09-24 18:50 | 0:21 | T | fault of 33KV shakghat feeder (PDB) | 55 | 19.25 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-04 18:18 | 2023-09-04 18:49 | 0:31 | T | O/L | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-05 08:11 | 2023-09-05 09:25 | 1:14 | T | O/L | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-05 14:25 | 2023-09-05 15:40 | 1:15 | T | Over bload | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-05 18:17 | 2023-09-05 19:28 | 1:11 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-07 22:55 | 2023-09-07 23:22 | 0:27 | T | Over Load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-09 18:15 | 2023-09-09 19:04 | 0:49 | T | Over Load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-10 12:16 | 2023-09-10 20:54 | 8:38 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-11 16:13 | 2023-09-11 17:56 | 1:43 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-11 18:15 | 2023-09-12 01:16 | 7:01 | T | Tripped showing 50/51 O/C. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-13 13:12 | 2023-09-13 14:28 | 1:16 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-13 14:55 | 2023-09-13 16:44 | 1:49 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-13 18:15 | 2023-09-13 23:20 | 5:05 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-15 21:51 | 2023-09-16 00:45 | 2:54 | T | Tripped showing O/C. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-16 18:03 | 2023-09-16 23:16 | 5:13 | T | Tripped showing O/C. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-17 11:16 | 2023-09-18 08:02 | 20:46 | T | Tripped showing O/C. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-18 16:30 | 2023-09-19 00:46 | 8:16 | T | Over Load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-19 20:07 | 2023-09-19 23:02 | 2:55 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-24 18:29 | 2023-09-24 19:09 | 0:40 | T | fault of 33KV shakghat feeder(PDB) | 35 | 23.3333 | Power interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-25 14:43 | 2023-09-25 21:45 | 7:02 | T | Tripped showing O/C. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-26 17:56 | 2023-09-27 01:15 | 7:19 | T | Over Load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-27 18:05 | 2023-09-28 08:23 | 14:18 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-28 13:10 | 2023-09-29 09:06 | 19:56 | T | Over load | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-29 17:55 | 2023-09-30 08:03 | 14:08 | T | Tripped showing O/C. relays. | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | T4 LT | 2023-09-30 12:58 | 2023-09-30 12:58 | 0:00 | T | Over Load | 0 | 0 | No interruption
|  |  | Total : | 159:36 |  | Unserved Energy: |  | 463.05
Khulna Grid Circle :
Barishal 230/132kV Grid Sub-Station | ATR-2 HT | 2023-09-23 02:40 | 2023-09-23 02:45 | 0:05 | T | TR prot trip | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-09-20 20:29 | 2023-09-20 21:28 | 0:59 | E/O | Red Hot Maintenance | 0 | 0 | No interruption
Benapole 132/33kV Grid Sub-Station | Transformer-1(406T) LT | 2023-09-30 20:15 | 2023-09-30 20:43 | 0:28 | T | Benapole Feeder fault | 36 | 16.8 | Power interruption
Benapole 132/33kV Grid Sub-Station | Transformer-2(416T) LT | 2023-09-30 20:15 | 2023-09-30 20:44 | 0:29 | T | benapole feeder fault | 36 | 17.4 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-09-17 11:35 | 2023-09-17 11:53 | 0:18 | T | 33kV Vanga-01 Breaker pole blast | 60 | 18 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-09-17 11:35 | 2023-09-17 11:54 | 0:19 | T | 33kV Vanga-01 Breaker pole blast | 60 | 19 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-09-28 14:56 | 2023-09-28 15:15 | 0:19 | T | Due to 33 Kv Line fault. | 6 | 1.9 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-09-28 15:25 | 2023-09-28 15:50 | 0:25 | T | Due to 33 Kv Breaker Fault. T3- CB, open. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-09-06 11:41 | 2023-09-06 14:39 | 2:58 | E/O | Bagerthat PBS-1 33kv feeder red hot maintenace (Y-phase) | 10 | 29.6667 | Power interruption
Gopalganj 132/33kV Grid Sub-Station | T2 LT | 2023-09-06 11:50 | 2023-09-06 12:45 | 0:55 | T | Gopalgonj West Zone 33kv feeder fult. | 64 | 58.6667 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | TR-1 425T HT | 2023-09-03 19:45 | 2023-09-03 20:03 | 0:18 | T | Due to 33kv satkhira feeder faulty. | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T HT | 2023-09-01 07:49 | 2023-09-01 10:00 | 2:11 | E/O | CB loop problem | 0 | 0 | No interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-09-10 10:18 | 2023-09-10 13:25 | 3:07 | E/O | 33 KV Red Phase CT oil Leakage. | 10 | 31.1667 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-1 LT | 2023-09-18 04:49 | 2023-09-18 05:22 | 0:33 | T | 33kv pbs-1 faulty byOC/EF | 16 | 8.8 | Power interruption
Mongla 132/33kV Grid Sub-Station | T-2 LT | 2023-09-18 04:49 | 2023-09-18 05:23 | 0:34 | T | 33kv pbs-1 faulty by OC/EF | 16 | 9.0667 | Power interruption
Noapara 132/33kV Grid Sub-Station | T-4 HT | 2023-09-20 01:24 | 2023-09-20 01:56 | 0:32 | T | WTI Trip | 19 | 10.1333 | Power interruption
Patuakhali 132/33kV Grid Sub-Station | 425T (T-3) HT | 2023-09-01 10:10 | 2023-09-01 12:13 | 2:03 | E/O | 33 kV incoming CT loup red hot work. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Generator Transformer-1 (GT-1) HT | 2023-09-01 13:45 | 2023-09-01 20:25 | 6:40 | T | Differential protection Relay operated. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 HT | 2023-09-01 13:45 | 2023-09-01 19:03 | 5:18 | T | Distance protection Relay operated. | 0 | 0 | No interruption
|  |  | Total : | 28:31 |  | Unserved Energy: |  | 220.6
HVDC Grid Circle :
Baghabari 230/132kV Grid Sub-Station | T-1 HT | 2023-09-26 18:05 | 2023-09-26 20:05 | 2:00 | E/O | PDB 132 Kv side maintanace work. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-2 Bank HT | 2023-09-03 12:42 | 2023-09-03 15:16 | 2:34 | T | Teripped showing PRV and mechanical trip relay. | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | T-2 Bank LT | 2023-09-26 10:32 | 2023-09-26 12:08 | 1:36 | E/O | Red hot maintenance work bushing clamp connector(Y-Phase) | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-09-04 08:26 | 2023-09-04 09:06 | 0:40 | T | 33 kv PBS feeder fault | 51 | 34 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-09-05 12:50 | 2023-09-05 12:59 | 0:09 | T | 33 kv Narail west zone feeder fault | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-3 HT | 2023-09-04 17:29 | 2023-09-05 13:47 | 20:18 | E/O | T3 x-former 33 kv side cable blast (B-phase) | 0 | 0 | No interruption
Jhenaidah 132/33kV Grid Sub-Station | Transformer T-1 LT | 2023-09-03 16:20 | 2023-09-03 17:25 | 1:05 | E/O | 33KV PBS BUS DS post Insulator Change Work. | 35 | 37.9167 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 HT | 2023-09-20 08:08 | 2023-09-20 08:38 | 0:30 | T | 33 kv feeder fault . | 40 | 20 | Power interruption
Kushtia 132/33kV Grid Sub-Station | T2 LT | 2023-09-08 07:10 | 2023-09-08 08:27 | 1:17 | E/O | T-2 A Bus PT Maintenance . | 30 | 38.5 | Power interruption
Magura 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-09-08 15:50 | 2023-09-08 17:23 | 1:33 | T | Water entered in oil temp. Meter. | 0 | 0 | No interruption
Shahjadpur 132/33kV Grid Sub-Station | T-2(415T) LT | 2023-09-20 22:47 | 2023-09-21 00:02 | 1:15 | T | Shahjadpur -1 feeder fault à¦à¦° à¦•à¦¾à¦°à¦£à§‡ trip à¦¨à¦¾ à¦•à¦°à¦¾à§Ÿ 132 kv transformer incoming bkr à¦¸à¦¹ trip à¦•à¦°à§‡à¥¤ | 14 | 17.5 | Power interruption
Shahjadpur 132/33kV Grid Sub-Station | T-4(435T) HT | 2023-09-30 11:55 | 2023-09-30 11:55 | 0:00 | E/O | Ullapara 33 kv incoming bus red hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 32:57 |  | Unserved Energy: |  | 147.9167
Bogura Grid Circle:
Bog-Sherpur 132/33kV Grid Sub-Station | Transformer-2 (414T) LT | 2023-09-17 07:06 | 2023-09-17 08:48 | 1:42 | E/O | For red-hot maintenance. | 10 | 17 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-09-17 06:30 | 2023-09-17 07:10 | 0:40 | E/O | For Bus Shift. | 60 | 40 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-09-17 09:30 | 2023-09-17 09:40 | 0:10 | E/O | By the Instruction of NLDC | 50 | 8.3333 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-09-14 14:30 | 2023-09-14 16:04 | 1:34 | E/O | Oil Likage. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-09-17 06:30 | 2023-09-17 09:33 | 3:03 | E/O | For Bus Shift. | 60 | 183 | Power interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-09-03 15:01 | 2023-09-03 16:12 | 1:11 | E/O | Due to emergency amint.work | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-09-06 06:22 | 2023-09-06 12:15 | 5:53 | E/O | Isolator replacement | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-09-08 06:25 | 2023-09-08 10:47 | 4:22 | E/O | Isolator replacement | 0 | 0 | No interruption | 26.8333 | 17
Bogura 230/132kV Grid Sub-Station | T-01 HT | 2023-09-30 20:08 | 2023-09-30 21:23 | 1:15 | E/O | Emergency red hot maintenance | 0 | 0 | No interruption | 27.2167 | 40
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-09-29 20:13 | 2023-09-30 00:04 | 3:51 | E/O | T-01 33Kv CB R phase outgoing clamp Red hot maintenance. | 0 | 0 | No interruption | 12.5 | 8.3333
Jaldhaka 132/33kV Grid Sub-Station | 406T LT | 2023-09-03 14:01 | 2023-09-03 15:53 | 1:52 | E/O | Red hot at 33 kv domer-1 feeder. | 20 | 37.3333 | Power interruption | 13.5 | 183
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-09-02 06:05 | 2023-09-02 06:58 | 0:53 | T | 132kv ( 432B ) Breaker trip without signal. | 0 | 0 | No interruption | 2 | 37.3333
Mithapukur 132/33kV Grid Sub-Station | TR-1(404T) LT | 2023-09-04 05:33 | 2023-09-04 06:43 | 1:10 | T | 33 KV Bus Section DS-2 R Phase Insulator Burst | 23 | 26.8333 | Power interruption | 39 | 18.6
Mithapukur 132/33kV Grid Sub-Station | TR-2 (414T) LT | 2023-09-04 05:33 | 2023-09-04 06:44 | 1:11 | T | 33 KV Bus Section DS-2 R Phase Insulator Burst | 23 | 27.2167 | Power interruption | 4.55 | 7.8333
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-09-11 14:55 | 2023-09-11 17:35 | 2:40 | E/O | Red hot maintenance. | 0 | 0 | No interruption | 4.55 | 27
Naogaon 132/33kV Grid Sub-Station | T-2 LT | 2023-09-16 12:02 | 2023-09-16 12:14 | 0:12 | T | Trip | 0 | 0 | No interruption | 2.6 | 46
Niamatpur 132/33kV Grid Sub-Station | 407T LT | 2023-09-19 08:25 | 2023-09-19 09:27 | 1:02 | E/O | red hot problem sapahar feeder under T-1 transformer | 18 | 18.6 | Power interruption | 1.1 | 106.5
Niamatpur 132/33kV Grid Sub-Station | 417T LT | 2023-09-24 06:06 | 2023-09-24 06:53 | 0:47 | E/O | Red hot 33 KV deluabari feeder. | 10 | 7.8333 | Power interruption | 1.2833 | 79.75
Panchagarh 132/33kV Grid Sub-Station | T-3(A+B)(427T) HT | 2023-09-07 14:05 | 2023-09-07 20:50 | 6:45 | E/O | T-3(B) Power Transformer at B and Y Phase Bushing Oil Leakage Removing Work. | 0 | 0 | No interruption |  | 114
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-09-18 14:35 | 2023-09-18 15:05 | 0:30 | T | fokirpara 33Kv Feeder LA Blust | 25 | 12.5 | Power interruption |  | 79.75
Purbasadipur 132/33kV Grid Sub-Station | T-1 Transformer (403T) HT | 2023-09-22 08:56 | 2023-09-22 09:23 | 0:27 | T |  | 30 | 13.5 | Power interruption |  | 114
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-09-18 14:35 | 2023-09-18 14:45 | 0:10 | T | Fokirpaera 33Kv Feeder LA Blust | 0 | 0 | No interruption |  | 29.3333
Purbasadipur 132/33kV Grid Sub-Station | T-3 Transformer (423T) LT | 2023-09-22 08:56 | 2023-09-22 09:04 | 0:08 | T |  | 15 | 2 | Power interruption |  | 16
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) LT | 2023-09-10 17:10 | 2023-09-10 18:28 | 1:18 | T | T-1 33KV BUS PT (Y-Phase) Blast. | 30 | 39 | Power interruption |  | 9.6667
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) LT | 2023-09-22 21:08 | 2023-09-22 22:56 | 1:48 | E/O | Transformer T-2 33 KV BUS Connector (R-Phase) Red hot Maintenance Work. | 15 | 27 | Power interruption |  | 54.25
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-09-07 16:24 | 2023-09-07 17:56 | 1:32 | E/O | JE. Mr. Sujon, NPBS-1 requested for T-3 33KV Bus shout down. | 30 | 46 | Power interruption |  | 67.9167
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) LT | 2023-09-02 22:56 | 2023-09-03 01:18 | 2:22 | E/O | T3,33 kV TDS B phase Red Hot | 45 | 106.5 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) HT | 2023-09-29 06:38 | 2023-09-29 08:05 | 1:27 | E/O | WORK FOR 33 KV BUS | 55 | 79.75 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-1(414T) LT | 2023-09-19 07:05 | 2023-09-19 08:21 | 1:16 | E/O | 33kv Dharsana feeder bus DS red hot | 90 | 114 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) HT | 2023-09-29 06:38 | 2023-09-29 08:05 | 1:27 | E/O | WORKS FOR 33 KV BUS | 55 | 79.75 | Power interruption
Rangpur 132/33kV Grid Sub-Station | T-2 (404T) LT | 2023-09-19 07:05 | 2023-09-19 08:21 | 1:16 | E/O | 33kv Dhasana feeder bus DS red hot | 90 | 114 | Power interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-09-20 11:55 | 2023-09-20 13:26 | 1:31 | E/O | Generator side maintenance work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-09-22 21:32 | 2023-09-23 03:30 | 5:58 | E/O | requested by XEN 20MW.Gt. for emergency maintenance. | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-09-24 08:35 | 2023-09-24 09:18 | 0:43 | T |  | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) HT | 2023-09-14 07:12 | 2023-09-14 08:40 | 1:28 | E/O | CT connector Y phase0 bolt red hot . | 20 | 29.3333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-09-03 10:15 | 2023-09-03 11:19 | 1:04 | E/O | Emergency Red hot maintenance of 33 kv T1 incoming CT (Y-phase). | 15 | 16 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-09-11 18:03 | 2023-09-11 18:32 | 0:29 | E/O | Emergency Red hot maintenance of T-1, 33 CT (Y-Ph.) | 20 | 9.6667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-09-04 23:12 | 2023-09-05 00:45 | 1:33 | E/O | Emergency Red Hot Maintenance | 35 | 54.25 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-1(422T) LT | 2023-09-20 17:21 | 2023-09-20 17:34 | 0:13 | T | Over current due to capacitor bank fault | 21 | 4.55 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) HT | 2023-09-29 23:43 | 2023-09-30 00:10 | 0:27 | T | 33 kV Feeder fault | 0 | 0 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) LT | 2023-09-20 17:21 | 2023-09-20 17:34 | 0:13 | T | Over current due to capacitor bank fault | 21 | 4.55 | Power interruption
Thakurgaon 132/33kV Grid Sub-Station | T-3(432T) HT | 2023-09-29 23:43 | 2023-09-29 23:55 | 0:12 | T | 33kV Feeder fault under T-2 Transformer | 13 | 2.6 | Power interruption
|  |  | Total : | 67:45 |  | Unserved Energy: |  | 1121.1
Others :
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 HT | 2023-09-06 18:58 | 2023-09-06 19:06 | 0:08 | T | Tripped showing 1.Over Current relay | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 HT | 2023-09-10 11:16 | 2023-09-10 11:22 | 0:06 | T | Tripped showing 1.Over Current relay | 0 | 0 | No interruption
|  |  | Total : | 0:14 |  | Unserved Energy: |  | 0:00
Total outage period of Sub-station Equipment : |  |  |  | 545:34 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
QF-LDC-24
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance | [9 empty] | 498.6333
Month: September 2023 | [9 empty] | 75.4667
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks | 574.1
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka 132/33kV Grid Sub-Station | Sreepur- Bhaluka 132 kV Ckt- 01 | 2023-09-22 12:04 | 2023-09-22 12:22 | 0:18 | T | Tripped showing Master relay | 90 | 27 | Power interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-09-19 14:18 | 2023-09-19 14:41 | 0:23 | E/O | Right of Way | 0 | 0 | No interruption
Kishoreganj 132/33kV Grid Sub-Station | Ashuganj Ckt-2 | 2023-09-22 12:04 | 2023-09-22 12:16 | 0:12 | T | None | 70 | 14 | Power interruption
Mirpur 132/33kV Grid Sub-Station | Aminbazar-1 | 2023-09-20 13:31 | 2023-09-20 14:52 | 1:21 | T | Rain | 128 | 172.8 | Power interruption
Mirpur 132/33kV Grid Sub-Station | Uttara Sector-18 | 2023-09-28 17:22 | 2023-09-28 17:54 | 0:32 | E/O | Red Phase CT Burst. | 76 | 40.5333 | Power interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-1 | 2023-09-16 11:35 | 2023-09-16 11:47 | 0:12 | T | Tripped showing Distance B-Phase, C-Phase | 0 | 0 | No interruption
Netrakona 132/33kV Grid Sub-Station | Mymensingh-Netrokona Ckt-1 | 2023-09-17 08:29 | 2023-09-17 09:04 | 0:35 | T | Unknown | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Sirajganj Ckt-2 | 2023-09-22 17:43 | 2023-09-22 18:47 | 1:04 | E/O | Instructed by NLDC | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | Sreepur-Valuka Ckt-2 | 2023-09-22 12:04 | 2023-09-22 12:24 | 0:20 | T | CB open due to over current. | 123 | 41 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-09-06 12:14 | 2023-09-06 12:24 | 0:10 | T | Tongi Side only(605B).Bashundhara end side both breaker trip. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-09-10 12:07 | 2023-09-10 12:24 | 0:17 | T | Tripped showing Distance Relay, Z-1, B phase relays. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-09-10 13:40 | 2023-09-10 17:28 | 3:48 | T | Tripped showing Distance Relay, Z-1, B phase relays. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-09-17 20:43 | 2023-09-17 21:25 | 0:42 | T | Tripped showing Distance Relay, Z-1, B phase relays. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-09-30 16:06 | 2023-09-30 16:12 | 0:06 | E/O | LA, B-Phase Wire Remove | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-1 | 2023-09-23 16:32 | 2023-09-23 16:49 | 0:17 | T | Tripped showing ABB(REL650) relays. | 82 | 23.2333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Kabirpur Ckt-2 | 2023-09-23 16:32 | 2023-09-23 16:46 | 0:14 | T | Tripped showing ABB(REL650) relays. | 82 | 19.1333 | Power interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara 3rd Phase Ckt | 2023-09-08 15:41 | 2023-09-08 15:55 | 0:14 | T | General | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Uttara Ckt | 2023-09-17 21:18 | 2023-09-17 21:28 | 0:10 | T | Tripped showing Distance Relay, phase-B, SOTF. relays. | 0 | 0 | No interruption
|  |  | Total : | 10:55 |  | Unserved Energy: |  | 337.7
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | Haripur | 2023-09-30 00:20 | 2023-09-30 00:35 | 0:15 | T | For KPPGL S/D, line load increased. So the line tripped for over load. | 172 | 43 | Power interruption |  | 120.3333 | 251.2167
Bhulta 400/230kV Grid Sub-Station | Rampura-01 | 2023-09-03 02:57 | 2023-09-03 07:10 | 4:13 | T | Tripped showing ZCOM Trip, EFCOM Trip, R-phase Trip, Dist. | 0 | 0 | Power interruption |  | 14.7833
Fatullah 132/33kV Grid Sub-Station | 132 kV Madanganj | 2023-09-18 15:08 | 2023-09-18 17:52 | 2:44 | E/O | Due to Emergency maint.work | 0 | 0 | Power interruption
Gulshan 132/33kV Grid Sub-Station | Rampura-2 | 2023-09-10 00:47 | 2023-09-16 16:09 | 159:22 | T | Tripped showing O/C, E/F & Distance relay | 0 | 0 | Power interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-1 | 2023-09-03 03:40 | 2023-09-03 04:15 | 0:35 | T | unknown | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | 230kV Bhulta-2 | 2023-09-03 03:40 | 2023-09-03 04:14 | 0:34 | T | Unknown | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-09-08 23:42 | 2023-09-08 23:49 | 0:07 | T | Tripped showing Circulating Current Protection (CC2): Y phase, (86T1). relays. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-09-08 23:50 | 2023-09-09 14:38 | 14:48 | T | Tripped showing Circulating Current Protection (CC2): Y phase, (86T1). relays. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-09-19 13:39 | 2023-09-19 16:18 | 2:39 | E/O | Red Hot Maintenance at Meghnaghat SS | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Narsingdi | 2023-09-17 12:45 | 2023-09-17 12:59 | 0:14 | T | Trip | 109 | 25.4333 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-09-17 20:16 | 2023-09-17 20:37 | 0:21 | T | Rain and strom. | 38 | 13.3 | Power interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-09-24 19:33 | 2023-09-24 19:33 | 0:00 | T | None | 0 | 0 | No interruption
Hasnabad 230/132kV Grid Sub-Station | Hasnabad-Keraniganj Ckt-1 | 2023-09-26 13:04 | 2023-09-26 13:35 | 0:31 | T | Unknown | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2023-09-05 21:59 | 2023-09-07 12:48 | 38:49 | E/O | As there is spark in the line conductor, the circuit breaker is opened under the direction of the officer-in-charge. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Hasnabad | 2023-09-21 14:08 | 2023-09-21 14:43 | 0:35 | T | Tripped showing 86.1 relays | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Summit 55 MW 132 kv Ckt | 2023-09-28 10:10 | 2023-09-28 11:28 | 1:18 | E/O | Emergency Red hot maintenance | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj-Fatullah 132KV Ckt | 2023-09-18 15:06 | 2023-09-18 17:53 | 2:47 | E/O | Emergency maint.work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Basundhara-01 | 2023-09-05 12:34 | 2023-09-05 12:44 | 0:10 | T | Unknown | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2023-09-10 00:46 | 2023-09-10 00:46 | 0:00 | T | B-ph U/G cable pothead burst | 0 | 0 | No interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Shyampur old-1(E07) | 2023-09-18 16:35 | 2023-09-18 17:05 | 0:30 | T | Above circuit tripped only from Shyampur (old) substation end. Due to LA brust in Transformer -2 Bay of Shyampur (old) substation. | 71 | 35.5 | Power interruption
Shyampur 230/132kV Grid Sub-Station | 132 kV Shyampur old-2(E10) | 2023-09-18 14:40 | 2023-09-18 17:22 | 2:42 | T | Tripped due to external materials. | 39 | 105.3 | Power interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-09-01 16:13 | 2023-09-01 20:00 | 3:47 | E/O | Corrective maintenance (Red hot B-Phase) | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 132kV MTR 2 | 2023-09-28 05:30 | 2023-09-28 12:27 | 6:57 | T | 230 Kv Side | 0 | 0 | No interruption
|  |  | Total : | 243:58 |  | Unserved Energy: |  | 222.5333
Chattogram Grid Circle :
Baroirhat 132/33kV Grid Sub-Station | Feni-1 | 2023-09-27 05:05 | 2023-09-27 05:25 | 0:20 | T | Distance trip | 0 | 0 | No interruption
Baroirhat 132/33kV Grid Sub-Station | Hat-2 | 2023-09-12 00:10 | 2023-09-12 00:30 | 0:20 | T | Distance trip | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | Chandraghona-Kaptai Ckt-02 | 2023-09-09 11:35 | 2023-09-09 11:59 | 0:24 | T | Tripped showing REL670 relays. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Cox's Bazar ckt-1 | 2023-09-08 07:34 | 2023-09-08 07:50 | 0:16 | T | Trip by Distence | 2 | 0.53333 | Power interruption
Halishahar 132/33kV Grid Sub-Station | Halishahar-Rampur Ckt-2 | 2023-09-24 11:57 | 2023-09-24 12:06 | 0:09 | T | Transient fault | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-01 | 2023-09-17 13:05 | 2023-09-17 13:17 | 0:12 | T | Tripped showing backup,special protection telay | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2023-09-17 13:05 | 2023-09-17 13:17 | 0:12 | T | Tripped showing backup,special protection telay | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Baroiarhat-02 | 2023-09-20 12:55 | 2023-09-20 12:59 | 0:04 | E/O | Emergency tree trimming | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | Kaptai-02 | 2023-09-28 21:57 | 2023-09-29 21:14 | 23:17 | T | Trip by Distence | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Halishahar | 2023-09-05 12:26 | 2023-09-05 12:48 | 0:22 | T | Line Trip | 0 | 0 | No interruption
Juldah 132/33kV Grid Sub-Station | 132 KV Julda-Sikalbaha | 2023-09-17 11:27 | 2023-09-17 13:01 | 1:34 | E/O | GI wire remove from no of 45 tower jumper (Emergency S/D). | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-1(Rampur) | 2023-09-18 09:54 | 2023-09-18 13:40 | 3:46 | E/O | Red hot | 0 | 0 | No interruption
Khulshi 132/33kV Grid Sub-Station | Khulshi-Halishahar CKT-2(Rampur) | 2023-09-18 14:44 | 2023-09-18 23:00 | 8:16 | E/O | Red hot | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-1 | 2023-09-18 12:54 | 2023-09-18 23:02 | 10:08 | E/O | Due to Emergency maint.work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Halishahar-2 | 2023-09-24 11:56 | 2023-09-24 12:04 | 0:08 | T | Fault | 0 | 0 | No interruption
Shikalbaha 230/132kV Grid Sub-Station | Hathazari-02 | 2023-09-29 16:39 | 2023-09-29 17:07 | 0:28 | T | Zcom Trip | 41 | 19.1333 | Power interruption
Shikalbaha 230/132kV Grid Sub-Station | Modunaghat Ckt-2(T.K Chemical) | 2023-09-17 13:20 | 2023-09-17 13:56 | 0:36 | T | Distance Zone-1 trip | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | Madunaghat-T.K. chemical | 2023-09-17 13:20 | 2023-09-17 13:57 | 0:37 | T | Distance Relay 3 phase trip, Ar in proges, | 25 | 15.4167 | Power interruption
|  |  | Total : | 51:09 |  | Unserved Energy: |  | 35.0833
Cumilla Grid Circle :
Brahmanbaria 132/33kV Grid Sub-Station | Brahmanbaria-Ashugonj Circuit-1 | 2023-09-20 08:35 | 2023-09-20 09:46 | 1:11 | E/O | Due to emergeny maint.work | 0 | 0 | No interruption
Chandpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2023-09-04 18:46 | 2023-09-04 18:46 | 0:00 | T | Tripped showing Line protection relay relays. | 92 | 0 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-09-01 12:24 | 2023-09-01 12:37 | 0:13 | T | Tripped showing Dist Trip relays. | 40 | 8.6667 | Power interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-09-10 14:18 | 2023-09-10 14:29 | 0:11 | T | Line Fault | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Feni line-02 | 2023-09-24 10:01 | 2023-09-24 14:38 | 4:37 | E/O | Line DS Y-phase REDHOT. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 132KV Cumilla(N)-Daudkandi Ckt-2 | 2023-09-27 06:23 | 2023-09-27 09:48 | 3:25 | E/O | Redhot remove. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2023-09-17 12:03 | 2023-09-17 12:45 | 0:42 | T | Dist. Prot. Operated | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-1 | 2023-09-17 13:05 | 2023-09-17 16:29 | 3:24 | T | Tripped showing Busbar Diff. Relay; Busbar Prot. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-09-17 13:05 | 2023-09-17 16:12 | 3:07 | T | Tripped showing Busbar Diff. Relay; Busbar Prot. | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Ashuganj Ckt-2 | 2023-09-26 10:43 | 2023-09-26 11:00 | 0:17 | T | Tripped showing Secondary distance Protection relay | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-1 | 2023-09-17 13:05 | 2023-09-17 14:34 | 1:29 | T | Tripped showing Busbar Diff. Relay | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-BSRM Ckt-2 | 2023-09-17 13:05 | 2023-09-17 14:21 | 1:16 | T | Tripped showing Busbar Diff. Relay | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt 1 | 2023-09-17 13:05 | 2023-09-17 13:29 | 0:24 | T | Tripped showing Busbar Diff. Relay | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Meghnagat Ckt-2 | 2023-09-17 13:05 | 2023-09-17 13:31 | 0:26 | T | Tripped showing Busbar Diff. Relay | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-1 | 2023-09-17 13:05 | 2023-09-17 14:04 | 0:59 | T | None | 0 | 0 | No interruption
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV Cumilla(N)-Shahajibazar Ckt-2 | 2023-09-17 13:05 | 2023-09-17 14:05 | 1:00 | T | None | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | Tripura Ckt-2 | 2023-09-07 16:24 | 2023-09-07 17:29 | 1:05 | E/O | SF6 Gas refilling at SM.Nagar end. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Titas 50 MW Power Plant Line | 2023-09-07 17:12 | 2023-09-11 11:33 | 90:21 | E/O | Emergency maintenance work at Titas power plant end. | 0 | 0 | No interruption
Daudkandi 132/33kV Grid Sub-Station | Titas 50 MW Power Plant Line | 2023-09-12 16:10 | 2023-09-13 11:58 | 19:48 | E/O | Emergency Maintenance work at Titas 50MW power plant end. | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | Chowddagram Ckt-2 | 2023-09-01 12:24 | 2023-09-01 12:39 | 0:15 | T | Tripe | 0 | 0 | No interruption
Feni 132/33kV Grid Sub-Station | PHP (ISML) Ckt | 2023-09-29 11:07 | 2023-09-29 11:20 | 0:13 | T | Tripped showing Distance Relay | 0 | 0 | No interruption
|  |  | Total : | 134:23 |  | Unserved Energy: |  | 8.6667
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-09-05 05:13 | 2023-09-05 08:06 | 2:53 | T | Tripped showing C phase Distance relay relays. | 0 | 0 | No interruption
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-09-10 11:46 | 2023-09-10 13:01 | 1:15 | E/O | Emergency Tree Trimming. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Bagerhat | 2023-09-01 14:10 | 2023-09-01 14:25 | 0:15 | E/O | Due to Restore Switching By Hand | 5 | 1.25 | Power interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-1 | 2023-09-01 14:10 | 2023-09-01 14:21 | 0:11 | E/O | Due to Restore Switching By Hand | 6 | 1.1 | Power interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Khulna Central-2 | 2023-09-01 13:40 | 2023-09-01 14:20 | 0:40 | T | Distance Trip, Zone-2 | 6 | 4 | Power interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-NWPGCL | 2023-09-01 18:54 | 2023-09-02 13:50 | 18:56 | E/O | Due to DS climp flashing | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-NWPGCL | 2023-09-15 08:43 | 2023-09-15 11:20 | 2:37 | E/O | Redhot Remove. | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Goalpara-Orion | 2023-09-01 14:11 | 2023-09-01 14:26 | 0:15 | E/O | Due to Restore Switching By Hand | 6 | 1.5 | Power interruption
Khulna (C) 132/33kV Grid Sub-Station | KPCL-2 | 2023-09-01 13:40 | 2023-09-01 14:32 | 0:52 | T | Faulty | 0 | 0 | No interruption
Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-01 | 2023-09-09 07:27 | 2023-09-09 12:34 | 5:07 | E/O | Bus maintenance at Patuakhali Substation. | 53 | 271.1833 | Power interruption
Payra 400/132/33kV Grid Sub-Station | Payra Patuakhali Line-02 | 2023-09-09 07:28 | 2023-09-09 12:35 | 5:07 | E/O | Bus maintenance at Patuakhali substation | 53 | 271.1833 | Power interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-2 (L-2) | 2023-09-20 14:29 | 2023-09-20 14:56 | 0:27 | T | Thundering | 0 | 0 | No interruption
|  |  | Total : | 38:35 |  | Unserved Energy: |  | 550.2167
HVDC Grid Circle :
Jhenaidah 132/33kV Grid Sub-Station | Jhenaidah-Magura 132kV Circuit-2(L6) | 2023-09-22 17:38 | 2023-09-22 18:43 | 1:05 | T | Distance Trip Z1 A-C & N, 12.59kM | 0 | 0 | No interruption
Jhenaidah 230/132kV Grid Sub-Station | Jhenaidah2-Jashore Ckt-1 | 2023-09-11 18:49 | 2023-09-11 23:45 | 4:56 | E/O | Due to Both Transformer over load. | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-09-03 13:35 | 2023-09-03 15:33 | 1:58 | E/O | only CB open | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-09-14 19:49 | 2023-09-24 14:31 | 234:42 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Pabna 132/33kV Grid Sub-Station | Pabna-Shahjadpur Line | 2023-09-26 10:18 | 2023-09-26 13:58 | 3:40 | E/O | Baghabari 230/132kV T2 Transformer S/D. | 0 | 0 | No interruption
|  |  | Total : | 246:21 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | Rangpur 132 KV Ckt1 | 2023-09-25 23:35 | 2023-09-26 00:49 | 1:14 | E/O | Red hot of Rangpur Grid SS | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-1 | 2023-09-06 05:30 | 2023-09-15 05:57 | 216:27 | E/O | With the permission of ALDC Bogura | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Bogura Ckt-2 | 2023-09-06 05:31 | 2023-09-15 05:58 | 216:27 | E/O | With the permission of ALDC Bogura | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-09-01 19:36 | 2023-09-06 05:27 | 105:51 | E/O | With the permission of NLDC. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-09-26 11:09 | 2023-09-26 17:58 | 6:49 | E/O | According to NLDC's instructions. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-09-26 20:09 | 2023-09-26 20:09 | 0:00 | E/O | According to instructions of ALDC, Bogura. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-09-26 10:57 | 2023-09-26 17:59 | 7:02 | E/O | According to NLDC's instructions. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-09-26 20:09 | 2023-09-26 20:09 | 0:00 | E/O | According to instructions of ALDC, Bogura. | 0 | 0 | No interruption
Jaldhaka 132/33kV Grid Sub-Station | Saidpur-Jaldhaka Ckt-01 | 2023-09-24 08:35 | 2023-09-24 09:17 | 0:42 | T | Due to heavy Rain and Thundering. | 0 | 0 | No interruption
Mithapukur 132/33kV Grid Sub-Station | Palashbari-2 | 2023-09-08 09:12 | 2023-09-08 11:09 | 1:57 | E/O | Only CB open | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | Bogura-1 | 2023-09-25 16:55 | 2023-09-25 17:04 | 0:09 | T | Weather is cloudy and thundering and havy rain fail. | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-01 | 2023-09-04 09:12 | 2023-09-04 11:55 | 2:43 | E/O | Palashbari-Mahasthangarh 132 kv line Ckt-1 "R" Phase Armaring Tower no (322-323). | 25 | 67.9167 | Power interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-01 | 2023-09-08 11:11 | 2023-09-08 11:47 | 0:36 | E/O | Due to emergency maint.work | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-02 | 2023-09-08 11:11 | 2023-09-08 11:47 | 0:36 | E/O | None | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mithapukur-01 | 2023-09-08 09:10 | 2023-09-08 11:10 | 2:00 | E/O | CB open | 0 | 0 | No interruption
Purbasadipur 132/33kV Grid Sub-Station | Saidpur Line-1 | 2023-09-24 04:03 | 2023-09-24 06:56 | 2:53 | T | Heavy Thundering | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Natore-1 | 2023-09-17 06:30 | 2023-09-17 08:42 | 2:12 | E/O | As per NLDC guidelines | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-GTPS | 2023-09-17 11:37 | 2023-09-17 13:16 | 1:39 | E/O | CT Maintenance | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Kurigram | 2023-09-26 06:44 | 2023-09-26 07:27 | 0:43 | T | None | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Lalmonirhat | 2023-09-26 06:44 | 2023-09-26 07:16 | 0:32 | T | None | 0 | 0 | No interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-1 | 2023-09-23 14:31 | 2023-09-23 14:37 | 0:06 | T | Tripped showing C phase Distance relay relays. | 11 | 1.1 | Power interruption
Rangpur 132/33kV Grid Sub-Station | Rangpur-Saidpur-2 | 2023-09-23 14:31 | 2023-09-23 14:38 | 0:07 | T | Tripped showing C phase Distance relay relays. | 11 | 1.2833 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-09-26 17:59 | 2023-09-26 20:08 | 2:09 | E/O | In Baghabari 230/132kV S/S T-01 has taken shutdown for this reason ALDC,Bogura request to CB open | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Shahjadpur | 2023-09-26 18:00 | 2023-09-26 20:08 | 2:08 | E/O | In Baghabari 230/132kV S/S T-01 has taken shutdown for this reason ALDC,Bogura request to CB open | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-09-04 17:55 | 2023-09-06 05:29 | 35:34 | E/O | only CB is open by the instruction of AE, NLDC. | 0 | 0 | No interruption
|  |  | Total : | 610:36 |  | Unserved Energy: |  | 70.3
Others :
Ashuganj 230/132/33kV Sub-Station | South-2(230kv) | 2023-09-09 12:14 | 2023-09-09 16:51 | 4:37 | E/O | maintenance work of ground wire. | 0 | 0
|  |  | Total : | 4:37 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 1340:34 | Hours
T = Tripping
E/O = Emergency Outage | [6 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month: September 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-09-06 10:10 | 2023-09-06 14:20 | 4:10 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-09-09 11:10 | 2023-09-09 15:48 | 4:38 | S/O | String repairing | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-09-15 06:38 | 2023-09-15 08:46 | 2:08 | S/O | Loop repairing work | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 132 kv Bus 01 | 2023-09-22 06:58 | 2023-09-22 16:46 | 9:48 | S/O | DS maintanence | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 LT | 2023-09-10 10:56 | 2023-09-10 15:11 | 4:15 | S/O | Red hot maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 LT | 2023-09-09 11:13 | 2023-09-09 12:53 | 1:40 | S/O | Isolatir repairing | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2023-09-02 08:35 | 2023-09-02 11:48 | 3:13 | S/O | Redhot Manitenance With Bus loop Change | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 LT | 2023-09-06 09:47 | 2023-09-06 14:12 | 4:25 | S/O | Maintenance | 0 | 0 | No interruption
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 LT | 2023-09-22 07:04 | 2023-09-22 17:07 | 10:03 | S/O | DS maintanence | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | 132 kv Busbar-2 | 2023-09-29 06:22 | 2023-09-29 10:37 | 4:15 | S/O | OAT-12(132kv side) Bus isolator-2 alignment problem. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | T-4 Kalabagan HT | 2023-09-23 09:11 | 2023-09-23 15:29 | 6:18 | S/O | Due to Electric pillar transfer. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 LT | 2023-09-01 06:23 | 2023-09-01 07:41 | 1:18 | S/O | conductor size measurment of 132 kv side. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 LT | 2023-09-29 06:25 | 2023-09-29 10:57 | 4:32 | S/O | OAT-12(132kv side) Bus isolator-2 alignment problem. | 0 | 0 | No interruption
Dhamrai 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-09-20 06:29 | 2023-09-20 09:25 | 2:56 | S/O | Red-hot maintenance work | 0 | 0 | No interruption
Jamalpur 132/33kV Grid Sub-Station | T-1 LT | 2023-09-28 06:51 | 2023-09-28 09:27 | 2:36 | S/O | 33 kv T1&T2 section DS high temperature maintenance. | 50 | 130 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-2 HT | 2023-09-28 06:51 | 2023-09-28 09:27 | 2:36 | S/O | 33 kv T1&T2 section DS high temperature maintenance. | 45 | 117 | Power interruption
Jamalpur 132/33kV Grid Sub-Station | T-4 HT | 2023-09-21 15:47 | 2023-09-21 17:40 | 1:53 | S/O | sw-2 feeder d/s red hot problem. | 7 | 13.1833 | Power interruption
Joydebpur 132/33kV Grid Sub-Station | GT-3 HT | 2023-09-18 08:22 | 2023-09-18 10:14 | 1:52 | S/O | Oil Refill | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Bus-2 | 2023-09-12 06:34 | 2023-09-12 08:52 | 2:18 | S/O | RPCL 100 BUS 2 DS red hot maintenance | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-3 (426T) LT | 2023-09-11 05:35 | 2023-09-11 06:17 | 0:42 | S/O | Redhot maintenance (T3 33kv bushing) | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) HT | 2023-09-10 12:51 | 2023-09-10 14:48 | 1:57 | S/O | T5(132kv CT Y -phase redhot Maintenance, 33Kv bushing R-Phase maintenance) | 17 | 33.15 | Power interruption
Kodda 132/33kV Grid Sub-Station | Tr-5 (446T) HT | 2023-09-11 06:19 | 2023-09-11 06:55 | 0:36 | S/O | T5 33kv bushing Redhot maintenance | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-2(35/50 MVA) LT | 2023-09-09 07:44 | 2023-09-09 14:43 | 6:59 | S/O | Redhot Maintenance. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-3 (50/75 MVA) LT | 2023-09-24 12:16 | 2023-09-24 15:42 | 3:26 | S/O | 33kV Incomer CB Emergency Test. | 0 | 0 | No interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) HT | 2023-09-01 15:30 | 2023-09-01 17:40 | 2:10 | S/O | Temperature rising maintenance by mpbs | 15 | 32.5 | Power interruption
Manikganj 132/33kV Grid Sub-Station | 132/33 kV Transformer GT-4 (50/75 MVA) LT | 2023-09-23 11:02 | 2023-09-23 15:47 | 4:45 | S/O | WTI & OTI Temperature sensor change. | 0 | 0 | No interruption
Mirpur 132/33kV Grid Sub-Station | T1 HT | 2023-09-12 02:25 | 2023-09-13 18:25 | 40:00 | S/O | 132kV CB Maintenance work | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | Bus-B | 2023-09-21 10:33 | 2023-09-21 13:42 | 3:09 | S/O | PBS Shutdown. | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | T-1 HT | 2023-09-02 09:59 | 2023-09-02 17:42 | 7:43 | S/O | For hotspot maintenance. | 0 | 0 | No interruption
Sreepur 230/132/33kV Grid Sub-Station | 132/33 kV T-1 HT | 2023-09-03 13:24 | 2023-09-03 15:00 | 1:36 | S/O | PBS maintenance work | 35 | 56 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-2 HT | 2023-09-04 06:30 | 2023-09-04 07:31 | 1:01 | S/O | High temperature of HT Bussing | 20 | 20.3333 | Power interruption
Tangail 132/33kV Grid Sub-Station | Tr-3 HT | 2023-09-23 15:48 | 2023-09-23 16:38 | 0:50 | S/O | Porabari 33kv feeder red hot | 40 | 33.3333 | Power interruption
|  |  | Total : | 149:48 |  | Unserved Energy: |  | 435.5
Dhaka (South) Grid Circle : | [10 empty] | 39.3333
Bhulta 132/33kV Grid Sub-Station | GT1 HT | 2023-09-23 07:13 | 2023-09-23 13:12 | 5:59 | S/O | Red hot maintenance for GT1 Tx. | 70 | 418.8333 | Power interruption
Charsaidpur 132/33kV Sub-Station | 132/33 kV GT-1 HT | 2023-09-25 09:40 | 2023-09-25 20:02 | 10:22 | S/O | for maintainance work | 0 | 0 | No interruption
Charsaidpur 132/33kV Sub-Station | 132/33 kV GT-2 HT | 2023-09-27 09:15 | 2023-09-27 17:50 | 8:35 | S/O | yearly maintenance | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132/33 kV GT-1 LT | 2023-09-17 09:23 | 2023-09-17 17:19 | 7:56 | S/O | Annual Maintenence | 0 | 0 | No interruption
Fatullah 132/33kV Grid Sub-Station | 132/33 kV GT-2 HT | 2023-09-19 09:39 | 2023-09-19 15:54 | 6:15 | S/O | Annual Maintenence | 0 | 0 | No interruption
Gulshan 132/33kV Grid Sub-Station | MT-1 HT | 2023-09-08 07:20 | 2023-09-08 09:42 | 2:22 | S/O | Red Hot Maintenance of Transformer MT-1 | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Bus-1 | 2023-09-14 09:49 | 2023-09-14 12:28 | 2:39 | S/O | Conductor and Clamp connector Change (Meghnaghat-1 and Bhulta-1) | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | 132KV Main Bus | 2023-09-20 16:35 | 2023-09-20 21:22 | 4:47 | S/O | Red hot maintenance | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus2 | 2023-09-22 08:51 | 2023-09-22 14:33 | 5:42 | S/O | As per request of meghnaghat power limited | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Bus2 | 2023-09-26 08:53 | 2023-09-26 14:12 | 5:19 | S/O | Busbar-2 shutdown for rectification of high temperature of ST bay Bus-2 DS-839S(Y phase) | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-1 LT | 2023-09-18 06:25 | 2023-09-18 08:25 | 2:00 | S/O | 33 kv Side D/S Fingure Change | 0 | 0 | No interruption
Narshingdi 132/33kV Grid Sub-Station | T-3 LT | 2023-09-18 21:36 | 2023-09-18 23:45 | 2:09 | S/O | à¦Ÿà¦¿-à§©, à§©à§©à¦•à§‡à¦­à¦¿ à¦‡à¦¨à¦•à¦¾à¦®à¦¿à¦‚ à¦²à¦¾à¦‡à¦¨ à¦¡à¦¿à¦à¦¸ à¦¹à¦Ÿà¦¸à§à¦ªà¦Ÿà¦¸ à¦®à§‡à¦‡à¦¨à§à¦Ÿà§‡à¦¨à§‡à¦¨à§à¦¸ à¥¤ | 0 | 0 | No interruption
Nawabganj 132/33kV Grid Sub-Station | 33kV Bus Section-2 | 2023-09-19 17:15 | 2023-09-19 18:07 | 0:52 | S/O | 33kV Kushumhati Feeder clamp maintenance. S/D taken by DPBS-2. | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 HT | 2023-09-02 05:42 | 2023-09-02 08:57 | 3:15 | S/O | Hot spot maintenance | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 HT | 2023-09-01 05:46 | 2023-09-01 08:44 | 2:58 | S/O | Red Hot Maintenance | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | T-1 LT | 2023-09-15 06:02 | 2023-09-15 10:59 | 4:57 | S/O | Maintenance work | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS A | 2023-09-19 11:19 | 2023-09-19 17:05 | 5:46 | S/O | Corrective maintenance work for Bashundhara line. Work done by Bashundhara. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | BUS B | 2023-09-20 10:26 | 2023-09-20 13:51 | 3:25 | S/O | Basundhara Line-132kv Bus-B Maintenance work. | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | 33 kV bus | 2023-09-16 06:53 | 2023-09-16 08:33 | 1:40 | S/O | à§©à§§ à¦•à§‡à¦­à¦¿ à¦¬à¦¾à¦¸ à¦•à¦¾à¦ªà¦²à¦¾à¦° à¦†à¦‡à¦¸à§‹à¦²à§‡à¦Ÿà¦° à¦°à§‡à¦¡à¦¹à¦Ÿ à¦à¦° à¦¸à¦‚à¦°à¦•à§à¦·à¦£ à¦•à¦¾à¦œ à¦®à§à¦¨à§à¦¸à¦¿à¦—à¦žà§à¦œ à¦ªà¦²à§à¦²à¦¿à¦¬à¦¿à¦¦à§à¦¯à§à§Ž à¦•à¦°à§à¦¤à§ƒà¦• à¦¬à¦¾à¦¸à§à¦¤à¦¬à¦¾à§Ÿà¦¨à¥¤ | 0 | 0 | No interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 HT | 2023-09-16 06:53 | 2023-09-16 08:30 | 1:37 | S/O | Due to red hot maintenance at 33kV bus isolator | 50 | 80.8333 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-01 LT | 2023-09-05 15:47 | 2023-09-05 16:58 | 1:11 | S/O | Due to red hot maintenance at 4 no feeder bus side of pbs. | 25.5 | 30.175 | Power interruption
Srinagar 132/33kV Grid Sub-Station | Tr-02 HT | 2023-09-16 06:54 | 2023-09-16 08:31 | 1:37 | S/O | Due to red hot maintenance at 33kV bus isolator | 25.5 | 41.225 | Power interruption
Uttara 132/33kV Grid Sub-Station | GT-01 LT | 2023-09-05 09:59 | 2023-09-05 12:02 | 2:03 | S/O | OTI damage | 0 | 0 | No interruption |  | 39.3333
|  |  | Total : | 93:26 |  | Unserved Energy: |  | 571.0667
Chattogram Grid Circle :
Bakulia 132/33kV Grid Sub-Station | Bus-A | 2023-09-08 09:12 | 2023-09-08 10:06 | 0:54 | D/W | None | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bus-A | 2023-09-14 09:30 | 2023-09-14 12:35 | 3:05 | D/W | For loop connection of C.B-632B | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | T-3 (422T) LT | 2023-09-23 06:06 | 2023-09-23 09:32 | 3:26 | S/O | T-03 y-phase Loop change work. | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | MAIN BUS-1 | 2023-09-20 09:40 | 2023-09-20 11:52 | 2:12 | S/O | Main bus 1 (kaptai ckt 01 bay incoming) | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | MAIN BUS-1 | 2023-09-21 16:37 | 2023-09-21 17:01 | 0:24 | D/W | Due to project work | 18 | 7.2 | Power interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2023-09-06 09:14 | 2023-09-06 11:37 | 2:23 | S/O | High Temperature Maintenance Work | 0 | 0 | No interruption
Chandraghona 132/33kV Grid Sub-Station | TR-01(406T) HT | 2023-09-21 16:37 | 2023-09-21 17:01 | 0:24 | D/W | Due to project work | 18 | 7.2 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-09-08 09:59 | 2023-09-08 11:13 | 1:14 | S/O | Fir 33KV PBS keranihut redhot maintenance | 30 | 37 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Power Transformer -T-2 HT | 2023-09-14 17:40 | 2023-09-14 18:55 | 1:15 | S/O | Shutdown taken by 33KV Keranihut PBS | 39 | 48.75 | Power interruption
GPH 230/33kV Grid Sub-Station | Transformer -2 (D07) HT | 2023-09-15 10:04 | 2023-09-15 14:38 | 4:34 | S/O | winding | 8 | 36.5333 | Power interruption
Halishahar 132/33kV Grid Sub-Station | 403T(TR-1) HT | 2023-09-09 09:58 | 2023-09-09 11:29 | 1:31 | S/O | Due to 33kV Side Red Hot maintenance by BPDB | 0 | 0 | No interruption
Halishahar 132/33kV Grid Sub-Station | 413T(TR-2) HT | 2023-09-09 11:36 | 2023-09-09 12:38 | 1:02 | S/O | TR LT side loop nut bolt red hot work by BPDB | 0 | 0 | No interruption
Hathazari 230/132/33kV Grid Sub-Station | T-01 HT | 2023-09-09 07:50 | 2023-09-09 17:46 | 9:56 | S/O | 33kv side new DS commissioning by REB. | 35 | 347.6667 | Power interruption
Madunaghat 132/33kV Grid Sub-Station | T-2 33kV BUS | 2023-09-16 11:14 | 2023-09-16 11:59 | 0:45 | S/O | Mohora-3 33kv feeder, BPDB source end DS maintenance work by BPDB | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2023-09-28 09:31 | 2023-09-28 20:01 | 10:30 | D/W | EGCB Bay Extension Project work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | TR-1, 718T HT | 2023-09-30 09:28 | 2023-09-30 17:19 | 7:51 | D/W | EGCB PROJECT WORK | 0 | 0 | No interruption
TK chemical 132kV Grid Sub-Station | 48/64MVA T-2(415T) HT | 2023-09-12 14:25 | 2023-09-12 15:35 | 1:10 | S/O | Earthing connection | 0 | 0 | No interruption
|  |  | Total : | 52:36 |  |  |  | 484.35
Cumilla Grid Circle :
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 LT | 2023-09-13 06:07 | 2023-09-13 09:48 | 3:41 | S/O | red hot remove | 0 | 0 | No interruption
Cumilla(S) 132/33kV Grid Sub-Station | TR-4 HT | 2023-09-18 09:31 | 2023-09-18 11:03 | 1:32 | S/O | same | 10 | 15.3333 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-1 HT | 2023-09-24 11:58 | 2023-09-24 13:27 | 1:29 | S/O | Red hot maintenance for 33KV Feeder of REB | 20 | 29.6667 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 HT | 2023-09-01 10:14 | 2023-09-01 11:27 | 1:13 | S/O | Red hot maintenance by PBD. | 12 | 14.6 | Power interruption
Kulaura 132/33kV Grid Sub-Station | TR-2 LT | 2023-09-24 11:56 | 2023-09-24 13:27 | 1:31 | S/O | Red hot maintenance for 33KV Feeder of REB | 20 | 30.3333 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-09-08 08:18 | 2023-09-08 09:50 | 1:32 | S/O | D/S 189A Y phase Riser Hotspot Maintenece work | 30 | 46 | Power interruption
Shahjibazar 132/33kV Grid Sub-Station | TR-04 HT | 2023-09-25 06:41 | 2023-09-25 08:54 | 2:13 | S/O | PBS 33KV Bus Coupler red hot Maintenance. Shutdown taken by PBS. | 0 | 0 | No interruption
|  |  | Total : | 13:11 |  | Unserved Energy: |  | 135.9333
Khulna Grid Circle : | [9 empty] | 251.2167
Barishal 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-09-14 08:30 | 2023-09-14 09:42 | 1:12 | S/O | WZ 33KV Jhalokathi feeder post insulator break down on 33kv bus and maintenance | 20 | 24 | Power interruption | 113.55
Barishal 132/33kV Grid Sub-Station | T-1 (405T) LT | 2023-09-21 06:50 | 2023-09-21 07:55 | 1:05 | S/O | 33kV Bus red hot maintenance | 15 | 16.25 | Power interruption
Barishal 132/33kV Grid Sub-Station | T-2 (415T) LT | 2023-09-25 09:49 | 2023-09-25 10:48 | 0:59 | S/O | Removal of high temperature. | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | 230kV BUS | 2023-09-27 14:42 | 2023-09-27 16:14 | 1:32 | D/W | Protection work of GIS | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | ATR-1 HT | 2023-09-27 15:47 | 2023-09-27 17:19 | 1:32 | D/W | project work | 0 | 0 | No interruption | 364.7667
Barishal 230/132kV Grid Sub-Station | ATR-2 LT | 2023-09-23 02:45 | 2023-09-23 02:45 | 0:00 | S/O | OLTC PRD maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | ATR-2 LT | 2023-09-23 02:46 | 2023-09-23 09:20 | 6:34 | S/O | PRD (OLTC) maintenance | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-4 LT | 2023-09-23 08:08 | 2023-09-23 09:46 | 1:38 | S/O | Red Hot Maintenance of Babuganj 33 kV DS | 0 | 0 | No interruption
Barishal 230/132kV Grid Sub-Station | T-5 LT | 2023-09-12 15:12 | 2023-09-12 17:10 | 1:58 | S/O | Red Hot Maintenance by PBS-1 | 50 | 98.3333 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-1 LT | 2023-09-07 07:45 | 2023-09-07 09:57 | 2:12 | S/O | High temperature maintenance | 7.5 | 16.5 | Power interruption
Bhandaria 132/33kV Grid Sub-Station | Transformer-2 LT | 2023-09-01 10:40 | 2023-09-01 11:45 | 1:05 | S/O | WZPDCL bhandaria taken SD | 15 | 16.25 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-09-06 11:04 | 2023-09-06 17:43 | 6:39 | S/O | Due to maint.work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-09-02 10:39 | 2023-09-02 20:03 | 9:24 | S/O | Due to maint.work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-09-16 07:25 | 2023-09-16 09:56 | 2:31 | S/O | 33 kv Bus Redhot Problem. | 50 | 125.8333 | Power interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-09-06 09:27 | 2023-09-06 10:55 | 1:28 | D/W | Due to project work | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | Transformer-3 LT | 2023-09-06 12:06 | 2023-09-06 13:56 | 1:50 | D/W | Due to project work | 0 | 0 | No interruption
Goalpara 132/33kV Grid Sub-Station | Bus 1 | 2023-09-02 08:42 | 2023-09-02 13:28 | 4:46 | S/O | Y- phase loop change breaker to bus -1 B- phase Clamp change breaker to bus -1 on NWPGCL line. | 0 | 0 | No interruption
Gopalganj 132/33kV Grid Sub-Station | T1 LT | 2023-09-14 07:14 | 2023-09-14 14:10 | 6:56 | S/O | Red hot maintenance (bpbs-1) | 12 | 83.2 | Power interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-09-02 09:09 | 2023-09-02 17:46 | 8:37 | D/W | Due to project work | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | ATR-02 LT | 2023-09-03 10:06 | 2023-09-03 17:59 | 7:53 | D/W | Due to project work | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | 230 KV Main Bus 1 | 2023-09-30 09:40 | 2023-09-30 09:40 | 0:00 | S/O | Due to GIS Bay Extension Piling Work by NWPGCL Project | 0 | 0 | No interruption
Khulna(S) 230/132kV Grid Sub-Station | TR-3 HT | 2023-09-02 12:17 | 2023-09-02 13:35 | 1:18 | S/O | Red Hot Removed Work | 0 | 0 | No interruption
Madaripur 132/33kV Grid Sub-Station | T1-405T HT | 2023-09-16 21:26 | 2023-09-16 22:05 | 0:39 | S/O | Takehat-01 source ds & 33kv wz feeder load ds red hot maintenance | 50 | 32.5 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T2-415T LT | 2023-09-18 09:21 | 2023-09-18 17:35 | 8:14 | S/O | Red Hot maintenance source DS B -phase 33KV Agailjhara Feeder Barishal PBS-2 | 17 | 139.9667 | Power interruption
Madaripur 132/33kV Grid Sub-Station | T3-426T LT | 2023-09-21 15:22 | 2023-09-21 17:50 | 2:28 | S/O | Due to project work | 0 | 0 | No interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-09-01 07:24 | 2023-09-01 09:37 | 2:13 | S/O | Red hot maintenance for 33 kV Feeder no-01 Source side DS (Y- phase). | 23 | 50.9833 | Power interruption
Narail 132/33kV Grid Sub-Station | TR1 (403-T) LT | 2023-09-23 13:04 | 2023-09-23 14:42 | 1:38 | S/O | 33 kv ( Tr-01) R phase top end DS red hot maintenance work. | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-4 LT | 2023-09-24 06:39 | 2023-09-24 08:34 | 1:55 | S/O | 436B (T4A) CB Top side high temperature measurement. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Generator Transformer-1 (GT-1) HT | 2023-09-15 10:31 | 2023-09-18 18:28 | 79:57 | D/W | For maintenance. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 HT | 2023-09-03 14:33 | 2023-09-03 18:08 | 3:35 | S/O | CT Testing of 230 KV Side. | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-1 HT | 2023-09-04 14:35 | 2023-09-04 17:06 | 2:31 | D/W | LCC panel Cable termination | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | ICT-2 LT | 2023-09-05 15:21 | 2023-09-05 17:40 | 2:19 | D/W | Relay Check | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Start-Up Transformer (SUT) HT | 2023-09-23 05:17 | 2023-09-23 10:51 | 5:34 | D/W | internal work | 0 | 0 | No interruption
Rampal 400/230kV Grid Sub-Station | Start-Up Transformer (SUT) HT | 2023-09-25 09:29 | 2023-09-25 15:29 | 6:00 | D/W | Cable Termination Testing | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | T-4 HT | 2023-09-30 10:25 | 2023-09-30 10:25 | 0:00 | S/O | T1 & T2 Transformer Full Load Charged. | 0 | 0 | No interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T HT | 2023-09-14 07:17 | 2023-09-14 09:09 | 1:52 | S/O | Red Hot Maintenance by PBS | 10 | 18.6667 | Power interruption
Shariatpur 132/33kV Grid Sub-Station | T2-416T LT | 2023-09-14 07:16 | 2023-09-14 09:10 | 1:54 | S/O | Red Hot Maintenance by PBS | 10 | 19 | Power interruption
|  |  | Total : | 191:58 |  | Unserved Energy : |  | 641.4833
HVDC Grid Circle
Baghabari 230/132kV Grid Sub-Station | Bus-1 | 2023-09-03 16:09 | 2023-09-03 16:09 | 0:00 | D/W | Rooppur Bay extension work. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-2 LT | 2023-09-18 11:45 | 2023-09-20 17:50 | 54:05 | S/O | 132/33kv Tr-2 Oil Centrifuging Work. | 0 | 0 | No interruption
Bheramara(GK) 132/33kV Grid Sub-Station | TR-4 LT | 2023-09-15 11:31 | 2023-09-17 17:42 | 54:11 | S/O | Oil centrifuge | 0 | 0 | No interruption
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 LT | 2023-09-24 20:29 | 2023-09-24 22:04 | 1:35 | S/O | Red hot maintenance | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | 132 kV Bus-A | 2023-09-12 10:35 | 2023-09-12 10:35 | 0:00 | D/W | Due to Project work | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-1 LT | 2023-09-23 07:09 | 2023-09-23 08:40 | 1:31 | S/O | BSCIC 33kV Breaker,Isolator Replacement | 50 | 75.8333 | Power interruption
Jashore 132/33kV Grid Sub-Station | T-3 HT | 2023-09-09 08:29 | 2023-09-09 08:29 | 0:00 | D/W | Shifting new transformer 3 | 0 | 0 | No interruption
Jashore 132/33kV Grid Sub-Station | T-3 LT | 2023-09-09 08:28 | 2023-09-09 08:28 | 0:00 | D/W | Shifting new transformer 3 | 0 | 0 | No interruption
Magura 132/33kV Grid Sub-Station | T-3 LT | 2023-09-26 10:03 | 2023-09-26 17:16 | 7:13 | S/O | Experimental testing of T-3 | 0 | 0 | No interruption
|  |  | Total : | 118:35 |  | Unserved Energy : |  | 75.8333
Bogura Grid Circle:
Barapukuria 230/132/33kV Grid Sub-Station | 132/33 KV T-4, 444T LT | 2023-09-17 08:22 | 2023-09-17 09:34 | 1:12 | S/O | Red hot maintenance work. | 30 | 36 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-1 HT | 2023-09-13 07:18 | 2023-09-13 08:39 | 1:21 | S/O | T-1 33 KV CT connector (R-phase) red hot. | 0 | 0 | No interruption
Bogura 132/33kV Grid Sub-Station | Transformer-2 HT | 2023-09-02 07:22 | 2023-09-02 09:06 | 1:44 | S/O | High temperature of 33KV DS Loop. (Y-Phase) | 15 | 26 | Power interruption
Bogura 132/33kV Grid Sub-Station | Transformer-3 HT | 2023-09-28 08:13 | 2023-09-28 10:25 | 2:12 | S/O | Junction point tightening work | 30 | 66 | Power interruption
Bogura 230/132kV Grid Sub-Station | 230KV Main 2 | 2023-09-01 05:50 | 2023-09-01 10:14 | 4:24 | S/O | Isolator change | 0 | 0 | No interruption
Chapai 132/33kV Grid Sub-Station | Main Bus | 2023-09-25 06:35 | 2023-09-25 09:30 | 2:55 | S/O | Main Bus S/D for Red hot maintenance | 28 | 81.6667 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-1 (405T) HT | 2023-09-25 06:05 | 2023-09-25 09:33 | 3:28 | S/O | Main Bus S/D for Red hot maintenance. | 10 | 34.6667 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-2 (415T) HT | 2023-09-25 06:07 | 2023-09-25 09:33 | 3:26 | S/O | Main Bus S/D for Red hot maintenance | 9 | 30.9 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-3 (425T) HT | 2023-09-25 06:07 | 2023-09-25 09:35 | 3:28 | S/O | Main Bus S/D for Red hot maintenance | 9 | 31.2 | Power interruption
Chapai 132/33kV Grid Sub-Station | T-4 (435T) HT | 2023-09-25 06:08 | 2023-09-25 09:35 | 3:27 | S/O | Main Bus S/D for Red hot maintenance | 0 | 0 | No interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-3 (427 T) HT | 2023-09-22 06:14 | 2023-09-22 10:04 | 3:50 | S/O | Development Work implementation by Joypurhat PBS | 9 | 34.5 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-3 (427 T) LT | 2023-09-23 06:16 | 2023-09-23 09:25 | 3:09 | S/O | Development Work implementation by Joypurhat PBS | 7 | 22.05 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) HT | 2023-09-22 06:15 | 2023-09-22 10:05 | 3:50 | S/O | Development Work implementation by Joypurhat PBS | 9 | 34.5 | Power interruption
Joypurhat 132/33kV Grid Sub-Station | Transformer T-4 (437 T) LT | 2023-09-23 06:17 | 2023-09-23 09:26 | 3:09 | S/O | Development Work implementation by Joypurhat PBS | 7 | 22.05 | Power interruption
Natore 132/33kV Grid Sub-Station | TR-3 (425 T) LT | 2023-09-27 06:56 | 2023-09-27 09:48 | 2:52 | S/O | Conductor loop change. | 0 | 0 | No interruption
Natore 132/33kV Grid Sub-Station | TR-4 (435 T) HT | 2023-09-09 11:31 | 2023-09-09 17:45 | 6:14 | S/O | Oil changing of OLTC | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | LV 132 KV BUS | 2023-09-07 11:14 | 2023-09-08 17:32 | 30:18 | D/W | Rohanpur 400/132 kV Grid 132 kVside Relay Test | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 33 kV T-1 Bus | 2023-09-13 07:27 | 2023-09-13 11:40 | 4:13 | S/O | T-1 33KV BUS PT Change. | 12 | 50.6 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-1(405T) HT | 2023-09-13 07:27 | 2023-09-13 11:39 | 4:12 | S/O | T-1 33KV BUS PT Change. | 12 | 50.4 | Power interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-2(415T) HT | 2023-09-14 07:06 | 2023-09-14 08:32 | 1:26 | S/O | Redhot maintenance work at 33 kv CT & CB connector. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | Transformer T-3 (425T) HT | 2023-09-03 16:01 | 2023-09-03 18:20 | 2:19 | S/O | Transformer T-3 132/33 KV, (80/120MVA). 33KV Bus DS (T-3 Bus Section-1 & 2 ) Maintenance Work. | 30 | 69.5 | Power interruption
Rajshahi 230/132/33kV Grid Sub-Station | 132/33 kV T-01 (406T) HT | 2023-09-24 08:16 | 2023-09-24 09:46 | 1:30 | S/O | Due maint.work | 0 | 0 | No interruption
Rajshahi 230/132/33kV Grid Sub-Station | 33 kV BUS | 2023-09-24 08:16 | 2023-09-24 09:47 | 1:31 | S/O | Due maint.work | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-01 HT | 2023-09-23 13:50 | 2023-09-23 16:20 | 2:30 | S/O | Black start test | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-2 (404T) LT | 2023-09-27 10:24 | 2023-09-27 12:26 | 2:02 | S/O | 33 KV Nilphamari -01 incoming isolator red hot | 0 | 0 | No interruption
Saidpur 132/33kV Grid Sub-Station | TR-4 (414T) LT | 2023-09-23 11:28 | 2023-09-23 14:02 | 2:34 | S/O | Red hot maintenance of 33 kV incoming isolator. | 10 | 25.6667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | Main Bus | 2023-09-15 06:30 | 2023-09-15 09:29 | 2:59 | D/W | Sirajgonj 132kV BUS shutdown for g2g project work | 90 | 268.5 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T1-(415) LT | 2023-09-15 06:12 | 2023-09-15 11:12 | 5:00 | D/W | Sirajgonj 132kV BUS shutdown for g2g project | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T2-(425) LT | 2023-09-15 06:02 | 2023-09-15 09:35 | 3:33 | D/W | Sirajgonj 132kV BUS shutdown for g2g project | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) HT | 2023-09-30 07:30 | 2023-09-30 09:32 | 2:02 | D/W | None | 3 | 6.1 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T3-(435) LT | 2023-09-29 06:08 | 2023-09-29 14:01 | 7:53 | D/W | To Changed T-3 & T-4 33KV BUS Section work | 18 | 141.9 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-09-15 06:04 | 2023-09-15 11:02 | 4:58 | D/W | Sirajgonj 132kV BUS shutdown for g2g project | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) HT | 2023-09-30 07:30 | 2023-09-30 09:40 | 2:10 | D/W | Due maint.work | 9 | 19.5 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-09-29 06:08 | 2023-09-29 14:01 | 7:53 | D/W | To Changed T-3 & T-4 33KV BUS Section work | 20 | 157.6667 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | T4-(445) LT | 2023-09-30 07:29 | 2023-09-30 07:29 | 0:00 | D/W | Due to project work | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | T-2(412T) HT | 2023-09-15 07:13 | 2023-09-15 08:55 | 1:42 | S/O | T-2 Incoming Breaker B-Phase Red Hot | 0 | 0 | No interruption
|  |  | Total : | 141:26 |  | Unserved Energy : |  | 1209.3667
Others :Nil
|  |  | Total : | 0:00 |  |  |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 761:00 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month: September 2023
Name of the Sub-station | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
|  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Aminbazar 400/230/132kV Grid Sub-Station | Kallyanpur-02 | 2023-09-15 06:58 | 2023-09-15 10:18 | 3:20 | S/O | Hot sport repairing | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-1 | 2023-09-11 08:52 | 2023-09-11 16:19 | 7:27 | D/W | 132 KV GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Ghorashal 132 kV Ckt-2 | 2023-09-13 08:15 | 2023-09-13 16:31 | 8:16 | D/W | GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2023-09-04 06:24 | 2023-09-04 17:10 | 10:46 | D/W | 132kv GIS S/S Work Purpose. | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-1 | 2023-09-22 08:22 | 2023-09-22 15:01 | 6:39 | D/W | GIS project work | 0 | 0 | No interruption
Ashuganj 230/132/33kV Sub-Station | Kishoreganj 132 kV Ckt-2 | 2023-09-23 08:52 | 2023-09-23 18:53 | 10:01 | S/O | Due to GIS project works. | 0 | 0 | No interruption
Kallyanpur 132/33kV Grid Sub-Station | 132Kv Kallyanpur-Aminbazar Ckt-01 | 2023-09-15 10:21 | 2023-09-15 17:35 | 7:14 | S/O | For loop changing work. | 0 | 0 | No interruption
Kodda 132/33kV Grid Sub-Station | RPCL 100 MW PS | 2023-09-12 06:28 | 2023-09-12 09:03 | 2:35 | S/O | Red hot maintenance of Bus 2 DS | 70 | 180.8333 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-1 | 2023-09-01 15:41 | 2023-09-01 17:14 | 1:33 | S/O | Temprature rising Maintenance by mps | 15 | 23.25 | Power interruption
Manikganj 132/33kV Grid Sub-Station | Manikganj- Kabirpur CKT-2 | 2023-09-09 09:31 | 2023-09-09 13:01 | 3:30 | S/O | Redhot Maintenance. | 0 | 0 | No interruption
Mymensingh 132/33kV Grid Sub-Station | Mymensingh-Kishoreganj Ckt-2 | 2023-09-09 14:16 | 2023-09-09 15:13 | 0:57 | S/O | Due to ROW Safety Purposes of 132kV -Mymensingh-Kish Liner Tower No 282 | 0 | 0 | No interruption
Savar 132/33kV Grid Sub-Station | 132kV Manikganj PS-Savar Ckt-2 | 2023-09-02 10:10 | 2023-09-02 17:32 | 7:22 | S/O | For Hotspot maintenance. | 0 | 0 | No interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-09-29 08:41 | 2023-09-29 16:27 | 7:46 | D/W | Due to maint.work | 90 | 699 | Power interruption
Tangail 132/33kV Grid Sub-Station | Kaliakair-2 | 2023-09-30 06:40 | 2023-09-30 13:18 | 6:38 | D/W | project work at mirzapur S/S | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-09-09 16:15 | 2023-09-09 18:59 | 2:44 | S/O | High Temperature Maintenance Work at Overhead line DS. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-1 | 2023-09-18 10:05 | 2023-09-18 15:50 | 5:45 | S/O | Tree trimming. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Basundhara Ckt-2 | 2023-09-20 09:33 | 2023-09-20 16:14 | 6:41 | S/O | Line maintanace | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Dhaka Metro Rail Ckt | 2023-09-12 13:20 | 2023-09-12 14:50 | 1:30 | D/W | Metering work. | 0 | 0 | No interruption
Tongi 230/132/33kV Grid Sub-Station | Tongi-Dhaka Metro Rail Ckt | 2023-09-22 10:59 | 2023-09-22 12:52 | 1:53 | S/O | PT Connection Test | 0 | 0 | No interruption
|  |  | Total : | 102:37 |  | Unserved Energy: |  | 903.0833
Dhaka (South) Grid Circle :
Bhulta 132/33kV Grid Sub-Station | Narsingdi | 2023-09-23 06:50 | 2023-09-23 09:10 | 2:20 | S/O | Red hot maintenance for Narsingdi Circuit. | 0 | 0 | Power interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-1 | 2023-09-08 07:04 | 2023-09-08 23:40 | 16:36 | S/O | maintenance work. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2023-09-16 06:58 | 2023-09-16 21:04 | 14:06 | S/O | two conductor change of tension tower to gentry at Meghnaghat sub-station. | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Meghnaghat-2 | 2023-09-24 12:58 | 2023-09-24 18:12 | 5:14 | S/O | Red-hot maintenance at wavetrap (Y-Phase) | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-09-03 06:12 | 2023-09-03 18:04 | 11:52 | S/O | Ordered by NLDC | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-09-05 06:09 | 2023-09-07 16:24 | 58:15 | S/O | from Other end | 0 | 0 | No interruption
Haripur 230/132kV Grid Sub-Station | Ullon (Maniknagar-2) | 2023-09-21 05:50 | 2023-09-21 05:50 | 0:00 | S/O | Work at another side. | 0 | 0 | No interruption
Keranigonj 230/132/33kV Grid Sub-Station | Lalbagh-3 | 2023-09-29 06:42 | 2023-09-29 09:02 | 2:20 | S/O | High temperature maintenance. | 0 | 0 | No interruption
Madanganj 132/33kV Grid Sub-Station | Madanganj -Munshiganj 132 kv Ckt-2 | 2023-09-30 08:51 | 2023-09-30 08:51 | 0:00 | S/O | Piling work done by RHD | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2023-09-05 06:28 | 2023-09-07 15:40 | 57:12 | S/O | Shutdown due to 6 Lan extension work(Tower Dismantled) by DPDC | 0 | 0 | No interruption
Maniknagar 132/33kV Grid Sub-Station | Haripur Ckt-2 | 2023-09-21 06:12 | 2023-09-24 19:12 | 85:00 | S/O | Tower maintenance work of DPDC | 0 | 0 | No interruption
Munshiganj 132/33kV Grid Sub-Station | Madanganj- Munshiganj- Ckt-2 | 2023-09-30 08:51 | 2023-09-30 23:50 | 14:59 | S/O | Due to Piling work done by RHD. | 0 | 0 | No interruption
Meghnaghat 230/132kV Grid Sub-Station | Meghnaghat-Haripur-01 | 2023-09-14 09:40 | 2023-09-14 12:57 | 3:17 | S/O | As per request of NLDC | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Gulshan Ckt-02 | 2023-09-06 07:10 | 2023-09-07 00:15 | 17:05 | S/O | Due to maint.work | 0 | 0 | No interruption
Rampura 230/132kV Grid Sub-Station | Ullon-01 | 2023-09-19 10:45 | 2023-09-20 16:44 | 29:59 | S/O | Work at Ullon end. | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT1 | 2023-09-10 14:34 | 2023-09-10 21:18 | 6:44 | S/O | Schedule maintenance done by EGCB | 0 | 0 | No interruption
Siddhirganj 132/33kV Grid Sub-Station | 120MW EGCB GT2 | 2023-09-11 09:50 | 2023-09-11 14:07 | 4:17 | S/O | Schedule Maintenance work by EGCB. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 1 | 2023-09-30 10:19 | 2023-09-30 17:18 | 6:59 | S/O | ST Transformer schedele check for EGCB end. | 0 | 0 | No interruption
Siddhirganj 230/132kV Grid Sub-Station | 335MW EGCB 2 | 2023-09-29 09:51 | 2023-09-29 16:21 | 6:30 | S/O | ST Transformer schedele check for EGCB end. | 0 | 0 | No interruption
Sonargaon 132/33kV Grid Sub-Station | Bus-Coupler | 2023-09-20 10:25 | 2023-09-20 13:29 | 3:04 | S/O | Basundha Line -132 kv Bus-B Maintenance Work. | 0 | 0 | No interruption
|  |  | Total : | 345:49 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
BSRM 230/33kV Grid Sub-Station | Mirsarai Ckt-2 | 2023-09-27 10:01 | 2023-09-27 15:19 | 5:18 | S/O | Deadline Checking. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Kulshi Ckt | 2023-09-13 12:45 | 2023-09-13 17:08 | 4:23 | D/W | CB-632B replacement work. | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-01 | 2023-09-02 14:48 | 2023-09-02 16:40 | 1:52 | D/W | Breaker 605B commissioning work | 0 | 0 | No interruption
Bakulia 132/33kV Grid Sub-Station | Bakalia-Sikalbaha Ckt-02 | 2023-09-07 13:10 | 2023-09-07 17:40 | 4:30 | D/W | Cb -615 Renovation work | 0 | 0 | No interruption
Baroaulia 132/33kV Grid Sub-Station | AKSPL | 2023-09-24 09:24 | 2023-09-24 12:55 | 3:31 | S/O | Due maint.work | 0 | 0 | No interruption
Coxsbazar 132/33kV Grid Sub-Station | Doh-Cox Ckt-2 | 2023-09-23 06:54 | 2023-09-23 13:35 | 6:41 | S/O | Due to Maintenance works of Dohazari main bus. | 0 | 0 | No interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-1 | 2023-09-23 07:42 | 2023-09-23 12:19 | 4:37 | D/W | Shikalbaha-02 GCB Installation. Shik-01 GCB Only open at Dohazari end. Power expressing from Shik-01 to Cox-01 line to Coxâ€™s Bazar Grid. 07:42 is the Dohazari Main BUS SD time. | 50 | 230.8333 | Power interruption
Dohazari 132/33kV Grid Sub-Station | Dohazari-Sikalbaha ckt-2 | 2023-09-23 06:51 | 2023-09-23 13:53 | 7:02 | D/W | Shikalbaha-02 GCB Installation *Power expressed through Dohazari X-fer BUS from Shikalbaha-01 to Cox'sBazar-01 line. | 50 | 351.6667 | Power interruption
Mirsorai 230/33kV Grid Sub-Station | 150 MW Power Station -02 | 2023-09-19 10:34 | 2023-09-27 15:41 | 197:07 | D/W | EGCB Bay Extention Work | 0.2 | 39.4233 | Power interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-1 | 2023-09-23 09:31 | 2023-09-23 15:15 | 5:44 | S/O | Annual maintenance (dead line checking) | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-1 | 2023-09-24 09:16 | 2023-09-24 15:04 | 5:48 | S/O | Annual maintenance | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-1 | 2023-09-25 09:27 | 2023-09-25 16:11 | 6:44 | S/O | Annual maintenance work | 0 | 0 | No interruption
Mirsorai 230/33kV Grid Sub-Station | BSRM-2 | 2023-09-26 09:30 | 2023-09-26 15:12 | 5:42 | S/O | Annual maintenance work | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-1 | 2023-09-18 09:53 | 2023-09-18 14:42 | 4:49 | S/O | due to high temperature at different point at mono pole. | 0 | 0 | No interruption
Rampur 230/132/33 kV GIS Grid Sub-Station | Khulshi-2 | 2023-09-18 14:55 | 2023-09-18 23:00 | 8:05 | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 271:53 |  | Unserved Energy: |  | 621.9233
Cumilla Grid Circle :
Chandpur 132/33kV Grid Sub-Station | 115MW CPGL Power Plant Incomer (L5) | 2023-09-05 13:15 | 2023-09-22 23:18 | 418:03 | S/O | Maintenance work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | HFPL line | 2023-09-22 06:31 | 2023-09-22 19:29 | 12:58 | D/W | ESPNERP Project work | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-01 | 2023-09-23 08:58 | 2023-09-23 20:13 | 11:15 | D/W | Chowmuhani-korerhat line stringing project work by ESPNER | 0 | 0 | No interruption
Chowmuhani 132/33kV Grid Sub-Station | Ramganj line-02 | 2023-09-23 08:58 | 2023-09-23 20:14 | 11:16 | D/W | Chowmuhani-korerhat line stringing project work by ESPNER | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-09-13 08:06 | 2023-09-13 17:46 | 9:40 | D/W | Due to GND Project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-09-16 07:36 | 2023-09-16 17:20 | 9:44 | D/W | Due to Project work | 0 | 0 | No interruption
Fenchuganj 230/132/33kV Grid Sub-Station | Sylhet-2 | 2023-09-30 07:17 | 2023-09-30 20:12 | 12:55 | D/W | Due to Project work | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | BPDB 60 MW | 2023-09-15 08:40 | 2023-09-15 15:29 | 6:49 | S/O | 952 Brekar Bus D/S connecting Rod Change | 0 | 0 | No interruption
Shahjibazar 132/33kV Grid Sub-Station | Shahjibazar-B.Baria Ckt-02 | 2023-09-15 08:40 | 2023-09-15 15:29 | 6:49 | S/O | 952 Brekar Bus D/S connecting Rod Change | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2023-09-13 08:07 | 2023-09-13 17:44 | 9:37 | D/W | South Surma Grid SS project work | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2023-09-16 07:35 | 2023-09-16 17:19 | 9:44 | D/W | Due to South Surma Line Connection | 0 | 0 | No interruption
Sylhet 132/33kV Grid Sub-Station | Sylhet-Fenchuganj SS | 2023-09-30 07:16 | 2023-09-30 07:16 | 0:00 | D/W | For South Surma GIS Grid Line LILI Purpose. | 0 | 0 | No interruption
|  |  | Total : | 518:50 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Bagerhat 132/33kV Grid Sub-Station | Bagerhat- Bhandaria | 2023-09-01 08:26 | 2023-09-01 12:51 | 4:25 | S/O | Armouring works | 0 | 0 | No interruption
Barishal 132/33kV Grid Sub-Station | 132 kv Summit power | 2023-09-03 16:15 | 2023-09-03 16:29 | 0:14 | S/O | For Summit End work, PT oil leakage. | 0 | 0 | No interruption
Faridpur 132/33kV Grid Sub-Station | 132 KV Rajbari ckt-1 | 2023-09-06 08:41 | 2023-09-06 21:12 | 12:31 | D/W | CT change. | 0 | 0 | No interruption
Gopalganj 400/132kV Grid Sub-Station | 132kV Madaripur Ckt-3 | 2023-09-05 09:25 | 2023-09-05 20:04 | 10:39 | D/W | Due to Project work | 0 | 0 | No interruption
Noapara 132/33kV Grid Sub-Station | khulna central - 1 | 2023-09-25 07:49 | 2023-09-25 19:40 | 11:51 | D/W | Noapara Khulna Central-Noapara ckt 01 loop conductor change. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | Barishal-Pautakhali 132kV Line | 2023-09-09 07:16 | 2023-09-09 12:55 | 5:39 | S/O | Maintenance work for Main Bus | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | PAYRA-PATUAKHALI CKT-2 | 2023-09-04 12:39 | 2023-09-04 13:29 | 0:50 | S/O | Gas refill work payra substation. | 0 | 0 | No interruption
Patuakhali 132/33kV Grid Sub-Station | UPPL (150MW) 132kV LINE | 2023-09-09 07:21 | 2023-09-09 12:52 | 5:31 | S/O | Maintenance for Main bus | 0 | 0 | No interruption
Rajbari 132/33kV Grid Sub-Station | Faridpur -1 | 2023-09-06 08:40 | 2023-09-06 21:07 | 12:27 | S/O | Due to Project work | 0 | 0 | No interruption
Satkhira 132/33kV Grid Sub-Station | Khulna South-2 (L-2) | 2023-09-02 07:36 | 2023-09-02 12:16 | 4:40 | S/O | Red-hot maintenance work at Khulna south substation. | 0 | 0 | No interruption
|  |  | Total : | 68:47 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
BIPTC 400/230kV Grid Sub-Station | Baharampur-2 | 2023-09-12 09:59 | 2023-09-12 23:28 | 13:29 | S/O | For Relay firmware upgradation. | 0 | 0 | No interruption
BIPTC 400/230kV Grid Sub-Station | Baharampur-2 | 2023-09-13 12:37 | 2023-09-13 16:54 | 4:17 | S/O | Line Isolator(Q9) Maintenance | 0 | 0 | No interruption
BIPTC 400/230kV Grid Sub-Station | Baharampur-4 | 2023-09-30 11:01 | 2023-09-30 18:28 | 7:27 | S/O | For replacement of broken insulator from India end | 0 | 0 | No interruption
Baghabari 230/132kV Grid Sub-Station | Baghabari- Ishurdi-2 | 2023-09-05 10:14 | 2023-09-05 17:49 | 7:35 | D/W | Busbar Stability test. | 0 | 0 | No interruption
|  |  | Total : | 32:48 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Amnura 132/33kV Grid Sub-Station | Amnura - Chapai Nawabganj | 2023-09-20 06:36 | 2023-09-25 09:39 | 123:03 | S/O | Corrective Maintenance in Chapainawabganj 132/33Kv grid Substation end. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-09-07 07:07 | 2023-09-14 05:26 | 166:19 | D/W | According to ALDC's instructions. | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-1 | 2023-09-14 08:57 | 2023-09-18 14:28 | 101:31 | D/W | With the permission of ALDC | 0 | 0 | No interruption
Bog-Sherpur 132/33kV Grid Sub-Station | Sherpur-Sirajgonj Ckt-2 | 2023-09-09 07:49 | 2023-09-14 05:26 | 117:37 | D/W | According to ALDC's instructions. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-3 | 2023-09-06 05:57 | 2023-09-06 12:13 | 6:16 | S/O | isolator replacement | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-09-01 05:50 | 2023-09-01 10:16 | 4:26 | S/O | Isolator change | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-09-04 05:49 | 2023-09-04 06:33 | 0:44 | S/O | Isolator Replacement Work. | 0 | 0 | No interruption
Bogura 230/132kV Grid Sub-Station | Bogura (W) CKT-4 | 2023-09-08 06:02 | 2023-09-08 11:42 | 5:40 | S/O | Isolator replacement | 0 | 0 | No interruption
Palashbari 132/33kV Grid Sub-Station | Mahasthangarh-01 | 2023-09-25 10:56 | 2023-09-25 11:48 | 0:52 | S/O | SPMD Working | 0 | 0 | No interruption
Rahanpur 400/132kV Grid Sub-Station | Rahanpur-Chapainawabganj 132 KV Line Ckt-02 | 2023-09-08 12:45 | 2023-09-08 17:28 | 4:43 | S/O | Gas leakage in GIL. | 0 | 0 | No interruption
Rajshahi 132/33kV Grid Sub-Station | 132 kV Raj(new)-1 | 2023-09-17 06:36 | 2023-09-17 08:38 | 2:02 | S/O | Emergency Maintenance | 25 | 50.8333 | Power interruption
Sirajganj 132/33kV Grid Sub-Station | Baghabari Express | 2023-09-15 06:12 | 2023-09-15 09:48 | 3:36 | D/W | Sirajgonj 132kV BUS shutdown for g2g project | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Shahjadpur | 2023-09-15 06:11 | 2023-09-15 09:29 | 3:18 | D/W | Sirajgonj 132kV BUS shutdown for g2g project | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-09-07 07:06 | 2023-09-08 17:45 | 34:39 | D/W | Due to Project work | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-1 | 2023-09-14 08:57 | 2023-09-18 14:27 | 101:30 | D/W | rerouting work . | 0 | 0 | No interruption
Sirajganj 132/33kV Grid Sub-Station | Sherpur-2 | 2023-09-09 07:48 | 2023-09-10 19:06 | 35:18 | S/O | OPGW Wire Stringing. | 0 | 0 | No interruption
Thakurgaon 132/33kV Grid Sub-Station | Purbasadipur-Thakurgaon Ckt-2 | 2023-09-22 09:45 | 2023-09-22 11:57 | 2:12 | S/O | Due to Project work | 0 | 0 | No interruption
|  |  | Total : | 713:46 |  | Unserved Energy: |  | 50.8333
Others :NIL
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 2054:30 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:September 2023
| Area | Previous Month (August' 2023) |  |  |  | Current Month (September '2023)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 19 | 13 | 45 | 77 | 26 | 12 | 51 | 89
2 | Dhaka (South) Grid Circle. | 31 | 21 | 28 | 80 | 24 | 11 | 43 | 78
3 | Chattogram Grid Circle. | 19 | 21 | 12 | 52 | 20 | 12 | 32 | 64
4 | Cumilla Grid Circle. | 27 | 14 | 25 | 66 | 47 | 17 | 19 | 83
5 | Khulna Grid Circle. | 22 | 16 | 50 | 88 | 18 | 13 | 47 | 78
6 | HVDC Grid Circle | 8 | 11 | 9 | 28 | 7 | 10 | 13 | 30
7 | Bogura Grid Circle. | 35 | 41 | 23 | 98 | 20 | 46 | 53 | 119
8 | Others | 1 | 1 |  | 2 | 2 | 1 |  | 3
9 | Total | 162 | 138 | 192 | 491 | 164 | 122 | 258 | 544
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:September 2023
| Area | Previous Month (August' 2023) |  |  |  | Current Month (September '2023)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 253.97 | 427.52 | 2683.2 | 3364.69 | 1074.2 | 488.28 | 1338.58 | 2901.06
2 | Dhaka (South) Grid Circle. | 4888.5 | 1812.1 | 784.92 | 7485.52 | 327.96 | 394.58 | 571.07 | 1293.61
3 | Chattogram Grid Circle. | 225.52 | 136.1 | 165.63 | 527.25 | 180.41 | 70.67 | 1106.27 | 1357.35
4 | Cumilla Grid Circle. | 3209.72 | 663.3 | 474.2 | 4347.22 | 264.07 | 207.65 | 135.93 | 607.65
5 | Khulna Grid Circle. | 433.95 | 356.32 | 785.25 | 1575.52 | 163.77 | 607.06 | 641.48 | 1412.31
6 | HVDC Grid Circle | 12 | 197.57 | 376.05 | 585.62 | 71.5 | 76.42 | 75.83 | 223.75
7 | Bogura Grid Circle. | 623.23 | 577.98 | 752.83 | 1954.04 | 135.13 | 1056.27 | 1260.2 | 2451.6
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 9646.89 | 4170.89 | 6022.08 | 19839.86 | 2217.04 | 2900.93 | 5129.36 | 10247.33
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:September 2023
A) Power Interruption | [10 empty] | 2 | 1
SL.No | Name of the Circle | Total Capacity of the Sub-Station | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
[6 empty] | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 14 | 8 | 22 | 6 | 2 | 14 | 1660.28
2 | Dhaka (South) | 5031.6 | 10 | 4 | 14 | 3 | 1 | 10 | 1071.09
3 | Chattogram | 2042 | 8 | 6 | 14 | 5 | 1 | 8 | 700.35
4 | Khulna | 2434 | 11 | 12 | 23 | 6 | 4 | 13 | 862.08
5 | HVDC | 5954.3 | 4 | 1 | 5 |  | 2 | 3 | 223.75
6 | Bogura | 3145.6 | 27 | 20 | 47 | 9 | 1 | 37 | 2330.47
7 | Cumilla | 2981 | 13 | 5 | 18 | 3 | 4 | 11 | 598.98
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 7447
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.91%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.94%
4 | Khulna | 99.05%
5 | HVDC | 99.98% | [6 empty] | Executive Engineer
6 | Bogura | 99.98% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [9 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:September 2023
A) Power Interruption
SL.No | Name of the Circle | Total length of Transmission line (Ckt-KM) | No. of Section in the Transmission Line | No of Power Interruption |  |  | Power Interruption Up to 30Mins | Power Interruption Up to 01Hrs | Power Interruption Above 01Hour | Amount of Interrupted Energy MWH | Remarks
|  |  |  | Forced | Scheduled | Total
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 6 | 3 | 9 | 4 | 1 | 4 | 1240.78
2 | Dhaka (South) | 990.29 | - | 5 |  | 5 | 4 |  | 1 | 222.53
3 | Chattogram | 917 | - | 3 | 3 | 6 | 2 | 1 | 3 | 657.01
4 | Khulna | 1238.4 | - | 6 | - | 6 | 3 | 1 | 2 | 550.22
5 | HVDC | 1325 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 3 | 1 | 4 | 2 |  | 2 | 121.13
7 | Cumilla | 1648.16 | - | 1 |  | 1 | 1 |  |  | 8.67
8 | Others | - | - | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 2800.34
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.98%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.94%
5 | Bheramara (HVDC) | 100%
6 | Bogura | 99.99%
7 | Cumilla | 99.98%
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:September 2023
Type of fault Period | Power failure due to | [7 empty] | Partial Grid failure |  | Total Grid failure |  | Remarks
| Trouble In Generation |  | Trouble In Grid S/S Equipment |  | Trouble In Transmission Line |  | Lightning in Transmission Line/Thunder Storm
| Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min. | Total No | Duration Hour / Min.
2023-09-01 | 18 | - | 18 | 27hr49 min | 7 | 14hr10 min | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:September 2023
Sub-station | Total Nos.of | Total | Total | Remarks
| Interruption | Duration of | Unserved
|  | Interruption | Energy
|  | Hrs./Mins. | (MWH)
Manikganj 132/33kV Grid Sub-Station | 3 | 14:46 | 657.5
Savar 132/33kV Grid Sub-Station | 2 | 0:26 | 22.2
Sherpur 132/33kV Grid Sub-Station | 4 | 4:01 | 97.42
Sreepur 230/132/33kV Grid Sub-Station | 1 | 2:22 | 23.6667
Tangail 132/33kV Grid Sub-Station | 3 | 1:38 | 189
Tongi 230/132/33kV Grid Sub-Station | 1 | 1:34 | 235
Bhaluka 132/33kV Grid Sub-Station | 1 | 0:18 | 27
Kishoreganj 132/33kV Grid Sub-Station | 1 | 0:12 | 14
Mirpur 132/33kV Grid Sub-Station | 2 | 1:53 | 213.33
Sreepur 230/132/33kV Grid Sub-Station | 1 | 0:20 | 41
Tongi 230/132/33kV Grid Sub-Station | 2 | 0:31 | 42.4
Jamalpur 132/33kV Grid Sub-Station | 3 | 7:05 | 260.18
Kodda 132/33kV Grid Sub-Station | 1 | 1:57 | 33.15
Manikganj 132/33kV Grid Sub-Station | 1 | 2:10 | 32.5
Sreepur 230/132/33kV Grid Sub-Station | 1 | 1:36 | 56
Tangail 132/33kV Grid Sub-Station | 2 | 1:51 | 53.67
Kodda 132/33kV Grid Sub-Station | 1 | 2:35 | 180.8333
Manikganj 132/33kV Grid Sub-Station | 1 | 1:33 | 23.25
Tangail 132/33kV Grid Sub-Station | 1 | 7:46 | 699
Bhulta 132/33kV Grid Sub-Station | 3 | 5:31 | 276.08
Hasnabad 132/33kV Grid Substation | 3 | 1:43 | 44.63
Madanganj 132/33kV Grid Sub-Station | 1 | 1:34 | 50.1333
Munshiganj 132/33kV Grid Sub-Station | 1 | 2:29 | 99.3333
Narshingdi 132/33kV Grid Sub-Station | 1 | 0:16 | 10.6667
Sonargaon 132/33kV Grid Sub-Station | 1 | 0:46 | 19.1667
Bhulta 132/33kV Grid Sub-Station | 1 | 0:15 | 43
Haripur 230/132kV Grid Sub-Station | 2 | 0:35 | 38.7
Shyampur 230/132kV Grid Sub-Station | 1 | 0:30 | 35.5
Shyampur 230/132kV Grid Sub-Station | 1 | 2:42 | 105.3
Bhulta 132/33kV Grid Sub-Station | 1 | 5:59 | 418.8333
Srinagar 132/33kV Grid Sub-Station | 3 | 4:25 | 152.2
Chandraghona 132/33kV Grid Sub-Station | 1 | 1:23 | 27.6667
Dohazari 132/33kV Grid Sub-Station | 1 | 0:12 | 2.4
Hathazari 230/132/33kV Grid Sub-Station | 3 | 3:24 | 141
Khagrachori 132/33kV Grid Sub-Station | 2 | 0:26 | 4.33
Madunaghat 132/33kV Grid Sub-Station | 1 | 0:58 | 40.6
Dohazari 132/33kV Grid Sub-Station | 1 | 0:16 | 0.53333
Shikalbaha 230/132kV Grid Sub-Station | 1 | 0:28 | 19.1333
TK chemical 132kV Grid Sub-Station | 1 | 0:37 | 15.4167
Chandraghona 132/33kV Grid Sub-Station | 2 | 0:48 | 14.4
Dohazari 132/33kV Grid Sub-Station | 2 | 2:29 | 85.75
GPH 230/33kV Grid Sub-Station | 1 | 4:34 | 36.5333
Hathazari 230/132/33kV Grid Sub-Station | 1 | 9:56 | 347.6667
Dohazari 132/33kV Grid Sub-Station | 2 | 11:39 | 582.5
Mirsorai 230/33kV Grid Sub-Station | 1 | 197:07 | 39.4233
Beanibazar 132/33kV Grid Sub-Station | 2 | 1:41 | 97.63
Chauddagram 132/33kV Grid Sub-Station | 1 | 1:08 | 31.7333
Chowmuhani 132/33kV Grid Sub-Station | 2 | 5:33 | 114.67
Cumilla(N) 230/132/33kV Grid Sub-Station | 3 | 4:24 | 64.53
Feni 132/33kV Grid Sub-Station | 2 | 5:05 | 103.98
Sylhet 132/33kV Grid Sub-Station | 3 | 1:20 | 50.5
Chowmuhani 132/33kV Grid Sub-Station | 1 | 0:13 | 8.6667
Cumilla(S) 132/33kV Grid Sub-Station | 1 | 1:32 | 15.3333
Kulaura 132/33kV Grid Sub-Station | 3 | 4:13 | 74.6
Shahjibazar 132/33kV Grid Sub-Station | 1 | 1:32 | 46
Benapole 132/33kV Grid Sub-Station | 2 | 0:57 | 34.2
Faridpur 132/33kV Grid Sub-Station | 3 | 0:56 | 38.9
Gopalganj 132/33kV Grid Sub-Station | 2 | 3:53 | 88.33
Mongla 132/33kV Grid Sub-Station | 3 | 4:14 | 49.03
Noapara 132/33kV Grid Sub-Station | 1 | 0:32 | 10.1333
Goalpara 132/33kV Grid Sub-Station | 4 | 1:21 | 7.85
Payra 400/132/33kV Grid Sub-Station | 2 | 10:14 | 542.37
Barishal 132/33kV Grid Sub-Station | 3 | 4:15 | 138.58
Bhandaria 132/33kV Grid Sub-Station | 1 | 2:12 | 16.5
Bhandaria 132/33kV Grid Sub-Station | 1 | 1:05 | 16.25
Faridpur 132/33kV Grid Sub-Station | 1 | 2:31 | 125.8333
Gopalganj 132/33kV Grid Sub-Station | 1 | 6:56 | 83.2
Madaripur 132/33kV Grid Sub-Station | 2 | 8:53 | 172.47
Narail 132/33kV Grid Sub-Station | 1 | 2:13 | 50.9833
Shariatpur 132/33kV Grid Sub-Station | 2 | 3:46 | 37.67
Jashore 132/33kV Grid Sub-Station | 1 | 0:40 | 34
Jhenaidah 132/33kV Grid Sub-Station | 1 | 1:05 | 37.9167
Kushtia 132/33kV Grid Sub-Station | 2 | 1:47 | 58.5
Shahjadpur 132/33kV Grid Sub-Station | 1 | 1:15 | 17.5
Jashore 132/33kV Grid Sub-Station | 1 | 1:31 | 75.8333
Bog-Sherpur 132/33kV Grid Sub-Station | 4 | 9:28 | 248.33
Jaldhaka 132/33kV Grid Sub-Station | 1 | 1:52 | 37.3333
Mithapukur 132/33kV Grid Sub-Station | 1 | 1:10 | 26.8333
Mithapukur 132/33kV Grid Sub-Station | 1 | 1:11 | 27.2167
Niamatpur 132/33kV Grid Sub-Station | 2 | 1:49 | 26.43
Purbasadipur 132/33kV Grid Sub-Station | 3 | 1:05 | 28
Rajshahi 132/33kV Grid Sub-Station | 4 | 7:00 | 218.5
Rangpur 132/33kV Grid Sub-Station | 1 | 1:27 | 79.75
Rangpur 132/33kV Grid Sub-Station | 1 | 1:16 | 114
Rangpur 132/33kV Grid Sub-Station | 1 | 1:27 | 79.75
Rangpur 132/33kV Grid Sub-Station | 1 | 1:16 | 114
Sirajganj 132/33kV Grid Sub-Station | 4 | 4:34 | 109.25
Thakurgaon 132/33kV Grid Sub-Station | 3 | 0:38 | 11.7
Palashbari 132/33kV Grid Sub-Station | 1 | 2:43 | 67.9167
Rangpur 132/33kV Grid Sub-Station | 2 | 0:13 | 2.38
Barapukuria 230/132/33kV Grid Sub-Station | 3 | 5:08 | 128
Chapai 132/33kV Grid Sub-Station | 4 | 13:17 | 178.43
Joypurhat 132/33kV Grid Sub-Station | 1 | 3:50 | 34.5
Joypurhat 132/33kV Grid Sub-Station | 1 | 3:09 | 22.05
Joypurhat 132/33kV Grid Sub-Station | 1 | 3:50 | 34.5
Joypurhat 132/33kV Grid Sub-Station | 1 | 3:09 | 22.05
Rajshahi 132/33kV Grid Sub-Station | 3 | 10:44 | 170.5
Saidpur 132/33kV Grid Sub-Station | 1 | 2:34 | 25.6667
Sirajganj 132/33kV Grid Sub-Station | 5 | 22:57 | 593.67
Rajshahi 132/33kV Grid Sub-Station | 1 | 2:02 | 50.8333
Total Unserved energy : | 176 | 510:22 | 10247.28
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:September 2023
Sl. No | Name | date_time | ss_MW
1 | Aftabnagar 132/33kV Grid Sub-Station | 2023-09-05 13:00 | 66
2 | Agargaon 230/132kV Grid Sub-Station | 2023-09-17 13:00 | 106
3 | Banani 132/33kV Grid Sub-Station | 2023-09-05 13:00 | 74
4 | Bangabhaban 132/33kV Grid Sub-Station | 2023-09-17 10:00 | 20
5 | Bashundhara 132/33kV Grid Sub-Station | 2023-09-17 13:00 | 180
6 | BashundharaCement 132/33kV Sub-Station | 2023-09-05 12:00 | 12
7 | Bhulta 132/33kV Grid Sub-Station | 2023-09-04 18:30 | 262
8 | Cantonment 132/33kV GIS Grid Sub-Station | 2023-09-05 14:00 | 168
9 | Charsaidpur 132/33kV Sub-Station | 2023-09-05 23:00 | 61
10 | Dhaka University 132/33kV Grid Sub-Station | 2023-09-02 12:00 | 40
11 | Dhamrai 132/33kV Grid Sub-Station | 2023-09-13 19:00 | 134
12 | Dhanmondi 132/33kV Grid Sub-Station | 2023-09-17 12:00 | 151
13 | Fatullah 132/33kV Grid Sub-Station | 2023-09-05 11:00 | 69
14 | Ghorashal 230/132/33kV Sub-Station | 2023-09-03 19:30 | 81
15 | Gulshan 132/33kV Grid Sub-Station | 2023-09-17 15:00 | 144
16 | HaripurSBU 132/33kV Sub-Station | 2023-09-16 11:00 | 174
17 | Hasnabad 132/33kV Grid Substation | 2023-09-28 13:00 | 113
18 | Joydebpur 132/33kV Grid Sub-Station | 2023-09-17 19:00 | 189
19 | Kabirpur 132/33kV Grid Sub-Station | 2023-09-12 12:00 | 304
20 | Kallyanpur 132/33kV Grid Sub-Station | 2023-09-17 19:30 | 126
21 | Kamrangirchar 132/33kV Grid Sub-Station | 2023-09-26 13:00 | 82.2
22 | Kazla 132/33kV Grid Sub-Station | 2023-09-05 18:30 | 112
23 | Keranigonj 230/132/33kV Grid Sub-Station | 2023-09-17 18:30 | 90
24 | Kodda 132/33kV Grid Sub-Station | 2023-09-18 12:00 | 299
25 | Lalbag 132/33kV Grid Sub-Station | 2023-09-21 13:00 | 102
26 | Madanganj 132/33kV Grid Sub-Station | 2023-09-03 23:00 | 52
27 | Madartek 132/33kV Grid Sub-Station | 2023-09-06 | 98.57
28 | Manikganj 132/33kV Grid Sub-Station | 2023-09-13 19:00 | 132
29 | Maniknagar 132/33kV Grid Sub-Station | 2023-09-11 13:00 | 106
30 | Matuail 132/33kV Grid Sub-Station | 2023-09-05 12:00 | 74
31 | Millgate Tongi 132/33kV Grid Sub-Station | 2023-09-27 18:00 | 112
32 | Mirpur 132/33kV Grid Sub-Station | 2023-09-17 15:00 | 150
33 | MI_Cement 132/33kV Grid Sub-Station | 2023-09-19 12:00 | 20.4
34 | Mogbazar 132/33kV Grid Sub-Station | 2023-09-17 16:00 | 153.9
35 | Motijheel 132/33kV Grid Sub-Station | 2023-09-05 12:00 | 48
36 | Munshiganj 132/33kV Grid Sub-Station | 2023-09-02 16:00 | 117
37 | Narinda 132/33kV Grid Sub-Station | 2023-09-05 13:00 | 85
38 | Narshingdi 132/33kV Grid Sub-Station | 2023-09-16 19:30 | 192
39 | Nawabganj 132/33kV Grid Sub-Station | 2023-09-07 20:00 | 57.7
40 | New Tongi 132/33kV Grid Sub-Station | 2023-09-11 12:00 | 84
41 | Postogola 132/33kV Grid Sub-Station | 2023-09-05 23:00 | 63
42 | Purbachal 132/33kV Grid Sub-Station | 2023-09-16 15:00 | 24
43 | Rahim Steel 132/33kV Sub-Station | 2023-09-16 09:00 | 47
44 | Rajendrapur 132/33kV Grid Sub-Station | 2023-09-03 22:00 | 112
45 | Satmasjid 132/33kV Grid Sub-Station | 2023-09-17 18:30 | 129
46 | Savar 132/33kV Grid Sub-Station | 2023-09-04 11:00 | 206
47 | ShahCement 132/33kV Grid Sub-Station | 2023-09-19 04:00 | 37
48 | Shitalakhya 132/33kV Grid Sub-Station | 2023-09-21 12:00 | 123.4
49 | Shyampur 132/33kV Grid Sub-Station | 2023-09-06 09:00 | 172
50 | Siddhirganj 132/33kV Grid Sub-Station | 2023-09-17 16:00 | 132
51 | Sonargaon 132/33kV Grid Sub-Station | 2023-09-13 22:00 | 97
52 | Sreepur 230/132/33kV Grid Sub-Station | 2023-09-27 16:00 | 84
53 | Srinagar 132/33kV Grid Sub-Station | 2023-09-05 22:00 | 49.68
54 | Tongi 230/132/33kV Grid Sub-Station | 2023-09-10 14:00 | 128
55 | Ullon 132/33kV Grid Sub-Station | 2023-09-30 | 52
56 | Uttara 132/33kV Grid Sub-Station | 2023-09-28 18:00 | 103
57 | UttaraNew 132/33kV Grid Sub-Station | 2023-09-17 18:30 | 79
58 | Zigatola 132/33kV Grid Sub-Station | 2023-09-02 13:00 | 80
59 | Agrabad 132/33kV Grid Sub-Station | 2023-09-13 21:00 | 116
60 | AKS 132/33kV Grid Sub-Station | 2023-09-23 21:00 | 24
61 | AKSML 230/33kV Grid Sub-Station | 2023-09-09 16:00 | 218
62 | Bakulia 132/33kV Grid Sub-Station | 2023-09-17 19:00 | 114
63 | Baroaulia 132/33kV Grid Sub-Station | 2023-09-14 | 75
64 | Baroirhat 132/33kV Grid Sub-Station | 2023-09-04 21:00 | 73
65 | BSRM 230/33kV Grid Sub-Station | 2023-09-28 09:00 | 197
66 | Chandraghona 132/33kV Grid Sub-Station | 2023-09-29 14:00 | 36
67 | Coxsbazar 132/33kV Grid Sub-Station | 2023-09-11 18:30 | 137
68 | Dohazari 132/33kV Grid Sub-Station | 2023-09-15 22:00 | 100
69 | GPH 230/33kV Grid Sub-Station | 2023-09-10 17:00 | 93
70 | Halishahar 132/33kV Grid Sub-Station | 2023-09-17 15:00 | 88
71 | Hathazari 230/132/33kV Grid Sub-Station | 2023-09-02 20:00 | 83
72 | Juldah 132/33kV Grid Sub-Station | 2023-09-17 10:00 | 28
73 | Kalurghat 132/33kV Grid Sub-Station | 2023-09-23 09:00 | 46
74 | Khagrachori 132/33kV Grid Sub-Station | 2023-09-26 19:00 | 36
75 | Khulshi 132/33kV Grid Sub-Station | 2023-09-04 16:00 | 201
76 | KSRM 132/33kV Grid Sub-Station | 2023-09-17 14:00 | 47
77 | Madunaghat 132/33kV Grid Sub-Station | 2023-09-17 19:00 | 61
78 | Matarbari 132/33kV Sub-Station | 2023-09-06 18:30 | 51
79 | Mirsorai 230/33kV Grid Sub-Station | 2023-09-02 19:30 | 6
80 | Modern Steel 132/11kV Grid Sub-Station | 2023-09-20 10:00 | 0.18
81 | Rampur 230/132/33 kV GIS Grid Sub-Station | 2023-09-26 20:00 | 33
82 | Rangamati 132/33kV Grid Sub-Station | 2023-09-04 18:30 | 20
83 | Shahmirpur 132/33kV Grid Sub-Station | 2023-09-24 01:00 | 58
84 | Shikalbaha 132/33kV Sub-Station | 2023-09-21 10:00 | 37
85 | Sholosohor 132/33kV Grid Sub-Station | 2023-09-16 16:00 | 46
86 | SSM 132/33kV Grid Sub-Station | 2023-09-26 15:00 | 134
87 | TK chemical 132kV Grid Sub-Station | 2023-09-06 22:00 | 33
88 | Ashuganj 230/132/33kV Sub-Station | 2023-09-17 13:00 | 85
89 | Brahmanbaria 132/33kV Grid Sub-Station | 2023-09-10 19:30 | 176
90 | Chandpur 132/33kV Grid Sub-Station | 2023-09-17 18:30 | 86
91 | Chauddagram 132/33kV Grid Sub-Station | 2023-09-02 22:00 | 67
92 | Chowmuhani 132/33kV Grid Sub-Station | 2023-09-16 19:30 | 246
93 | Cumilla(N) 230/132/33kV Grid Sub-Station | 2023-09-05 12:00 | 189
94 | Cumilla(S) 132/33kV Grid Sub-Station | 2023-09-13 23:00 | 174
95 | Daudkandi 132/33kV Grid Sub-Station | 2023-09-27 20:00 | 154
96 | Feni 132/33kV Grid Sub-Station | 2023-09-05 22:00 | 141
97 | Kachua 132/33kV Grid Sub-Station | 2023-09-17 18:30 | 91
98 | PHP 132/33kV Sub-Station | 2023-09-21 08:00 | 9
99 | Ramganj 132/33kV Grid Sub-Station | 2023-09-12 23:00 | 126
100 | Bhaluka 132/33kV Grid Sub-Station | 2023-09-13 11:00 | 134
101 | Jamalpur 132/33kV Grid Sub-Station | 2023-09-18 22:00 | 181
102 | Kishoreganj 132/33kV Grid Sub-Station | 2023-09-08 22:00 | 166
103 | Mymensingh 132/33kV Grid Sub-Station | 2023-09-29 18:30 | 246
104 | Netrakona 132/33kV Grid Sub-Station | 2023-09-01 21:00 | 150
105 | Sherpur 132/33kV Grid Sub-Station | 2023-09-16 20:00 | 168
106 | Tangail 132/33kV Grid Sub-Station | 2023-09-16 21:00 | 256
107 | Beanibazar 132/33kV Grid Sub-Station | 2023-09-16 18:30 | 96
108 | Chhatak 132/33kV Grid Sub-Station | 2023-09-03 20:00 | 39
109 | Fenchuganj 230/132/33kV Grid Sub-Station | 2023-09-30 19:00 | 57
110 | Kulaura 132/33kV Grid Sub-Station | 2023-09-11 19:30 | 56
111 | Shahjibazar 132/33kV Grid Sub-Station | 2023-09-11 19:00 | 131
112 | Sreemongol 132/33kV Grid Sub-Station | 2023-09-16 18:30 | 78
113 | Sunamganj 132/33kV Grid Sub-Station | 2023-09-12 20:00 | 61
114 | Sylhet 132/33kV Grid Sub-Station | 2023-09-30 18:00 | 184
115 | Bagerhat 132/33kV Grid Sub-Station | 2023-09-17 22:00 | 100
116 | Benapole 132/33kV Grid Sub-Station | 2023-09-17 22:00 | 72
117 | Bheramara(GK) 132/33kV Grid Sub-Station | 2023-09-10 19:00 | 71
118 | Chuadanga 132/33kV Grid Sub-Station | 2023-09-02 19:00 | 123
119 | Faridpur 132/33kV Grid Sub-Station | 2023-09-17 21:00 | 179
120 | Goalpara 132/33kV Grid Sub-Station | 2023-09-02 13:00 | 40
121 | Gollamari 132/33kV Grid Sub-Station | 2023-09-16 16:00 | 65
122 | Gopalganj 132/33kV Grid Sub-Station | 2023-09-17 21:00 | 116.2
123 | Jashore 132/33kV Grid Sub-Station | 2023-09-06 19:00 | 155
124 | Jhenaidah 132/33kV Grid Sub-Station | 2023-09-09 19:00 | 146
125 | Khulna (C) 132/33kV Grid Sub-Station | 2023-09-17 18:30 | 104
126 | Kushtia 132/33kV Grid Sub-Station | 2023-09-11 19:30 | 156
127 | Madaripur 132/33kV Grid Sub-Station | 2023-09-02 23:00 | 116
128 | Magura 132/33kV Grid Sub-Station | 2023-09-06 19:00 | 78.5
129 | Mongla 132/33kV Grid Sub-Station | 2023-09-27 09:00 | 38
130 | Narail 132/33kV Grid Sub-Station | 2023-09-06 19:00 | 62
131 | Noapara 132/33kV Grid Sub-Station | 2023-09-02 21:00 | 53
132 | Rajbari 132/33kV Grid Sub-Station | 2023-09-06 19:30 | 82
133 | Satkhira 132/33kV Grid Sub-Station | 2023-09-17 22:00 | 139
134 | Shariatpur 132/33kV Grid Sub-Station | 2023-09-16 22:00 | 89
135 | Barguna 132/33kV Grid Sub-Station | 2023-09-17 23:00 | 24
136 | Barishal 132/33kV Grid Sub-Station | 2023-09-05 22:00 | 111
137 | Barishal 230/132kV Grid Sub-Station | 2023-09-05 21:00 | 112
138 | Bhandaria 132/33kV Grid Sub-Station | 2023-09-02 22:00 | 54
139 | Borhanuddin 230/33kV Grid Sub-Station | 2023-09-02 23:00 | 73
140 | Patuakhali 132/33kV Grid Sub-Station | 2023-09-02 23:00 | 118
141 | Payra 400/132/33kV Grid Sub-Station | 2023-09-13 22:00 | 28
142 | Amnura 132/33kV Grid Sub-Station | 2023-09-02 21:00 | 61
143 | Bhangura 132/33kV Grid Sub-Station | 2023-09-05 19:00 | 40
144 | Bog-Sherpur 132/33kV Grid Sub-Station | 2023-09-15 04:00 | 74
145 | Bogura 132/33kV Grid Sub-Station | 2023-09-17 19:00 | 196
146 | Chapai 132/33kV Grid Sub-Station | 2023-09-01 21:00 | 76
147 | Ishurdi 132/33kV Grid Sub-Station | 2023-09-05 21:00 | 83
148 | Joypurhat 132/33kV Grid Sub-Station | 2023-09-13 21:00 | 72
149 | Mahasthangarh 132/33kV Grid Sub-Station | 2023-09-18 | 88
150 | Naogaon 132/33kV Grid Sub-Station | 2023-09-05 21:00 | 151
151 | Natore 132/33kV Grid Sub-Station | 2023-09-03 18:30 | 172
152 | Niamatpur 132/33kV Grid Sub-Station | 2023-09-16 23:00 | 99
153 | Pabna 132/33kV Grid Sub-Station | 2023-09-06 21:00 | 135
154 | Rajshahi 132/33kV Grid Sub-Station | 2023-09-02 19:00 | 185
155 | Rajshahi 230/132/33kV Grid Sub-Station | 2023-09-03 | 48
156 | Ruppur 132/11kV Grid Sub-Station | 2023-09-28 16:00 | 6.8
157 | Shahjadpur 132/33kV Grid Sub-Station | 2023-09-17 20:00 | 129
158 | Sirajganj 132/33kV Grid Sub-Station | 2023-09-10 20:00 | 132
159 | Barapukuria 230/132/33kV Grid Sub-Station | 2023-09-15 08:00 | 70
160 | Jaldhaka 132/33kV Grid Sub-Station | 2023-09-15 19:00 | 85
161 | Kurigram 132/33kV Grid Sub-Station | 2023-09-27 18:30 | 75
162 | Lalmonirhat 132/33kV Grid Sub-Station | 2023-09-07 21:00 | 60
163 | Mithapukur 132/33kV Grid Sub-Station | 2023-09-05 18:30 | 54
164 | Palashbari 132/33kV Grid Sub-Station | 2023-09-18 20:00 | 148
165 | Panchagarh 132/33kV Grid Sub-Station | 2023-09-05 19:00 | 73
166 | Purbasadipur 132/33kV Grid Sub-Station | 2023-09-11 19:30 | 132
167 | Rangpur 132/33kV Grid Sub-Station | 2023-09-28 19:00 | 162
168 | Saidpur 132/33kV Grid Sub-Station | 2023-09-12 19:00 | 116
169 | Thakurgaon 132/33kV Grid Sub-Station | 2023-09-11 22:00 | 116
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:September 2023
Area | Load (MW) | Date | Hour | Remarks
Dhaka | 5449.38 | 2023-09-17 | 20:00
Chattogram | 1522 | 2023-09-26 | 15:00
Cumilla | 1382 | 2023-09-02 | 21:00
Mymensingh | 1186 | 2023-09-15 | 21:00
Sylhet | 647 | 2023-09-05 | 18:30
Khulna | 1854.2 | 2023-09-17 | 21:00
Barishal | 496 | 2023-09-10 | 22:00
Rajshahi | 1617 | 2023-09-05 | 21:00
Rangpur | 978 | 2023-09-28 | 18:30
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month:September 2023
SL. | 400 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
No. |  | Voltage | Voltage |  | Voltage
|  | kV | kV |  | kV
1 | Aminbazar 400/230/132kV Grid Sub-Station | 400 | 409 | 2023-09-05 13:00 | 376 | 2023-09-11 12:00
2 | Bhulta 400/230kV Grid Sub-Station | 400 | 407 | 2023-09-03 04:00 | 373 | 2023-09-06 15:00
3 | Bibiana 400/230kV Sub-Station | 400 | 404 | 2023-09-01 14:00 | 388 | 2023-09-03 09:00
4 | BIPTC | 400 | 405 | 2023-09-20 06:00 | 387 | 2023-09-12 13:00
5 | Gopalganj 400/132kV Grid Sub-Station | 400 | 408 | 2023-09-15 07:00 | 387 | 2023-09-28 23:00
6 | Kaliakoir 400/230/132kV Grid Sub-Station | 400 | 392 | 2023-09-03 05:00 | 358 | 2023-09-27 12:00
7 | Payra 400kV Sub-Station | 400 | 415 | 2023-09-04 07:00 | 402 | 2023-09-28 22:00
8 | Rahanpur 400/132kV Grid Sub-Station | 400 | 409 | 2023-09-24 17:00 | 379 | 2023-09-05 02:00
9 | Rampal 400/230kV Grid Sub-Station | 400 | 411 | 2023-09-15 07:00 | 385 | 2023-09-28 23:00
| 230 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Agargaon 230/132kV Grid Sub-Station | 230 | 235 | 2023-09-03 04:00 | 217 | 2023-09-27 12:00
2 | AKSML 230/33kV Grid Sub-Station | 230 | 255 | 2023-09-02 15:00 | 215 | 2023-09-07 09:00
3 | Baghabari 230/132kV Grid Sub-Station | 230 | 232 | 2023-09-03 06:00 | 214 | 2023-09-17 20:00
4 | Barapukuria 230/132/33kV Grid Sub-Station | 230 | 225 | 2023-09-24 05:00 | 203 | 2023-09-01 19:00
5 | Barishal 230/132kV Grid Sub-Station | 230 | 239 | 2023-09-01 07:00 | 226 | 2023-09-15 23:00
6 | Bheramara 230/132kV Grid Sub-Station | 230 | 238 | 2023-09-13 | 213 | 2023-09-17 19:00
7 | Bogura 230/132kV Grid Sub-Station | 230 | 235 | 2023-09-06 06:00 | 209 | 2023-09-18 01:00
8 | BSRM 230/33kV Grid Sub-Station | 230 | 239 | 2023-09-17 20:00 | 217 | 2023-09-07 09:00
9 | Cumilla(N) 230/132/33kV Grid Sub-Station | 230 | 234 | 2023-09-09 18:00 | 220 | 2023-09-05 09:00
10 | Fenchuganj 230/132/33kV Grid Sub-Station | 230 | 238 | 2023-09-15 19:00 | 227 | 2023-09-05 18:30
11 | Ghorashal 230/132/33kV Sub-Station | 230 | 240 | 2023-09-03 04:00 | 230 | 2023-09-01
12 | GPH 230/33kV Grid Sub-Station | 230 | 236 | 2023-09-03 19:00 | 203 | 2023-09-19 13:00
13 | Haripur 230/132kV Grid Sub-Station | 230 | 234 | 2023-09-15 19:00 | 221 | 2023-09-05 14:00
14 | Hasnabad 230/132kV Grid Sub-Station | 230 | 235 | 2023-09-15 17:00 | 219 | 2023-09-27 12:00
15 | Hathazari 230/132/33kV Grid Sub-Station | 230 | 238 | 2023-09-03 19:00 | 217 | 2023-09-10 16:00
16 | Ishurdi 230/132kV Grid Sub-Station | 230 | 236 | 2023-09-10 18:00 | 212 | 2023-09-17 19:00
17 | Jhenaidah 230/132kV Grid Sub-Station | 230 | 229 | 2023-09-07 10:00 | 203 | 2023-09-17 19:00
18 | Keranigonj 230/132/33kV Grid Sub-Station | 230 | 235 | 2023-09-15 19:00 | 217 | 2023-09-27 12:00
19 | Khulna(S) 230/132kV Grid Sub-Station | 230 | 238 | 2023-09-20 06:00 | 216 | 2023-09-28 22:00
20 | Maniknagar 230/132kV Grid Sub-Station | 230 | 235 | 2023-09-15 19:00 | 218 | 2023-09-05 13:00
21 | Meghnaghat 230/132kV Grid Sub-Station | 230 | 244 | 2023-09-15 18:00 | 226 | 2023-09-05 13:00
22 | Mirsorai 230/33kV Grid Sub-Station | 230 | 239 | 2023-09-17 19:30 | 216 | 2023-09-10 15:00
23 | Rajshahi 230/132/33kV Grid Sub-Station | 230 | 237 | 2023-09-07 18:00 | 209 | 2023-09-17 19:00
24 | Rampura 230/132kV Grid Sub-Station | 230 | 236 | 2023-09-15 19:30 | 218 | 2023-09-05 12:00
25 | Shikalbaha 230/132kV Grid Sub-Station | 230 | 237 | 2023-09-17 18:30 | 216 | 2023-09-10 16:00
26 | Shyampur 230/132kV Grid Sub-Station | 230 | 236 | 2023-09-15 19:00 | 219 | 2023-09-05 13:00
27 | Siddhirganj 230/132kV Grid Sub-Station | 230 | 238 | 2023-09-15 19:00 | 222 | 2023-09-05 12:00
28 | Sirajgonj 230 kV Switching Station | 230 | 239 | 2023-09-22 06:00 | 226 | 2023-09-17 20:00
29 | Sreepur 230/132/33kV Grid Sub-Station | 230 | 234 | 2023-09-22 06:00 | 220 | 2023-09-05 09:00
30 | Tongi 230/132/33kV Grid Sub-Station | 230 | 240 | 2023-09-03 04:00 | 214 | 2023-09-04 13:00
| 132 KV Substation | Rated | Maxm | Date and Time | Minm | Date and Time | Remarks
SL. |  | Voltage | Voltage |  | Voltage
No. |  | kV | kV |  | kV
1 | Aftabnagar 132/33kV Grid Sub-Station | 132 | 142 | 2023-09-03 04:00 | 125 | 2023-09-05 12:00
2 | Agrabad 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-03 19:00 | 124 | 2023-09-10 15:00
3 | AKS 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-15 09:00 | 124 | 2023-09-09 13:00
4 | Amnura 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-16 17:00 | 116 | 2023-09-01 23:00
5 | Ashuganj 230/132/33kV Sub-Station | 132 | 140 | 2023-09-02 | 125 | 2023-09-06 02:00
6 | Bagerhat 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-18 06:00 | 117 | 2023-09-28 22:00
7 | Bakulia 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-03 19:00 | 125 | 2023-09-10 16:00
8 | Banani 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-03 04:00 | 125 | 2023-09-03 12:00
9 | Bangabhaban 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-15 19:00 | 123 | 2023-09-05 13:00
10 | Barguna 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-18 06:00 | 126 | 2023-09-28 23:00
11 | Barishal 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-18 06:00 | 124 | 2023-09-28 23:00
12 | Baroaulia 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-03 19:00 | 125 | 2023-09-10 15:00
13 | Baroirhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-17 15:00 | 119 | 2023-09-11 03:00
14 | Bashundhara 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-03 04:00 | 122 | 2023-09-04 15:00
15 | BashundharaCement 132/33kV Sub-Station | 132 | 138 | 2023-09-15 19:00 | 126 | 2023-09-27 12:00
16 | Beanibazar 132/33kV Grid Sub-Station | 132 | 131 | 2023-09-13 08:00 | 117 | 2023-09-30 23:00
17 | Benapole 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-15 16:00 | 117 | 2023-09-10 22:00
18 | Bhaluka 132/33kV Grid Sub-Station | 132 | 130 | 2023-09-22 17:00 | 116 | 2023-09-04 13:00
19 | Bhandaria 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-18 06:00 | 119 | 2023-09-17 19:00
20 | Bhangura 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-03 06:00 | 123 | 2023-09-17 20:00
21 | Bheramara(GK) 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-15 17:00 | 121 | 2023-09-17 19:00
22 | Bhulta 132/33kV Grid Sub-Station | 132 | 131 | 2023-09-22 13:00 | 119 | 2023-09-10 16:00
23 | Bog-Sherpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-08 10:00 | 113 | 2023-09-17 22:00
24 | Bogura 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-24 16:00 | 113 | 2023-09-01 12:00
25 | Brahmanbaria 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-29 06:00 | 119 | 2023-09-05 13:00
26 | Cantonment 132/33kV GIS Grid Sub-Station | 132 | 135 | 2023-09-03 04:00 | 122 | 2023-09-11 12:00
27 | Chandpur 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-17 19:30 | 113 | 2023-09-28 22:00
28 | Chandraghona 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-06 23:00 | 127 | 2023-09-10 16:00
29 | Chapai 132/33kV Grid Sub-Station | 132 | 134 | 2023-09-24 17:00 | 118 | 2023-09-03 21:00
30 | Charsaidpur 132/33kV Sub-Station | 132 | 140 | 2023-09-15 19:00 | 127 | 2023-09-27 12:00
31 | Chauddagram 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-17 19:00 | 119 | 2023-09-30
32 | Chhatak 132/33kV Grid Sub-Station | 132 | 130 | 2023-09-04 06:00 | 121 | 2023-09-03 19:30
33 | Chowmuhani 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-17 19:30 | 113 | 2023-09-10 07:00
34 | Chuadanga 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-22 11:00 | 113 | 2023-09-10 23:00
35 | Coxsbazar 132/33kV Grid Sub-Station | 132 | 128 | 2023-09-03 18:30 | 113 | 2023-09-02 03:00
36 | Cumilla(S) 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-17 19:30 | 122 | 2023-09-26 12:00
37 | Daudkandi 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-17 20:00 | 116 | 2023-09-27 12:00
38 | Dhaka University 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-03 03:00 | 125 | 2023-09-05 13:00
39 | Dhamrai 132/33kV Grid Sub-Station | 132 | 142 | 2023-09-03 04:00 | 123 | 2023-09-27 12:00
40 | Dhanmondi 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-15 19:00 | 125.7 | 2023-09-27 12:00
41 | Dohazari 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-03 18:30 | 120 | 2023-09-09 20:00
42 | Faridpur 132/33kV Grid Sub-Station | 132 | 132 | 2023-09-22 07:00 | 119 | 2023-09-28 23:00
43 | Fatullah 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-15 19:00 | 123 | 2023-09-05 13:00
44 | Feni 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-17 18:30 | 120 | 2023-09-30
45 | Goalpara 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-18 17:00 | 124 | 2023-09-28 22:00
46 | Gollamari 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-17 06:00 | 125 | 2023-09-10 23:00
47 | Gopalganj 132/33kV Grid Sub-Station | 132 | 134 | 2023-09-15 19:00 | 121 | 2023-09-28 22:00
48 | Gulshan 132/33kV Grid Sub-Station | 132 | 145 | 2023-09-17 22:00 | 125 | 2023-09-03 12:00
49 | Halishahar 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-03 19:00 | 123 | 2023-09-07 09:00
50 | HaripurSBU 132/33kV Sub-Station | 132 | 141 | 2023-09-16 06:00 | 129 | 2023-09-10 16:00
51 | Hasnabad 132/33kV Grid Substation | 132 | 138 | 2023-09-15 19:00 | 128 | 2023-09-27 12:00
52 | Ishurdi 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-14 18:00 | 122 | 2023-09-17 19:00
53 | Jaldhaka 132/33kV Grid Sub-Station | 132 | 135 | 2023-09-20 17:00 | 113 | 2023-09-02 22:00
54 | Jamalpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-09-06 18:30 | 113 | 2023-09-16 11:00
55 | Jashore 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-15 17:00 | 119 | 2023-09-10 22:00
56 | Jhenaidah 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-15 17:00 | 122 | 2023-09-17 20:00
57 | Joydebpur 132/33kV Grid Sub-Station | 132 | 145 | 2023-09-03 04:00 | 126 | 2023-09-27 12:00
58 | Joypurhat 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-24 15:00 | 113 | 2023-09-01 19:00
59 | Juldah 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-06 23:00 | 125 | 2023-09-10 15:00
60 | Kabirpur 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-17 22:00 | 119 | 2023-09-27 12:00
61 | Kachua 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-17 19:30 | 116 | 2023-09-08 02:00
62 | Kallyanpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-25 18:00 | 119 | 2023-09-06 16:00
63 | Kalurghat 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-03 19:00 | 126 | 2023-09-07 09:00
64 | Kamrangirchar 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-15 18:30 | 117 | 2023-09-06 16:00
65 | Kazla 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-15 18:30 | 123 | 2023-09-05 13:00
66 | Khagrachori 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-02 22:00 | 125 | 2023-09-10 16:00
67 | Khulna (C) 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-18 06:00 | 122 | 2023-09-28 22:00
68 | Khulshi 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-06 23:00 | 122 | 2023-09-10 16:00
69 | Kishoreganj 132/33kV Grid Sub-Station | 132 | 134 | 2023-09-22 17:00 | 118 | 2023-09-04 13:00
70 | Kodda 132/33kV Grid Sub-Station | 132 | 145 | 2023-09-03 04:00 | 122 | 2023-09-26 15:00
71 | KSRM 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-03 19:00 | 125 | 2023-09-07 09:00
72 | Kulaura 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-29 06:00 | 126 | 2023-09-10 18:30
73 | Kurigram 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-20 17:00 | 113 | 2023-09-02 21:00
74 | Kushtia 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-15 17:00 | 118 | 2023-09-17 19:00
75 | Lalbag 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-01 16:00 | 122 | 2023-09-27 12:00
76 | Lalmonirhat 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-19 07:00 | 113 | 2023-09-01 22:00
77 | Madanganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-15 19:00 | 126 | 2023-09-27 12:00
78 | Madaripur 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-19 06:00 | 123 | 2023-09-28 23:00
79 | Madartek 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-03 04:00 | 125 | 2023-09-05 13:00
80 | Madunaghat 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-06 19:30 | 126 | 2023-09-07 09:00
81 | Magura 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-23 06:00 | 121 | 2023-09-17 16:00
82 | Mahasthangarh 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-08 11:00 | 119 | 2023-09-05 05:00
83 | Manikganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-09 21:00 | 122 | 2023-09-16 14:00
84 | Maniknagar 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-15 19:00 | 124 | 2023-09-05 13:00
85 | Matarbari 132/33kV Sub-Station | 132 | 137 | 2023-09-29 16:00 | 113 | 2023-09-01 20:00
86 | Matuail 132/33kV Grid Sub-Station | 132 | 137.5 | 2023-09-15 19:00 | 127 | 2023-09-27 12:00
87 | Millgate Tongi 132/33kV Grid Sub-Station | 132 | 143 | 2023-09-03 04:00 | 120 | 2023-09-02 15:00
88 | Mirpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-17 07:00 | 122 | 2023-09-06 10:00
89 | Mithapukur 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-03 19:30 | 116 | 2023-09-01 19:00
90 | MI_Cement 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-17 21:00 | 126.8 | 2023-09-27 12:00
91 | Modern Steel 132/11kV Grid Sub-Station | 132 | 138 | 2023-09-06 23:00 | 125 | 2023-09-07 09:00
92 | Mogbazar 132/33kV Grid Sub-Station | 132 | 145 | 2023-09-03 04:00 | 125 | 2023-09-05 13:00
93 | Mongla 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-18 06:00 | 119 | 2023-09-28 22:00
94 | Motijheel 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-23 03:00 | 123 | 2023-09-05 13:00
95 | Munshiganj 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-15 19:00 | 127 | 2023-09-12 09:00
96 | Mymensingh 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-06 18:30 | 113 | 2023-09-06 11:00
97 | Naogaon 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-24 16:00 | 113 | 2023-09-06 23:00
98 | Narail 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-12 17:00 | 118 | 2023-09-17 20:00
99 | Narshingdi 132/33kV Grid Sub-Station | 132 | 134 | 2023-09-03 03:00 | 120 | 2023-09-05 12:00
100 | Natore 132/33kV Grid Sub-Station | 132 | 134 | 2023-09-17 08:00 | 114 | 2023-09-17 20:00
101 | Nawabganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-15 18:00 | 123 | 2023-09-27 15:00
102 | Netrakona 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-05 18:30 | 113 | 2023-09-04
103 | New Tongi 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-03 07:00 | 123 | 2023-09-27 12:00
104 | Niamatpur 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-24 16:00 | 113 | 2023-09-02 13:00
105 | Noapara 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-08 06:00 | 122 | 2023-09-10 22:00
106 | Pabna 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-22 06:00 | 121 | 2023-09-10 22:00
107 | Palashbari 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-24 14:00 | 114 | 2023-09-01 19:00
108 | Panchagarh 132/33kV Grid Sub-Station | 132 | 142 | 2023-09-22 19:30 | 113 | 2023-09-01 04:00
109 | Patuakhali 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-04 | 130 | 2023-09-24 01:00
110 | PHP 132/33kV Sub-Station | 132 | 139 | 2023-09-17 19:30 | 118 | 2023-09-06 13:00
111 | Postogola 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-15 19:00 | 127 | 2023-09-27 12:00
112 | Purbachal 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-03 04:00 | 121 | 2023-09-27 12:00
113 | Purbasadipur 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-22 18:00 | 113 | 2023-09-01 13:00
114 | Rahim Steel 132/33kV Sub-Station | 132 | 138 | 2023-09-15 19:00 | 129 | 2023-09-10 16:00
115 | Rajbari 132/33kV Grid Sub-Station | 132 | 132 | 2023-09-21 14:00 | 117 | 2023-09-28 22:00
116 | Rajendrapur 132/33kV Grid Sub-Station | 132 | 147 | 2023-09-29 19:30 | 122 | 2023-09-10 15:00
117 | Rajshahi 132/33kV Grid Sub-Station | 132 | 134 | 2023-09-14 18:00 | 119 | 2023-09-17 19:00
118 | Ramganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-17 14:00 | 113 | 2023-09-01 22:00
119 | Rangamati 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-06 23:00 | 126 | 2023-09-10 16:00
120 | Rangpur 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-19 08:00 | 113 | 2023-09-01 22:00
121 | Ruppur 132/11kV Grid Sub-Station | 132 | 138 | 2023-09-15 17:00 | 122 | 2023-09-17 19:00
122 | Saidpur 132/33kV Grid Sub-Station | 132 | 135 | 2023-09-20 17:00 | 113 | 2023-09-01 19:00
123 | Satkhira 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-18 09:00 | 116 | 2023-09-28 22:00
124 | Satmasjid 132/33kV Grid Sub-Station | 132 | 135 | 2023-09-22 06:00 | 122 | 2023-09-27 12:00
125 | Savar 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-06 19:30 | 122 | 2023-09-06 10:00
126 | ShahCement 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-20 03:00 | 127 | 2023-09-27 12:00
127 | Shahjadpur 132/33kV Grid Sub-Station | 132 | 142 | 2023-09-15 07:00 | 129 | 2023-09-17 19:00
128 | Shahjibazar 132/33kV Grid Sub-Station | 132 | 135 | 2023-09-29 06:00 | 121 | 2023-09-28 13:00
129 | Shahmirpur 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-06 23:00 | 125 | 2023-09-09 15:00
130 | Shariatpur 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-18 17:00 | 121 | 2023-09-27 22:00
131 | Sherpur 132/33kV Grid Sub-Station | 132 | 139 | 2023-09-21 17:00 | 113 | 2023-09-12 19:30
132 | Shitalakhya 132/33kV Grid Sub-Station | 132 | 139.6 | 2023-09-15 19:00 | 126.8 | 2023-09-27 12:00
133 | Sholosohor 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-06 23:00 | 124 | 2023-09-10 16:00
134 | Shyampur 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-15 18:00 | 123 | 2023-09-03 15:00
135 | Siddhirganj 132/33kV Grid Sub-Station | 132 | 138 | 2023-09-15 19:00 | 128 | 2023-09-27 12:00
136 | Sirajganj 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-03 06:00 | 113 | 2023-09-17 20:00
137 | Sonargaon 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-17 19:00 | 126 | 2023-09-10 12:00
138 | Sreemongol 132/33kV Grid Sub-Station | 132 | 133 | 2023-09-29 06:00 | 122 | 2023-09-29 01:00
139 | Srinagar 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-05 23:00 | 123 | 2023-09-27 12:00
140 | SSM 132/33kV Grid Sub-Station | 132 | 141 | 2023-09-03 23:00 | 128 | 2023-09-10 15:00
141 | Sunamganj 132/33kV Grid Sub-Station | 132 | 130 | 2023-09-23 15:00 | 117 | 2023-09-01 23:00
142 | Sylhet 132/33kV Grid Sub-Station | 132 | 131 | 2023-09-29 06:00 | 125 | 2023-09-05 18:30
143 | Tangail 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-03 05:00 | 120 | 2023-09-29 23:00
144 | Thakurgaon 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-22 19:00 | 113 | 2023-09-01 10:00
145 | TK chemical 132kV Grid Sub-Station | 132 | 139 | 2023-09-06 23:00 | 125 | 2023-09-07 09:00
146 | Ullon 132/33kV Grid Sub-Station | 132 | 140 | 2023-09-03 04:00 | 125 | 2023-09-03 12:00
147 | Uttara 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-03 04:00 | 121 | 2023-09-06 13:00
148 | UttaraNew 132/33kV Grid Sub-Station | 132 | 136 | 2023-09-03 04:00 | 121 | 2023-09-06 10:00
149 | Zigatola 132/33kV Grid Sub-Station | 132 | 137 | 2023-09-03 04:00 | 124 | 2023-09-27 12:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:September 2023
substation | transformer | voltage_level | mw | mva | date_time
Aminbazar 400/230/132kV Grid Sub-Station | ATR-02 | 400/230 | 390 | 551.5433 | 2023-08-31 08:00
Aminbazar 400/230/132kV Grid Sub-Station | ATR-03 | 400/230 | 452 | 511.7656 | 2023-08-03 11:00
Bhulta 400/230kV Grid Sub-Station | ATR-01 | 400/230 | -260 | 302.1854 | 2023-08-08 09:00
Bhulta 400/230kV Grid Sub-Station | ATR-02 | 400/230 | -260 | 302.1854 | 2023-08-08 09:00
Bibiana 400/230kV Sub-Station | ICT-01 | 400/230 | -181 | 181.3974 | 2023-08-01 05:00
Bibiana 400/230kV Sub-Station | ICT-02 | 400/230 | -178 | 178.4741 | 2023-08-01 05:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR1 | 400/230 | 102 | 275.5721 | 2023-08-19 12:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/230kV TR2 | 400/230 | 45 | 402.5233 | 2023-08-26 11:00
Madunaghat_I 400/230kV Grid Sub-Station | ATR-01 | 400/230 | 374 | 402.2188 | 2023-08-07 12:00
Rampal 400/230kV Grid Sub-Station | ICT-1 | 400/230 | -13192 | 13192.0001 | 2023-08-31 18:00
Rampal 400/230kV Grid Sub-Station | ICT-2 | 400/230 | -256.77 | 259.0641 | 2023-08-21 22:00
Aminbazar 400/230/132kV Grid Sub-Station | 400/132kV Interim Transformer | 400/132 | 221 | 283.7693 | 2023-08-25 11:00
Gopalganj 400/132kV Grid Sub-Station | ATR-01 | 400/132 | -180 | 180.4688 | 2023-08-27 19:00
Gopalganj 400/132kV Grid Sub-Station | ATR-02 | 400/132 | -124 | 128.5768 | 2023-08-13 19:30
Gopalganj 400/132kV Grid Sub-Station | ATR-03 | 400/132 | -180 | 180.4688 | 2023-08-27 19:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR1 | 400/132 | 299 | 334.5161 | 2023-08-23 01:00
Kaliakoir 400/230/132kV Grid Sub-Station | 400/132kV TR2 | 400/132 | 299 | 316.5707 | 2023-08-23 07:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-01 | 400/132 | -83 | 90.471 | 2023-08-18 22:00
Payra 400/132/33kV Grid Sub-Station | 400/132/33 kV Auto Transformer-02 | 400/132 | -83 | 90.471 | 2023-08-18 22:00
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
substation | transformer | voltage_level | mw | mva | date_time
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-1 ( 705T1) | 230/132 | 195 | 210.7724 | 2023-08-01 13:00
Agargaon 230/132kV Grid Sub-Station | 230kV Transformer-2 ( 715T2) | 230/132 | 252 | 270.749 | 2023-08-04 10:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-01 | 230/132 | 183 | 185.4427 | 2023-08-22 16:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-02 | 230/132 | 183 | 185.4427 | 2023-08-22 16:00
Aminbazar 400/230/132kV Grid Sub-Station | 230/132kv Tr-03 | 230/132 | 144 | 148.4318 | 2023-08-22 07:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-11 | 230/132 | 115 | 132.0984 | 2023-08-24 21:00
Ashuganj 230/132/33kV Sub-Station | TR-OAT-12 | 230/132 | 187 | 187.131 | 2023-08-09 19:00
Baghabari 230/132kV Grid Sub-Station | T-1 | 230/132 | 216 | 244.2376 | 2023-08-09 02:00
Baghabari 230/132kV Grid Sub-Station | T-2 Bank | 230/132 | 155 | 166.2077 | 2023-08-10 01:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-01, 703T | 230/132 | 199 | 206.7293 | 2023-08-25 17:00
Barapukuria 230/132/33kV Grid Sub-Station | 230/132 KV T-02, 713T | 230/132 | 188 | 203.5387 | 2023-08-06 19:30
Barapukuria 230/132/33kV Grid Sub-Station | 230/132KV T-06, 723T | 230/132 | 243 | 252.8814 | 2023-08-06 19:30
Barishal 230/132kV Grid Sub-Station | ATR-1 | 230/132 | 175 | 178.0842 | 2023-08-04
Barishal 230/132kV Grid Sub-Station | ATR-2 | 230/132 | 175 | 178.0842 | 2023-08-04
Bheramara 230/132kV Grid Sub-Station | Transformer-1 | 230/132 | -105 | 118.072 | 2023-08-05 19:30
Bheramara 230/132kV Grid Sub-Station | Transformer-2 | 230/132 | -105 | 118.072 | 2023-08-05 19:30
Bogura 230/132kV Grid Sub-Station | T-01 | 230/132 | 210 | 214.56 | 2023-08-03 19:30
Bogura 230/132kV Grid Sub-Station | T-02 | 230/132 | 210 | 214.56 | 2023-08-03 19:30
Bogura 230/132kV Grid Sub-Station | T-03 | 230/132 | 284 | 289.4685 | 2023-08-03 19:30
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-01 | 230/132 | 188 | 207.1545 | 2023-08-19 07:00
Cumilla(N) 230/132/33kV Grid Sub-Station | 230KV T-02 | 230/132 | 190 | 201.1368 | 2023-08-19 21:00
Fenchuganj 230/132/33kV Grid Sub-Station | AT-02 | 230/132 | 225 | 231.6247 | 2023-08-24 21:00
Ghorashal 230/132/33kV Sub-Station | AT1 | 230/132 | 105 | 105 | 2023-08-05 09:00
Ghorashal 230/132/33kV Sub-Station | AT2 | 230/132 | 76 | 107.4802 | 2023-08-09 06:00
Haripur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 162 | 174.9286 | 2023-08-28 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 162 | 174.9286 | 2023-08-28 12:00
Haripur 230/132kV Grid Sub-Station | Auto TR-3 | 230/132 | 162 | 174.9286 | 2023-08-28 12:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-1 | 230/132 | 53 | 89.4036 | 2023-08-14 22:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-2 | 230/132 | 53 | 89.4036 | 2023-08-14 22:00
Hasnabad 230/132kV Grid Sub-Station | AUTO TR-3 | 230/132 | 53 | 89.4036 | 2023-08-14 22:00
Hathazari 230/132/33kV Grid Sub-Station | MT-01 | 230/132 | 112 | 115.2085 | 2023-08-30 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-02 | 230/132 | 112 | 115.2085 | 2023-08-30 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-03 | 230/132 | 112 | 115.2085 | 2023-08-30 12:00
Hathazari 230/132/33kV Grid Sub-Station | MT-04 | 230/132 | 64 | 134.2386 | 2023-08-28 03:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-01 | 230/132 | 120 | 136 | 2023-08-29 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-02 | 230/132 | 120 | 136 | 2023-08-29 22:00
Ishurdi 230/132kV Grid Sub-Station | 230/132 kV T-03 | 230/132 | 120 | 136 | 2023-08-29 22:00
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 1 | 230/132 | -222 | 250.4795 | 2023-08-30 19:30
Jhenaidah 230/132kV Grid Sub-Station | Transformer- 2 | 230/132 | -166 | 257.6141 | 2023-08-23 09:00
Kaliakoir 400/230/132kV Grid Sub-Station | 230/132kV TR1 | 230/132 | 206 | 209.8476 | 2023-08-18 23:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-1 | 230/132 | 164 | 170.8801 | 2023-08-21 23:00
Keranigonj 230/132/33kV Grid Sub-Station | ATR-2 | 230/132 | 0 | 0 | 2023-08-01
Keranigonj 230/132/33kV Grid Sub-Station | ATR-3 | 230/132 | 259 | 270.2036 | 2023-08-22 10:00
Khulna(S) 230/132kV Grid Sub-Station | TR-1 | 230/132 | -143 | 144.8378 | 2023-08-22 22:00
Khulna(S) 230/132kV Grid Sub-Station | TR-2 | 230/132 | -143 | 144.8378 | 2023-08-22 22:00
Khulna(S) 230/132kV Grid Sub-Station | TR-3 | 230/132 | -1123 | 1123.1287 | 2023-08-26 03:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-01(705T) | 230/132 | 212 | 226.241 | 2023-08-18 15:00
Maniknagar 230/132kV Grid Sub-Station | Auto Transformer-02 (715T) | 230/132 | 166 | 181.7471 | 2023-08-01 13:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-01 (704T) | 230/132 | -175 | 195.4329 | 2023-08-21 12:00
Rajshahi 230/132/33kV Grid Sub-Station | 230/132 kV ATR-02 (714T) | 230/132 | -185 | 194.7973 | 2023-08-29 17:00
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-01 (706T) | 230/132 | 1 | 1.4142 | 2023-08-01
Rampur 230/132/33 kV GIS Grid Sub-Station | ATR-02 (716T) | 230/132 | 1 | 1 | 2023-08-29 15:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 01 | 230/132 | 211 | 212.3605 | 2023-08-30 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 02 | 230/132 | 211 | 212.3605 | 2023-08-30 13:00
Rampura 230/132kV Grid Sub-Station | Auto Transformer - 03 | 230/132 | 211 | 212.3605 | 2023-08-30 13:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 01 | 230/132 | 233 | 255.566 | 2023-08-29 21:00
Shikalbaha 230/132kV Grid Sub-Station | ATR 02 | 230/132 | 233 | 255.566 | 2023-08-29 21:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-1 | 230/132 | 119 | 131.947 | 2023-08-05 10:00
Shyampur 230/132kV Grid Sub-Station | Auto TR-2 | 230/132 | 119 | 131.947 | 2023-08-05 10:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 1 | 230/132 | 239 | 264.7961 | 2023-08-08 11:00
Siddhirganj 230/132kV Grid Sub-Station | MTR 2 | 230/132 | 239 | 264.7961 | 2023-08-08 11:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-1 | 230/132 | 172.85 | 181.0708 | 2023-08-09 19:00
Sreepur 230/132/33kV Grid Sub-Station | 230/132 kV T-2 | 230/132 | 173.61 | 181.8619 | 2023-08-09 19:00
Tongi 230/132/33kV Grid Sub-Station | T-01 | 230/132 | 218 | 221.2871 | 2023-08-21 10:00
Tongi 230/132/33kV Grid Sub-Station | T-02 | 230/132 | 218 | 221.2871 | 2023-08-21 10:00
Tongi 230/132/33kV Grid Sub-Station | T-03 | 230/132 | 218 | 221.2871 | 2023-08-21 10:00
423
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-37
|  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month: September 2023 | [5 empty] | (For Evening Peak) | [8 empty] | Month: September 2023 | [5 empty] | (For Day Peak)
| Peak Hour |  | Total load shed (SS end) | [12 empty] | Peak Hour |  | Total load shed (SS end)
Date | Generation (Gen End) | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand (Gen End) |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2023-09-01 | 14239 | 14380 | 135 | 21:00 | 0 | 0 | 0 | 0 | 18 | 70 | 27 | 0 | 20 | - | 2023-09-01 | 12420 | 12500 | 76 | 12:00 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | -
2023-09-02 | 14757 | 15100 | 328 | 21:00 | 10 | 0 | 0 | 0 | 45 | 125 | 45 | 0 | 103 | - | 2023-09-02 | 12764 | 12764 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-03 | 14498 | 15100 | 575 | 21:00 | 80 | 0 | 0 | 100 | 70 | 100 | 95 | 0 | 130 | - | 2023-09-03 | 13214 | 13295 | 77 | 12:00 | 62 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | -
2023-09-04 | 14462 | 15200 | 705 | 19:30 | 60 | 0 | 130 | 0 | 170 | 130 | 80 | 0 | 135 | - | 2023-09-04 | 13081 | 13230 | 142 | 12:00 | 27 | 0 | 0 | 0 | 0 | 90 | 25 | 0 | 0 | -
2023-09-05 | 14489 | 15350 | 822 | 21:00 | 42 | 185 | 112 | 30 | 119 | 145 | 65 | 0 | 124 | - | 2023-09-05 | 13711 | 13900 | 180 | 12:00 | 47 | 0 | 0 | 0 | 0 | 115 | 18 | 0 | 0 | -
2023-09-06 | 14180 | 14700 | 497 | 21:00 | 50 | 0 | 0 | 20 | 100 | 222 | 105 | 0 | 0 | - | 2023-09-06 | 12621 | 13400 | 763 | 12:00 | 75 | 185 | 93 | 125 | 70 | 85 | 75 | 30 | 25 | -
2023-09-07 | 14125 | 14500 | 358 | 21:00 | 0 | 0 | 10 | 0 | 180 | 10 | 50 | 0 | 108 | - | 2023-09-07 | 12594 | 13200 | 579 | 12:00 | 245 | 194 | 20 | 0 | 120 | 0 | 0 | 0 | 0 | -
2023-09-08 | 13259 | 13300 | 39 | 19:30 | 0 | 0 | 0 | 0 | 0 | 39 | 0 | 0 | 0 | - | 2023-09-08 | 10585 | 10585 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-09 | 14763 | 15000 | 226 | 21:00 | 5 | 52 | 0 | 0 | 42 | 45 | 40 | 0 | 42 | - | 2023-09-09 | 12009 | 12035 | 25 | 12:00 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-10 | 14709 | 15370 | 631 | 21:00 | 80 | 0 | 0 | 10 | 100 | 300 | 46 | 0 | 95 | - | 2023-09-10 | 12987 | 13350 | 347 | 12:00 | 100 | 0 | 0 | 0 | 72 | 175 | 0 | 0 | 0 | -
2023-09-11 | 14728 | 15175 | 427 | 20:00 | 27 | 0 | 0 | 0 | 165 | 138 | 18 | 0 | 79 | - | 2023-09-11 | 13311 | 13500 | 180 | 12:00 | 90 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | -
2023-09-12 | 14441 | 14800 | 343 | 21:00 | 0 | 0 | 0 | 0 | 135 | 130 | 25 | 0 | 53 | - | 2023-09-12 | 13299 | 13435 | 130 | 12:00 | 65 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | -
2023-09-13 | 14531 | 14830 | 289 | 21:00 | 0 | 0 | 0 | 0 | 58 | 86 | 51 | 0 | 94 | - | 2023-09-13 | 12668 | 12780 | 107 | 12:00 | 43 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | -
2023-09-14 | 14157 | 14450 | 280 | 20:00 | 15 | 0 | 0 | 0 | 25 | 90 | 80 | 0 | 70 | - | 2023-09-14 | 12610 | 12610 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-15 | 13926 | 14050 | 118 | 21:00 | 0 | 0 | 0 | 0 | 30 | 48 | 40 | 0 | 0 | - | 2023-09-15 | 11455 | 11455 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-16 | 14938 | 15350 | 393 | 21:00 | 0 | 0 | 0 | 7 | 80 | 138 | 80 | 0 | 88 | - | 2023-09-16 | 12605 | 12675 | 67 | 12:00 | 10 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | -
2023-09-17 | 14277 | 14900 | 595 | 19:00 | 25 | 0 | 35 | 0 | 20 | 245 | 110 | 0 | 160 | - | 2023-09-17 | 13849 | 13950 | 96 | 12:00 | 13 | 0 | 0 | 0 | 0 | 83 | 0 | 0 | 0 | -
2023-09-18 | 14465 | 14650 | 177 | 19:30 | 0 | 0 | 0 | 0 | 25 | 122 | 30 | 0 | 0 | - | 2023-09-18 | 12998 | 13080 | 78 | 12:00 | 0 | 0 | 0 | 0 | 0 | 78 | 0 | 0 | 0 | -
2023-09-19 | 13694 | 13890 | 187 | 20:00 | 0 | 0 | 0 | 0 | 25 | 132 | 30 | 0 | 0 | - | 2023-09-19 | 12559 | 12630 | 68 | 12:00 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 0 | 0 | -
2023-09-20 | 13204 | 13250 | 44 | 19:00 | 0 | 0 | 0 | 0 | 0 | 44 | 0 | 0 | 0 | - | 2023-09-20 | 11865 | 11865 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-21 | 12861 | 12861 | 0 | 19:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-09-21 | 11696 | 11696 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-22 | 12183 | 12183 | 0 | 21:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-09-22 | 10398 | 10398 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-23 | 13201 | 13240 | 37 | 19:30 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 0 | 0 | - | 2023-09-23 | 10699 | 10699 | 0 | 11:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-24 | 12852 | 12852 | 0 | 20:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | - | 2023-09-24 | 11824 | 11824 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-25 | 14022 | 14120 | 94 | 19:00 | 0 | 0 | 0 | 0 | 0 | 64 | 30 | 0 | 0 | - | 2023-09-25 | 12262 | 12262 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-26 | 14632 | 14750 | 113 | 20:00 | 22 | 0 | 0 | 0 | 15 | 48 | 28 | 0 | 0 | - | 2023-09-26 | 12429 | 12429 | 0 | 12:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-27 | 14693 | 14900 | 198 | 20:00 | 0 | 0 | 0 | 0 | 30 | 75 | 93 | 0 | 0 | - | 2023-09-27 | 12661 | 12690 | 27 | 12:00 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -
2023-09-28 | 14539 | 14700 | 154 | 20:00 | 0 | 0 | 0 | 0 | 25 | 100 | 29 | 0 | 0 | - | 2023-09-28 | 12235 | 12315 | 76 | 12:00 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 0 | 0 | -
2023-09-29 | 13402 | 13485 | 79 | 20:00 | 0 | 0 | 0 | 0 | 20 | 30 | 29 | 0 | 0 |  | 2023-09-29 | 11852 | 12000 | 141 | 12:00 | 0 | 0 | 0 | 0 | 0 | 141 | 0 | 0 | 0
2023-09-30 | 13735 | 13900 | 158 | 20:00 | 19 | 0 | 0 | 0 | 19 | 100 | 20 | 0 | 0 |  | 2023-09-30 | 11277 | 11450 | 165 | 12:00 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 0 | 0
| Max. L/S | - |  | - | [10 empty] | Max. L/S
| Min. L/S | - |  | - | [10 empty] | Min. L/S
| No. of Days | - |  | - | [10 empty] | No. of Days
| Average L/S | [13 empty] | Average L/S
|  | - | - | - | [11 empty] | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:September 2023
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 14938 | 2023-09-16 | 21:00
2 | Maximum Day Peak Genaration | MW | 13849 | 2023-09-17 | 12:00
3 | Maximum Evening Peak Demand | MW | 15370 | 2023-09-30 | 20:00
4 | Minimum Generation | MW | 9737 | 2023-09-22 | 6:00
5 | Average of the daily evening peak Genaration | MW | 14065.4 | - | -
6 | Average of the daily day peak Genaration | MW | 12351.2667 | - | -
7 | Maximum load shed (Evening Peak) | MW | 822 | 2023-09-05 | 19:30
8 | Minimum load shed | MW | 0 | 2023-09-21 | 19:30
9 | Total nos. of load shed days | Day | 12 | - | -
10 | Average load shed ( Avg. of the 30 days in the month) | MW/Day | 266.7333 | - | -
11 | Total Generation | MkWh | 9031.0556 | - | -
12 | Total Generation by BPDB | MkWh | 1988.9761 | % of total Gen. | 22.02%
13 | Total Generation by IPP | MkWh | 2517.3271 | '' | 27.87%
14 | A) Total Generation by Generation Companies | MkWh | 2508.5487 | '' | 27.78%
| B) Total Generation by REB | MkWh | 114.4824 | " | 1.268%
| C) Total Generation by RENTAL | MkWh | 249.813 | " | 2.766%
| D) Total Imported from India (BIPTC) | MkWh | 645.3585 | " | 7.146%
| E) Total Imported from Tripura, India (A.C) | MkWh | 1006.5497 | " | 11.15%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4256.3488 | % of total Gen. | 47.15%
| B) Oil | MkWh | 1193.9999 | '' | 13.23%
| C) Hydro | MkWh | 135.9844 | '' | 1.506%
| D) Solar | MkWh | 62.0683 | '' | 0.6876%
| E) Coal | MkWh | 2633.5692 | '' | 29.17%
| F) BIPTC (Import from India) | MkWh | 645.3585 | '' | 7.149%
| G) A.C (Import from Tripura, India) | MkWh | 99.7517 | '' | 1.105%
| H) Wind | MkWh | 3.9749 |  | 0.08325%
16 | Maximun of the daily total Generation . | MkWh | 324.9973 | 2023-09-17
17 | Monthly Load factor | % | 77.424 | - | -
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 40555.315 | - | -
| A) Gas | M.Taka | 4737.177 | - | -
| B) Liquid fuel | M.Taka | 14112.2028 | - | -
| C) Coal | M.Taka | 18044.8882 | - | -
| D) BIPTC (Import from India) | M.Taka | 2942.8349 | - | -
| E) Tripura(Import from India) | M.Taka | 718.2121 | - | -
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1544.0821 | 2023-09-10
| A) Gas | M.Taka | 169.5771 | 2023-09-10
| B) Liquid fuel | M.Taka | 792.3548 | 2023-09-10
| C) Coal | M.Taka | 741.2708 | 2023-09-21
| D) BIPTC (Import from India) | M.Taka | 102.3629 | 2023-09-10
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 4.4907
| B) Excluding Hydro & Solar | Taka/kWhR | 4.5934
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 105.76 | 30/09/2023 | 06:00
b) | Actual | FT (MSL) | 108.09 | 30/09/2023 | 6:00
22 | Peak Genaration of September 2022 | MW | 13712 | 2022-09-01 | 22:00
23 | Peak Demand of September 2022 | MW | 14695 | 2022-09-01 | 20:00
24 | Maximum peak Generation recorded upto 30/09/2023 | MW | 15648 | 19/04/2023 | 21:00
25 | Maximum peak Demand recorded upto 30/09/2023 | MW | 16096 | 19/04/2023 | 21:00
26 | Maximum load shed recorded upto 30/09/2023 | MW | 4395 | 2022-10-04 | 21:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## FGMO_Daily
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Monthly status of Free Governor Mode of Operation (FGMO) Power Plants
Month:September 2023
SL | Plant Name | Owner | Installed capacity | FGMO Status
|  |  | (MW) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | bar: FGMO Status 1 to FGMO Status 30
1 | Bibiyana-III 400 MW CCPP | BPDB | 400 | bar: FGMO Status 1 to FGMO Status 30
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220
6 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
7 | Meghnaghat CCPP(Summit) | IPP | 335 | bar: FGMO Status 15 to FGMO Status 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | bar: FGMO Status 29 to FGMO Status 30
9 | Ashuganj 450 MW CCPP(North) | APSCL | 361 | bar: FGMO Status 12 to FGMO Status 30
10 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | bar: FGMO Status 6 to FGMO Status 30
11 | Ashuganj 420 MW CCPP(East) | APSCL | 400
12 | Ashuganj 55 MW PP (Precision) | QRPP | 55
13 | Bheramara 410 MW CCPP | NWPGCL | 410
14 | Haripur 412 MW CCPP | EGCB | 412
15 | Fenchugonj CCPP Phase-1 | BPDB | 97
16 | Fenchugonj CCPP Phase-2 | BPDB | 104
17 | Siddhirganj 2x120 MW GTPP | EGCB | 210
18 | Shikalbaha 225 MW CCPP | BPDB | 225
19 | Shikalbaha Peaking GT | BPDB | 150
20 | Shahjibazar 330 MW CCPP | BPDB | 330
21 | Chandpur 150 MW CCPP | BPDB | 163
22 | Bhola 225 MW CCPP | BPDB | 194
23 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365
24 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210
25 | Siddhirganj 335 MW CCPP | EGCB | 335
26 | Bibiyana-III 400 MW CCPP | BPDB | 400
27 | Sylhet 225 MW CCPP | BPDB | 231
28 | RPCL 210 MW CCPP | IPP | 210
29 | Khulna 225 MW CCPP | NWPGCL | 230
30 | a) Baghabari 71 MW GTPP | BPDB | 71
| b) Baghabari 100 MW GTPP | BPDB | 100
31 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50
32 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410
33 | Bibiyana South 400 MW CCPP | BPDB | 383
34 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274
35 | Shajibazar 100 MW PP | BPDB | 100
36 | Payra 1320 MW Unit-1 | BCPCL | 622
37 | Kushiara 163 MW CCPP (KP) | IPP | 163
38 | Haripur 360MW CCPP(HPL) | IPP | 360
39 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450
* Data Collected from Daily Operational Reports by NOD
due to gas shortage

## FGMO Weekly
Power Grid Company Of Bangladesh Ltd.
NLDC, Aftabnagar, Dhaka.
Summary of Weekly Status of Free Governor Mode of Operation (FGMO) Power Plants
Last Week Status |  |  |  |  | SR at 50 Hz (MW)
SL | Plant Name | Owner | Installed capacity | Capability Status of Last Week | 05.10.2023 | 28.09.2023 | 21.09.2023 | 14.09.2023 | 07.09.2022
(MW)
1 | Bibiana-II 341 MW CCPP (Summit) | IPP | 341 | Capable | 45 | 45 | 45 | 45 | 45
2 | Shahjibazar GTPP Unit 8 & 9 | BPDB | 70 | Capable
3 | Sirajgonj 400 MW CCPP Unit-4 | IPP | 414 | Capable
4 | Sirajgonj 225MW CCPP Unit-3 | NWPGCL | 220 | Capable
5 | Sirajgonj 225MW CCPP Unit-2 | NWPGCL | 220 | Capable
6 | Meghnaghat CCPP(Summit) | IPP | 335 | Capable | 20 | 20 | 20 | 20
7 | Ashuganj 450 MW CCPP(North) | APSCL | 360 | Capable | 30 | 30 | 30 | 30
8 | Ashuganj 225 MW CCPP | APSCL | 221 | Capable | 20 | 20 | 20
9 | Bheramara 410 MW CCPP | NWPGCL | 410 | Capable
10 | Haripur 412 MW CCPP | EGCB | 412 | Capable
11 | Fenchugonj CCPP Phase-1 | BPDB | 97 | Capable | 2 | 2 | 2 | 2 | 2
12 | Chandpur 150 MW CCPP | BPDB | 163 | Capable
13 | Siddhirganj 2x120 MW GTPP | EGCB | 210 | Capable
14 | Shikalbaha 225 MW CCPP | BPDB | 225 | Capable
15 | Shikalbaha Peaking GT | BPDB | 150 | Capable
16 | Shahjibazar 330 MW CCPP | BPDB | 330 | Capable
17 | Ashuganj 450 MW CCPP(South) | APSCL | 360 | Capable | 40 | 40 | 40 | 40 | 40
18 | Fenchugonj CCPP Phase-2 | BPDB | 104 | Capable | 2 | 2 | 2 | 2 | 2
19 | Bhola 225 MW CCPP | BPDB | 194 | Capable
20 | Ghorasal 365 MW CCPP Unit-7 | BPDB | 365 | Capable
21 | Sirajgonj 225MW CCPP Unit-1 | NWPGCL | 210 | Capable
22 | Siddhirganj 335 MW CCPP | EGCB | 335 | Capable but not tested recently
23 | Bibiyana-III 400 MW CCPP | BPDB | 400 | Capable |  |  | 30 | 30 | 30
24 | Sylhet 225 MW CCPP | BPDB | 231 | Capable
25 | RPCL 210 MW CCPP | IPP | 210 | Capable but not tested recently
26 | Khulna 225 MW CCPP | NWPGCL | 230 | Capable but not tested recently
27 | a) Baghabari 71 MW GTPP | BPDB | 71 | Not Capable but feasible
| b) Baghabari 100 MW GTPP | BPDB | 100 | Not Capable but feasible
28 | Karnaphuli Hydro PP Unit: 1 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 2 | BPDB | 40 | Capable
| Karnaphuli Hydro PP Unit: 3 | BPDB | 50 | Capable
| Karnaphuli Hydro PP Unit: 4 | BPDB | 50 | Not Capable but feasible
| Karnaphuli Hydro PP Unit: 5 | BPDB | 50 | Not Capable but feasible
29 | a) Ghorasal Repowered CCPP Unit-3 | BPDB | 416 | Not Capable but feasible
| b) Ghorasal Repowered CCPP Unit-4 | BPDB | 410 | Not Capable but feasible
30 | Bibiyana South 400 MW CCPP | BPDB | 383 | Capable
31 | Barapukuria 275 MW TPP Unit-3 | BPDB | 274 | Not Capable but feasible
32 | Shajibazar 100 MW PP | BPDB | 100 | Not Capable but feasible
33 | Payra 1320 MW Unit-1 | BCPCL | 622 | Capable
34 | Kushiara 163 MW CCPP (KP) | IPP | 163 | Not Capable but feasible
35 | Bhola Nutan Bidyut | IPP | 220 | Capable
36 | Haripur 360MW CCPP(HPL) | IPP | 360 | Not Capable but feasible
37 | Meghnaghat 450 MW CCPP(MPL) | IPP | 450 | Not Capable but feasible
Total Installed capacity |  |  |  |  | 10616 | 10616 | 10616 | 10616 | 10616
Total active FGMO capacity |  |  |  |  | 1634 | 1634 | 2034 | 1814 | 1164
Total Spinning Reserve |  |  |  |  | 159 | 159 | 189 | 169 | 119
Total Number of Plants Running on FGMO |  |  |  |  | 7 | 7 | 8 | 7 | 5
Total Plants in list |  |  |  |  | 37 | 37 | 37 | 37 | 37
Total Units in list |  |  |  |  | 43 | 43 | 43 | 43 | 43
Capable |  |  |  |  | 29 | 29 | 29 | 29 | 29
Capable but not tested recently |  |  |  |  | 3 | 3 | 3 | 3 | 3
Capable but not tested yet |  |  |  |  | 0 | 0 | 0 | 0 | 0
Not Capable but feasible |  |  |  |  | 11 | 11 | 11 | 11 | 11
* Data Collected from Weekly FGMO Reports by NOD